## Introduction
Data Dictionary
Column Heading | Description
Associated GSP | Name of the upstream Grid Supply Point (GSP) which supplies the substation. Note that some GSPs which run in parallel are reported as groups.
Substation | Name of the substation for which the generation and demand headroom figures have been calculated.
Supply Level | Identifier for whether the substation is a Primary or a Bulk Supply Point. The definition is supplied in the 'NDP 2026 Introduction & Methodology Report'.
Voltage Level (kV) | Voltage of the lower voltage side of the transformation at the substation.
Scenario | Identifier for one of the four Distribution Future Energy Scenarios (DFES) the headroom figures refer to. Holistic Transition was chosen as the best view scenario for the NDP 2026.
Units | The units used to define the headroom available at each substation under each scenario and all of the years reported on (see below).
2024 | Defines the year snapshot for the headroom calculation, where the year refers to the end of the fiscal year.
2025
2026
2027
2028
2029
2030
2031
2032
2033
2034
2035
2036
2037
2038
2039
2040
2045
2050
East Midlands
Network Headroom Report 2026
May 2026
v1.0
How to use this workbook
The 'Demand Headroom' and 'Generation Headroom' sheets contain data as described by the data dictionary below. Cells highlighted in red indicate zero headroom, which is defined as the point at which adding demand or generation at a given substation would cause a thermal overload to occur on an related asset in the network. The impact of some high-certainty medium-term reinforcement schemes on the network has been included from the year 2030. This may be observed as a step change increase in the available headroom from the year 2030.
The 'Fault Level Contribution' sheet contains the total make and break contribution (kA) from the demand and generation expected to connect at each primary substation for each year and scenario under the DFES forecasts. The existing maximum prospective fault levels under normal system running conditions and the make and break switchgear ratings at bussing points can be taken from the LTDS Table 4.
In the context of the NHR, zero headroom does not necessarily mean a prospective customer would not be able to connect. This data should not be used to make connections decisions as it is intended to provide a view of the capacity of the network against the DFES scenarios rather than a view of the contractually available capacity. Prospective customers should follow the regular connections application process to gain an accurate assessment of the headroom available for their connection.
Summary
This Network Headroom Report (NHR) workbook provides a view of the capacity to connect additional demand and generation to NGED's East Midlands network, in line with the load growth forecasted across the four Distribution Future Energy Scenarios (DFES) out to 2050. The DFES 2024 publication was used as the basis for this NHR to align with the forecasts used for the Network Development Reports.
The NHR forms one part of the wider Network Development Plan (NDP), and it is recommended to view this report alongside the NDP Introduction & Methodology Report and the Network Development Reports which are presented as an interactive map on the Network Opportunity and Development Map (NODM).

## Demand Headroom
Associated GSP | Substation | Supply Level | Voltage Level (kV) | Scenario | Units | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 3.2 | 2.6 | 2.1 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 3 | 2.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 3.1 | 2.4 | 1.8 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 3 | 2.3 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.4 | 6.1 | 5.5 | 5.4 | 5.3 | 5.1 | 4.6 | 4.3 | 3.8 | 3.5 | 3.2 | 2.7 | 2 | 1.3 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.4 | 5.9 | 5 | 4.5 | 4.1 | 3.5 | 2.9 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.4 | 6 | 5.2 | 4.9 | 4.7 | 4.4 | 3.9 | 3.4 | 2.5 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.4 | 5.9 | 5.2 | 4.9 | 4.5 | 4.2 | 3.6 | 2.9 | 2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.4 | 3.1 | 2.8 | 2.7 | 2.4 | 2.2 | 1.6 | 1.4 | 1 | 0.8 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.4 | 3 | 2.5 | 2 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.4 | 3.1 | 2.7 | 2.5 | 2.1 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.4 | 3.1 | 2.7 | 2.3 | 1.8 | 1.3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 13.2 | 13.1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 13.2 | 13.1 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 13.2 | 13.1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 13.2 | 13.1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.4 | 8.2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.4 | 7.8 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.4 | 7.9 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.4 | 7.9 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 7.9 | 7.9 | 7.9 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 7.9 | 7.8 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 7.9 | 7.8 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 7.9 | 7.8 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 25.1 | 20.4 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 25.1 | 18.7 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 25.1 | 19.2 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 25.1 | 19 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 26.4 | 15.9 | 15.4 | 14.5 | 12.8 | 10.9 | 6.4 | 4.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 26.4 | 14.7 | 13.1 | 10.3 | 7.4 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 26.4 | 15 | 13.8 | 12 | 9.4 | 6.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 26.4 | 15 | 13.8 | 12 | 9.5 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 47.7 | 40.2 | 38.9 | 36.1 | 31.9 | 29.9 | 10.8 | 8.7 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 47.7 | 39.1 | 36.8 | 31.4 | 26.2 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 47.7 | 39.5 | 37.5 | 34.5 | 28.4 | 24.5 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 47.7 | 39.4 | 37.4 | 33.4 | 28.6 | 25.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 13.3 | 13.1 | 12.7 | 11.1 | 9.3 | 8.7 | 7.6 | 7.2 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 13.3 | 12.9 | 12.3 | 10.1 | 8.2 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 13.3 | 13 | 12.5 | 11.7 | 8.5 | 6.8 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 13.3 | 13 | 12.4 | 10.5 | 8.8 | 7.4 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 3.9 | 3.8 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 3.9 | 3.5 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 3.9 | 3.5 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 3.9 | 3.5 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.1 | 6.9 | 6.6 | 6.3 | 5.7 | 5.1 | 4 | 2.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.1 | 6.6 | 6 | 5.3 | 4.4 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.1 | 6.7 | 6.3 | 5.9 | 5.1 | 4.3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.1 | 6.7 | 6.2 | 5.7 | 4.9 | 3.8 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 13.1 | 9.3 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 13.1 | 9.1 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 13.1 | 9.2 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 13.1 | 9.1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.4 | 4.7 | 4.1 | 3.4 | 3.1 | 2.8 | 2 | 1.4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.4 | 4.7 | 4 | 3.2 | 2.7 | 2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.4 | 4.7 | 4.1 | 3.4 | 3.1 | 2.8 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.4 | 4.7 | 4 | 3.3 | 2.9 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.4 | 14.1 | 13.8 | 12.8 | 12.6 | 12.5 | 12.1 | 11.8 | 11.5 | 11.2 | 10.9 | 10.5 | 10.1 | 9.6 | 9.1 | 8.7 | 8.2 | 5.8 | 3.8
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.4 | 14.1 | 12.7 | 12.5 | 12.2 | 11.8 | 11.3 | 10.7 | 10.1 | 9.4 | 8.8 | 8.4 | 7.7 | 7.1 | 6.5 | 5.9 | 5.3 | 3.2 | 1.6
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.4 | 14.1 | 12.8 | 12.7 | 12.5 | 12.2 | 11.7 | 11.1 | 10.5 | 9.9 | 9.2 | 8.5 | 7.7 | 6.9 | 6.2 | 5.5 | 4.9 | 2.4 | 0
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.4 | 14.1 | 12.8 | 12.6 | 12.3 | 12 | 11.5 | 11 | 10.4 | 9.9 | 9.3 | 8.6 | 7.9 | 7.2 | 6.6 | 6 | 5.5 | 3.6 | 2.2
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 59 | 21.3 | 16.7 | 12.5 | 8.5 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 59 | 18.7 | 10.4 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 59 | 19.6 | 12.3 | 7.5 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 59 | 19.3 | 12.2 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 10 | 6.9 | 6.8 | 6.6 | 5.5 | 5.2 | 4.8 | 4.4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 10 | 6.8 | 6.5 | 6.1 | 4.8 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 10 | 6.8 | 6.6 | 6.2 | 5 | 4.7 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 10 | 6.8 | 6.6 | 6.3 | 5 | 4.6 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 6.1 | 5.8 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 6.1 | 5.4 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 6.1 | 5.5 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 6.1 | 5.5 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.4 | 11.2 | 11.1 | 10.9 | 10.7 | 10.4 | 6.9 | 4.7 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.4 | 11 | 10.6 | 10 | 7.9 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.4 | 11.1 | 10.8 | 10.5 | 10 | 6.8 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.4 | 11 | 10.8 | 10.3 | 9.9 | 6.8 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.9 | 6.9 | 6.8 | 6.6 | 5.5 | 5.2 | 4.7 | 4.3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.9 | 6.7 | 6.5 | 6.1 | 4.8 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.9 | 6.8 | 6.6 | 6.2 | 5 | 4.7 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.9 | 6.8 | 6.6 | 6.3 | 5 | 4.6 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 5.3 | 4.7 | 3.5 | 2.8 | 2.1 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 5 | 3.9 | 2.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 5.1 | 4.2 | 2.9 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 5.1 | 4.2 | 2.7 | 1.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.1 | 13.9 | 13.8 | 13.5 | 13.3 | 13.2 | 13 | 12.7 | 12.4 | 12.1 | 11.8 | 11.4 | 11.1 | 10.8 | 10.5 | 10.3 | 10 | 8.6 | 0
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.1 | 13.8 | 13.4 | 13 | 12.6 | 12.3 | 11.6 | 11.1 | 10.5 | 9.9 | 9.3 | 8.7 | 8.4 | 8 | 7.6 | 5.5 | 2.4 | 0 | 0
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.1 | 13.8 | 13.5 | 13 | 12.6 | 12.3 | 11.7 | 11.2 | 10.8 | 10.3 | 9.8 | 9.2 | 8.7 | 8.2 | 7.8 | 7.2 | 4 | 0 | 0
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.1 | 13.8 | 13.6 | 13.2 | 12.8 | 12.5 | 11.9 | 11.5 | 11 | 10.6 | 10.1 | 9.5 | 9.2 | 8.8 | 8.5 | 8.2 | 6.2 | 0 | 0
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 7.3 | 7.1 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 7.3 | 6.7 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 7.3 | 6.9 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 7.3 | 6.8 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.6 | 6.4 | 5.3 | 5 | 4.6 | 4.2 | 3.3 | 2.9 | 2.3 | 1.9 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.6 | 6.2 | 4.9 | 4.2 | 3.6 | 3 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.6 | 6.3 | 5 | 4.6 | 4 | 3.5 | 2.6 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.6 | 6.3 | 5.1 | 4.4 | 3.8 | 3.3 | 2.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 12.2 | 2.4 | 2.2 | 1.9 | 1.7 | 1.4 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 12.2 | 2.2 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 12.2 | 2.2 | 2.2 | 1.7 | 1.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 12.2 | 2.2 | 2.1 | 1.6 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.9 | 6.7 | 6.5 | 6 | 5.6 | 5.2 | 7.6 | 7.1 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.9 | 6.3 | 5.7 | 4 | 3.1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.9 | 6.4 | 5.9 | 4.7 | 4 | 3.4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.9 | 6.4 | 5.9 | 5.1 | 4.3 | 3.7 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.1 | 18.1 | 17.9 | 17.9 | 17.9 | 17.8 | 17.8 | 17.7 | 17.6 | 17.5 | 17.4 | 17.3 | 17.1 | 16.9 | 16.8 | 16.6 | 16.4 | 2.5 | 0
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.1 | 18.1 | 17.8 | 17.7 | 17.6 | 17.5 | 17.3 | 17.1 | 16.8 | 16.5 | 15.5 | 11.8 | 8.1 | 4.5 | 0.8 | 0 | 0 | 0 | 0
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.1 | 18.1 | 17.8 | 17.8 | 17.7 | 17.6 | 17.5 | 17.3 | 17.1 | 16.9 | 16.7 | 16.4 | 13.6 | 9 | 4.1 | 0 | 0 | 0 | 0
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.1 | 18.1 | 17.8 | 17.7 | 17.7 | 17.6 | 17.5 | 17.4 | 17.2 | 17 | 16.8 | 16.5 | 12.4 | 8 | 3.9 | 0 | 0 | 0 | 0
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.9 | 12.3 | 11.7 | 11.2 | 9.9 | 8.5 | 5.4 | 4.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.9 | 11.8 | 10.8 | 9.7 | 7.9 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.9 | 11.9 | 10.8 | 9.7 | 7.8 | 5.3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.9 | 11.9 | 11 | 10 | 8.4 | 6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WARWICK 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 11.1 | 8.4 | 8.1 | 7.8 | 6.9 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WARWICK 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 11.1 | 7.8 | 6.9 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WARWICK 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 11.1 | 7.9 | 7.3 | 6.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WARWICK 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 11.1 | 7.9 | 7.3 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 34.7 | 21.3 | 16.6 | 12.5 | 8.5 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 34.7 | 18.7 | 10.4 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 34.7 | 19.6 | 12.3 | 7.5 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 34.7 | 19.2 | 12.2 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | Wellesbourne | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.3 | 11.9 | 12 | 12 | 12.1 | 12.1 | 11.7 | 11.7 | 11.7 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 10.2 | 0
Berkswell 132kV | Wellesbourne | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.3 | 11.9 | 12 | 12 | 12.1 | 12.1 | 11.7 | 11.7 | 11.7 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 9 | 5.4 | 2.4 | 0 | 0
Berkswell 132kV | Wellesbourne | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.3 | 11.9 | 12 | 12 | 12.1 | 12.1 | 11.7 | 11.7 | 11.7 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.4 | 7.3 | 4 | 0 | 0
Berkswell 132kV | Wellesbourne | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.3 | 11.9 | 12 | 12 | 12.1 | 12.1 | 11.7 | 11.7 | 11.7 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.7 | 8.6 | 6.2 | 0 | 0
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.1 | 5.9 | 5.7 | 5.5 | 5.4 | 5.2 | 4.6 | 4.4 | 3.9 | 3.6 | 3.2 | 2.7 | 2 | 1.3 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.1 | 5.5 | 5.1 | 4.2 | 3.7 | 3 | 2.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.1 | 5.6 | 5.4 | 4.7 | 4.3 | 4 | 3.3 | 2.8 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.1 | 5.6 | 5.3 | 4.9 | 4.4 | 3.9 | 3 | 2.3 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.4 | 0.9 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 5 | 4.9 | 4.8 | 4.7 | 4.6 | 4.5 | 4.3 | 4.1 | 3.9 | 3.6 | 3.3 | 2.9 | 2.5 | 2.2 | 1.9 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 4.9 | 4.8 | 4.5 | 4.4 | 4.1 | 3.8 | 3.3 | 2.8 | 2.2 | 1.7 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 5 | 4.9 | 4.8 | 4.7 | 4.6 | 4.4 | 4 | 3.5 | 3 | 2.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 4.9 | 4.8 | 4.7 | 4.5 | 4.3 | 4.1 | 3.7 | 3.2 | 2.7 | 2.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.6 | 9 | 9.1 | 9.1 | 9.2 | 9.2 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.2 | 9.1 | 9 | 8.9 | 8.8 | 8.4 | 8
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.6 | 9 | 9 | 9 | 9 | 9 | 9 | 8.9 | 8.8 | 8.7 | 8.7 | 8.6 | 8.4 | 8.3 | 8.2 | 8 | 7.9 | 7.5 | 7.2
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.6 | 9 | 9 | 9.1 | 9.1 | 9.1 | 9 | 9 | 9 | 8.9 | 8.9 | 8.7 | 8.6 | 8.4 | 8.2 | 8.1 | 8 | 7.5 | 7.1
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.6 | 9 | 9 | 9.1 | 9.1 | 9.1 | 9.1 | 9 | 9 | 8.9 | 8.9 | 8.8 | 8.6 | 8.5 | 8.4 | 8.2 | 8.2 | 7.8 | 7.6
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.2 | 14 | 14 | 13.9 | 13.8 | 13.4 | 13.2 | 13.3 | 13.3 | 13.3 | 13.3 | 13.2 | 13.2 | 13.1 | 11 | 5.1 | 0 | 0 | 0
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.2 | 14 | 13.9 | 13.8 | 13.3 | 13.1 | 13.1 | 13 | 13 | 12.9 | 10.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.2 | 14 | 14 | 13.3 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13 | 13 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.2 | 14 | 13.9 | 13.9 | 13.3 | 13.1 | 13.1 | 13.1 | 13.1 | 13 | 12.4 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 28.3 | 13 | 12 | 10.6 | 8.7 | 6.4 | 4.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 28.3 | 11.7 | 9.1 | 5.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 28.3 | 12.3 | 10.6 | 8.2 | 5.6 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 28.3 | 12.2 | 10.2 | 7.5 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.4 | 10.4 | 10.3 | 10.3 | 10.2 | 10.1 | 10 | 9.8 | 9.6 | 9.4 | 9.2 | 9 | 8.7 | 8.4 | 8 | 7.8 | 7.5 | 6 | 4.5
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.4 | 10.3 | 10.2 | 10 | 9.8 | 9.6 | 9.3 | 8.9 | 8.4 | 7.9 | 7.4 | 7.1 | 6.7 | 6.3 | 5.9 | 5.5 | 5.2 | 4 | 3.1
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.4 | 10.3 | 10.3 | 10.2 | 10.1 | 9.9 | 9.7 | 9.3 | 8.8 | 8.4 | 7.9 | 7.3 | 6.8 | 6.3 | 5.9 | 5.4 | 5 | 3.6 | 2.5
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.4 | 10.3 | 10.2 | 10.1 | 10 | 9.8 | 9.5 | 9.2 | 8.7 | 8.3 | 7.8 | 7.2 | 6.7 | 6.2 | 5.8 | 5.4 | 5.1 | 3.9 | 3.1
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 6.5 | 6.4 | 6.4 | 6.3 | 6.2 | 6.1 | 6 | 5.8 | 5.7 | 5.6 | 5.4 | 5.1 | 4.2 | 2.5 | 1 | 0 | 0 | 0
Bicker Fen 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 6.4 | 6.3 | 6.1 | 6 | 5.8 | 5.6 | 5.2 | 4.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 6.5 | 6.4 | 6.3 | 6.2 | 6.1 | 6 | 5.7 | 5.4 | 4.1 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 6.5 | 6.4 | 6.3 | 6.1 | 5.9 | 5.7 | 5.4 | 5.1 | 3.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.9 | 5.4 | 5.3 | 5.1 | 4.8 | 4.4 | 3.9 | 3.5 | 2.7 | 2.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.9 | 5.3 | 4.8 | 3.9 | 3.2 | 2.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.9 | 5.3 | 5.2 | 4.7 | 4.3 | 3.7 | 2.9 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.9 | 5.3 | 5 | 4.4 | 3.7 | 3 | 2.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 17.1 | 15.7 | 15.4 | 15 | 14.1 | 13 | 11.6 | 9.9 | 6.9 | 4.7 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 17.1 | 14.8 | 13.5 | 11.5 | 9.3 | 6.6 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 17.1 | 15.3 | 14.5 | 13.7 | 12.4 | 10.7 | 7.7 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 17.1 | 15.2 | 14.2 | 13 | 11.1 | 9 | 6.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.1 | 7.7 | 7.4 | 6.9 | 6.5 | 6.2 | 5.9 | 5.6 | 4.8 | 4.4 | 3.9 | 2.7 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.1 | 7.5 | 6.8 | 6 | 5.2 | 4.6 | 3.9 | 2.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.1 | 7.6 | 7.1 | 6.6 | 6.1 | 5.7 | 5.2 | 4.1 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.1 | 7.5 | 7 | 6.3 | 5.6 | 5.1 | 4.5 | 3.5 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 28.1 | 12.9 | 11.9 | 10.5 | 8.6 | 6.3 | 4.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 28.1 | 11.6 | 9.1 | 5.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 28.1 | 12.3 | 10.6 | 8.1 | 5.5 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 28.1 | 12.1 | 10.2 | 7.5 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.7 | 0.7 | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.7 | 0.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.7 | 0.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.5 | 4.3 | 4.2 | 4.1 | 3.9 | 3.6 | 3.3 | 3 | 2.6 | 2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.5 | 4.2 | 3.9 | 3.5 | 3.1 | 2.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.5 | 4.2 | 4.1 | 3.9 | 3.6 | 3.3 | 2.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.5 | 4.2 | 4.1 | 3.8 | 3.4 | 2.9 | 2.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.4 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.2 | 6 | 5.7 | 4.6 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.4 | 6.3 | 6.3 | 6.2 | 5.9 | 5.6 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.4 | 6.3 | 6.3 | 6.3 | 6.3 | 6.1 | 5.9 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.4 | 6.3 | 6.3 | 6.3 | 6.1 | 5.9 | 5.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.5 | 10.4 | 10.3 | 10.2 | 10 | 9.7 | 9.5 | 9.2 | 8.8 | 8.5 | 8.2 | 7.8 | 7.1 | 6.5 | 5.9 | 5.3 | 4.6 | 1.7 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.5 | 10.2 | 9.8 | 9.4 | 8.8 | 8.3 | 7.8 | 6.9 | 6 | 4.9 | 4.1 | 3.3 | 2.5 | 1.7 | 0.8 | 0 | 0 | 0 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.5 | 10.2 | 10 | 9.4 | 9 | 8.6 | 8.1 | 7.5 | 6.6 | 5.9 | 5.1 | 4.2 | 3.2 | 2.3 | 1.3 | 0 | 0 | 0 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.5 | 10.2 | 10 | 9.7 | 9.2 | 8.8 | 8.4 | 7.8 | 7 | 6.3 | 5.5 | 4.5 | 3.7 | 2.8 | 2 | 1.3 | 0.7 | 0 | 0
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 52.4 | 43.4 | 43 | 42.6 | 41.8 | 40.8 | 32.5 | 31.4 | 28.9 | 26.6 | 23.9 | 20.2 | 16.3 | 12.5 | 9 | 6.1 | 3.5 | 0 | 0
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 52.4 | 42.5 | 41 | 39.4 | 37.3 | 34.9 | 25.5 | 20.5 | 15.1 | 8.9 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 52.4 | 42.8 | 41.6 | 40.3 | 38.8 | 37.4 | 27.7 | 23.7 | 18.8 | 14.8 | 10.9 | 6.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 52.4 | 42.7 | 41.8 | 40.6 | 38.9 | 37 | 27.5 | 24 | 19.6 | 14.9 | 10.1 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 3.9 | 3.9 | 3.9 | 3.8 | 3.7 | 3.8 | 3.6 | 3 | 2.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 3.7 | 3.5 | 3.2 | 2.8 | 2.4 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 3.8 | 3.7 | 3.5 | 3.3 | 3.1 | 3 | 2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 3.8 | 3.6 | 3.4 | 3.1 | 2.8 | 2.7 | 1.9 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.9 | 10.6 | 10.4 | 10.3 | 10.1 | 9.8 | 9.1 | 8.7 | 7.9 | 7.3 | 6.6 | 5.6 | 4.3 | 2.9 | 1.6 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.9 | 10.1 | 9.5 | 8.8 | 8.2 | 7.3 | 6.3 | 4.5 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.9 | 10.3 | 9.8 | 9.5 | 9.1 | 8.5 | 7.4 | 6 | 4.3 | 2.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.9 | 10.2 | 9.8 | 9.4 | 8.9 | 8.2 | 7.2 | 5.9 | 4.4 | 2.9 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 14.8 | 13.6 | 13 | 12.4 | 11.4 | 10 | 21.1 | 19.6 | 17.2 | 15.6 | 13.9 | 11.5 | 8.2 | 4.9 | 1.6 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 14.8 | 12.5 | 10.7 | 8.6 | 6.2 | 3.4 | 14 | 9 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 14.8 | 12.9 | 11.6 | 9.9 | 8.2 | 6.2 | 17.5 | 13.7 | 9.2 | 5.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 14.8 | 12.8 | 11.6 | 10.1 | 7.8 | 5.6 | 16.3 | 12.9 | 8.8 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.9 | 1.5 | 1.4 | 1.2 | 1.1 | 1.1 | 4.7 | 4.7 | 4.8 | 4.9 | 5 | 4.9 | 4.7 | 4.6 | 4.4 | 4.3 | 4.1 | 3.4 | 2.6
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.9 | 1.3 | 1 | 0.5 | 0 | 0 | 4.3 | 4.3 | 4.2 | 4.1 | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 3 | 2.9 | 2.3 | 1.9
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.9 | 1.4 | 1.2 | 1 | 0.9 | 0.5 | 4.4 | 4.4 | 4.3 | 4.3 | 4.2 | 4 | 3.7 | 3.5 | 3.2 | 3 | 2.8 | 2.2 | 1.7
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.9 | 1.4 | 1.2 | 0.8 | 0.7 | 0 | 4.4 | 4.4 | 4.3 | 4.3 | 4.2 | 4 | 3.8 | 3.5 | 3.3 | 3.1 | 3 | 2.6 | 2.3
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.4 | 0 | 0 | 0 | 0 | 0 | 9.1 | 8.8 | 8 | 7.3 | 6.5 | 5.5 | 4.4 | 3.4 | 2.4 | 1.5 | 0 | 0 | 0
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.4 | 0 | 0 | 0 | 0 | 0 | 7.6 | 5.9 | 4.4 | 2.8 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.4 | 0 | 0 | 0 | 0 | 0 | 7.6 | 6.3 | 5 | 3.9 | 2.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.4 | 0 | 0 | 0 | 0 | 0 | 7.8 | 6.6 | 5.2 | 3.9 | 2.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11 | 4.4 | 4.4 | 4.2 | 4 | 3.7 | 4.7 | 4.4 | 3.9 | 3.5 | 3.1 | 2.6 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11 | 4.2 | 3.9 | 3.4 | 2.7 | 2.1 | 3 | 1.9 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11 | 4.3 | 4 | 3.6 | 3.2 | 2.8 | 3.8 | 3 | 2.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11 | 4.3 | 4.1 | 3.8 | 3.3 | 2.8 | 3.7 | 2.9 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 3.2 | 2.6 | 2.3 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.8 | 5.7 | 5.2 | 4.7 | 4.1 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.8 | 5.4 | 4.5 | 3.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.8 | 5.4 | 4.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.8 | 5.4 | 4.7 | 3.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.1 | 2.1 | 2.1 | 2 | 1.8 | 1.8 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2 | 2 | 1.9 | 1.9 | 1.8 | 1.5 | 1.2
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.1 | 2.1 | 1.7 | 0.9 | 0 | 0 | 2.1 | 2 | 2 | 1.9 | 1.8 | 1.8 | 1.7 | 1.6 | 1.5 | 1.5 | 1.4 | 1.2 | 1
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.1 | 2.1 | 1.9 | 1.6 | 1.4 | 0.8 | 2.1 | 2.1 | 2 | 2 | 1.9 | 1.8 | 1.7 | 1.6 | 1.5 | 1.5 | 1.4 | 1.1 | 0.8
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.1 | 2.1 | 1.9 | 1.3 | 1.1 | 0 | 2.1 | 2.1 | 2 | 1.9 | 1.8 | 1.7 | 1.7 | 1.6 | 1.5 | 1.4 | 1.3 | 1.1 | 0.9
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 3.5 | 3.2 | 2.6 | 2.3 | 1.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 2.8 | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 2.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 46.6 | 37.5 | 36.7 | 35.9 | 34.6 | 31.9 | 9.6 | 7.7 | 4.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 46.6 | 36.4 | 34.3 | 31.5 | 27.2 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 46.6 | 36.7 | 34.9 | 30.8 | 27.2 | 24.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 46.6 | 36.7 | 34.9 | 32.4 | 28.1 | 24 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.1 | 15.9 | 15.4 | 15 | 14.4 | 14.2 | 15 | 14.2 | 14.1 | 14 | 14 | 13.6 | 13.2 | 12.8 | 12.5 | 12.2 | 12 | 10.8 | 9.7
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.1 | 15.8 | 15.3 | 14.6 | 13.9 | 13.1 | 13.8 | 13.1 | 12.5 | 12 | 11.7 | 11.4 | 11.1 | 10.8 | 10.6 | 10.3 | 10 | 9.1 | 8.4
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.1 | 15.8 | 15.3 | 14.9 | 14.1 | 13 | 14 | 13.3 | 12.7 | 12.4 | 12.1 | 11.7 | 11.3 | 10.8 | 10.4 | 10.1 | 9.8 | 8.9 | 8.3
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.1 | 15.8 | 15.3 | 14.7 | 14.4 | 13.3 | 13.9 | 13.4 | 13 | 12.6 | 12.3 | 11.9 | 11.6 | 11.3 | 10.9 | 10.7 | 10.5 | 9.7 | 9.4
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 37 | 35.4 | 34.5 | 33.6 | 31.3 | 30.3 | 22.3 | 20.4 | 18.8 | 17.6 | 16.8 | 14.9 | 11.9 | 8.7 | 5.1 | 2.3 | 0 | 0 | 0
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 37 | 34.6 | 32.9 | 30.7 | 27.1 | 24 | 15.3 | 11.4 | 7.2 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 37 | 34.8 | 33.4 | 32.2 | 28.7 | 26.1 | 17.8 | 14.5 | 10.7 | 7.3 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 37 | 34.8 | 33.5 | 31.8 | 28.8 | 25.9 | 17 | 14.3 | 11 | 7.9 | 4.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.6 | 16.4 | 16 | 15.7 | 15.3 | 14.9 | 14.3 | 13.7 | 12.9 | 12.3 | 11.7 | 10.9 | 10 | 9 | 8 | 7.1 | 6.1 | 1.8 | 0
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.6 | 16.2 | 15.4 | 14.7 | 13.9 | 13 | 12 | 10.6 | 8.9 | 7.2 | 5.8 | 4.7 | 3.5 | 2.2 | 1 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.6 | 16.3 | 15.6 | 15 | 14.5 | 14 | 13.1 | 12.1 | 10.7 | 9.5 | 8.2 | 6.7 | 5.1 | 3.5 | 1.8 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.6 | 16.2 | 15.7 | 15.1 | 14.5 | 13.8 | 12.9 | 11.8 | 10.5 | 9.3 | 8 | 6.6 | 5.3 | 3.9 | 2.7 | 1.7 | 1 | 0 | 0
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.3 | 9.9 | 9.9 | 9.9 | 9.8 | 9.4 | 8.7 | 8.5 | 8.1 | 7.8 | 7.5 | 7.1 | 6.5 | 6.1 | 5.6 | 5.2 | 4.7 | 2.6 | 0.9
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.3 | 9.8 | 9.7 | 9.5 | 8.9 | 8.5 | 7.6 | 6.9 | 6.2 | 5.5 | 5 | 4.6 | 4.1 | 3.6 | 3 | 2.5 | 2 | 0 | 0
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.3 | 9.9 | 9.8 | 9.3 | 9.1 | 8.9 | 8.1 | 7.6 | 7.1 | 6.7 | 6.3 | 5.7 | 4.9 | 4.2 | 3.5 | 2.8 | 2.3 | 0 | 0
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 9.8 | 9.8 | 9.7 | 9.1 | 8.8 | 8 | 7.5 | 6.9 | 6.4 | 5.8 | 5.1 | 4.5 | 3.8 | 3.1 | 2.6 | 2.2 | 0 | 0
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 3.5 | 3.5 | 3.5 | 3.4 | 3.4 | 3.2 | 3 | 2.7 | 2.4 | 2.1 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 3.2 | 2.9 | 2.6 | 2.3 | 1.9 | 1.4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 3.3 | 3.1 | 2.9 | 2.7 | 2.5 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 3.3 | 3.2 | 3 | 2.8 | 2.6 | 2.1 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.6 | 3.8 | 3.5 | 3.2 | 2.6 | 2 | 8.7 | 8.5 | 8.1 | 7.4 | 6.6 | 5.6 | 4.5 | 3.4 | 2.4 | 1.5 | 0 | 0 | 0
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.6 | 3.3 | 2.2 | 0.7 | 0 | 0 | 7.6 | 6 | 4.4 | 2.9 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.6 | 3.5 | 2.6 | 1.6 | 0 | 0 | 7.7 | 6.4 | 5.1 | 4 | 2.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.6 | 3.5 | 2.5 | 1.2 | 0 | 0 | 7.6 | 6.7 | 5.3 | 4 | 2.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.8 | 3.7 | 2.4 | 2.1 | 1.9 | 6.9 | 6.2 | 4.2 | 3.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.5 | 3.2 | 1.1 | 0.6 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.6 | 3.4 | 1.8 | 0.9 | 0.5 | 4.3 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.6 | 3.3 | 1.3 | 0.9 | 0 | 3.8 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 29.5 | 28.4 | 28.3 | 26.8 | 26.7 | 26.6 | 26.3 | 26.2 | 26 | 25.8 | 25.7 | 25.4 | 24.7 | 23.7 | 22.7 | 22 | 21.7 | 20.3 | 19.1
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 29.5 | 28.2 | 26.6 | 26.4 | 26.2 | 25.9 | 25.6 | 25 | 24.3 | 23.4 | 22.4 | 21.2 | 20.2 | 19.4 | 19 | 18.5 | 17.9 | 16 | 15.1
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 29.5 | 28.3 | 26.5 | 26.4 | 26.2 | 25.8 | 25.1 | 24.4 | 23.7 | 23.1 | 22.5 | 21.8 | 21 | 20.4 | 19.7 | 19.2 | 18.7 | 16.5 | 15.4
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 29.5 | 28.3 | 26.7 | 26.5 | 26.3 | 26.1 | 25.7 | 25.2 | 24.5 | 23.7 | 22.8 | 22 | 21.3 | 20.6 | 20.2 | 19.8 | 19.6 | 18.5 | 18
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.4 | 14.3 | 14.3 | 14.3 | 14.2 | 14.1 | 14 | 13.8 | 13.6 | 13.4 | 13.1 | 12.8 | 12.4 | 12 | 11.6 | 11.2 | 10.4 | 7 | 3.9
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.4 | 14.2 | 14.1 | 13.9 | 13.7 | 13.4 | 13.1 | 12.6 | 12 | 11.1 | 10.3 | 9.5 | 8.6 | 7.7 | 6.9 | 6 | 5.1 | 1.6 | 0
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.4 | 14.3 | 14.2 | 14.2 | 14.1 | 14 | 13.8 | 13.4 | 12.8 | 12.3 | 11.7 | 11 | 9.7 | 8.5 | 7.3 | 6.2 | 5.2 | 1.5 | 0
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.4 | 14.3 | 14.2 | 14.1 | 13.9 | 13.7 | 13.4 | 13 | 12.5 | 12 | 11.4 | 10.7 | 9.7 | 8.6 | 7.6 | 6.8 | 6.1 | 3.6 | 2.5
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 3.2 | 2.6 | 2.3 | 1.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 45.9 | 45.1 | 42.8 | 42.2 | 41.4 | 40.4 | 37.9 | 36.5 | 33.9 | 32 | 29.7 | 26.5 | 22.2 | 17.6 | 13.1 | 9.2 | 5.5 | 0 | 0
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 45.9 | 42.1 | 39.9 | 37.5 | 35.2 | 32.6 | 28.6 | 22.3 | 16 | 9.2 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 45.9 | 42.5 | 40.6 | 38.9 | 37.3 | 35.5 | 31.5 | 27.3 | 22.1 | 17.4 | 12.3 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 45.9 | 42.4 | 41 | 39.2 | 37.3 | 35.4 | 31.5 | 27.6 | 22.5 | 17.7 | 12.3 | 6.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 9.4 | 9.2 | 9 | 8.7 | 8.4 | 8.1 | 7.1 | 6.6 | 5.8 | 5.3 | 4.6 | 3.8 | 2.3 | 0.8 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 9.4 | 8.8 | 8.2 | 7.4 | 6.6 | 5.7 | 4.2 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 9.4 | 8.9 | 8.3 | 7.8 | 7.3 | 6.7 | 5.3 | 3.8 | 2.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 9.4 | 8.9 | 8.5 | 7.9 | 7.4 | 6.9 | 5.5 | 4.3 | 2.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.4 | 0 | 0 | 0 | 0 | 0 | 11.9 | 11.2 | 10 | 8.5 | 6.7 | 5.2 | 3.9 | 2.5 | 1.1 | 0 | 0 | 0 | 0
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.4 | 0 | 0 | 0 | 0 | 0 | 8.3 | 5.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.4 | 0 | 0 | 0 | 0 | 0 | 9.5 | 7.7 | 5.7 | 4.1 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.4 | 0 | 0 | 0 | 0 | 0 | 8.8 | 6.9 | 4.8 | 3.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.9 | 8.1 | 8 | 7.7 | 7.5 | 7.3 | 6.8 | 6.1 | 4.1 | 3.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.9 | 7.9 | 7.3 | 6.5 | 6 | 4.9 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.9 | 8 | 7.4 | 7 | 6.5 | 6.1 | 4.2 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.9 | 7.9 | 7.5 | 6.8 | 6.5 | 5.9 | 3.8 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 6.7 | 6.5 | 6.3 | 6.2 | 6 | 13.4 | 13.2 | 13.1 | 13 | 12.8 | 12.6 | 12.4 | 12.1 | 11.8 | 11.6 | 11.3 | 10 | 8.9
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 6.6 | 6.2 | 5.9 | 5.7 | 5.5 | 12.7 | 12.3 | 11.9 | 11.4 | 11.1 | 10.7 | 10.3 | 9.9 | 9.5 | 9 | 8.6 | 6.5 | 5.5
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 6.6 | 6.3 | 6 | 5.9 | 5.6 | 13 | 12.6 | 12.3 | 12 | 11.7 | 11.1 | 10.6 | 10 | 9.4 | 8.9 | 8.4 | 6.2 | 5
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.6 | 6.3 | 6.1 | 5.8 | 5.6 | 12.8 | 12.5 | 12.2 | 12 | 11.6 | 11.2 | 10.9 | 10.5 | 10.1 | 9.8 | 9.5 | 8.5 | 7.9
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.7 | 16.3 | 16 | 15.4 | 14.7 | 13.3 | 11.1 | 9.5 | 7.2 | 5.1 | 3.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.7 | 15.9 | 14.8 | 13.5 | 11.3 | 9.1 | 6 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.7 | 16 | 15.3 | 13.6 | 12 | 10.4 | 7.7 | 4.8 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.7 | 16 | 15.2 | 14.2 | 12 | 10.1 | 7.2 | 4.7 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.1 | 8.8 | 8.6 | 8.4 | 8.1 | 7.8 | 7 | 6.5 | 5.4 | 4.5 | 3.6 | 2.6 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.1 | 8.5 | 7.8 | 7.2 | 6.6 | 5.8 | 4.6 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.1 | 8.6 | 8.1 | 7.8 | 7.3 | 6.7 | 4.7 | 2.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.1 | 8.6 | 8.1 | 7.7 | 7.2 | 6.6 | 5.5 | 3.9 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.2 | 15.8 | 15.4 | 15.1 | 14.6 | 14.2 | 8 | 7.6 | 6.3 | 4.7 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.2 | 15.4 | 14.6 | 13.7 | 12.9 | 11.9 | 5.4 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.2 | 15.5 | 14.9 | 14.4 | 13.8 | 13.2 | 5.9 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.2 | 15.5 | 14.9 | 14.3 | 13.5 | 12.8 | 6.3 | 4.5 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.1 | 10.6 | 8.8 | 7.7 | 6.5 | 5.7 | 5.3 | 4.4 | 3 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.1 | 10.1 | 7.6 | 5.7 | 4 | 2.5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.1 | 10.2 | 7.8 | 6.2 | 4.9 | 3.7 | 2.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.1 | 10.2 | 7.9 | 6.5 | 4.9 | 3.7 | 2.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 19.7 | 16.2 | 13.8 | 12 | 9.8 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 19.7 | 14.6 | 10.3 | 6.4 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 19.7 | 15.1 | 11.3 | 8.2 | 5.4 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 19.7 | 15 | 11.6 | 8.6 | 5.1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.1 | 8 | 7.9 | 7.8 | 7.7 | 7.5 | 20.7 | 20.4 | 19.7 | 19 | 18.1 | 17 | 15.9 | 15 | 14.3 | 13.8 | 13.2 | 10.2 | 7
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.1 | 7.8 | 7.4 | 7 | 6.7 | 6.1 | 18.9 | 17.6 | 15.9 | 13.8 | 12.6 | 11.3 | 10.1 | 9.3 | 8.6 | 7.8 | 7.1 | 4.4 | 2.8
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.1 | 7.8 | 7.5 | 7.3 | 7 | 6.7 | 19.2 | 17.8 | 15.9 | 14.6 | 13.5 | 12.4 | 11.3 | 10.4 | 9.5 | 8.7 | 8 | 5 | 3.2
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.1 | 7.8 | 7.6 | 7.3 | 7 | 6.6 | 19.4 | 18.4 | 17 | 15.2 | 13.6 | 12.2 | 11 | 10.1 | 9.3 | 8.5 | 7.9 | 5.8 | 4.8
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.4 | 1.9 | 1.7 | 1.5 | 1.4 | 1.4 | 8.6 | 8.3 | 7.9 | 7.7 | 7.4 | 7 | 6.5 | 5.9 | 5.4 | 4.9 | 4.4 | 2 | 0
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.4 | 1.7 | 1.3 | 0.7 | 0 | 0 | 7.4 | 6.7 | 5.9 | 5 | 4.3 | 3.8 | 3.2 | 2.5 | 1.8 | 1.1 | 0 | 0 | 0
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.4 | 1.8 | 1.5 | 1.2 | 1.1 | 0.6 | 8.1 | 7.6 | 6.8 | 6.1 | 5.4 | 4.5 | 3.6 | 2.7 | 1.9 | 1 | 0 | 0 | 0
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.4 | 1.8 | 1.5 | 1 | 0.8 | 0 | 7.7 | 7.1 | 6.4 | 5.8 | 5.1 | 4.4 | 3.5 | 2.6 | 1.9 | 1.1 | 0.6 | 0 | 0
Chesterfield 132kV | PINXTON 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 7.5 | 7.3 | 7.4 | 7.6 | 7.7 | 7.4 | 3.3 | 3.1 | 3 | 2.9 | 3 | 2.7 | 2.4 | 2 | 1.6 | 1.3 | 0.9 | 0 | 0
Chesterfield 132kV | PINXTON 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 7.5 | 7.1 | 6.9 | 6.8 | 6.3 | 5.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | PINXTON 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 7.5 | 7.2 | 6.9 | 6.4 | 5.8 | 5.1 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | PINXTON 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 7.5 | 7.1 | 7.2 | 7.2 | 6.8 | 6.2 | 1.6 | 1.3 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.4 | 16.4 | 16.3 | 16.2 | 16.2 | 16.2 | 9.5 | 9.5 | 9.3 | 9.3 | 9.2 | 8.9 | 8.6 | 8.3 | 8.1 | 7.9 | 7.7 | 6.5 | 5.3
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.4 | 16.1 | 15.8 | 15.6 | 15.4 | 15.1 | 8.3 | 7.7 | 7.1 | 6.5 | 6 | 5.2 | 4.5 | 3.6 | 2.8 | 1.9 | 1.1 | 0 | 0
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.4 | 16.2 | 15.9 | 15.8 | 15.6 | 15.5 | 8.7 | 8.5 | 8.2 | 7.9 | 7.6 | 6.9 | 6 | 5 | 4.2 | 3.3 | 2.5 | 0 | 0
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.4 | 16.2 | 15.9 | 15.8 | 15.6 | 15.4 | 8.6 | 8.4 | 8 | 7.7 | 7.3 | 6.8 | 6.4 | 5.9 | 5.5 | 5 | 4.7 | 3.8 | 2.7
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.8 | 3.8 | 3.8 | 3.8 | 3.6 | 3.8 | 3.5 | 2.9 | 2.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.7 | 3.5 | 3.1 | 2.8 | 2.4 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 3.1 | 2.9 | 2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.7 | 3.6 | 3.4 | 3.1 | 2.8 | 2.7 | 1.9 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.4 | 7.3 | 7.5 | 7.6 | 7.7 | 7.9 | 8 | 8.1 | 8.3 | 8.4 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.4 | 7.3 | 7.5 | 7.6 | 7.7 | 7.9 | 8 | 8.1 | 8.3 | 8.4 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.4 | 7.3 | 7.5 | 7.6 | 7.7 | 7.9 | 8 | 8.1 | 8.3 | 8.4 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.4 | 7.3 | 7.5 | 7.6 | 7.7 | 7.9 | 8 | 8.1 | 8.3 | 8.4 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.7 | 2.7 | 2.6 | 2.6 | 2.5 | 2.4 | 2.3 | 2.2 | 2.1 | 1.9 | 1.4 | 0.9
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.8 | 2.8 | 2.7 | 2.7 | 2.6 | 2.6 | 2.5 | 2.4 | 2.2 | 2 | 1.9 | 1.8 | 1.7 | 1.5 | 1.4 | 1.3 | 1.1 | 0.6 | 0
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.7 | 2.7 | 2.6 | 2.5 | 2.4 | 2.2 | 2.1 | 1.9 | 1.7 | 1.5 | 1.3 | 1.1 | 0 | 0
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.8 | 2.8 | 2.8 | 2.7 | 2.7 | 2.7 | 2.6 | 2.5 | 2.4 | 2.3 | 2.1 | 2 | 1.8 | 1.6 | 1.4 | 1.3 | 1.2 | 0.8 | 0.5
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.2 | 10.1 | 10 | 9.9 | 9.9 | 9.8 | 2.7 | 2.6 | 2.5 | 2.4 | 2.4 | 2.2 | 1.9 | 1.6 | 1.2 | 1 | 0.6 | 0 | 0
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.2 | 10 | 9.8 | 9.6 | 9.4 | 9.2 | 2 | 1.6 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.2 | 10 | 9.9 | 9.8 | 9.7 | 9.6 | 2.3 | 1.9 | 1.4 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.2 | 10 | 9.9 | 9.7 | 9.5 | 9.4 | 2.2 | 1.9 | 1.5 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.3 | 10.1 | 10 | 9.9 | 9.7 | 9.4 | 4.6 | 4.3 | 3.8 | 3.5 | 3.2 | 2.7 | 2.1 | 1.3 | 0.7 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.3 | 9.9 | 9.6 | 9.1 | 8.7 | 8.1 | 3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.3 | 9.9 | 9.7 | 9.4 | 9.1 | 8.7 | 3.4 | 2.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.3 | 9.9 | 9.7 | 9.3 | 8.9 | 8.4 | 3.2 | 2.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 8 | 7.9 | 6.1 | 5.9 | 5.7 | 5.4 | 4.9 | 4.6 | 4.1 | 3.7 | 3.3 | 2.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 8 | 5.8 | 5.4 | 4.8 | 4.1 | 3.5 | 2.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 8 | 5.9 | 5.4 | 4.8 | 4.5 | 3.9 | 3 | 2.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 8 | 5.9 | 5.6 | 5.1 | 4.5 | 4 | 3.3 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.1 | 7.9 | 6.1 | 5.9 | 5.7 | 5.4 | 4.9 | 4.6 | 4.1 | 3.7 | 3.3 | 2.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.1 | 5.9 | 5.4 | 4.8 | 4.1 | 3.5 | 2.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.1 | 6 | 5.5 | 4.8 | 4.5 | 3.9 | 3 | 2.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.1 | 5.9 | 5.6 | 5.1 | 4.5 | 4.1 | 3.3 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14 | 14 | 14.1 | 14.2 | 14.3 | 14.4 | 14.5 | 14.6 | 14.7 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.7 | 14.6 | 14.4
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14 | 14 | 14.1 | 14.2 | 14.3 | 14.4 | 14.5 | 14.6 | 14.6 | 14.7 | 14.8 | 14.8 | 14.8 | 14.7 | 14.7 | 14.6 | 14.6 | 14.5 | 14.4
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14 | 14 | 14.1 | 14.2 | 14.3 | 14.4 | 14.5 | 14.6 | 14.6 | 14.7 | 14.8 | 14.8 | 14.8 | 14.8 | 14.7 | 14.6 | 14.6 | 14.4 | 14.3
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14 | 14 | 14.1 | 14.2 | 14.3 | 14.3 | 14.5 | 14.5 | 14.6 | 14.7 | 14.7 | 14.7 | 14.7 | 14.6 | 14.6 | 14.5 | 14.5 | 14.4 | 14.2
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.7 | 5.6 | 5.6 | 5.5 | 5.4 | 5.3 | 5.1 | 4.8 | 4.6 | 4.4 | 4.2 | 4 | 3.6 | 3.3 | 2.9 | 2.6 | 2.2 | 0.7 | 0
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.7 | 5.5 | 5.4 | 5.2 | 4.9 | 4.6 | 4.3 | 3.9 | 3.4 | 2.8 | 2.4 | 2.1 | 1.7 | 1.3 | 0.9 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.7 | 5.6 | 5.5 | 5.3 | 5.1 | 5 | 4.9 | 4.5 | 4.1 | 3.7 | 3.3 | 2.8 | 2.3 | 1.8 | 1.3 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.7 | 5.6 | 5.5 | 5.4 | 5.1 | 4.9 | 4.5 | 4.2 | 3.8 | 3.4 | 2.9 | 2.4 | 2 | 1.5 | 1 | 0.7 | 0 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 2.6 | 2.2 | 1.7 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 2.3 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 2.3 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.4 | 5.5 | 5.3 | 5.1 | 4.8 | 4.4 | 4.1 | 3.9 | 3.4 | 3 | 2.7 | 2.2 | 1.7 | 1.2 | 0.7 | 0 | 0 | 0 | 0
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.4 | 5.2 | 4.8 | 4.3 | 3.7 | 3 | 2.6 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.4 | 5.3 | 4.9 | 4.5 | 4 | 3.4 | 2.8 | 2.2 | 1.7 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.4 | 5.3 | 5 | 4.7 | 4.1 | 3.4 | 2.9 | 2.1 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.9 | 2 | 1.7 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.9 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.9 | 1.8 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.9 | 1.8 | 1.3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 74.8 | 64.2 | 63.6 | 60.3 | 59.4 | 58.5 | 57.2 | 56.1 | 53.4 | 52.2 | 49.5 | 47.5 | 44.3 | 40.7 | 37.3 | 34.2 | 31.4 | 19.8 | 10.4
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 74.8 | 63.4 | 60.5 | 56.8 | 55.1 | 53.2 | 51.2 | 47.3 | 41.1 | 36.8 | 32.3 | 28.1 | 24.1 | 20.4 | 17.1 | 13.6 | 10.2 | 0 | 0
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 74.8 | 63.7 | 60.9 | 58.5 | 56.5 | 55 | 53 | 49.9 | 44 | 40.6 | 36.7 | 32.4 | 27.7 | 23.3 | 18.8 | 14.8 | 11.1 | 0 | 0
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 74.8 | 63.6 | 61.2 | 57.9 | 56.4 | 54.9 | 52.8 | 50.2 | 44.6 | 41.3 | 37.5 | 33 | 29 | 25 | 21.6 | 18.8 | 16.8 | 7.9 | 3.5
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.1 | 11.4 | 11.4 | 11.4 | 11.4 | 11.3 | 11.1 | 11 | 10.7 | 10.4 | 10.2 | 9.8 | 9.4 | 9 | 8.6 | 8.3 | 7.9 | 4.5 | 0.9
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.1 | 11.3 | 11.1 | 10.9 | 10.8 | 10.5 | 10.2 | 9.4 | 8.6 | 7.9 | 7.4 | 6.8 | 5.7 | 4.5 | 3.3 | 2 | 0.9 | 0 | 0
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.1 | 11.3 | 11.2 | 11.2 | 11.1 | 11 | 10.5 | 10 | 9.5 | 9.1 | 8.7 | 8.1 | 7.5 | 6.3 | 4.8 | 3.3 | 2.3 | 0 | 0
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.1 | 11.3 | 11.3 | 11.2 | 11 | 10.9 | 10.6 | 10 | 9.4 | 8.9 | 8.3 | 7.8 | 7.3 | 6.2 | 4.9 | 3.9 | 3.2 | 0 | 0
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.1 | 2.6 | 2.2 | 1.8 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.1 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.1 | 2.4 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.1 | 2.3 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.5 | 5.2 | 4.8 | 4.2 | 3.5 | 2.8 | 14.1 | 14 | 13.7 | 13.6 | 13.6 | 13.5 | 13.4 | 13.2 | 13 | 12.8 | 12.5 | 11.5 | 10.2
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.5 | 4.6 | 3.6 | 1.9 | 1 | 0 | 14.1 | 13.7 | 13.3 | 12.7 | 12.4 | 12.3 | 12 | 11.8 | 11.6 | 11.3 | 11.1 | 9.4 | 7.8
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.5 | 4.9 | 4.1 | 3.4 | 2.1 | 0.9 | 14.4 | 14.1 | 13.8 | 13.5 | 13.2 | 12.8 | 12.5 | 12.1 | 11.8 | 11.5 | 11.3 | 9.1 | 7.5
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.5 | 4.8 | 4 | 2.8 | 2.1 | 0.5 | 14.1 | 13.9 | 13.5 | 13.2 | 13 | 12.7 | 12.3 | 12 | 11.7 | 11.5 | 11.3 | 10.3 | 9.6
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.2 | 6.1 | 6.1 | 6 | 5.9 | 5.8 | 5.6 | 5.3 | 4.3 | 3.5 | 2.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.2 | 6 | 5.8 | 5.5 | 5.1 | 4.4 | 3.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.2 | 6 | 5.9 | 5.7 | 5.5 | 5.1 | 3.9 | 2.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.2 | 6 | 5.9 | 5.7 | 5.5 | 5 | 4 | 2.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7 | 5.9 | 5.5 | 5.1 | 3.5 | 2.8 | 14.7 | 14.3 | 14 | 13.6 | 13.4 | 13.2 | 12.9 | 12.6 | 12.2 | 12 | 11.6 | 10 | 8.8
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7 | 5.5 | 4.8 | 3.8 | 1.4 | 0 | 13.4 | 12.9 | 12.4 | 12 | 11.7 | 11.4 | 11 | 10.7 | 10.3 | 9.9 | 9.6 | 8.2 | 7.3
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7 | 5.6 | 5.1 | 4.6 | 2.1 | 0.9 | 13.7 | 13.3 | 12.9 | 12.5 | 12.2 | 11.7 | 11.2 | 10.7 | 10.2 | 9.7 | 9.3 | 7.8 | 6.9
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7 | 5.6 | 5 | 4.3 | 2.1 | 0.5 | 13.7 | 13.3 | 13 | 12.7 | 12.3 | 11.9 | 11.5 | 11 | 10.6 | 10.2 | 10 | 8.8 | 8.4
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.9 | 3.7 | 3.7 | 3.7 | 3.6 | 3.5 | 3.7 | 3.5 | 2.9 | 2.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.9 | 3.6 | 3.3 | 3 | 2.7 | 2.3 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.9 | 3.6 | 3.5 | 3.3 | 3.1 | 3 | 2.9 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.9 | 3.6 | 3.5 | 3.3 | 3 | 2.7 | 2.6 | 1.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.9 | 8.1 | 8 | 7.6 | 7.5 | 7.3 | 6.8 | 6.1 | 4.1 | 3.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.9 | 7.9 | 7.3 | 6.5 | 6 | 4.9 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.9 | 7.9 | 7.4 | 7 | 6.5 | 6.1 | 4.2 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.9 | 7.9 | 7.5 | 6.8 | 6.5 | 5.9 | 3.8 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 39.7 | 37.4 | 36.7 | 36 | 35.2 | 34.1 | 65.9 | 64.6 | 62.8 | 61.4 | 59.7 | 57.5 | 54.8 | 52.2 | 49.7 | 47.3 | 44.8 | 33.7 | 24.6
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 39.7 | 36.7 | 35 | 33.2 | 31.2 | 29.3 | 60.1 | 56.4 | 52.4 | 48.2 | 44.8 | 41.6 | 38.4 | 35.2 | 32.1 | 28.8 | 25.6 | 12.1 | 4.4
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 39.7 | 37 | 35.6 | 33.8 | 32.6 | 31.4 | 62.6 | 60 | 56.7 | 53.7 | 50.5 | 46.4 | 42.1 | 37.8 | 33.5 | 29.6 | 26.3 | 12.1 | 3.6
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 39.7 | 36.9 | 35.7 | 34.3 | 32.6 | 31 | 61.9 | 59.2 | 56 | 53.2 | 49.9 | 46 | 42.6 | 38.9 | 35.7 | 33.1 | 31.1 | 22.5 | 18.1
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.8 | 2.7 | 2.6 | 2.5 | 2.4 | 2.2 | 2.5 | 2.2 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.8 | 2.6 | 2.2 | 1.9 | 1.6 | 1.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.8 | 2.6 | 2.3 | 2.1 | 1.8 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.8 | 2.6 | 2.3 | 2 | 1.7 | 1.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.7 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.5 | 10.5 | 10.4 | 10.4 | 10.3 | 10.1 | 9.8 | 9.5 | 9.2 | 8.9 | 8.6 | 7.2 | 5.9
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.7 | 10.6 | 10.5 | 10.4 | 10.3 | 10.1 | 10 | 9.8 | 9.7 | 9 | 8.4 | 7.7 | 7 | 6.3 | 6.1 | 5.8 | 5.6 | 4.5 | 3.8
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.7 | 10.6 | 10.5 | 10.4 | 10.4 | 10.3 | 10.3 | 9.8 | 9.2 | 8.7 | 8.2 | 7.4 | 7.1 | 6.8 | 6.5 | 6.2 | 5.9 | 4.7 | 3.9
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.7 | 10.6 | 10.5 | 10.5 | 10.3 | 10.3 | 10.2 | 10 | 9.8 | 9.6 | 9.3 | 8.9 | 8.5 | 8.1 | 7.8 | 7.5 | 7.2 | 6 | 5.2
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.4 | 5.3 | 5.3 | 5.3 | 5.3 | 5.2 | 5.1 | 5 | 4.7 | 4.4 | 4.1 | 3.8 | 3.3 | 1.7 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.4 | 5.3 | 5.2 | 5.1 | 4.9 | 4.6 | 4.2 | 3.7 | 3.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.4 | 5.3 | 5.3 | 5.2 | 5.1 | 5.1 | 4.8 | 4.4 | 3.9 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.4 | 5.3 | 5.2 | 5.2 | 5.1 | 4.8 | 4.5 | 4.1 | 3.6 | 3.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.6 | 2.4 | 2.3 | 2.2 | 2 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.6 | 2.2 | 1.9 | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.6 | 2.3 | 2.1 | 1.9 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.6 | 2.3 | 2.1 | 1.8 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.8 | 8.6 | 8.5 | 8.4 | 8.2 | 7.2 | 6.1 | 5.6 | 4.4 | 2.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.8 | 8.2 | 7.5 | 6.6 | 5 | 3.4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.8 | 8.3 | 7.3 | 5.3 | 3.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.8 | 8.3 | 7.6 | 6.9 | 5.2 | 3.6 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.7 | 7.5 | 7.5 | 7.4 | 7.3 | 7.1 | 6.3 | 6 | 5.4 | 5 | 4.6 | 4 | 3.2 | 2.4 | 1.6 | 0.8 | 0 | 0 | 0
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.7 | 7.3 | 7 | 6.5 | 6 | 5.3 | 4.2 | 3.1 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.7 | 7.4 | 7.2 | 6.8 | 6.4 | 6.2 | 5.4 | 4.7 | 3.7 | 2.8 | 1.8 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.7 | 7.3 | 7.1 | 6.8 | 6.4 | 5.9 | 4.8 | 3.9 | 2.8 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.1 | 7.1 | 6.9 | 6.6 | 6.2 | 5.5 | 5 | 4.2 | 3.5 | 2.7 | 2.1 | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.1 | 6.8 | 6.3 | 5.6 | 4.7 | 3.6 | 2.6 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.1 | 6.9 | 6.3 | 5.4 | 4.2 | 3.2 | 2.5 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.1 | 6.9 | 6.5 | 5.9 | 4.9 | 3.9 | 3.1 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.2 | 15.9 | 15.2 | 14.8 | 14.4 | 14.1 | 13.6 | 13.2 | 12.7 | 12.2 | 11.6 | 10.7 | 9.9 | 9.1 | 8.4 | 7.9 | 7.4 | 4.6 | 1.8
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.2 | 15.6 | 14.3 | 13.5 | 13 | 12.4 | 11.7 | 10.5 | 9.3 | 7.5 | 6.1 | 4.9 | 3.7 | 2.6 | 1.6 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.2 | 15.7 | 14.5 | 13.7 | 13.2 | 12.9 | 12.3 | 11.2 | 9.9 | 8.7 | 7.8 | 6.7 | 5.3 | 4.1 | 2.7 | 1.5 | 0.6 | 0 | 0
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.2 | 15.7 | 14.6 | 13.8 | 13.2 | 12.4 | 11.6 | 10.8 | 9.9 | 8.7 | 7.4 | 6.1 | 5.2 | 4 | 3.2 | 2.5 | 2.1 | 0 | 0
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 44.1 | 13.9 | 11.7 | 9.5 | 7.6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 44.1 | 12.2 | 7.7 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 44.1 | 12.5 | 8.2 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 44.1 | 12.4 | 8.7 | 4.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 20.8 | 20.7 | 20.7 | 20.6 | 20.4 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 20.8 | 20.4 | 20.2 | 19.8 | 19.3 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 20.8 | 20.6 | 20.5 | 20.3 | 20.2 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 20.8 | 20.5 | 20.3 | 20.1 | 19.7 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 4.4 | 4.1 | 3.8 | 3.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13 | 12.8 | 12.6 | 12.3 | 11.7 | 11.1 | 5.5 | 4.7 | 3.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13 | 12.5 | 11.9 | 10.9 | 10.1 | 9.1 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13 | 12.6 | 12 | 11.1 | 10 | 8.7 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13 | 12.5 | 12 | 11 | 10.1 | 8.8 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 27.4 | 17.9 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 27.4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 27.4 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 27.4 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.1 | 6.9 | 6.6 | 6.3 | 5.7 | 5.1 | 4 | 2.8 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.1 | 6.6 | 6 | 5.3 | 4.4 | 3.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.1 | 6.7 | 6.3 | 5.9 | 5.1 | 4.3 | 3.3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.1 | 6.7 | 6.2 | 5.7 | 4.9 | 3.8 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.5 | 9.3 | 8.6 | 8.1 | 7.6 | 7.1 | 6.4 | 6 | 5.2 | 4.5 | 3.6 | 2.7 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.5 | 9.1 | 7.5 | 6.3 | 5.4 | 4.5 | 3.2 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.5 | 9.1 | 7.6 | 6.6 | 5.8 | 4.9 | 3.9 | 3.3 | 2.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.5 | 9.1 | 7.9 | 7.1 | 6.3 | 5.5 | 4.3 | 3.4 | 2.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 10.5 | 7.7 | 7.4 | 7.2 | 6.8 | 6.4 | 7.1 | 6.8 | 6.3 | 5.9 | 5.4 | 4.8 | 4.2 | 3.8 | 3.4 | 3 | 2.6 | 0.5 | 0
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 10.5 | 7.2 | 6.7 | 6.1 | 5.4 | 4.6 | 5 | 3.7 | 2.4 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 10.5 | 7.2 | 6.7 | 6.2 | 5.4 | 4.7 | 5 | 4.2 | 3.3 | 2.5 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 10.5 | 7.2 | 6.7 | 6.2 | 5.5 | 4.8 | 5.2 | 4.4 | 3.5 | 2.6 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9 | 8.8 | 8.3 | 8 | 7.7 | 7.3 | 6.4 | 6 | 5.2 | 4.8 | 4.1 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9 | 8.5 | 7.5 | 6.4 | 5.3 | 4.2 | 2.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9 | 8.6 | 7.7 | 7.1 | 6.3 | 4.7 | 3.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9 | 8.6 | 7.8 | 7.4 | 6.4 | 5.5 | 5.1 | 2.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 18.2 | 11.6 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 18.2 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 18.2 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 18.2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.1 | 7.5 | 6.1 | 4.7 | 3.3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.1 | 7.2 | 5.5 | 3.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.1 | 7.3 | 5.7 | 4.1 | 2.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.1 | 7.3 | 5.6 | 4 | 2.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 6.4 | 6 | 5.8 | 5.5 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 6.1 | 5.3 | 4.7 | 4.1 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 6.2 | 5.6 | 5.3 | 5 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 6.2 | 5.6 | 5.2 | 4.7 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 15.7 | 15.6 | 15.5 | 15.3 | 15 | 14.8 | 14.6 | 14 | 13.9 | 13.8 | 13.7 | 13 | 12.8 | 12.6 | 12.3 | 12.2 | 12.1 | 11.9 | 11.4
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 15.7 | 15.5 | 15.2 | 14.6 | 14.1 | 13.6 | 12.9 | 12.3 | 11.4 | 10.1 | 9.1 | 7.6 | 6.3 | 5.1 | 3.8 | 2.6 | 1.3 | 0 | 0
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 15.7 | 15.5 | 15.2 | 14.8 | 14.3 | 13.7 | 13.1 | 12.5 | 11.8 | 10.8 | 10.5 | 9.3 | 8.1 | 7 | 5.8 | 4.5 | 3.4 | 0 | 0
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 15.7 | 15.5 | 15.2 | 14.9 | 14.7 | 14.1 | 13.5 | 13.3 | 12.7 | 12.2 | 11.2 | 10.8 | 10.5 | 10.3 | 10.1 | 9.9 | 9.7 | 8.6 | 7.6
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.5 | 11.4 | 11 | 9.2 | 8.4 | 8.3 | 9.5 | 8.6 | 8.1 | 7.6 | 7.1 | 6.3 | 5.1 | 3.9 | 2.3 | 0 | 0 | 0 | 0
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.5 | 11.3 | 9.6 | 8.5 | 8.2 | 6.3 | 6 | 5.3 | 4.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.5 | 11.3 | 9.7 | 9.5 | 8 | 6.8 | 7.7 | 7.1 | 6.1 | 4.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.5 | 11.3 | 9.7 | 8.8 | 8.5 | 6.7 | 6.5 | 5.9 | 5 | 4 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.3 | 10.9 | 4.3 | 1.4 | 0 | 0 | 2.4 | 2.5 | 2.7 | 2.9 | 3.2 | 3.1 | 3 | 3 | 2.9 | 2.1 | 1.3 | 1 | 0.8
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.3 | 7 | 3.3 | 1.2 | 1.3 | 0 | 1.9 | 2.1 | 2.3 | 2.4 | 1.9 | 0.9 | 0.8 | 0.7 | 0.6 | 0.6 | 0.5 | 0 | 0
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.3 | 7 | 3.3 | 3.4 | 0 | 0 | 2.2 | 2.3 | 2.5 | 1.8 | 0.8 | 0.7 | 0.6 | 0.5 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 7 | 3.3 | 1.3 | 1.5 | 0 | 2.1 | 2.3 | 2.5 | 2.7 | 2.5 | 1.4 | 0.9 | 0.8 | 0.7 | 0.7 | 0.6 | 0.5 | 0
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 4.9 | 4.5 | 4.1 | 3.5 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 4.3 | 3.4 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 4.5 | 3.9 | 3.2 | 2.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 4.5 | 3.8 | 3 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12 | 11.2 | 10.6 | 9.5 | 9.1 | 8.6 | 10 | 9.4 | 8.3 | 7 | 5.5 | 3.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12 | 11 | 9.8 | 8.2 | 6.1 | 2.8 | 7.1 | 5.2 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12 | 11.1 | 9.9 | 9.1 | 5.6 | 2.8 | 7.1 | 5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12 | 11.1 | 10.1 | 8.8 | 7.5 | 4.5 | 7.9 | 6.5 | 4.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.1 | 6.9 | 6.3 | 5.8 | 5.6 | 4.6 | 3.5 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.1 | 6.5 | 5.2 | 4.3 | 3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.1 | 6.6 | 5.2 | 3.6 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.1 | 6.6 | 5.3 | 4.6 | 3.3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 38.3 | 30.3 | 27.6 | 25.2 | 23.3 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 38.3 | 28.9 | 23.1 | 18 | 11.6 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 38.3 | 29.4 | 23.8 | 17.4 | 10.2 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 38.3 | 29.2 | 24.4 | 20.6 | 14.6 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 18.2 | 14.3 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 18.2 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 18.2 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 18.2 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.4 | 7.4 | 7.4 | 7.3 | 7.3 | 7.3 | 7.3 | 7.1 | 6.7 | 6.4 | 5.9 | 5.2 | 4.2 | 3.2 | 2.3 | 1.4 | 0 | 0 | 0
Coventry 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.4 | 7.3 | 7.3 | 7 | 6.7 | 6.3 | 6 | 5.3 | 4.4 | 2.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.4 | 7.3 | 7.3 | 7.3 | 7.1 | 6.9 | 6.6 | 4.9 | 3.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.4 | 7.3 | 7.3 | 7.3 | 7 | 6.6 | 6.4 | 5.9 | 5.2 | 4.1 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 14.3 | 14.1 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 14.3 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 14.3 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 14.3 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 17.1 | 11.1 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 17.1 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 17.1 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 17.1 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.3 | 11.2 | 11.4 | 11.4 | 10.9 | 11.4 | 11.4 | 11.5 | 11.6 | 11.4 | 11.1 | 10.7 | 10.1 | 9.6 | 9.1 | 8.8 | 8.4 | 6.7 | 5.2
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.3 | 11.2 | 11.3 | 11.3 | 11.1 | 9.5 | 10.8 | 10.3 | 9.9 | 9.1 | 8.6 | 7.4 | 6.4 | 5.5 | 5.1 | 4.7 | 4.4 | 2.9 | 1.6
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.3 | 11.2 | 11.3 | 11.2 | 11 | 10.5 | 10.6 | 10.3 | 9.9 | 9.4 | 8.4 | 7.4 | 6.7 | 6 | 5.5 | 5.1 | 4.8 | 3 | 1.5
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 11.2 | 11.3 | 11.4 | 11.4 | 10.6 | 11.3 | 11.2 | 11 | 10.4 | 9.9 | 9.3 | 7.9 | 6.7 | 5.9 | 5.3 | 4.9 | 4.1 | 3.6
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.3 | 8.2 | 8.1 | 8 | 7.9 | 7.7 | 7.7 | 7.5 | 7.2 | 7 | 6.4 | 5.4 | 4.4 | 3.4 | 2.4 | 1.5 | 0.5 | 0 | 0
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.3 | 8 | 7.6 | 7.4 | 7.1 | 6.7 | 6.6 | 5.8 | 4.8 | 2.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.3 | 8 | 7.7 | 7.5 | 7.3 | 7 | 6.7 | 5 | 3.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.3 | 8 | 7.7 | 7.4 | 7.1 | 6.8 | 6.5 | 6 | 5.3 | 4.2 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.7 | 5.4 | 5.1 | 4.7 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.4 | 4.8 | 4.2 | 3.6 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.4 | 5.1 | 4.9 | 4.3 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.4 | 5.1 | 4.7 | 4.2 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.8 | 7.2 | 7 | 6.6 | 6.3 | 5.9 | 4.8 | 4.2 | 3.3 | 2.5 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.8 | 6.7 | 6 | 5 | 3.9 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.8 | 6.8 | 6.2 | 5.3 | 4.4 | 3.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.8 | 6.8 | 6.2 | 5.4 | 4.7 | 3.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.1 | 15 | 15 | 14.9 | 14.9 | 14.9 | 14.9 | 14.8 | 14.7 | 11.3 | 6.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.1 | 14.9 | 14.8 | 14.7 | 14.6 | 14.4 | 10.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.1 | 15 | 14.9 | 14.8 | 14.8 | 14.2 | 9.7 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.1 | 15 | 14.9 | 14.8 | 14.7 | 14.6 | 12.2 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 4.4 | 4.1 | 3.8 | 3.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 23.2 | 22.8 | 22.2 | 21.4 | 20.5 | 19.2 | 17.5 | 16.6 | 15.7 | 14.9 | 14 | 13.2 | 12.3 | 11.3 | 9.9 | 9 | 8.2 | 4.1 | 0.5
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 23.2 | 22.3 | 21.3 | 19.7 | 18.3 | 16.3 | 14.1 | 10 | 5.5 | 7.9 | 5.4 | 3.5 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 23.2 | 22.4 | 21.6 | 20.5 | 19.2 | 16.1 | 13.2 | 9.5 | 5.6 | 11.2 | 9.8 | 8 | 5.9 | 3.8 | 1.8 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 23.2 | 22.4 | 21.5 | 20.3 | 18.9 | 17 | 15.6 | 12.5 | 8.8 | 5.1 | 7.2 | 5.6 | 4.4 | 3 | 1.9 | 0.9 | 0 | 0 | 0
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 36.7 | 32.9 | 31.8 | 30.4 | 28.4 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 36.7 | 31.1 | 28.6 | 25 | 21.3 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 36.7 | 31.5 | 29.3 | 26.6 | 23.4 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 36.7 | 31.4 | 29.3 | 26.5 | 23.2 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.9 | 7.6 | 7.3 | 6.9 | 6.5 | 5.8 | 5 | 4.2 | 3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.9 | 7.3 | 6.5 | 5.6 | 4.5 | 3.3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.9 | 7.4 | 6.8 | 5.9 | 4.9 | 3.9 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.9 | 7.4 | 6.8 | 6 | 5 | 4 | 2.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.7 | 8.6 | 8.7 | 8.7 | 8.8 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.7 | 8.6 | 8.7 | 8.7 | 8.8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.7 | 8.6 | 8.7 | 8.7 | 8.8 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.7 | 8.6 | 8.7 | 8.7 | 8.8 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.3 | 4.2 | 4.2 | 4.2 | 4.1 | 4.1 | 1.5 | 1.4 | 1.3 | 1.3 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.3 | 4.2 | 4.1 | 4 | 3.9 | 3.8 | 1.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.3 | 4.2 | 4.2 | 4.1 | 4.1 | 4.1 | 1.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.3 | 4.2 | 4.1 | 4.1 | 4 | 3.9 | 1.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.2 | 6.4 | 5.4 | 4.6 | 3.3 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.2 | 6 | 4.7 | 3.3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.2 | 6.2 | 5.2 | 4.2 | 2.9 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.2 | 6.2 | 5 | 3.7 | 2.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.9 | 5.6 | 5.6 | 5.6 | 5.5 | 4.3 | 3.7 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.9 | 5.5 | 5.3 | 5.2 | 4.4 | 2.1 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.9 | 5.5 | 5.4 | 3.9 | 2.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.9 | 5.5 | 5.4 | 5.3 | 4.6 | 2.5 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.3 | 0.8 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | Burton 11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 33.1 | 32.5 | 32.1 | 31.7 | 31.1 | 29.9 | 26.4 | 24.7 | 22.5 | 20.2 | 18.7 | 16.7 | 14.3 | 12 | 6.9 | 0 | 0 | 0 | 0
Drakelow 132kV | Burton 11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 33.1 | 31.8 | 30.7 | 29.4 | 27.4 | 25 | 20.7 | 16.9 | 12.2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | Burton 11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 33.1 | 32 | 31.3 | 29.9 | 28.4 | 26.7 | 23.1 | 20.6 | 16.9 | 13.9 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | Burton 11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 33.1 | 31.9 | 31.2 | 30.3 | 28.5 | 26.5 | 22 | 19.2 | 15.3 | 12.1 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 47.7 | 46.7 | 46.2 | 45.7 | 44.8 | 42.3 | 38.9 | 35.9 | 32.1 | 28.6 | 23.9 | 19.2 | 13.7 | 8.3 | 4 | 0 | 0 | 0 | 0
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 47.7 | 45.6 | 43.8 | 41.9 | 37.8 | 33.1 | 28.1 | 19.7 | 10.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 47.7 | 46 | 44.6 | 41.5 | 38.8 | 35.3 | 31.4 | 26.5 | 19.2 | 13 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 47.7 | 45.9 | 44.8 | 43.5 | 40.2 | 37.1 | 33 | 27.4 | 19.2 | 12.6 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 76.5 | 69.8 | 69.5 | 69.1 | 68.6 | 65.8 | 58.7 | 54.3 | 48.7 | 44.1 | 36.1 | 30.5 | 25.2 | 21.6 | 20.7 | 19.9 | 19 | 14.2 | 8.9
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 76.5 | 69.2 | 68.4 | 67.4 | 64.7 | 59.6 | 51.6 | 44.2 | 36 | 29 | 22.9 | 16.8 | 12.2 | 7.8 | 6.3 | 4.6 | 3.2 | 0 | 0
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 76.5 | 69.4 | 68.7 | 65.4 | 62.8 | 55.2 | 48.2 | 41.6 | 34.1 | 27.8 | 22.6 | 18.1 | 13.6 | 11.9 | 10.3 | 8.7 | 7.5 | 1.1 | 0
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 76.5 | 69.3 | 68.8 | 68.1 | 65.7 | 61.9 | 56.2 | 49.1 | 41.4 | 34.9 | 28.8 | 22.5 | 18.2 | 13.9 | 9.8 | 8.6 | 7.8 | 4.6 | 2.3
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 51.6 | 30.9 | 29.4 | 28 | 26.2 | 24.2 | 30.5 | 28.3 | 25.8 | 23.9 | 22.2 | 19.7 | 15.9 | 12.3 | 8.9 | 5.6 | 2.3 | 0 | 0
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 51.6 | 30.2 | 27.9 | 25.5 | 22.5 | 19.3 | 24.9 | 21 | 16.8 | 12 | 8.2 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 51.6 | 30.5 | 28.6 | 26.7 | 24.5 | 22.4 | 28.7 | 25.8 | 22.1 | 18.8 | 15 | 8.9 | 3 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 51.6 | 30.4 | 28.4 | 26.4 | 23.8 | 21.3 | 26.8 | 23.5 | 19.6 | 16.2 | 12.5 | 7.1 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11 | 10.6 | 10.7 | 10.7 | 10.6 | 10 | 9.2 | 8.4 | 7.4 | 6.6 | 6.3 | 5.5 | 4.4 | 3.3 | 2.2 | 1.3 | 0 | 0 | 0
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11 | 10.3 | 10.1 | 9.7 | 8.5 | 7.1 | 5.9 | 4.1 | 2.6 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11 | 10.4 | 10.3 | 9.6 | 8.7 | 7.8 | 6.8 | 5.9 | 5 | 4.3 | 3.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11 | 10.4 | 10.3 | 10.1 | 9.2 | 8.3 | 7.3 | 6 | 4.6 | 3.7 | 2.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 2.9 | 2.9 | 2.9 | 2.9 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 2.8 | 2.7 | 2.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 2.9 | 2.9 | 2.7 | 2.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 2.9 | 2.8 | 2.7 | 2.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.1 | 11.9 | 11.8 | 11.6 | 11.4 | 10.5 | 9.8 | 9.8 | 9.6 | 9.4 | 9.1 | 8.8 | 8.6 | 8.5 | 8.1 | 7.9 | 7.6 | 6.2 | 4.3
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.1 | 11.7 | 11.5 | 11.2 | 10.1 | 9.6 | 8.9 | 8.4 | 7.4 | 6.6 | 5.9 | 5.3 | 4.6 | 4 | 3.4 | 2.7 | 2.2 | 0 | 0
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.1 | 11.8 | 11.6 | 10.6 | 10.4 | 10.1 | 9.4 | 9.4 | 9 | 8.5 | 8.1 | 7.5 | 6.9 | 6.2 | 5.6 | 5 | 4.6 | 1.8 | 0
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.1 | 11.8 | 11.6 | 11.4 | 10.3 | 10 | 9.3 | 9.1 | 8.4 | 7.9 | 7.3 | 6.6 | 6 | 5.4 | 5 | 4.5 | 4.2 | 3.1 | 1.9
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6 | 6 | 5.9 | 5.9 | 5.9 | 5.7 | 5.5 | 5.3 | 4.9 | 4.6 | 4.2 | 3.8 | 3.3 | 2.7 | 2.2 | 1.7 | 1.2 | 0 | 0
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6 | 5.9 | 5.8 | 5.7 | 5.3 | 4.8 | 4.4 | 3.8 | 3.1 | 2.3 | 1.7 | 1.3 | 0.9 | 0.5 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6 | 5.9 | 5.8 | 5.7 | 5.5 | 5.4 | 5.2 | 4.7 | 4 | 3.5 | 3 | 2.4 | 1.8 | 1.3 | 0.7 | 0 | 0 | 0 | 0
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6 | 5.9 | 5.9 | 5.8 | 5.6 | 5.2 | 4.8 | 4.2 | 3.5 | 2.8 | 2.1 | 1.3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.6 | 9.4 | 9.2 | 9.1 | 8.8 | 8 | 13.9 | 10.9 | 7.3 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.6 | 9.2 | 8.8 | 8.4 | 7.5 | 5.5 | 10.6 | 6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.6 | 9.2 | 9 | 8 | 7.1 | 2.1 | 8 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.6 | 9.2 | 9 | 8.7 | 8 | 6.8 | 14 | 9.4 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.6 | 6.4 | 5.4 | 4.6 | 3.3 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.6 | 6 | 4.7 | 3.3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.6 | 6.2 | 5.2 | 4.2 | 2.9 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.6 | 6.1 | 5 | 3.7 | 2.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.3 | 0.8 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | Banbury 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 32 | 29.9 | 29.8 | 29.8 | 29.5 | 29.4 | 26.9 | 26.2 | 23.9 | 22.7 | 20.2 | 17.5 | 14.9 | 12.5 | 10.8 | 0 | 0 | 0 | 0
East Claydon 132kV | Banbury 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 32 | 29.2 | 28.6 | 27.8 | 27 | 26.1 | 22.9 | 18.7 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | Banbury 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 32 | 29.4 | 28.9 | 28.5 | 27.9 | 26.8 | 21.7 | 17.2 | 12.8 | 10.3 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | Banbury 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 32 | 29.3 | 29 | 28.6 | 28 | 27.4 | 24.9 | 21.7 | 17.8 | 15.1 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17 | 16.7 | 16.5 | 16.1 | 15.6 | 15.2 | 14.2 | 13.7 | 13 | 12.5 | 12 | 11.1 | 10.2 | 9.2 | 8.2 | 7.3 | 6.4 | 1.9 | 0
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17 | 16.2 | 15.5 | 14.3 | 13.5 | 12.5 | 11 | 9.1 | 7.2 | 5.1 | 3.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17 | 16.4 | 15.8 | 15 | 14.3 | 13.6 | 12.3 | 11.1 | 9.7 | 8.5 | 7 | 4.6 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17 | 16.3 | 15.8 | 15 | 14.2 | 13.3 | 11.9 | 10.8 | 9.4 | 8.2 | 6.7 | 4.9 | 3.4 | 1.8 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 31.8 | 8.7 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 31.8 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 31.8 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 31.8 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15 | 5.9 | 5.9 | 5.8 | 5.8 | 5.8 | 5.7 | 5.6 | 5.4 | 5.4 | 5.3 | 5.1 | 4.8 | 4.5 | 4.2 | 3.9 | 3.6 | 2.1 | 0.8
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15 | 5.8 | 5.7 | 5.5 | 5.4 | 5.2 | 4.9 | 4.6 | 4.2 | 3.7 | 3.4 | 3.1 | 2.8 | 2.4 | 2.1 | 1.8 | 1.5 | 0 | 0
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15 | 5.9 | 5.8 | 5.6 | 5.5 | 5.5 | 5.3 | 5 | 4.6 | 4.3 | 3.9 | 3.5 | 3 | 2.5 | 2.1 | 1.6 | 1.2 | 0 | 0
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15 | 5.9 | 5.8 | 5.6 | 5.5 | 5.4 | 5.2 | 5 | 4.6 | 4.4 | 4 | 3.6 | 3.2 | 2.8 | 2.4 | 2.1 | 1.9 | 0.8 | 0
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 61.4 | 51.3 | 49.1 | 46.9 | 44.8 | 43.9 | 39.5 | 34.3 | 31.5 | 29.7 | 27.5 | 25 | 22.3 | 19.5 | 17.2 | 0 | 0 | 0 | 0
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 61.4 | 50.8 | 47.8 | 44.3 | 41.5 | 38.7 | 33.1 | 26.4 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 61.4 | 51 | 48.1 | 45.2 | 42.2 | 37.3 | 32.9 | 27.2 | 22.5 | 19.5 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 61.4 | 50.9 | 48.1 | 44.7 | 42.7 | 39.2 | 35.8 | 30.1 | 24.8 | 20.9 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.2 | 8.1 | 7.8 | 7.7 | 7.5 | 7.4 | 8 | 8 | 7.8 | 7.8 | 7.7 | 7.4 | 6.9 | 6.4 | 5.9 | 5.5 | 4.9 | 2.3 | 0
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.2 | 8 | 7.5 | 7.2 | 6.9 | 6.7 | 7 | 6.4 | 5.8 | 5.1 | 4.6 | 3.9 | 3.1 | 2.5 | 1.9 | 1.3 | 0.7 | 0 | 0
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.2 | 8 | 7.7 | 7.4 | 7.2 | 6.9 | 7.3 | 6.9 | 6.3 | 5.8 | 5.3 | 4.5 | 3.7 | 2.9 | 2.2 | 1.4 | 0.7 | 0 | 0
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.2 | 8 | 7.6 | 7.4 | 7 | 6.8 | 7.2 | 6.8 | 6.1 | 5.5 | 4.8 | 4 | 3.2 | 2.4 | 1.7 | 1 | 0.5 | 0 | 0
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 18.3 | 4.4 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 18.3 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 18.3 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 18.3 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.5 | 6.2 | 3.5 | 2.7 | 1.8 | 1.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.5 | 6 | 2.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.5 | 6.1 | 3.2 | 1.9 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.5 | 6.1 | 3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.5 | 4.1 | 3.8 | 3.4 | 3 | 2.6 | 2.1 | 1.6 | 1.2 | 1.2 | 1.2 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.5 | 4 | 3.5 | 3 | 2.5 | 1.9 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.5 | 4.1 | 3.6 | 3.2 | 2.8 | 2.2 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.5 | 4 | 3.6 | 3.1 | 2.6 | 2.1 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.9 | 6.2 | 5.9 | 5.8 | 5.7 | 5.6 | 6.2 | 6 | 5.7 | 5.6 | 5.4 | 4.9 | 4.2 | 3.5 | 2.8 | 2.3 | 1.8 | 0 | 0
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.9 | 5.9 | 5 | 4.7 | 4.4 | 4 | 4.2 | 3.3 | 2.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.9 | 6 | 5.1 | 4.9 | 4.6 | 4.1 | 4.3 | 3.8 | 3.2 | 2.7 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.9 | 6 | 5.5 | 5.3 | 5 | 4.6 | 4.8 | 4.2 | 3.3 | 2.6 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.3 | 3.1 | 3 | 2.9 | 2.7 | 2.6 | 1.8 | 1.6 | 1.2 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.3 | 2.7 | 2.2 | 1.7 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.3 | 2.8 | 2.4 | 2 | 1.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.3 | 2.8 | 2.5 | 2.1 | 1.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.2 | 6.3 | 5.7 | 5.7 | 5.7 | 5.7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.4 | 7.2 | 7.1 | 6.9 | 6.8 | 6.3 | 3.2 | 0
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.2 | 5.5 | 5.3 | 5.1 | 4.9 | 4.8 | 6.3 | 6.1 | 5.8 | 4.2 | 3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.2 | 5.5 | 5.2 | 4.9 | 4.6 | 4.3 | 5.8 | 5.7 | 5.6 | 5.5 | 5.4 | 4.1 | 2.8 | 1.6 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.2 | 5.5 | 5.4 | 5.4 | 5.3 | 5.2 | 6.9 | 6.7 | 6.6 | 6.5 | 5.7 | 4.6 | 3.9 | 3.1 | 2.4 | 1.4 | 0 | 0 | 0
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.5 | 6.9 | 6.8 | 6.7 | 6.6 | 6.6 | 6.7 | 6.6 | 6.3 | 6.1 | 5.8 | 5.4 | 4.7 | 3.9 | 3.2 | 2.5 | 1.9 | 0 | 0
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.5 | 6.6 | 6.2 | 5.7 | 5.3 | 4.8 | 4.8 | 3.7 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.5 | 6.7 | 6.3 | 6.1 | 5.7 | 5.4 | 5.4 | 4.6 | 3.8 | 2.9 | 1.9 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.5 | 6.7 | 6.4 | 6.2 | 5.9 | 5.6 | 5.7 | 5.1 | 4.2 | 3.4 | 2.5 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5 | 5 | 5 | 5 | 5 | 4.9 | 4.9 | 4.9 | 4.8 | 4.7 | 4.7 | 4.6 | 4.4 | 4.2 | 4.1 | 3.9 | 3.8 | 3 | 2.3
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5 | 4.9 | 4.9 | 4.8 | 4.8 | 4.7 | 4.6 | 4.4 | 4.2 | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 2.9 | 2.7 | 2.5 | 1.7 | 1.2
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5 | 5 | 4.9 | 4.9 | 4.9 | 4.8 | 4.8 | 4.6 | 4.4 | 4.2 | 4 | 3.7 | 3.4 | 3.2 | 2.9 | 2.6 | 2.4 | 1.5 | 0.9
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5 | 5 | 4.9 | 4.9 | 4.8 | 4.7 | 4.6 | 4.5 | 4.3 | 4.1 | 3.9 | 3.7 | 3.5 | 3.2 | 3 | 2.8 | 2.7 | 2 | 1.5
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.2 | 6.1 | 5.9 | 5.9 | 5.7 | 5.5 | 5.4 | 5.2 | 4.8 | 4.6 | 4.3 | 3.8 | 3.2 | 2.5 | 1.8 | 1.3 | 0.6 | 0 | 0
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.2 | 5.7 | 5.3 | 4.8 | 4.4 | 3.9 | 3.5 | 2.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.2 | 5.8 | 5.4 | 5.1 | 4.8 | 4.5 | 4 | 3.5 | 2.8 | 2.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.2 | 5.8 | 5.5 | 5.2 | 4.8 | 4.4 | 4 | 3.3 | 2.4 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.7 | 6.4 | 6.5 | 6.6 | 6.7 | 6.8 | 6.7 | 7 | 7 | 7.1 | 7.1 | 7 | 6.7 | 6.4 | 6.2 | 5.9 | 5.7 | 4.4 | 3.2
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.7 | 6.3 | 6.2 | 6.2 | 6.1 | 6.1 | 6 | 5.8 | 5.6 | 5.3 | 5.1 | 4.8 | 4.4 | 4.1 | 3.8 | 3.5 | 3.2 | 1.6 | 0
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.7 | 6.3 | 6.2 | 6.2 | 6.2 | 6.1 | 5.9 | 6.2 | 6 | 5.9 | 5.7 | 5.3 | 4.8 | 4.5 | 4 | 3.6 | 3.3 | 1.8 | 0.8
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.7 | 6.3 | 6.3 | 6.4 | 6.4 | 6.4 | 6.3 | 6.2 | 6.1 | 6 | 5.8 | 5.4 | 5.1 | 4.7 | 4.4 | 4.1 | 4 | 3 | 2.5
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6 | 5.8 | 5.7 | 5.5 | 5.4 | 5.2 | 5.2 | 4.9 | 4.3 | 3.9 | 3.4 | 2.7 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6 | 5.4 | 4.9 | 4.4 | 3.8 | 3.1 | 2.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6 | 5.5 | 5.1 | 4.7 | 4.4 | 4 | 3.8 | 3 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6 | 5.5 | 5.2 | 4.8 | 4.4 | 3.9 | 3.6 | 2.6 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.7 | 6.6 | 5.8 | 4.8 | 4 | 3.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.7 | 6.3 | 4.9 | 3.3 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.7 | 6.4 | 5.1 | 4.4 | 3.3 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.7 | 6.3 | 5.2 | 4 | 3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.5 | 10.3 | 9.9 | 9.4 | 8.9 | 8.6 | 4.4 | 4.2 | 3.8 | 3.5 | 3.2 | 2.7 | 2.1 | 1.3 | 0.6 | 0 | 0 | 0 | 0
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.5 | 10.1 | 9.3 | 8.3 | 7.7 | 7.1 | 2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.5 | 10.2 | 9.6 | 9 | 8.5 | 8.3 | 4.2 | 3.6 | 2.7 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.5 | 10.1 | 9.5 | 8.8 | 8.2 | 7.8 | 3.5 | 2.9 | 2.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.4 | 9.3 | 9.3 | 9.3 | 8.9 | 8.6 | 7.8 | 7.8 | 7.7 | 7.6 | 7.5 | 7.2 | 6.9 | 6.4 | 6 | 5.7 | 5.4 | 4.2 | 2.9
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.4 | 9.2 | 9 | 8.8 | 8.3 | 7.7 | 6.9 | 6.5 | 6.1 | 5.5 | 5 | 4.5 | 4 | 3.6 | 3.1 | 2.6 | 2.1 | 0 | 0
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.4 | 9.3 | 9 | 9 | 8.3 | 7.8 | 6.8 | 6.5 | 6 | 5.8 | 5.3 | 4.6 | 3.8 | 3 | 2.2 | 1.5 | 0.9 | 0 | 0
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.4 | 9.3 | 9.2 | 9.1 | 8.5 | 8.1 | 7.3 | 7 | 6.6 | 6.2 | 5.8 | 5.3 | 4.9 | 4.5 | 4.1 | 3.6 | 3.3 | 2.2 | 1.3
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.2 | 11.8 | 11.7 | 11.6 | 11.5 | 11.4 | 11.3 | 11.2 | 11 | 10.9 | 10.7 | 10.6 | 10.3 | 10 | 9.7 | 9.5 | 9.3 | 8.7 | 7.9
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.2 | 11.7 | 11.4 | 11.2 | 10.9 | 10.7 | 10.4 | 10 | 9.5 | 9 | 8.4 | 7.8 | 7.3 | 6.8 | 6.4 | 5.9 | 5.5 | 4.1 | 3.3
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.2 | 11.7 | 11.4 | 11.1 | 10.9 | 10.4 | 9.9 | 9.6 | 9.3 | 9.1 | 8.8 | 8.4 | 8 | 7.5 | 7.1 | 6.7 | 6.2 | 4.8 | 3.9
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.2 | 11.7 | 11.5 | 11.3 | 11.1 | 10.8 | 10.6 | 10.3 | 9.8 | 9.4 | 9 | 8.7 | 8.4 | 8.1 | 7.9 | 7.7 | 7.4 | 6.9 | 6.3
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.3 | 3.1 | 3 | 2.9 | 2.8 | 2.6 | 1.8 | 1.5 | 1.1 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.3 | 2.8 | 2.2 | 1.7 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.3 | 2.8 | 2.4 | 2 | 1.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.3 | 2.8 | 2.5 | 2.1 | 1.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 24.7 | 24.2 | 23 | 21.9 | 20.8 | 20.3 | 18.6 | 14.9 | 12.9 | 11.4 | 9.8 | 8.5 | 7.5 | 6.6 | 6 | 5.5 | 4.9 | 2.7 | 1
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 24.7 | 24.1 | 22.6 | 20.9 | 19.8 | 18.7 | 16.5 | 12.3 | 9.6 | 8 | 6.8 | 5.5 | 4.3 | 3.3 | 2.7 | 2.1 | 1.5 | 0 | 0
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 24.7 | 24.2 | 22.5 | 21 | 19.4 | 16.1 | 14.3 | 10.8 | 8.6 | 7.4 | 6.5 | 5.4 | 4.4 | 3.8 | 3.2 | 2.5 | 1.9 | 0 | 0
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 24.7 | 24.2 | 22.6 | 20.8 | 19.8 | 18.4 | 18.4 | 14.4 | 11.3 | 9.3 | 7.7 | 6.1 | 4.8 | 3.5 | 2.6 | 1.9 | 1.4 | 0 | 0
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.8 | 8.5 | 2.1 | 1.8 | 1.2 | 0.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.8 | 8.4 | 1.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.8 | 8.5 | 2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.8 | 8.4 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 28 | 24.7 | 15.9 | 12.7 | 8.8 | 5.8 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 28 | 23.2 | 12.9 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 28 | 23.7 | 13.9 | 8.9 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 28 | 23.6 | 14.1 | 9.2 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 25.1 | 25.1 | 24.4 | 23.2 | 21.6 | 19.8 | 17.5 | 15.6 | 13.1 | 12.1 | 10.3 | 10.1 | 9.6 | 9.2 | 8.7 | 8.3 | 7.8 | 5.6 | 3.7
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 25.1 | 24.9 | 24 | 22.6 | 20.8 | 18.8 | 16.4 | 13.9 | 11 | 9.3 | 7.1 | 6.7 | 6.1 | 5.5 | 4.9 | 4.3 | 3.6 | 0.7 | 0
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 25.1 | 25 | 24.1 | 22.9 | 21.3 | 19.4 | 17.3 | 15.3 | 12.5 | 11.1 | 9 | 8.2 | 7.4 | 6.5 | 5.7 | 5 | 4.4 | 1.6 | 0
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 25.1 | 25 | 24.2 | 22.9 | 21.1 | 19 | 16.6 | 14.4 | 11.6 | 10.2 | 8.1 | 7.4 | 6.7 | 6.1 | 5.4 | 5 | 4.7 | 3 | 2.3
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.9 | 3.8 | 3.7 | 3.6 | 3.5 | 3.5 | 3.4 | 3.1 | 3 | 2.8 | 2.5 | 2.1 | 1.7 | 1.2 | 0.9 | 0 | 0 | 0
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.8 | 3.6 | 3.3 | 3.1 | 2.9 | 2.7 | 2.2 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.8 | 3.7 | 3.6 | 3.5 | 3.4 | 3.3 | 2.9 | 2.3 | 1.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.8 | 3.7 | 3.5 | 3.3 | 3.1 | 3 | 2.6 | 2.2 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.3 | 10.2 | 9 | 7.5 | 6 | 5.8 | 7.4 | 4.6 | 4.3 | 4.1 | 3.9 | 3.2 | 2.3 | 1.5 | 0.7 | 0 | 0 | 0 | 0
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.3 | 10.1 | 8.7 | 6.7 | 4.9 | 3 | 4.4 | 2.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.3 | 10.1 | 8.8 | 7.1 | 5.2 | 3 | 5.2 | 2.9 | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 10.1 | 8.9 | 6.8 | 6.1 | 3.2 | 4.5 | 3 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.8 | 6.6 | 6.3 | 5.7 | 5.2 | 4.8 | 5.3 | 4.9 | 4.4 | 4.1 | 3.6 | 3 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.8 | 6.3 | 5.6 | 4.7 | 3.9 | 3.2 | 3.4 | 2.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.8 | 6.4 | 5.8 | 5.1 | 4.5 | 4 | 4.1 | 3.3 | 2.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.8 | 6.4 | 5.8 | 5 | 4.2 | 3.6 | 3.7 | 2.8 | 1.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.9 | 6.7 | 6.1 | 5 | 3.7 | 2.4 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.9 | 6.3 | 5.2 | 3.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.9 | 6.4 | 5.3 | 3.8 | 2.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.9 | 6.4 | 5.4 | 3.9 | 2.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.8 | 1.7 | 1.8 | 1.5 | 1 | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.8 | 1.7 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.8 | 1.7 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.8 | 1.7 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.8 | 3.4 | 3.1 | 2 | 1.2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.7 | 3.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.7 | 3.3 | 2.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.7 | 3.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.4 | 11.3 | 10.9 | 10.4 | 9.9 | 9.6 | 9.3 | 8.4 | 8.1 | 7.7 | 7.3 | 6.7 | 6.1 | 5.4 | 4.8 | 4.5 | 4.1 | 2 | 0
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.4 | 11.1 | 10.4 | 9.5 | 8.7 | 7.8 | 7 | 5.8 | 4.3 | 2.5 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.4 | 11.2 | 10.6 | 10 | 9.3 | 8.3 | 7.9 | 7 | 5.7 | 4.6 | 4.1 | 3.3 | 2.5 | 1.6 | 0.9 | 0 | 0 | 0 | 0
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.4 | 11.1 | 10.7 | 9.8 | 9.4 | 8.2 | 7.4 | 6.5 | 5.4 | 4 | 3 | 2 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.7 | 3.7 | 3.7 | 3.6 | 3.6 | 3.1 | 3 | 2.9 | 2.8 | 2.7 | 2.6 | 2.4 | 2.3 | 2.1 | 1.9 | 1.7 | 1 | 0
East Claydon 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3.7 | 3.6 | 3.5 | 3.4 | 3.3 | 2.8 | 2.5 | 2.3 | 2 | 1.8 | 1.6 | 1.4 | 1.2 | 1 | 0.8 | 0.6 | 0 | 0
East Claydon 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.7 | 3.7 | 3.6 | 3.6 | 3.6 | 3 | 2.9 | 2.6 | 2.4 | 2.2 | 1.9 | 1.6 | 1.3 | 1.1 | 0.8 | 0.6 | 0 | 0
East Claydon 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.7 | 3.6 | 3.6 | 3.5 | 3.5 | 2.9 | 2.7 | 2.5 | 2.3 | 2.1 | 1.8 | 1.5 | 1.1 | 0.9 | 0.6 | 0 | 0 | 0
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.5 | 7.3 | 7.2 | 6.7 | 6.1 | 5.3 | 4.4 | 4 | 3.5 | 3 | 2.8 | 2.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.5 | 7.1 | 6.8 | 5.9 | 4.9 | 3.5 | 2.1 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.5 | 7.2 | 7 | 6.2 | 5.2 | 3.9 | 2.5 | 2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.5 | 7.2 | 7.1 | 6.2 | 5.3 | 4 | 2.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.1 | 19.8 | 19.5 | 19.4 | 19.2 | 16.3 | 13.9 | 11.8 | 9.2 | 7.2 | 4.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.1 | 19.5 | 19 | 16.6 | 12.3 | 8.3 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.1 | 19.6 | 19.2 | 16.7 | 13.1 | 9.2 | 5.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.1 | 19.6 | 19.2 | 17.8 | 13.8 | 10.1 | 6.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.7 | 5.3 | 4 | 3.3 | 2.3 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.3 | 3.8 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.4 | 4 | 2.6 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.4 | 4.1 | 3.1 | 1.9 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 31.6 | 22.7 | 19.5 | 14.4 | 11.6 | 7 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 31.6 | 20.6 | 11.8 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 31.6 | 21.3 | 12.6 | 6.8 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 31.6 | 21.1 | 13.4 | 8.7 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.7 | 7.4 | 7.1 | 6.8 | 6.4 | 5.9 | 5.3 | 4.8 | 4.2 | 3.6 | 3 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.7 | 7.3 | 6.8 | 6.3 | 5.8 | 5.2 | 4.6 | 3.7 | 2.8 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.7 | 7.3 | 6.9 | 6.6 | 6.2 | 5.7 | 5.1 | 4.5 | 3.7 | 2.9 | 2.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.7 | 7.3 | 6.9 | 6.5 | 6 | 5.4 | 4.7 | 4 | 3.2 | 2.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.8 | 5.7 | 5.5 | 5.1 | 4.8 | 4.4 | 3.9 | 3.5 | 3 | 2.5 | 2.2 | 1.7 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.8 | 5.3 | 4.9 | 3.6 | 2.8 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.8 | 5.4 | 5.1 | 4.2 | 3.6 | 3 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.8 | 5.4 | 5.1 | 4.5 | 3.8 | 3.2 | 2.3 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | HINCKLEY 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 11.1 | 7.7 | 7.3 | 6.9 | 6.3 | 5.7 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | HINCKLEY 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 11.1 | 7.2 | 6.3 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | HINCKLEY 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 11.1 | 7.3 | 6.7 | 6 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | HINCKLEY 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 11.1 | 7.3 | 6.6 | 5.9 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.6 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 14 | 11.9 | 9.2 | 7.2 | 4.9 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.6 | 15.4 | 15.3 | 15.2 | 12.4 | 8.4 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.6 | 15.4 | 15.2 | 15.1 | 13.1 | 9.3 | 5.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.6 | 15.4 | 15.4 | 15.3 | 13.8 | 10.2 | 6.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.8 | 12.7 | 12.7 | 12.6 | 12.5 | 12.3 | 12.1 | 11.8 | 11.4 | 11.1 | 10.9 | 10.4 | 9.9 | 9.3 | 8.8 | 8.4 | 7.9 | 5.4 | 3.3
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.8 | 12.4 | 12.2 | 11.8 | 11.4 | 10.9 | 10.5 | 9.5 | 8.4 | 7.3 | 6.4 | 5.7 | 5 | 4.4 | 3.7 | 3 | 2.5 | 0 | 0
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.8 | 12.5 | 12.4 | 12.2 | 11.9 | 11.6 | 11.3 | 10.8 | 10.2 | 9.6 | 8.9 | 8.1 | 7.1 | 6.1 | 5.1 | 4.3 | 3.7 | 1.4 | 0.7
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.8 | 12.5 | 12.3 | 12 | 11.7 | 11.3 | 10.8 | 10.2 | 9.4 | 8.8 | 8.1 | 7.1 | 6.4 | 5.6 | 4.8 | 4.3 | 4 | 2.7 | 2.2
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14 | 13.5 | 12.8 | 11.5 | 10.7 | 9.9 | 8.8 | 7.9 | 6.7 | 5.7 | 4.6 | 3.3 | 2 | 0.7 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14 | 12.7 | 11.4 | 7.1 | 5.7 | 4.2 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14 | 12.9 | 11.6 | 7.8 | 6.6 | 5.4 | 4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14 | 12.8 | 11.7 | 9.9 | 8.6 | 7 | 5.3 | 3.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 4.3 | 2.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 4.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 4.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 5.1 | 5 | 4.8 | 4.6 | 4.4 | 4.1 | 3.7 | 3.2 | 2.6 | 2.1 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 5.1 | 4.6 | 4.1 | 3.4 | 2.7 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 5.1 | 4.7 | 4.3 | 3.8 | 3.2 | 2.6 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 5.1 | 4.7 | 4.3 | 3.8 | 3.1 | 2.5 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.1 | 19.1 | 19.2 | 19.1 | 19.1 | 19 | 18.9 | 19 | 19 | 19.1 | 19.2 | 19.1 | 19.2 | 19.2 | 19.3 | 19.5 | 19.5 | 19.5 | 19
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.1 | 18.9 | 18.9 | 18.3 | 18.2 | 18 | 17.9 | 17.7 | 17.3 | 16.9 | 16.6 | 16.1 | 15.6 | 15.3 | 14.9 | 14.6 | 14.3 | 13.2 | 12.9
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.1 | 19 | 19.1 | 18.5 | 18.4 | 18.5 | 18.5 | 18.6 | 18.8 | 18.9 | 18.9 | 18.6 | 18.2 | 18 | 17.8 | 17.6 | 17.4 | 15.6 | 14.5
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.1 | 18.9 | 19 | 18.8 | 18.7 | 18.5 | 18.3 | 18.4 | 18.4 | 18.2 | 18 | 17.5 | 17.3 | 17.1 | 17 | 16.9 | 16.9 | 16.8 | 15.8
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6 | 5.9 | 5.3 | 4.7 | 4 | 3.3 | 2.6 | 2 | 1.8 | 1.7 | 1.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6 | 5.8 | 5.1 | 4.3 | 3.5 | 2.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6 | 5.8 | 5.1 | 4.4 | 3.6 | 2.8 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6 | 5.8 | 5.2 | 4.4 | 3.6 | 2.7 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.5 | 12.3 | 12.2 | 12 | 11.8 | 11.5 | 11.2 | 11.2 | 11 | 10.9 | 10.8 | 10.3 | 10.1 | 9.9 | 9.6 | 9.3 | 8.9 | 6.7 | 4.2
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.5 | 11.9 | 11.6 | 10.8 | 10.2 | 9.7 | 9.1 | 7.9 | 6.8 | 5.3 | 3.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.5 | 12 | 11.9 | 11.5 | 11.3 | 10.9 | 10.5 | 10.2 | 8.9 | 7.5 | 6.2 | 3.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.5 | 12 | 11.7 | 11.3 | 10.9 | 10.4 | 9.8 | 9.4 | 8.9 | 8.2 | 7.2 | 5.8 | 5 | 4.1 | 3.5 | 2.8 | 2.5 | 0 | 0
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 6.8 | 6.6 | 6.4 | 6.1 | 5.8 | 5.3 | 3.4 | 2.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 6.8 | 6.2 | 5.6 | 4.8 | 3.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 6.8 | 6.3 | 6 | 5.6 | 4.8 | 3.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.3 | 5.9 | 5.3 | 4.2 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 7.8 | 7.6 | 7.4 | 7.1 | 6.8 | 6.5 | 6 | 5.5 | 4.8 | 4.2 | 3.6 | 2.9 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 7.8 | 7.2 | 6.7 | 5.9 | 5.2 | 4.3 | 3.4 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 7.8 | 7.3 | 6.9 | 6.4 | 5.9 | 5.4 | 4.8 | 3.8 | 2.6 | 1.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 7.8 | 7.3 | 6.9 | 6.4 | 5.8 | 5.2 | 4.5 | 3.4 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.3 | 4.2 | 4.2 | 3.9 | 3.6 | 3 | 1.7 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.3 | 4 | 3.7 | 3.1 | 2.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.3 | 4 | 3.8 | 3.4 | 2.8 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.3 | 4 | 3.8 | 3.3 | 2.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.5 | 3.3 | 2.9 | 2.6 | 2.3 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3.2 | 2.7 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.3 | 2.8 | 2.2 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.3 | 2.8 | 2 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.9 | 6.8 | 4.4 | 4.1 | 3.9 | 3.5 | 3.2 | 2.8 | 2.3 | 1.9 | 1.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.9 | 4.4 | 3.8 | 3.1 | 2.6 | 1.9 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.9 | 4.4 | 4 | 3.4 | 3.1 | 2.7 | 2.2 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.9 | 4.4 | 4 | 3.5 | 3 | 2.5 | 2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 18.9 | 18.6 | 18.3 | 18 | 17.5 | 17 | 16.3 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 18.9 | 18.1 | 17.3 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 18.9 | 18.3 | 17.5 | 16.7 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 18.9 | 18.2 | 17.7 | 17 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 13.4 | 13.1 | 9.7 | 9 | 8.2 | 6.6 | 4.6 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 13.4 | 9.6 | 7.9 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 13.4 | 9.7 | 8.6 | 6.7 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 13.4 | 9.7 | 9 | 7.1 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 2.4 | 2 | 1.7 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.7 | 8.6 | 8.3 | 8 | 7.8 | 7.5 | 7 | 6.6 | 6.1 | 5.7 | 5.1 | 4.4 | 3.6 | 2.7 | 1.8 | 1.1 | 0 | 0 | 0
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.7 | 8.2 | 7.6 | 6.5 | 5.6 | 4.7 | 3.7 | 2.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.7 | 8.4 | 8 | 7.3 | 6.9 | 6.4 | 5.8 | 5 | 3.9 | 3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.7 | 8.3 | 7.9 | 7.3 | 6.7 | 6.1 | 5.4 | 4.6 | 3.5 | 2.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.6 | 11.4 | 10.9 | 10.5 | 10.2 | 9.9 | 9.8 | 9.5 | 9.1 | 8.8 | 8.5 | 8.1 | 7.5 | 7 | 6.6 | 6.2 | 5.8 | 3.7 | 2
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.6 | 11.2 | 10.6 | 9.9 | 9.6 | 8.9 | 8.5 | 7.7 | 7 | 6 | 5.3 | 4.4 | 3.6 | 2.7 | 2 | 1.1 | 0 | 0 | 0
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.6 | 11.3 | 10.7 | 10.3 | 9.9 | 9.4 | 9.1 | 8.6 | 7.9 | 7.4 | 6.7 | 5.8 | 4.8 | 3.7 | 2.7 | 1.8 | 1.1 | 0 | 0
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.6 | 11.3 | 10.7 | 10.1 | 9.8 | 9.3 | 8.9 | 8.4 | 7.7 | 7.2 | 6.6 | 5.9 | 5.2 | 4.5 | 3.9 | 3.4 | 3.1 | 1.7 | 1.2
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15 | 14.5 | 13.5 | 12.4 | 11.2 | 10.2 | 8.9 | 7.7 | 6.2 | 5 | 3.7 | 2.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15 | 14 | 12.4 | 10.6 | 9 | 7.4 | 5.7 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15 | 14.2 | 12.7 | 11.1 | 9.7 | 8.3 | 6.8 | 5 | 2.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15 | 14.1 | 12.6 | 10.9 | 9.2 | 7.7 | 5.8 | 3.8 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.5 | 5.5 | 4.8 | 4 | 3.1 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.5 | 5.2 | 4.2 | 3.3 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.5 | 5.2 | 4.2 | 2.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.5 | 5.2 | 4.2 | 3.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.5 | 1.3 | 1.3 | 1.3 | 1.3 | 1.2 | 1.2 | 1.1 | 1 | 0.9 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.5 | 1.3 | 1.2 | 1.1 | 1 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.5 | 1.3 | 1.3 | 1.2 | 1.2 | 1 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.5 | 1.3 | 1.3 | 1.2 | 1.1 | 1 | 0.8 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.9 | 3.8 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.8 | 3.8 | 3.7 | 3.6 | 3.4 | 3.2 | 3 | 2.9 | 2.7 | 1.7 | 0.8
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.9 | 3.8 | 3.7 | 3.7 | 3.6 | 3.5 | 3.5 | 3.3 | 3.1 | 2.8 | 2.6 | 2.4 | 2.2 | 1.9 | 1.7 | 1.5 | 0 | 0 | 0
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.9 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.7 | 3.6 | 3.4 | 3.2 | 3.1 | 2.8 | 2.4 | 2.1 | 1.8 | 1.5 | 1.2 | 0 | 0
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.9 | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.6 | 3.5 | 3.3 | 3.1 | 2.9 | 2.7 | 2.4 | 2.1 | 1.9 | 1.6 | 1.5 | 0.7 | 0
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.2 | 7.5 | 7.5 | 7.3 | 6.9 | 6.8 | 6.7 | 6.5 | 6.3 | 6.4 | 6.3 | 6.1 | 5.6 | 5.3 | 5 | 4.7 | 4.4 | 2.7 | 0.9
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.2 | 7.5 | 7.3 | 6.6 | 6.3 | 5.9 | 5.6 | 5 | 4.4 | 3.9 | 3.5 | 3.1 | 2.6 | 2.2 | 1.8 | 1.4 | 1 | 0 | 0
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.2 | 7.5 | 7.4 | 7.1 | 6.8 | 6.6 | 6.4 | 6 | 5.5 | 5.3 | 5 | 4.5 | 3.9 | 3.4 | 2.8 | 2.3 | 1.9 | 0 | 0
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.2 | 7.5 | 7.4 | 6.9 | 6.6 | 6.3 | 5.9 | 5.5 | 5 | 4.8 | 4.4 | 3.8 | 3.4 | 2.9 | 2.4 | 2.1 | 1.8 | 0 | 0
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.2 | 19 | 18.4 | 17.7 | 17.1 | 15.9 | 14.9 | 14.6 | 14 | 13.4 | 12.8 | 12 | 11.3 | 10.5 | 9.9 | 9.4 | 8.8 | 5.9 | 3.2
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.2 | 18.5 | 17.5 | 16.1 | 14.4 | 13 | 11.9 | 10.4 | 8.7 | 6.7 | 5.1 | 3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.2 | 18.7 | 17.8 | 16.3 | 15.4 | 14.7 | 13.8 | 13.2 | 12.2 | 11.2 | 10 | 7.7 | 5.4 | 3.2 | 1.3 | 0 | 0 | 0 | 0
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.2 | 18.6 | 17.7 | 16.8 | 15.2 | 14 | 12.9 | 12.1 | 11.1 | 10 | 8.7 | 7.1 | 5.9 | 4.6 | 3.7 | 3 | 2.5 | 0 | 0
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.2 | 12.6 | 10.6 | 9.8 | 8.7 | 7.5 | 6.2 | 4.9 | 3.7 | 2.8 | 1.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.2 | 11.2 | 9.7 | 8.1 | 6.5 | 4.7 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.2 | 11.3 | 10.2 | 9 | 7.8 | 6.4 | 4.4 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.2 | 11.3 | 10 | 8.8 | 7.4 | 5.8 | 4 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.3 | 9 | 8.9 | 8.6 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.3 | 8.9 | 8.7 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.3 | 8.9 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.3 | 8.9 | 8.7 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.6 | 6.6 | 6.5 | 6.4 | 6.3 | 6.2 | 6 | 5.8 | 5.4 | 4.9 | 4.4 | 1.9 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 6.7 | 6.6 | 6.5 | 6.4 | 6.3 | 6.2 | 6 | 5.7 | 5 | 4.4 | 3.9 | 3.4 | 2.8 | 2.3 | 1.6 | 0.6 | 0 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 6.7 | 6.7 | 6.7 | 6.6 | 6.6 | 6.5 | 6.4 | 6.1 | 5.9 | 5.5 | 4.8 | 3.9 | 3 | 2.2 | 1.4 | 0 | 0 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.7 | 6.7 | 6.6 | 6.6 | 6.5 | 6.4 | 6.2 | 6 | 5.9 | 5.2 | 4.4 | 3.7 | 2.9 | 2.3 | 1.7 | 1.3 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.3 | 8.1 | 7.8 | 5.5 | 4.8 | 3.3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.3 | 7.9 | 5.5 | 4.7 | 2.9 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.3 | 8 | 5.8 | 4.3 | 3.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.3 | 8 | 5.8 | 5 | 3.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.4 | 9.3 | 9.2 | 9.1 | 8.9 | 8.7 | 8.4 | 8.1 | 7.8 | 7.5 | 7.3 | 6.8 | 5.8 | 4.7 | 3.7 | 2.8 | 1.7 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.4 | 9.2 | 8.9 | 8.5 | 8.1 | 7.7 | 7.2 | 6.1 | 4.7 | 3.1 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.4 | 9.2 | 9.1 | 8.9 | 8.6 | 8.4 | 8 | 7.5 | 6.7 | 5.6 | 4.2 | 2.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.4 | 9.2 | 9 | 8.8 | 8.5 | 8.1 | 7.7 | 7 | 5.8 | 4.6 | 3.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.3 | 4.2 | 3.4 | 2.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.3 | 3.8 | 2.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.3 | 3.9 | 2.8 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.3 | 3.9 | 2.7 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.5 | 9.5 | 9.6 | 9.7 | 9.7 | 9.8 | 9.8 | 9.9 | 9.9 | 9.9 | 9.9 | 9.7 | 8.9 | 8 | 6.4 | 4.6 | 3.7 | 2.8 | 2.2
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.5 | 9.4 | 9.5 | 9.5 | 9.6 | 9.6 | 9.6 | 9.4 | 9.3 | 9 | 8.1 | 6.5 | 5.2 | 4 | 3.2 | 2.9 | 2.7 | 1.9 | 1.4
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.5 | 9.5 | 9.6 | 9.6 | 9.7 | 9.6 | 9.4 | 9.1 | 8.8 | 8.1 | 6.8 | 5.8 | 4.6 | 3.6 | 3.2 | 2.9 | 2.7 | 1.7 | 1
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.5 | 9.5 | 9.5 | 9.6 | 9.6 | 9.6 | 9.6 | 9.5 | 9.2 | 8.9 | 8.2 | 6.6 | 5.2 | 4 | 3.1 | 2.7 | 2.6 | 1.8 | 1.2
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.3 | 7.2 | 7.2 | 7.1 | 7.1 | 7 | 6.9 | 6.8 | 6.3 | 6 | 5.6 | 5.2 | 4.7 | 4.2 | 3.6 | 3.1 | 2.6 | 0.5 | 0
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.3 | 7.2 | 7.1 | 7 | 6.8 | 6.3 | 5.9 | 5.3 | 4.6 | 3.9 | 3.5 | 3.1 | 2.6 | 2.3 | 2.1 | 1.8 | 1.5 | 0.7 | 0
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.3 | 7.2 | 7.2 | 7.1 | 7 | 7 | 6.7 | 6.4 | 5.8 | 5.3 | 4.8 | 4.3 | 3.7 | 3.2 | 2.8 | 2.3 | 2 | 0.9 | 0
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.3 | 7.2 | 7.1 | 7.1 | 6.9 | 6.6 | 6.2 | 5.6 | 4.9 | 4.2 | 3.5 | 2.8 | 2 | 1.3 | 0.6 | 0 | 0 | 0 | 0
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15 | 14.5 | 14.4 | 14.1 | 13.6 | 13.1 | 12.5 | 11.9 | 11.1 | 10.3 | 9.4 | 8.3 | 6.8 | 5.1 | 3.5 | 2.2 | 0.9 | 0 | 0
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15 | 14.1 | 13.7 | 13 | 11.9 | 11 | 10 | 8.3 | 6.3 | 4.3 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15 | 14.2 | 13.9 | 13.1 | 12.4 | 11.4 | 10.2 | 8.7 | 6.8 | 5.4 | 3.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15 | 14.2 | 14 | 13.4 | 12.3 | 11.4 | 10.2 | 8.8 | 6.9 | 5.3 | 3.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Hayfield | Primary Substation | 11 | Counterfactual | Headroom (MW) | 31.9 | 31.9 | 31.6 | 31.4 | 30.8 | 30.2 | 29.5 | 28.9 | 28.2 | 27.7 | 27 | 26.4 | 25.7 | 25.1 | 24.4 | 23.8 | 23.2 | 20.4 | 20.5
Grendon 132kV | Hayfield | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 31.9 | 31.9 | 31.6 | 31.3 | 30.7 | 30.1 | 29.5 | 28.8 | 28 | 27.3 | 26.6 | 25.8 | 24.9 | 24 | 23.1 | 22.1 | 21.3 | 17.4 | 17.4
Grendon 132kV | Hayfield | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 31.9 | 31.9 | 31.6 | 31.3 | 30.8 | 30.2 | 29.7 | 29 | 28.3 | 27.7 | 26.9 | 26.1 | 25.2 | 24.4 | 23.5 | 22.5 | 21.6 | 18 | 18
Grendon 132kV | Hayfield | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 31.9 | 31.9 | 31.6 | 31.4 | 30.7 | 30.1 | 29.4 | 28.7 | 28 | 27.4 | 26.8 | 26.2 | 25.6 | 25 | 24.4 | 23.8 | 23.3 | 20.7 | 20.7
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.7 | 2.6 | 2.3 | 1.9 | 1.8 | 1.7 | 1.3 | 1.1 | 1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.6 | 2.1 | 1.7 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.6 | 2.3 | 2 | 1.7 | 1.4 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.6 | 2.2 | 1.9 | 1.5 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.9 | 12.7 | 12.7 | 12.5 | 12.4 | 12.3 | 12 | 11.7 | 10.8 | 9.8 | 8.1 | 5.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.9 | 12.5 | 12.1 | 11.4 | 11.1 | 10.5 | 9.4 | 7.1 | 4.4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.9 | 12.6 | 12.2 | 11.7 | 10.9 | 9.7 | 8.2 | 6.4 | 4.4 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.9 | 12.6 | 12.2 | 11.5 | 11 | 10.1 | 8.8 | 7 | 4.9 | 2.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 54.7 | 29.7 | 25.1 | 20.3 | 14.6 | 9.8 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 54.7 | 27.6 | 20.7 | 13 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 54.7 | 28.1 | 21.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 54.7 | 28 | 21.9 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 42.8 | 30.7 | 25.7 | 13.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 42.8 | 27.4 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 42.8 | 27.9 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 42.8 | 27.8 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.1 | 15.1 | 15.1 | 15.1 | 15 | 15 | 15 | 14.9 | 14.9 | 14.8 | 14.8 | 14.7 | 14.5 | 14.4 | 14.2 | 14.1 | 13.9 | 13.1 | 12.3
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.1 | 15 | 14.8 | 14.7 | 14.6 | 14.4 | 14.3 | 14 | 13.7 | 13.4 | 13.2 | 12.9 | 12.7 | 12.5 | 12.3 | 12 | 11.8 | 10.8 | 10.3
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.1 | 15 | 14.9 | 14.8 | 14.6 | 14.5 | 14.4 | 14.3 | 14.1 | 14 | 13.8 | 13.6 | 13.4 | 13.1 | 12.9 | 12.7 | 12.6 | 11.7 | 11
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.1 | 15 | 14.9 | 14.9 | 14.8 | 14.7 | 14.6 | 14.4 | 14.2 | 14 | 13.8 | 13.5 | 13.3 | 13.1 | 12.9 | 12.8 | 12.7 | 12.1 | 11.7
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.6 | 8.5 | 8.5 | 8.4 | 8.3 | 8.2 | 8.1 | 7.9 | 7.5 | 7.2 | 6.8 | 6.3 | 5.7 | 5.1 | 4.5 | 3.9 | 3.2 | 0 | 0
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.6 | 8.4 | 8.1 | 7.7 | 7.5 | 7.1 | 6.6 | 5.7 | 4.7 | 3.8 | 3 | 2.3 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.6 | 8.4 | 8.2 | 8 | 7.7 | 7.3 | 7 | 6.4 | 5.8 | 5 | 4.1 | 3.2 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.6 | 8.4 | 8.2 | 7.9 | 7.7 | 7.3 | 6.9 | 6.2 | 5.5 | 4.9 | 4.2 | 3.3 | 2.5 | 1.7 | 0.9 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 65.2 | 32.3 | 19.3 | 9.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 65.2 | 25.6 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 65.2 | 27.5 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 65.2 | 26.9 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.7 | 4.9 | 2.7 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.7 | 4.3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.7 | 4.5 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.7 | 4.4 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.2 | 7.8 | 7.9 | 7.8 | 7.7 | 7.5 | 7.3 | 7.1 | 6.7 | 6.5 | 6.2 | 5.7 | 5.1 | 4.4 | 3.6 | 2.2 | 0.9 | 0 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.2 | 7.5 | 7.3 | 6.9 | 6.5 | 6.1 | 5.6 | 4.7 | 3.7 | 2.5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.2 | 7.6 | 7.5 | 7.2 | 6.9 | 6.5 | 6.1 | 5.4 | 4.6 | 3.8 | 2.9 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.2 | 7.6 | 7.5 | 7.2 | 6.9 | 6.5 | 6 | 5.3 | 4.4 | 3.6 | 2.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.1 | 8.5 | 8.5 | 8.5 | 8.4 | 8.4 | 8.4 | 8.3 | 8.3 | 8.2 | 8.2 | 8.1 | 8 | 7.9 | 7.8 | 7.8 | 7.7 | 7.3 | 6.9
Grendon 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.1 | 8.5 | 8.4 | 8.4 | 8.3 | 8.3 | 8.2 | 8.1 | 8 | 7.9 | 7.7 | 7.6 | 7.5 | 7.4 | 7.3 | 7.2 | 7.1 | 6.8 | 6.6
Grendon 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.1 | 8.5 | 8.5 | 8.4 | 8.4 | 8.4 | 8.3 | 8.2 | 8.1 | 8 | 7.9 | 7.7 | 7.6 | 7.5 | 7.4 | 7.2 | 7.1 | 6.7 | 6.4
Grendon 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.1 | 8.5 | 8.5 | 8.4 | 8.4 | 8.3 | 8.2 | 8.2 | 8 | 7.9 | 7.8 | 7.6 | 7.5 | 7.4 | 7.3 | 7.1 | 7.1 | 6.7 | 6.5
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.4 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.1 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 18.2 | 17.4 | 15 | 9.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 18.2 | 16.8 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 18.2 | 17 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 18.2 | 16.9 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.3 | 13.9 | 13.2 | 12.7 | 12.2 | 11 | 9.9 | 8.8 | 7.9 | 7.2 | 6.6 | 5.8 | 4.9 | 3.9 | 3 | 2.3 | 1.5 | 0 | 0
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.3 | 13.3 | 11.3 | 10.3 | 8.5 | 6.8 | 5.2 | 3.3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.3 | 13.4 | 11.5 | 9.8 | 8.2 | 6.7 | 5.6 | 4.7 | 3.4 | 2.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.3 | 13.4 | 12.3 | 11.4 | 9.8 | 8.2 | 6.5 | 5.3 | 4 | 2.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 9.8 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 9.8 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.6 | 10.5 | 10.4 | 10.4 | 10.3 | 10.1 | 10 | 9.8 | 9.4 | 9.2 | 9 | 8.6 | 8 | 7.5 | 6.9 | 6.4 | 5.8 | 3.3 | 1.2
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.6 | 10.3 | 10 | 9.5 | 9.2 | 8.8 | 8.3 | 7.5 | 6.6 | 5.7 | 4.9 | 4.1 | 3.4 | 2.6 | 1.9 | 1 | 0 | 0 | 0
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.6 | 10.4 | 10.2 | 9.8 | 9.6 | 9.4 | 9.2 | 8.7 | 8 | 7.5 | 6.8 | 5.9 | 4.8 | 3.7 | 2.6 | 1.7 | 0.9 | 0 | 0
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.6 | 10.3 | 10.2 | 9.9 | 9.6 | 9.4 | 9 | 8.5 | 7.9 | 7.3 | 6.7 | 5.8 | 5.1 | 4.3 | 3.6 | 3.1 | 2.7 | 1 | 0
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 9.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 9.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.5 | 8.3 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7.1 | 6.3 | 5.7 | 5 | 4.1 | 3.3 | 2.4 | 1.6 | 1.1 | 0.6 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.5 | 8.1 | 7.4 | 6.7 | 6.2 | 5.7 | 5.3 | 3.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.5 | 8.2 | 7.6 | 7.3 | 7.1 | 6.9 | 6 | 4.8 | 3.3 | 2.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.5 | 8.1 | 7.6 | 7.2 | 6.7 | 6.3 | 5.9 | 4.8 | 3.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 10.2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 10.2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 6.4 | 5.8 | 5.6 | 5.4 | 5.1 | 4.7 | 4.4 | 3.9 | 3.5 | 3.1 | 2.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 6.2 | 5.3 | 4.9 | 4.4 | 3.8 | 3.3 | 2.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 6.2 | 5.4 | 5.1 | 4.8 | 4.5 | 4 | 3 | 2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 6.2 | 5.5 | 5.1 | 4.6 | 4.1 | 3.5 | 2.7 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 36.3 | 32 | 19.1 | 9.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 36.3 | 25.4 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 36.3 | 27.3 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 36.3 | 26.7 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15 | 14.9 | 12.8 | 10.5 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15 | 14.8 | 9.7 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15 | 14.8 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15 | 14.8 | 10.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.8 | 2.6 | 2.3 | 2 | 1.8 | 1.7 | 1.3 | 1.1 | 1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.6 | 2.1 | 1.7 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.7 | 2.3 | 2 | 1.7 | 1.4 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.6 | 2.2 | 1.9 | 1.5 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.8 | 1.6 | 1.6 | 1.5 | 1.4 | 1.3 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.8 | 1.5 | 1.3 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.8 | 1.6 | 1.5 | 1.4 | 1.2 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.8 | 1.5 | 1.4 | 1.2 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.4 | 9.1 | 8.8 | 8.6 | 8.5 | 8.3 | 8.1 | 8 | 8 | 8 | 7.9 | 7.9 | 7.8 | 7.7 | 7.7 | 7.6 | 7.6 | 7.1 | 6.3
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.4 | 9 | 8.7 | 8.5 | 8.3 | 8 | 7.8 | 7.6 | 7.5 | 7.3 | 7.1 | 6.8 | 6.5 | 6.1 | 5.6 | 5 | 0 | 0 | 0
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.4 | 9 | 8.7 | 8.5 | 8.3 | 8 | 7.7 | 7.6 | 7.5 | 7.4 | 7.3 | 7.2 | 6.9 | 6.5 | 5.9 | 5.4 | 4.9 | 0 | 0
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.4 | 9 | 8.6 | 8.4 | 8.2 | 7.8 | 7.5 | 7.4 | 7.4 | 7.3 | 7.2 | 7.1 | 7 | 6.8 | 6.5 | 6.2 | 5.9 | 5 | 4.4
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.4 | 13.3 | 13.1 | 12.9 | 12.7 | 12.4 | 12 | 11.7 | 11.4 | 11.2 | 10.9 | 10.5 | 9.9 | 9.4 | 8.6 | 7.4 | 6.2 | 0 | 0
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.4 | 13.2 | 12.9 | 12.5 | 12.1 | 11.7 | 11.2 | 10.5 | 9.1 | 6.9 | 5.2 | 3.8 | 2.2 | 0.9 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.4 | 13.2 | 13 | 12.8 | 12.5 | 12.2 | 11.8 | 11.3 | 10.7 | 9.8 | 8.2 | 6.4 | 4.6 | 2.8 | 1.1 | 0 | 0 | 0 | 0
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.4 | 13.2 | 13 | 12.7 | 12.3 | 11.9 | 11.4 | 10.8 | 10.2 | 9.2 | 7.3 | 5.3 | 3.7 | 1.8 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.8 | 5.7 | 5.6 | 5.5 | 5.5 | 5.3 | 5.2 | 5 | 4.9 | 4.7 | 4.5 | 4.2 | 3.9 | 3.5 | 3.2 | 2.9 | 1.3 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.7 | 5.5 | 5.3 | 5.1 | 4.8 | 4.6 | 4.1 | 3.5 | 3 | 2.5 | 1.9 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.7 | 5.6 | 5.5 | 5.3 | 5.1 | 4.9 | 4.5 | 4 | 3.5 | 3 | 2.4 | 1.7 | 1.1 | 0.5 | 0 | 0 | 0 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.7 | 5.6 | 5.4 | 5.2 | 5 | 4.8 | 4.4 | 4 | 3.5 | 3 | 2.4 | 1.9 | 1.3 | 0.9 | 0 | 0 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.8 | 14.2 | 11.1 | 7.4 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.8 | 13.6 | 9.5 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.8 | 13.7 | 9.8 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.8 | 13.7 | 9.8 | 5.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.5 | 14.9 | 14.9 | 14.6 | 14 | 13.5 | 12.9 | 12.2 | 11.4 | 10.6 | 9.7 | 8.5 | 7 | 5.2 | 3.6 | 2.2 | 0.9 | 0 | 0
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.5 | 14.5 | 14.1 | 13.4 | 12.3 | 11.3 | 10.3 | 8.5 | 6.5 | 4.5 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.5 | 14.7 | 14.3 | 13.5 | 12.8 | 11.8 | 10.5 | 8.9 | 7 | 5.5 | 3.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.5 | 14.6 | 14.4 | 13.8 | 12.7 | 11.7 | 10.5 | 9 | 7.1 | 5.4 | 3.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10 | 9.8 | 9.7 | 9.6 | 9.4 | 9.2 | 9 | 8.8 | 8.3 | 7.9 | 7.5 | 6.9 | 6.2 | 5.4 | 4.7 | 4 | 3.2 | 0 | 0
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10 | 9.5 | 9 | 8.5 | 7.9 | 7.2 | 6.6 | 5.5 | 4.3 | 3.1 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10 | 9.5 | 9 | 8.6 | 8.1 | 7.6 | 6.9 | 6.2 | 5.4 | 4.7 | 3.8 | 2.7 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10 | 9.5 | 9.2 | 8.9 | 8.6 | 8.1 | 7.5 | 6.6 | 5.6 | 4.6 | 3.5 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.9 | 3.8 | 3.8 | 3.7 | 3.6 | 3.5 | 3.4 | 3.2 | 3 | 2.8 | 2.6 | 2.3 | 2 | 1.7 | 1.3 | 1 | 0.6 | 0 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.9 | 3.7 | 3.6 | 3.4 | 3.2 | 3 | 2.7 | 2.2 | 1.8 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.9 | 3.8 | 3.7 | 3.7 | 3.6 | 3.5 | 3.3 | 2.9 | 2.5 | 2.1 | 1.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.9 | 3.8 | 3.7 | 3.6 | 3.4 | 3.2 | 2.9 | 2.6 | 2.2 | 1.7 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 24.8 | 24.7 | 24.7 | 24.7 | 24.7 | 19.4 | 13.6 | 8.2 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 24.8 | 24.6 | 24.4 | 24.3 | 18.3 | 10.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 24.8 | 24.6 | 24.5 | 24.4 | 19.4 | 12.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 24.8 | 24.6 | 24.5 | 24.4 | 19.7 | 12.1 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 41 | 39.1 | 34.4 | 30.3 | 25.4 | 19.4 | 13.6 | 8.2 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 41 | 36.7 | 31.6 | 25.8 | 18.3 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 41 | 37.1 | 32.4 | 26.1 | 19.4 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 41 | 37 | 32.4 | 27.1 | 19.7 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.6 | 13.4 | 13.3 | 13.1 | 12.9 | 12.7 | 12.5 | 12.1 | 11.5 | 11.1 | 10.7 | 10.1 | 9.3 | 8.5 | 7.7 | 6.9 | 6.1 | 2.5 | 0
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.6 | 13.1 | 12.7 | 12 | 11.4 | 10.8 | 10 | 8.7 | 7.2 | 5.7 | 4.6 | 3.4 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.6 | 13.3 | 13 | 12.6 | 12.3 | 12 | 11.7 | 10.9 | 9.9 | 8.9 | 8 | 6.4 | 4.7 | 3.1 | 1.4 | 0 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.6 | 13.2 | 13 | 12.5 | 12.2 | 11.8 | 11.4 | 10.6 | 9.5 | 8.5 | 7.5 | 6.4 | 5.3 | 4.2 | 3.2 | 2.5 | 2 | 0 | 0
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.7 | 7.3 | 6.5 | 5.6 | 4.6 | 3.5 | 2.5 | 1.9 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.7 | 7 | 5.8 | 4.5 | 3.3 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.7 | 7.1 | 6.1 | 5 | 3.9 | 2.7 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.7 | 7.1 | 6 | 4.7 | 3.5 | 2.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.7 | 11.5 | 11.3 | 11.1 | 11 | 10.7 | 10.2 | 9.3 | 7.8 | 6.1 | 4.4 | 2.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.7 | 11.3 | 10.7 | 10.1 | 9.6 | 9 | 8 | 5.3 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.7 | 11.4 | 10.8 | 10.2 | 9.7 | 9.2 | 8 | 5.5 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.7 | 11.4 | 10.8 | 10.3 | 9.7 | 9.1 | 8.1 | 6.2 | 4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.4 | 17.1 | 16.9 | 16.6 | 16.3 | 16 | 15.6 | 15.3 | 14.8 | 14.4 | 14 | 13.3 | 12.2 | 11 | 9.9 | 8.9 | 8.1 | 4.4 | 0.6
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.4 | 16.6 | 15.9 | 15.2 | 14.5 | 13.6 | 12.8 | 11.4 | 9.6 | 7.5 | 5.5 | 3.8 | 2.5 | 1.3 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.4 | 16.8 | 16 | 15.5 | 15 | 14.3 | 13.5 | 12.4 | 10.9 | 9.8 | 8.8 | 7.5 | 6.1 | 4.8 | 3.4 | 2.1 | 1.1 | 0 | 0
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.4 | 16.7 | 16.2 | 15.7 | 15.1 | 14.5 | 13.8 | 12.8 | 11.3 | 9.7 | 8.1 | 6.6 | 5.5 | 4.3 | 3.2 | 2.3 | 1.7 | 0 | 0
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.8 | 11.6 | 11.5 | 11.3 | 11.1 | 10.8 | 10.5 | 10.2 | 9.6 | 9.1 | 8.5 | 8 | 7.4 | 6.7 | 6.1 | 5.6 | 4.9 | 2 | 0
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.8 | 11.3 | 10.9 | 10.4 | 9.8 | 9.1 | 8.4 | 7.2 | 5.8 | 4.6 | 3.7 | 2.8 | 1.8 | 0.8 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.8 | 11.4 | 11.1 | 10.6 | 10.1 | 9.5 | 9.1 | 8.4 | 7.6 | 6.9 | 6 | 4.9 | 3.6 | 2.2 | 0.9 | 0 | 0 | 0 | 0
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.8 | 11.4 | 11.1 | 10.7 | 10.2 | 9.6 | 8.9 | 8.1 | 7.2 | 6.5 | 5.7 | 4.7 | 3.9 | 3 | 2.1 | 1.5 | 1 | 0 | 0
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.6 | 6.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.6 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.6 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.7 | 7.6 | 7.6 | 7.5 | 7.4 | 7.3 | 7.3 | 7.2 | 7 | 6.9 | 6.7 | 6.5 | 6.1 | 5.8 | 5.4 | 5.1 | 4.8 | 3 | 1.4
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.7 | 7.5 | 7.3 | 7.1 | 6.8 | 6.6 | 6.4 | 5.9 | 5.4 | 5 | 4.6 | 4.3 | 3.9 | 3.5 | 3.1 | 2.6 | 2.1 | 0 | 0
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.7 | 7.5 | 7.4 | 7.1 | 7 | 6.9 | 6.8 | 6.4 | 6.1 | 5.9 | 5.6 | 5.1 | 4.5 | 4 | 3.4 | 2.8 | 2.3 | 0 | 0
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.7 | 7.5 | 7.4 | 7.2 | 7 | 6.9 | 6.7 | 6.2 | 5.9 | 5.6 | 5.3 | 4.8 | 4.4 | 3.9 | 3.4 | 3 | 2.8 | 1.3 | 0.6
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.5 | 2.4 | 2.2 | 2.1 | 2 | 1.9 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.5 | 2.2 | 1.8 | 1.5 | 1.3 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.5 | 2.3 | 1.9 | 1.8 | 1.6 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.5 | 2.3 | 2 | 1.7 | 1.5 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.5 | 10.2 | 10 | 9.8 | 9.5 | 9.2 | 8.8 | 8.3 | 7.5 | 6.9 | 6.2 | 5.2 | 4 | 2.6 | 1.1 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.5 | 9.7 | 8.9 | 8.1 | 7.2 | 6.3 | 5.3 | 3.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.5 | 9.9 | 9.2 | 8.8 | 8.3 | 7.6 | 6.9 | 5.7 | 4.1 | 2.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.5 | 9.8 | 9.4 | 8.9 | 8.3 | 7.6 | 6.6 | 5.3 | 3.7 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 11.1 | 10.8 | 10.5 | 10.2 | 9.8 | 9.4 | 9.1 | 8.7 | 8.1 | 7.7 | 7.3 | 6.6 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 11.1 | 10.3 | 9.5 | 8.5 | 7.7 | 6.7 | 5.9 | 4.4 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 11.1 | 10.4 | 9.6 | 8.9 | 8.2 | 7.5 | 6.7 | 5.8 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 11.1 | 10.4 | 9.8 | 9.1 | 8.4 | 7.6 | 6.8 | 5.9 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 47.2 | 45.8 | 43.6 | 41 | 38.3 | 35.9 | 33.1 | 29.1 | 25.3 | 22.1 | 19.3 | 14.5 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 47.2 | 44.1 | 39.6 | 35.1 | 31.2 | 25.1 | 19.9 | 11.7 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 47.2 | 44.6 | 39.7 | 37.2 | 32.8 | 27.5 | 22.3 | 15.3 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 47.2 | 44.5 | 40.8 | 37.1 | 33.6 | 28.4 | 23.3 | 16.9 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 9.8 | 9.1 | 8.5 | 8 | 7.1 | 6.2 | 5.3 | 4.3 | 2.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 9.8 | 8.4 | 7.2 | 5.8 | 4.3 | 2.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 9.8 | 8.6 | 7.7 | 6.8 | 5.7 | 4.4 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 9.8 | 8.6 | 7.5 | 6.4 | 4.8 | 3.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.1 | 8.1 | 8 | 7.9 | 7.9 | 7.8 | 7.8 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.6 | 7.6 | 7.5 | 7.4 | 7.4 | 7.1 | 6.8
Ratcliffe 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.1 | 8.1 | 7.9 | 7.9 | 7.8 | 7.7 | 7.7 | 7.6 | 7.5 | 7.4 | 7.4 | 7.3 | 7.2 | 7.2 | 7.1 | 7 | 7 | 6.7 | 6.5
Ratcliffe 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.1 | 8.1 | 8 | 7.9 | 7.9 | 7.8 | 7.8 | 7.7 | 7.6 | 7.6 | 7.5 | 7.4 | 7.3 | 7.2 | 7.1 | 7 | 6.9 | 6.6 | 6.4
Ratcliffe 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.1 | 8.1 | 8 | 7.9 | 7.8 | 7.8 | 7.7 | 7.6 | 7.5 | 7.5 | 7.4 | 7.3 | 7.2 | 7.1 | 7.1 | 7 | 6.9 | 6.7 | 6.5
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.3 | 2 | 1.8 | 1.5 | 1.3 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.3 | 1.7 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.3 | 1.8 | 1.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.3 | 1.8 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.3 | 6.7 | 6.1 | 5.3 | 4.4 | 4.1 | 3.6 | 2.9 | 2.1 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.3 | 6.6 | 5.9 | 5 | 3.9 | 3.4 | 2.8 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.3 | 6.6 | 5.9 | 5 | 3.9 | 3.4 | 2.7 | 2.1 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.3 | 6.6 | 5.9 | 5.1 | 4 | 3.5 | 2.8 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.7 | 5.5 | 4.7 | 4 | 3.1 | 2.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.7 | 5.2 | 3.9 | 2.9 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.7 | 5.3 | 3.8 | 3.1 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.7 | 5.3 | 4.2 | 3.2 | 2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.2 | 1.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.2 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.5 | 6.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.5 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.5 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.5 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.8 | 6.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.8 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.8 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.8 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.7 | 6.5 | 6 | 5.7 | 5.3 | 4.9 | 4.4 | 3.9 | 2.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.7 | 6.1 | 5.1 | 4.1 | 3.3 | 2.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.7 | 6.2 | 5.3 | 4.6 | 3.9 | 2.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.7 | 6.2 | 5.4 | 4.7 | 4 | 3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 22.3 | 20.9 | 19.4 | 17.9 | 16.2 | 14.8 | 12.9 | 10.6 | 6.6 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 22.3 | 19.6 | 16.4 | 13.1 | 9.6 | 6.1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 22.3 | 20 | 17.2 | 14.6 | 11.7 | 8.6 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 22.3 | 19.9 | 17.5 | 14.9 | 12 | 8.8 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.5 | 14.4 | 14.3 | 14.3 | 14.3 | 14.2 | 14.1 | 13.9 | 13.4 | 13 | 12.6 | 12.1 | 11.4 | 10.6 | 9.9 | 9.1 | 8.4 | 4.8 | 1.4
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.5 | 14.3 | 14.2 | 14 | 13.8 | 13.3 | 12.9 | 12 | 11 | 10 | 9.1 | 8.3 | 7.4 | 6.8 | 6.2 | 5.6 | 5.1 | 3.2 | 1.9
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.5 | 14.3 | 14.3 | 14.2 | 14.2 | 14.1 | 13.5 | 12.8 | 11.9 | 11.2 | 10.3 | 9.4 | 8.5 | 7.7 | 6.9 | 6.1 | 5.4 | 3 | 1.3
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.5 | 14.3 | 14.2 | 14.2 | 14 | 13.6 | 13 | 12.3 | 11 | 10 | 8.7 | 7.4 | 6.3 | 5.1 | 4.2 | 3.1 | 2.4 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 27.8 | 26.7 | 25.6 | 24 | 22.9 | 21.7 | 19.8 | 17.2 | 13.5 | 10 | 6.8 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 27.8 | 25.6 | 23 | 19.6 | 16.9 | 13.5 | 9.4 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 27.8 | 26.1 | 23.2 | 21 | 18.8 | 16.2 | 11.6 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 27.8 | 26 | 23.9 | 21.1 | 18.8 | 16.1 | 12.1 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stalybridge 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.5 | 17.4 | 17.3 | 17.3 | 17.2 | 17.1 | 17.2 | 17.2 | 16.9 | 16.7 | 16.5 | 16.2 | 15.8 | 15.3 | 14.9 | 14.5 | 14 | 12 | 9.8
Stalybridge 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.5 | 17.3 | 17.1 | 16.9 | 16.7 | 16.4 | 16.5 | 15.9 | 15.3 | 14.6 | 14.1 | 13.7 | 13.2 | 12.6 | 12 | 11.5 | 11 | 9 | 7.5
Stalybridge 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.5 | 17.3 | 17.3 | 17.2 | 17.1 | 17 | 17.1 | 16.7 | 16.1 | 15.6 | 15 | 14.3 | 13.6 | 12.9 | 12.2 | 11.5 | 10.9 | 8.6 | 7
Stalybridge 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.5 | 17.3 | 17.2 | 17.1 | 16.9 | 16.7 | 16.7 | 16.4 | 15.8 | 15.3 | 14.8 | 14.1 | 13.4 | 12.6 | 12.1 | 11.4 | 11 | 9.3 | 8.4
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.7 | 6.5 | 6.5 | 6.5 | 6.5 | 6.4 | 7 | 7 | 6.9 | 6.9 | 6.9 | 6.7 | 6.4 | 6.2 | 5.9 | 5.6 | 5.3 | 3.9 | 2.3
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.7 | 6.4 | 6.4 | 6.2 | 6.1 | 6 | 6.5 | 6.3 | 6 | 5.7 | 5.4 | 5.1 | 4.6 | 4.2 | 3.8 | 3.4 | 3 | 1.9 | 1.3
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.7 | 6.4 | 6.4 | 6.4 | 6.3 | 6.3 | 6.8 | 6.7 | 6.5 | 6.3 | 6 | 5.5 | 5 | 4.6 | 4.1 | 3.7 | 3.3 | 1.9 | 0.9
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.7 | 6.4 | 6.4 | 6.3 | 6.2 | 6 | 6.6 | 6.4 | 6.1 | 5.8 | 5.5 | 5 | 4.5 | 3.9 | 3.5 | 3.1 | 2.7 | 1.6 | 0.8
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.7 | 6.5 | 6.6 | 6.6 | 6.5 | 6.5 | 7.1 | 7.1 | 7 | 7 | 7 | 6.8 | 6.5 | 6.2 | 5.9 | 5.7 | 5.4 | 4 | 2.4
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.7 | 6.5 | 6.4 | 6.3 | 6.2 | 6 | 6.6 | 6.3 | 6.1 | 5.8 | 5.5 | 5.2 | 4.7 | 4.2 | 3.9 | 3.4 | 3.1 | 1.9 | 1.3
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.7 | 6.5 | 6.5 | 6.5 | 6.4 | 6.3 | 6.9 | 6.7 | 6.5 | 6.4 | 6.1 | 5.6 | 5.1 | 4.6 | 4.2 | 3.7 | 3.3 | 1.9 | 0.9
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.7 | 6.5 | 6.5 | 6.4 | 6.3 | 6.1 | 6.6 | 6.4 | 6.2 | 5.9 | 5.5 | 5 | 4.6 | 4 | 3.6 | 3.1 | 2.8 | 1.6 | 0.8
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.1 | 12 | 12 | 12 | 12 | 11.9 | 11.8 | 11.6 | 11.2 | 10.8 | 10.4 | 9.9 | 9.3 | 8.7 | 8 | 7.4 | 6.8 | 4.2 | 1.8
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.1 | 12 | 12 | 11.8 | 11.6 | 11.1 | 10.6 | 9.9 | 9 | 8.3 | 7.6 | 7 | 6.4 | 5.9 | 5.6 | 5.2 | 4.9 | 4.1 | 3.5
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.1 | 12 | 12 | 11.9 | 11.8 | 11.7 | 11.3 | 10.8 | 10.1 | 9.5 | 8.9 | 8.2 | 7.5 | 6.9 | 6.4 | 5.8 | 5.4 | 4.2 | 3.4
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.1 | 12 | 12 | 11.9 | 11.8 | 11.4 | 10.8 | 10.2 | 9.2 | 8.4 | 7.4 | 6.5 | 5.5 | 4.6 | 3.8 | 3 | 2.5 | 0.8 | 0
Staythorpe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.5 | 7.2 | 6.8 | 4.3 | 3.9 | 3.3 | 2.7 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.5 | 6.9 | 4 | 3.1 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.5 | 7 | 4.3 | 3.5 | 2.8 | 2.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.5 | 7 | 4.2 | 3.4 | 2.5 | 1.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.5 | 7.2 | 6.8 | 4.3 | 3.9 | 3.3 | 2.7 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.5 | 6.9 | 4 | 3.1 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.5 | 7 | 4.3 | 3.5 | 2.8 | 2.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.5 | 7 | 4.2 | 3.4 | 2.5 | 1.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.7 | 5.7 | 5.6 | 5.5 | 5.4 | 5.2 | 5 | 4.7 | 4.5 | 4 | 3.5 | 2.8 | 2.1 | 1.3 | 0.6 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.7 | 5.5 | 5.4 | 5.2 | 4.9 | 4.6 | 3.7 | 2.7 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.7 | 5.7 | 5.6 | 5.5 | 5.4 | 5.1 | 4.6 | 3.7 | 2.9 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.7 | 5.6 | 5.5 | 5.3 | 5.1 | 4.7 | 4.2 | 3.1 | 2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.4 | 7.2 | 6.8 | 4.3 | 3.9 | 3.3 | 2.7 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.4 | 6.9 | 4 | 3.1 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.4 | 7 | 4.3 | 3.5 | 2.8 | 2.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.4 | 7 | 4.2 | 3.4 | 2.5 | 1.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6.9 | 6.6 | 6.3 | 6.1 | 5.9 | 5.8 | 5.5 | 5.2
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7 | 7 | 7 | 7 | 7 | 7 | 6.9 | 6.9 | 6.7 | 6.5 | 6.2 | 5.9 | 5.8 | 5.7 | 5.6 | 5.5 | 5.4 | 5.2 | 5
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7 | 7 | 7 | 7 | 7 | 6.9 | 6.8 | 6.6 | 6.4 | 6.2 | 6.2 | 6.1 | 6 | 5.8 | 5.7 | 5.6 | 5.6 | 5.2 | 5
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7 | 7 | 7 | 7 | 7 | 6.9 | 6.9 | 6.8 | 6.6 | 6.3 | 5.9 | 5.8 | 5.7 | 5.5 | 5.4 | 5.3 | 5.3 | 5 | 4.7
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 54.8 | 51.3 | 42.3 | 41 | 39 | 36.6 | 33.3 | 29.7 | 24.9 | 21.1 | 16.3 | 11 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 54.8 | 42.3 | 39.9 | 36.6 | 32.8 | 28.2 | 22.1 | 13.6 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 54.8 | 42.9 | 40.9 | 38.6 | 36.2 | 32.2 | 26.8 | 19.5 | 10.9 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 54.8 | 42.7 | 40.8 | 38.3 | 34.8 | 30.8 | 25.8 | 18.7 | 10.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.3 | 18.2 | 17.3 | 16.4 | 15.4 | 14.6 | 13.7 | 12.8 | 11.8 | 11.1 | 11 | 10.7 | 10.4 | 10 | 9.7 | 9.4 | 8.8 | 3.9 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.3 | 18.2 | 17.2 | 16 | 14.8 | 13.8 | 12.8 | 11.7 | 10.6 | 10.2 | 10 | 9.3 | 7.8 | 6.5 | 5.4 | 4.2 | 3.3 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.3 | 18.2 | 17.2 | 16.1 | 14.9 | 13.8 | 12.8 | 11.8 | 10.7 | 10.4 | 10.1 | 9.8 | 8.8 | 7.3 | 6 | 4.6 | 3.5 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.3 | 18.2 | 17.2 | 16 | 15.1 | 13.9 | 12.8 | 11.8 | 10.8 | 10.4 | 10.1 | 9.8 | 8 | 6.1 | 4.7 | 3.2 | 2.1 | 0 | 0
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 24 | 21.8 | 16.1 | 15.7 | 15.2 | 14.7 | 14 | 13.3 | 12.4 | 11.8 | 11 | 10.3 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 24 | 16.3 | 15.9 | 15.2 | 14.6 | 13.7 | 12.7 | 11.5 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 24 | 16.3 | 16 | 15.5 | 15 | 14.4 | 13.7 | 12.8 | 10.9 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 24 | 16.3 | 16 | 15.4 | 14.8 | 14 | 13.1 | 12 | 10.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 18.3 | 17.9 | 15.1 | 14.7 | 14.3 | 13.5 | 12.1 | 10.8 | 9.4 | 8.3 | 6.3 | 4.6 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 18.3 | 15.1 | 14.3 | 13.4 | 12.4 | 11.2 | 9.2 | 6.4 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 18.3 | 15.2 | 14.6 | 13.9 | 13.3 | 11.4 | 9.4 | 6.8 | 4.2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 18.3 | 15.2 | 14.6 | 13.9 | 13 | 11.9 | 10.8 | 8.5 | 6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 13.6 | 10.1 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 13.6 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 13.6 | 9.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 13.6 | 9.2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.1 | 5.8 | 5.7 | 5.5 | 5 | 4.7 | 4.2 | 3.6 | 2.8 | 2.2 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.1 | 5.5 | 5 | 4.4 | 3.6 | 2.8 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.1 | 5.7 | 5.2 | 4.8 | 4.3 | 3.7 | 2.9 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.1 | 5.6 | 5.3 | 4.8 | 4 | 3.2 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6 | 5.7 | 5.6 | 5.4 | 5 | 4.6 | 4.1 | 3.6 | 2.8 | 2.2 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6 | 5.5 | 5 | 4.3 | 3.6 | 2.8 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6 | 5.6 | 5.1 | 4.7 | 4.2 | 3.7 | 2.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6 | 5.6 | 5.3 | 4.7 | 4 | 3.2 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.4 | 16 | 14.2 | 13.3 | 12.8 | 12.5 | 11.7 | 11 | 10 | 9.2 | 8.6 | 7.5 | 6.3 | 5 | 3.8 | 3.1 | 2.3 | 0 | 0
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.4 | 15.6 | 13.4 | 11.7 | 10.8 | 9.8 | 8.5 | 6.7 | 4.6 | 2.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.4 | 15.7 | 13.5 | 12.5 | 11.6 | 10.6 | 9.4 | 8.1 | 6.5 | 5 | 3.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.4 | 15.7 | 13.7 | 12.2 | 11.7 | 10.7 | 9.5 | 8.2 | 6.5 | 4.9 | 3.4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.7 | 5.7 | 5.6 | 5.5 | 5.4 | 5.4 | 5.3 | 5.2 | 5.1 | 5 | 4.9 | 4.7 | 4.6 | 4.4 | 4.2 | 4.1 | 3.9 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.7 | 5.6 | 5.6 | 5.4 | 5.3 | 5.1 | 4.9 | 4.7 | 4.5 | 4.2 | 4 | 3.2 | 1.9 | 0.6 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.7 | 5.7 | 5.6 | 5.4 | 5.3 | 5.3 | 5.2 | 5 | 4.8 | 4.5 | 4.2 | 3.9 | 2.6 | 0.9 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.7 | 5.7 | 5.6 | 5.5 | 5.3 | 5.2 | 5 | 4.9 | 4.7 | 4.5 | 4.1 | 3.8 | 2.5 | 0.8 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.5 | 10.2 | 10.1 | 9.9 | 9.6 | 9.3 | 9 | 8.6 | 8 | 7.5 | 7 | 6.4 | 5.5 | 4.4 | 3.2 | 1.6 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.5 | 10.1 | 9.7 | 9.2 | 8.7 | 8.1 | 7.4 | 6.2 | 5 | 3.7 | 2.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.5 | 10.2 | 9.9 | 9.6 | 9.2 | 8.8 | 8.3 | 7.3 | 6.1 | 5 | 3.8 | 2.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.5 | 10.1 | 9.8 | 9.5 | 9 | 8.5 | 7.9 | 7 | 6 | 4.9 | 3.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.8 | 4.7 | 4.7 | 4.3 | 3.9 | 3.3 | 2.8 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.8 | 4.7 | 4 | 3.1 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.8 | 4.7 | 4.3 | 3.6 | 2.9 | 2.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.8 | 4.7 | 4.2 | 3.5 | 2.5 | 1.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.7 | 3.3 | 3 | 2.9 | 2.7 | 2.5 | 2.2 | 2 | 1.8 | 1.7 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3.6 | 3.1 | 2.5 | 2.2 | 1.9 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.6 | 3.2 | 2.8 | 2.6 | 2.2 | 1.9 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.6 | 3.2 | 2.6 | 2.4 | 2.1 | 1.7 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.4 | 4 | 4 | 3.9 | 3.9 | 3.9 | 3.8 | 3.7 | 3.6 | 3.5 | 3.4 | 3.2 | 2.9 | 2.6 | 2.4 | 2.1 | 1.2 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.4 | 3.9 | 3.8 | 3.7 | 3.6 | 3.5 | 3.3 | 3.1 | 2.7 | 2.3 | 1.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.4 | 3.9 | 3.9 | 3.9 | 3.9 | 3.8 | 3.7 | 3.5 | 3.2 | 2.9 | 2.5 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.4 | 3.9 | 3.9 | 3.8 | 3.7 | 3.6 | 3.5 | 3.3 | 3 | 2.7 | 2.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.4 | 5.3 | 5.2 | 5.2 | 5.1 | 5 | 4.8 | 4.7 | 4.5 | 4.3 | 4.1 | 3.5 | 2.9 | 2.1 | 1.3 | 0.6 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.4 | 5.2 | 5.1 | 5 | 4.8 | 4.6 | 4.4 | 3.8 | 2.7 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.4 | 5.3 | 5.2 | 5.2 | 5.1 | 5 | 4.7 | 4.4 | 3.8 | 2.9 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.4 | 5.3 | 5.2 | 5.1 | 4.9 | 4.8 | 4.5 | 4.2 | 3.1 | 2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.1 | 6 | 5.8 | 5.8 | 5.7 | 5.7 | 5.6 | 5.4 | 5 | 4.8 | 4.5 | 4.2 | 3.6 | 3 | 2.5 | 2 | 1.5 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.1 | 5.9 | 5.7 | 5.5 | 5.4 | 5 | 4.7 | 4.1 | 3.5 | 2.9 | 2.2 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.1 | 5.9 | 5.8 | 5.7 | 5.7 | 5.6 | 5.3 | 4.9 | 4.3 | 3.8 | 3 | 2.2 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.1 | 5.9 | 5.7 | 5.7 | 5.5 | 5.3 | 5 | 4.5 | 3.9 | 3.4 | 2.7 | 1.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.4 | 10.1 | 9.9 | 9.8 | 9.5 | 9.2 | 8.9 | 8.5 | 7.9 | 7.4 | 6.9 | 6.3 | 5.4 | 4.4 | 3.2 | 1.5 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.4 | 10 | 9.6 | 9.1 | 8.6 | 8 | 7.3 | 6.2 | 4.9 | 3.6 | 2.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.4 | 10 | 9.8 | 9.5 | 9.1 | 8.7 | 8.2 | 7.3 | 6.1 | 5 | 3.8 | 2.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.4 | 10 | 9.7 | 9.4 | 8.9 | 8.4 | 7.8 | 7 | 5.9 | 4.8 | 3.4 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.5 | 4.2 | 4.4 | 4.1 | 3.7 | 3.2 | 2.7 | 2.3 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.5 | 4.3 | 3.7 | 2.8 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.5 | 4.5 | 4 | 3.4 | 2.8 | 2.3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.5 | 4.4 | 4 | 3.3 | 2.6 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11 | 10.8 | 2.6 | 2.3 | 2 | 1.7 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11 | 2.5 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11 | 2.6 | 1.9 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11 | 2.6 | 2 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.3 | 13 | 11.9 | 11 | 10.4 | 9.2 | 8.6 | 7.9 | 6.7 | 5.6 | 4.6 | 3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.3 | 12.4 | 10.8 | 9.2 | 7.3 | 5.8 | 4.7 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.3 | 12.6 | 11.1 | 9.1 | 8 | 6.8 | 5.4 | 3.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.3 | 12.6 | 11.1 | 9.9 | 8.2 | 7.1 | 6 | 4.2 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 5.1 | 4.9 | 4.8 | 4.5 | 4.2 | 3.9 | 3.4 | 2.7 | 2.1 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 4.6 | 4 | 3.2 | 2.6 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 4.7 | 4.2 | 3.8 | 3.3 | 2.8 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 4.7 | 4.3 | 3.8 | 3.2 | 2.7 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.3 | 8 | 7.9 | 7.7 | 7.5 | 7 | 6.6 | 6.2 | 5.3 | 4.5 | 3.7 | 2.7 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.3 | 7.6 | 7.1 | 6.4 | 5.4 | 4.6 | 3.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.3 | 7.8 | 7.5 | 6.8 | 6.3 | 5.8 | 4.5 | 2.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.3 | 7.7 | 7.4 | 6.9 | 6.1 | 5.5 | 4.6 | 3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.9 | 8.4 | 7.6 | 6.9 | 6.2 | 5.2 | 4.7 | 4.1 | 3.3 | 2.7 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.9 | 7.9 | 6.6 | 5.2 | 3.4 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.9 | 8 | 6.9 | 5.4 | 4.5 | 3.7 | 3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.9 | 8 | 6.9 | 5.8 | 4.2 | 3.4 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.5 | 4 | 3.7 | 2.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.5 | 3.3 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.5 | 3.5 | 2.9 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.5 | 3.5 | 2.8 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.6 | 3.5 | 3 | 2.8 | 2.6 | 2.3 | 1.9 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3.2 | 2.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.3 | 2.9 | 1.4 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.3 | 3 | 2.2 | 1.7 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 34.8 | 32 | 20.9 | 17.1 | 13.1 | 7.9 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 34.8 | 20.4 | 13.4 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 34.8 | 21.6 | 16 | 7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 34.8 | 21.3 | 16 | 9.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 34.5 | 31.8 | 20.7 | 17 | 13 | 7.9 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 34.5 | 20.2 | 13.3 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 34.5 | 21.4 | 15.9 | 7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 34.5 | 21.1 | 15.8 | 9.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.5 | 4 | 3.7 | 2.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.5 | 3.3 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.5 | 3.5 | 2.9 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.5 | 3.5 | 2.8 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 35.5 | 34.1 | 31.1 | 29.6 | 27.7 | 25.6 | 23.8 | 21.8 | 18.7 | 16.2 | 13.4 | 9.5 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 35.5 | 31.5 | 29.2 | 26.3 | 22.8 | 19.4 | 15.9 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 35.5 | 32 | 30.3 | 28.2 | 25.8 | 23.3 | 19.5 | 10 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 35.5 | 31.8 | 29.9 | 27.7 | 24.3 | 21.5 | 18 | 12.7 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.9 | 4.1 | 3.6 | 2.9 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.9 | 3.5 | 2.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.9 | 3.8 | 2.9 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.9 | 3.7 | 2.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 5.1 | 4.2 | 3.7 | 3 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 5.1 | 3.7 | 2.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 5.1 | 3.9 | 3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 5.1 | 3.9 | 2.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.6 | 3.8 | 3.3 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.6 | 3.3 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.6 | 3.5 | 2.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.6 | 3.5 | 2.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.7 | 11.4 | 11 | 10.6 | 10.1 | 9.5 | 9.1 | 8.7 | 8.3 | 7.7 | 6.9 | 5.6 | 3.9 | 2.2 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.7 | 11.3 | 10.7 | 10 | 9.1 | 8.3 | 7.1 | 3.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.7 | 11.4 | 10.9 | 10.3 | 9.7 | 9 | 8.2 | 5.3 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.7 | 11.3 | 10.8 | 10.2 | 9.4 | 8.7 | 7.9 | 5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.9 | 2.8 | 2.8 | 2.8 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.9 | 2.8 | 2.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.9 | 2.8 | 2.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.9 | 2.8 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.6 | 5.4 | 5.3 | 5 | 4.5 | 4 | 3.6 | 2.8 | 2.3 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.4 | 5 | 4.5 | 3.7 | 3 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.5 | 5.3 | 4.7 | 4.4 | 4 | 3.3 | 2.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.4 | 5.2 | 4.9 | 4.1 | 3.4 | 2.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.5 | 4.3 | 3.7 | 3.3 | 2.7 | 2.1 | 1.6 | 1.2 | 0.9 | 0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.5 | 4.2 | 3.5 | 2.9 | 2.2 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.5 | 4.2 | 3.6 | 3.1 | 2.4 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.5 | 4.2 | 3.6 | 3 | 2.3 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.1 | 3.1 | 3.1 | 3.1 | 3 | 2.9 | 2.7 | 2.4 | 2.1 | 1.9 | 1.7 | 1.3 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.1 | 3 | 3 | 2.9 | 2.8 | 2.5 | 2.2 | 1.7 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.1 | 3.1 | 3.1 | 3 | 3 | 2.8 | 2.4 | 2 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.1 | 3 | 3 | 3 | 2.9 | 2.6 | 2.3 | 1.8 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.4 | 6.1 | 6 | 5.9 | 5.7 | 5.4 | 5.2 | 4.9 | 4.5 | 4.1 | 3.5 | 2.7 | 1.7 | 0.5 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.4 | 5.9 | 5.7 | 5.3 | 4.7 | 4.2 | 3.7 | 2.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.4 | 6 | 5.9 | 5.5 | 5.3 | 5 | 4.7 | 4.1 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.4 | 6 | 5.8 | 5.5 | 5 | 4.6 | 4.1 | 3.1 | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.8 | 9.7 | 7.9 | 7.9 | 7.7 | 7.4 | 7.2 | 7 | 6.6 | 6.2 | 5.7 | 4.9 | 3.6 | 2.3 | 1 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.8 | 7.9 | 7.7 | 7.4 | 6.8 | 6.5 | 6.2 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.8 | 7.9 | 7.8 | 7.4 | 7.2 | 7.1 | 6.6 | 2.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.8 | 7.9 | 7.8 | 7.6 | 7 | 6.7 | 6.3 | 5.5 | 4.6 | 3.1 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 4.9 | 4.6 | 4.3 | 3.9 | 3.6 | 3.2 | 2.8 | 2.2 | 1.7 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 4.7 | 4.1 | 3.5 | 2.8 | 2.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 4.7 | 4.3 | 3.9 | 3.4 | 2.9 | 2.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 4.7 | 4.3 | 3.8 | 3.1 | 2.6 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 6.6 | 6.3 | 5.9 | 5.4 | 5.1 | 4.8 | 4.4 | 3.5 | 2.8 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 6.4 | 5.8 | 5.1 | 4.4 | 3.7 | 3.1 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 6.5 | 6 | 5.6 | 5.1 | 4.6 | 3.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.4 | 5.9 | 5.4 | 4.7 | 4.2 | 3.6 | 2.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 13.2 | 10.8 | 8.7 | 6.9 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 13.2 | 9.1 | 5.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 13.2 | 9.9 | 7.1 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 13.2 | 9.7 | 6.6 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 12.8 | 10.4 | 8.4 | 6.6 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 12.8 | 8.8 | 5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 12.8 | 9.5 | 6.9 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 12.8 | 9.4 | 6.4 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.3 | 9 | 8.8 | 8.7 | 8.5 | 7.7 | 7.1 | 6.5 | 5.5 | 4.5 | 4.2 | 3.7 | 3 | 2.2 | 1.5 | 0.8 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.3 | 8.9 | 8.5 | 8.1 | 6.9 | 5.8 | 4.8 | 3.4 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.3 | 8.9 | 8.7 | 7.7 | 7 | 6.2 | 5.2 | 4 | 3.1 | 2.4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.3 | 8.9 | 8.6 | 8.4 | 7.2 | 6.3 | 5.2 | 4.1 | 2.8 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 12.8 | 10.4 | 8.4 | 6.6 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 12.8 | 8.8 | 5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 12.8 | 9.5 | 6.9 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 12.8 | 9.4 | 6.4 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.9 | 14.5 | 14.3 | 14.1 | 13.7 | 13.1 | 12.6 | 12.1 | 11.4 | 10.9 | 10.3 | 9.5 | 8.4 | 7.2 | 6.1 | 5.2 | 4.1 | 0 | 0
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.9 | 14.2 | 13.7 | 13.1 | 12 | 11.2 | 10.4 | 9 | 7.4 | 5.7 | 4.3 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.9 | 14.3 | 14 | 13.3 | 12.8 | 12.3 | 11.7 | 10.7 | 9.6 | 8.4 | 7.1 | 5.5 | 3.8 | 2.1 | 0.5 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.9 | 14.3 | 13.9 | 13.5 | 12.5 | 11.9 | 11.1 | 10.1 | 8.9 | 7.7 | 6.4 | 4.9 | 3.4 | 1.8 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 19.8 | 17.6 | 15 | 13.2 | 10.8 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 19.8 | 16.1 | 11.6 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 19.8 | 16.8 | 13.5 | 9.6 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 19.8 | 16.6 | 13 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 5.2 | 5.2 | 5.1 | 5 | 5 | 4.8 | 4.7 | 4.4 | 4.3 | 4.1 | 3.8 | 3.5 | 3.1 | 2.8 | 2.5 | 2.2 | 0.9 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 5.2 | 5 | 4.9 | 4.7 | 4.5 | 4.3 | 3.8 | 3.3 | 2.8 | 2.4 | 2 | 1.5 | 1.1 | 0.7 | 0 | 0 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 5.2 | 5.1 | 5.1 | 5 | 4.9 | 4.6 | 4.2 | 3.7 | 3.2 | 2.8 | 2.2 | 1.7 | 1.3 | 0.9 | 0 | 0 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 5.2 | 5.1 | 5 | 4.9 | 4.7 | 4.5 | 4.1 | 3.7 | 3.2 | 2.7 | 2.2 | 1.6 | 1.1 | 0.7 | 0 | 0 | 0 | 0
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 6.8 | 6.7 | 6.6 | 6.5 | 6.4 | 6.2 | 5.9 | 5.4 | 4.9 | 4.4 | 3.9 | 3.2 | 2.5 | 1.8 | 1.1 | 0 | 0 | 0
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 6.7 | 6.6 | 6.4 | 6.1 | 5.5 | 4.9 | 4.1 | 3.2 | 2.2 | 1.3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 6.7 | 6.7 | 6.6 | 6.5 | 6.3 | 5.8 | 5.2 | 4.3 | 3.5 | 2.6 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.7 | 6.6 | 6.5 | 6.2 | 5.8 | 5.2 | 4.4 | 3.3 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5 | 4.1 | 3.6 | 3 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5 | 3.6 | 2.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5 | 3.8 | 2.9 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5 | 3.8 | 2.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.1 | 10.9 | 10.9 | 10.9 | 10.9 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.6 | 10.4 | 10.2 | 10.1 | 10 | 9.8 | 8.7 | 7.4
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.1 | 10.9 | 10.8 | 10.7 | 10.4 | 10.3 | 10.3 | 10.1 | 9.8 | 9.4 | 9.1 | 8.7 | 8.2 | 7.9 | 7.6 | 7.3 | 7.1 | 6.1 | 5.6
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.1 | 10.9 | 10.9 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.4 | 10.2 | 10 | 9.5 | 9.2 | 8.8 | 8.6 | 8.2 | 8 | 6.7 | 5.8
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.1 | 10.9 | 10.8 | 10.8 | 10.4 | 10.4 | 10.3 | 10.2 | 9.9 | 9.6 | 9.2 | 8.6 | 8.2 | 7.8 | 7.6 | 7.2 | 7.1 | 6.4 | 5.7
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.7 | 4.4 | 4.1 | 3.8 | 3.4 | 2.8 | 2.2 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.7 | 4.2 | 3.6 | 2.9 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.7 | 4.3 | 3.8 | 3.2 | 2.7 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.7 | 4.2 | 3.8 | 3.3 | 2.4 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5 | 4.9 | 4.9 | 4.9 | 4.9 | 4.8 | 4.8 | 4.8 | 4.7 | 4.6 | 4.6 | 4.4 | 4.2 | 4 | 3.9 | 3.7 | 3.6 | 2.9 | 2.4
Walpole 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5 | 4.9 | 4.9 | 4.8 | 4.7 | 4.6 | 4.5 | 4.3 | 4.1 | 3.9 | 3.6 | 3.4 | 3.2 | 2.9 | 2.8 | 2.6 | 2.4 | 0.8 | 0
Walpole 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5 | 4.9 | 4.9 | 4.9 | 4.9 | 4.8 | 4.7 | 4.6 | 4.4 | 4.2 | 3.9 | 3.6 | 3.3 | 3 | 2.8 | 2.6 | 2.5 | 0 | 0
Walpole 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5 | 4.9 | 4.9 | 4.9 | 4.8 | 4.7 | 4.6 | 4.5 | 4.3 | 4.1 | 3.8 | 3.6 | 3.2 | 2.9 | 2.7 | 2.5 | 2.4 | 2.1 | 0
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.8 | 5.4 | 4.8 | 4.4 | 4 | 3.5 | 3 | 2.3 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.8 | 4.9 | 3.9 | 2.6 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.8 | 5 | 4.1 | 3.1 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.8 | 5 | 4.1 | 3.2 | 2.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.7 | 6.6 | 6.5 | 6.3 | 6.2 | 6 | 5.8 | 5.9 | 5.9 | 6 | 6 | 5.8 | 6 | 6.2 | 6.3 | 6.6 | 6.8 | 7.5 | 7.4
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.7 | 6.3 | 6.1 | 5.6 | 5.4 | 5 | 4.6 | 4 | 3.2 | 2.3 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.7 | 6.4 | 6.5 | 6.4 | 6.5 | 6.6 | 6.5 | 6.7 | 6.6 | 6.7 | 6.6 | 6 | 5.3 | 4.8 | 4.3 | 3.8 | 3.5 | 0 | 0
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.7 | 6.3 | 6.2 | 6 | 5.7 | 5.5 | 5.2 | 5.1 | 4.9 | 4.7 | 4.5 | 3.9 | 3.8 | 3.7 | 3.7 | 3.8 | 4 | 4.4 | 3.9
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.3 | 9 | 8.7 | 8.4 | 7.6 | 6.7 | 5.7 | 4.7 | 3.3 | 2.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.3 | 8.8 | 8.1 | 7.5 | 6.4 | 5 | 3.7 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.3 | 8.9 | 8.4 | 7.9 | 7.1 | 6.1 | 5.1 | 3.6 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.3 | 8.8 | 8.4 | 7.8 | 6.7 | 5.6 | 4.2 | 2.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.2 | 3.7 | 3.4 | 2.9 | 2.3 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.2 | 3.4 | 2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.2 | 3.6 | 3 | 2.1 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.2 | 3.6 | 3 | 2.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.9 | 4.6 | 4.3 | 4 | 3.6 | 3.2 | 2.7 | 2.1 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.9 | 4.2 | 3.5 | 2.6 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.9 | 4.3 | 3.6 | 2.9 | 2.2 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.9 | 4.3 | 3.7 | 3 | 2.3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 50.9 | 49.4 | 48.1 | 46.4 | 44.1 | 40.9 | 37.7 | 34.1 | 29.5 | 24.2 | 17.3 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 50.9 | 47.6 | 44.6 | 40.3 | 35.3 | 29.8 | 22.8 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 50.9 | 48.2 | 46.2 | 42.5 | 39.1 | 35.5 | 31.3 | 22.3 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 50.9 | 48 | 45.8 | 42.7 | 37.9 | 33.4 | 28.1 | 17.7 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN No 2 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 7.7 | 7.4 | 7.1 | 6.7 | 6.3 | 5.4 | 4.4 | 3.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN No 2 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 7.7 | 7 | 6.4 | 5.2 | 4.4 | 2.9 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN No 2 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 7.7 | 7.1 | 6.8 | 6.2 | 5.6 | 4.6 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN No 2 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 7.7 | 7.1 | 6.6 | 5.8 | 5 | 3.7 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.2 | 4.4 | 3.7 | 2.5 | 1.5 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.2 | 4.1 | 3.1 | 1.9 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.2 | 4.2 | 3.1 | 2.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.2 | 4.2 | 3.2 | 2.1 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.5 | 12.4 | 12.3 | 12.3 | 12.2 | 12.1 | 12 | 11.9 | 11.7 | 11.6 | 11.5 | 11.3 | 11.1 | 10.8 | 10.5 | 10.3 | 10 | 8.8 | 7.7
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.5 | 12.3 | 12.2 | 12 | 11.9 | 11.7 | 11.5 | 11.1 | 10.8 | 10.4 | 10 | 9.8 | 9.5 | 9.2 | 9 | 8.7 | 8.5 | 7.5 | 6.8
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.5 | 12.4 | 12.3 | 12.2 | 12.1 | 12 | 11.9 | 11.6 | 11.3 | 11 | 10.7 | 10.2 | 9.8 | 9.4 | 9.1 | 8.7 | 8.4 | 7.2 | 6.3
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.5 | 12.4 | 12.3 | 12.2 | 12 | 11.8 | 11.6 | 11.4 | 11 | 10.7 | 10.4 | 10 | 9.6 | 9.1 | 8.8 | 8.5 | 8.3 | 7.4 | 6.7
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 3.5 | 3.2 | 2.9 | 2.5 | 2.2 | 1.8 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 3.1 | 2.5 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 3.2 | 2.7 | 2.1 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 3.2 | 2.7 | 2.1 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 6.5 | 6.4 | 6.1 | 5.8 | 4.7 | 3.8 | 2.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 6.2 | 5.6 | 4.8 | 3.2 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 6.3 | 5.9 | 4.4 | 3.2 | 2.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.3 | 5.9 | 5.3 | 3.9 | 2.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 6.7 | 6.4 | 5.9 | 5.2 | 3.7 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 6.5 | 5.7 | 3.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 6.6 | 6 | 4.7 | 3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 6.6 | 6 | 4.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.6 | 10.4 | 10.4 | 10.3 | 10.1 | 10 | 9.8 | 9.6 | 9.1 | 8.8 | 8.5 | 8 | 7.3 | 6.5 | 5.7 | 4.9 | 4.2 | 0.5 | 0
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.6 | 10.2 | 9.9 | 9.6 | 9.2 | 8.7 | 8.3 | 7.2 | 6.1 | 4.9 | 4 | 3.3 | 2.5 | 1.7 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.6 | 10.3 | 10.1 | 10 | 9.8 | 9.6 | 9.3 | 8.6 | 7.6 | 6.8 | 5.9 | 4.8 | 3.6 | 2.4 | 1.3 | 0 | 0 | 0 | 0
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.6 | 10.3 | 10.1 | 9.9 | 9.6 | 9.3 | 8.8 | 8.1 | 7.3 | 6.5 | 5.5 | 4.5 | 3.4 | 2.3 | 1.4 | 0 | 0 | 0 | 0
West Burton 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 30.8 | 29.6 | 28.5 | 27 | 25.6 | 24.9 | 24 | 22.1 | 20.7 | 19.6 | 18.4 | 16.5 | 13.5 | 10 | 6.2 | 2.6 | 0 | 0 | 0
West Burton 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 30.8 | 28.7 | 26.7 | 24.5 | 23 | 19.9 | 17.1 | 13.9 | 10.4 | 6.9 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 30.8 | 28.9 | 27 | 25.7 | 23.2 | 20.9 | 19.4 | 17.1 | 14.6 | 11.8 | 8.1 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 30.8 | 28.9 | 27.1 | 25.2 | 23.9 | 20.9 | 18.5 | 16.3 | 13.7 | 11.4 | 8.6 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.9 | 2.8 | 2.6 | 2.6 | 2.6 | 2.5 | 2.5 | 2.4 | 2.2 | 2.1 | 2 | 1.7 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.9 | 2.7 | 2.3 | 2.1 | 2 | 1.8 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.9 | 2.7 | 2.4 | 2.3 | 2.2 | 2 | 1.9 | 1.6 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.9 | 2.7 | 2.4 | 2.3 | 2.1 | 1.9 | 1.7 | 1.4 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.9 | 2.8 | 2.8 | 2.7 | 2.3 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.9 | 2.8 | 2.6 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.9 | 2.8 | 2.8 | 2.1 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.9 | 2.8 | 2.7 | 2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.3 | 3.1 | 2.7 | 2.3 | 1.8 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3 | 2.3 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.1 | 2.6 | 2.1 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.1 | 2.6 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.9 | 8.6 | 8.4 | 8.3 | 8.2 | 7.7 | 5 | 4.7 | 3.6 | 2.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.9 | 8.4 | 8 | 7.6 | 7 | 6.4 | 3.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.9 | 8.5 | 8.3 | 7.7 | 7.5 | 7.2 | 3.7 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.9 | 8.4 | 8.2 | 7.9 | 7.3 | 6.8 | 3.9 | 2.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.6 | 3.5 | 3.5 | 3.4 | 3.4 | 3.3 | 1.1 | 1 | 0.8 | 0.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.6 | 3.4 | 3.3 | 3.2 | 3 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.6 | 3.5 | 3.4 | 3.3 | 3.2 | 3.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.6 | 3.4 | 3.4 | 3.3 | 3.1 | 3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.7 | 5.6 | 5.4 | 5.2 | 4.9 | 4.7 | 4.3 | 3.4 | 2.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.4 | 4.9 | 4.2 | 3.6 | 2.9 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.5 | 5.2 | 4.8 | 4.4 | 4 | 3.5 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.5 | 5.1 | 4.6 | 4.1 | 3.6 | 3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 6.5 | 6.4 | 5.3 | 5 | 4.7 | 1.1 | 1.1 | 1 | 0.9 | 0.9 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 6.3 | 4.9 | 4.7 | 4.2 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 6.4 | 5.1 | 5.2 | 4.8 | 4.6 | 1 | 1 | 0.8 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.3 | 5.1 | 4.9 | 4.4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.4 | 6.1 | 5.4 | 4.6 | 3.5 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.4 | 5.7 | 4.4 | 2.8 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.4 | 5.8 | 4.6 | 3.4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.4 | 5.8 | 4.7 | 3.3 | 2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.1 | 6.7 | 6.3 | 5.9 | 5.4 | 4.2 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.1 | 6.5 | 5.9 | 5.1 | 3.8 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.1 | 6.5 | 6.1 | 4.6 | 4 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.1 | 6.5 | 6 | 5.4 | 4.3 | 2.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.6 | 1.8 | 1.8 | 1.8 | 1.7 | 1.2 | 18 | 17.9 | 17.6 | 17.4 | 17.2 | 16.4 | 16 | 15.7 | 15.2 | 14.8 | 14.5 | 12.6 | 10.8
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.6 | 1.7 | 1.6 | 1.4 | 0.5 | 0 | 17.2 | 16.7 | 16.2 | 15.2 | 14.3 | 13.9 | 13.3 | 12.9 | 12.5 | 12.1 | 11.7 | 10 | 7.4
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.6 | 1.7 | 1.7 | 1 | 0.9 | 0.6 | 17.5 | 17 | 16.5 | 15.2 | 14.8 | 14.2 | 13.7 | 13.1 | 12.6 | 12.1 | 11.7 | 9.2 | 6.1
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.6 | 1.7 | 1.7 | 1.6 | 0.8 | 0 | 17.3 | 16.9 | 16.4 | 15.9 | 14.5 | 14 | 13.4 | 12.9 | 12.4 | 12 | 11.6 | 10.3 | 8.8
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.9 | 3.2 | 3 | 2.8 | 2.6 | 2.4 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.9 | 2.8 | 2.2 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.9 | 2.9 | 2.4 | 2 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.9 | 2.9 | 2.5 | 1.9 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.7 | 11.6 | 11.5 | 11.4 | 11.3 | 11.1 | 10.9 | 10.6 | 9.8 | 8.7 | 7.5 | 6.4 | 5.7 | 5.1 | 4.6 | 4.2 | 3.8 | 1.8 | 0
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.7 | 11.4 | 11.1 | 10.7 | 10.3 | 9.9 | 9.5 | 7.8 | 5.9 | 4.2 | 3.2 | 2.7 | 2 | 1.4 | 0.8 | 0 | 0 | 0 | 0
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.7 | 11.5 | 11.1 | 10.8 | 10.4 | 10 | 8.9 | 7.5 | 5.9 | 4.8 | 4 | 3.4 | 2.6 | 1.8 | 1 | 0 | 0 | 0 | 0
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.7 | 11.5 | 11.2 | 10.8 | 10.5 | 10 | 9.5 | 8.2 | 6.8 | 5.4 | 4.3 | 3.6 | 3 | 2.4 | 1.8 | 1.4 | 1 | 0 | 0
Willington 132kV | DERBY 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 36.3 | 31.3 | 30.6 | 29.9 | 22.6 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 36.3 | 30.3 | 28.9 | 27 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 36.3 | 30.5 | 29.6 | 28.5 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 36.3 | 30.4 | 29.4 | 28.1 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 51.7 | 29.2 | 21.2 | 16.3 | 4.9 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 51.7 | 27.9 | 18.3 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 51.7 | 28.4 | 19.1 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 51.7 | 28.3 | 19.3 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.3 | 10.1 | 8.3 | 8 | 7.6 | 7.5 | 7.6 | 7.5 | 7.3 | 7.2 | 7 | 6.7 | 6.5 | 6.2 | 5.9 | 5.7 | 5.4 | 3.7 | 1.9
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.3 | 9.8 | 7.8 | 7.3 | 6.8 | 6.4 | 6.4 | 5.8 | 5.1 | 4.4 | 3.7 | 2.9 | 2.1 | 1.3 | 0.6 | 0 | 0 | 0 | 0
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.3 | 9.9 | 7.9 | 7.4 | 6.9 | 6.7 | 6.6 | 6.4 | 5.9 | 5.4 | 4.9 | 4 | 3.2 | 2.4 | 1.6 | 0.9 | 0 | 0 | 0
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.3 | 9.8 | 7.9 | 7.4 | 7 | 6.7 | 6.7 | 6.3 | 5.9 | 5.5 | 4.9 | 4.1 | 3.5 | 2.9 | 2.3 | 1.8 | 1.4 | 0 | 0
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.3 | 1.6 | 1.7 | 1.7 | 1.6 | 1.1 | 6.9 | 6.9 | 6.5 | 6.3 | 6 | 5.6 | 5.3 | 4.9 | 4.6 | 4.3 | 4 | 2.8 | 2
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.3 | 1.5 | 1.5 | 1.3 | 0 | 0 | 6.5 | 5.7 | 5.3 | 4.8 | 4.5 | 4.2 | 3.9 | 3.6 | 3.3 | 3 | 2.6 | 1.6 | 1
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.3 | 1.6 | 1.6 | 0.9 | 0.8 | 0.6 | 6.2 | 5.9 | 5.5 | 5.2 | 4.9 | 4.5 | 4.1 | 3.7 | 3.3 | 2.9 | 2.6 | 1.5 | 0.8
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.3 | 1.6 | 1.5 | 1.5 | 0.7 | 0 | 6.5 | 5.8 | 5.4 | 5 | 4.7 | 4.3 | 4 | 3.6 | 3.2 | 2.9 | 2.6 | 1.8 | 1.5
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5 | 4.6 | 4.3 | 3.9 | 3.6 | 3.2 | 2.8 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5 | 4.2 | 3.4 | 2.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5 | 4.3 | 3.6 | 2.7 | 2 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5 | 4.3 | 3.6 | 2.7 | 2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.4 | 15.3 | 15.3 | 15.2 | 15.2 | 15.1 | 8.4 | 8.3 | 8.1 | 8 | 7.8 | 7.6 | 7.2 | 6.9 | 6.5 | 6.2 | 5.8 | 4.1 | 2.6
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.4 | 15.2 | 15.1 | 14.9 | 14.7 | 14.5 | 7.7 | 7.2 | 6.7 | 6.2 | 5.8 | 5.4 | 5 | 4.6 | 4.2 | 3.8 | 3.4 | 1.7 | 0.5
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.4 | 15.2 | 15.2 | 15.1 | 15 | 14.9 | 8.2 | 7.9 | 7.5 | 7.1 | 6.6 | 6.1 | 5.5 | 4.9 | 4.4 | 3.8 | 3.4 | 1.7 | 0.6
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.4 | 15.2 | 15.1 | 15 | 14.9 | 14.7 | 8 | 7.7 | 7.3 | 6.9 | 6.5 | 6 | 5.5 | 5 | 4.5 | 4.2 | 3.9 | 2.5 | 1.9
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.2 | 9 | 8.9 | 8.7 | 8.3 | 7.8 | 6.5 | 5.8 | 4.6 | 3.6 | 2.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.2 | 8.7 | 8.1 | 7.4 | 6.4 | 5.3 | 3.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.2 | 8.8 | 8.4 | 7.7 | 7 | 6.3 | 4.6 | 3.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.2 | 8.8 | 8.4 | 7.8 | 7.1 | 6.1 | 4 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.4 | 11.4 | 11.5 | 11.6 | 11.7 | 11.8 | 12.1 | 12.2 | 12.2 | 12.2 | 10.9 | 9.7 | 8.1 | 5 | 2.3 | 0 | 0 | 0 | 0
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.4 | 11.4 | 11.4 | 11.5 | 11.6 | 11.7 | 12 | 11.3 | 9 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.4 | 11.4 | 11.5 | 11.6 | 11.7 | 11.7 | 12.1 | 11.2 | 8.8 | 4.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.4 | 11.4 | 11.5 | 11.6 | 11.6 | 11.7 | 12 | 12.1 | 10.2 | 6.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.5 | 12 | 11.1 | 10.3 | 9.5 | 8.7 | 7.5 | 6.7 | 5.4 | 4.4 | 3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.5 | 11.6 | 10.1 | 8.4 | 6.7 | 4.8 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.5 | 11.7 | 10.4 | 8.7 | 7.3 | 5.5 | 3.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.5 | 11.7 | 10.5 | 9.1 | 7.9 | 6.5 | 4.6 | 2.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.7 | 6.6 | 6.6 | 6.4 | 5.9 | 4.5 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.7 | 6.5 | 6.1 | 5.3 | 3.7 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.7 | 6.6 | 6.5 | 4.8 | 4.1 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.7 | 6.6 | 6.4 | 5.7 | 4.3 | 2.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11 | 10.8 | 10.6 | 10.4 | 10.1 | 9.4 | 8.8 | 8.3 | 7.6 | 7 | 6.2 | 5.2 | 4 | 3 | 2.2 | 1.5 | 0.8 | 0 | 0
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11 | 10.6 | 10.2 | 9.6 | 8.7 | 8 | 7 | 5.5 | 4 | 2.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11 | 10.7 | 10.4 | 9.8 | 9.4 | 8.7 | 7.9 | 6.7 | 5.4 | 4.2 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11 | 10.6 | 10.3 | 9.8 | 9 | 8.3 | 7.3 | 6.1 | 4.9 | 3.7 | 2.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.4 | 4.2 | 4.1 | 3.7 | 3.6 | 3.4 | 3.1 | 2.9 | 2.8 | 2.7 | 2.6 | 2.4 | 2 | 1.6 | 1.2 | 0.9 | 0 | 0 | 0
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.4 | 4.1 | 3.3 | 3.3 | 3 | 2.7 | 2 | 1.6 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.4 | 4.1 | 3.5 | 3.6 | 3.4 | 3.4 | 2.9 | 2.7 | 2.4 | 2.1 | 1.8 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.4 | 4.1 | 3.5 | 3.5 | 3.2 | 2.9 | 2.3 | 2 | 1.6 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.2 | 6.1 | 6.1 | 6.1 | 6 | 6 | 5.4 | 5.3 | 5.1 | 4.9 | 4.7 | 4.4 | 4 | 3.6 | 3.2 | 2.9 | 2.6 | 0.8 | 0
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.2 | 6.1 | 5.9 | 5.7 | 5.5 | 5.4 | 4.5 | 4 | 3.4 | 2.9 | 2.5 | 2.1 | 1.7 | 1.2 | 0.7 | 0 | 0 | 0 | 0
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.2 | 6.1 | 6 | 6 | 5.9 | 5.8 | 5 | 4.7 | 4.4 | 3.9 | 3.4 | 2.8 | 2.1 | 1.5 | 0.9 | 0 | 0 | 0 | 0
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.2 | 6.1 | 6 | 5.9 | 5.7 | 5.6 | 4.7 | 4.3 | 3.9 | 3.5 | 3 | 2.5 | 2 | 1.3 | 0.8 | 0 | 0 | 0 | 0
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 6.9 | 6.7 | 6.5 | 6.3 | 5.7 | 4.2 | 3.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 6.6 | 5.7 | 4.6 | 3.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 6.7 | 6.3 | 5.4 | 4.3 | 3.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 6.7 | 6.3 | 5.6 | 4.5 | 3.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.3 | 6.3 | 6.2 | 6.2 | 6.1 | 6 | 3.4 | 3.2 | 2.9 | 2.7 | 2.5 | 2.3 | 2 | 1.7 | 1.4 | 1.2 | 0.9 | 0 | 0
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.3 | 6.2 | 6 | 5.9 | 5.5 | 5.2 | 2.5 | 2.1 | 1.6 | 1.2 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.3 | 6.2 | 6.1 | 5.9 | 5.6 | 5.4 | 3 | 2.7 | 2.4 | 2.1 | 1.7 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.3 | 6.2 | 6.1 | 6 | 5.7 | 5.5 | 2.8 | 2.5 | 2 | 1.7 | 1.4 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.5 | 6.9 | 6.2 | 5.5 | 4.7 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.5 | 6 | 4.5 | 3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.5 | 6.2 | 4.8 | 3.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.5 | 6.1 | 4.9 | 3.6 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.3 | 10.1 | 10 | 9.8 | 9.5 | 9.3 | 8.8 | 8.4 | 7.6 | 6.8 | 5.9 | 5 | 4.1 | 3.2 | 2.4 | 1.7 | 0.8 | 0 | 0
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.3 | 9.8 | 9.3 | 8.6 | 8.1 | 7.4 | 6.4 | 4.4 | 2.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.3 | 9.9 | 9.5 | 9.1 | 8.6 | 8.1 | 6.9 | 5.7 | 4.4 | 3.3 | 2.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.3 | 9.9 | 9.5 | 9.1 | 8.6 | 8 | 7 | 5.6 | 4.3 | 3.1 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.1 | 7.1 | 6.8 | 6.4 | 5.9 | 4.5 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.1 | 6.8 | 6.2 | 5.3 | 3.7 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.1 | 6.9 | 6.5 | 4.8 | 4.1 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.1 | 6.9 | 6.4 | 5.7 | 4.3 | 2.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6 | 5.9 | 5.6 | 5.5 | 5.2 | 5 | 4.5 | 4.2 | 3.6 | 3.2 | 2.5 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6 | 5.5 | 4.9 | 4.3 | 3.8 | 3.1 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6 | 5.6 | 5.1 | 4.8 | 4.5 | 4 | 3.4 | 2.4 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6 | 5.6 | 5.2 | 4.8 | 4.4 | 4 | 3.3 | 2.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.4 | 7.1 | 5.9 | 4.6 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.4 | 6.8 | 5.1 | 3.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.4 | 6.9 | 5.3 | 3.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.4 | 6.9 | 5.3 | 3.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 6.8 | 6.3 | 5.9 | 5.5 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 6.3 | 5.1 | 3.8 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 6.5 | 5.6 | 4.3 | 3.1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 6.5 | 5.6 | 4.8 | 3.7 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.2 | 10.5 | 10 | 3.7 | 1 | 0 | 1.5 | 1.6 | 1.5 | 1.5 | 1.4 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.2 | 10.3 | 9.5 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.2 | 10.3 | 9.5 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.2 | 10.3 | 9.7 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.8 | 8.3 | 7.7 | 6.9 | 6.4 | 5.7 | 4.2 | 3.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.8 | 7.7 | 5.7 | 4.6 | 3.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.8 | 7.9 | 6.3 | 5.4 | 4.3 | 3.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.8 | 7.9 | 6.4 | 5.6 | 4.4 | 3.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.7 | 7.5 | 7.5 | 6.9 | 6.4 | 5.7 | 4.1 | 3.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.7 | 7.4 | 5.7 | 4.6 | 3.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.7 | 7.5 | 6.3 | 5.4 | 4.3 | 3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.7 | 7.4 | 6.4 | 5.6 | 4.4 | 3.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 41.2 | 40.1 | 37.3 | 34.7 | 31.6 | 27.5 | 23.7 | 19.9 | 16.4 | 13.4 | 10.2 | 0 | 0
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 29.3 | 23.1 | 16.2 | 11.1 | 6.7 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 36.8 | 32 | 26.3 | 21 | 16.5 | 11.2 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 36.2 | 31.8 | 26.4 | 20.9 | 14.7 | 9.2 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0

## Generation Headroom
Associated GSP | Substation | Supply Level | Voltage Level (kV) | Scenario | Units | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.4 | 12.2 | 12.1 | 11.9 | 11.8 | 11.7 | 11.6 | 11.5 | 11.4 | 11.3 | 11.1 | 11 | 10.9 | 10.7 | 10.6 | 10.5 | 10.5 | 9.7 | 7.9
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.4 | 12.1 | 11.7 | 11.4 | 11 | 10.8 | 10.6 | 10.5 | 10.3 | 10 | 9.7 | 9.2 | 8.5 | 7.6 | 7 | 6.3 | 5 | 0 | 0
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.4 | 12 | 11.6 | 11.2 | 10.8 | 10.4 | 10.1 | 9.7 | 9.2 | 8.8 | 8.5 | 6.7 | 5 | 4.3 | 3.8 | 3.2 | 2.5 | 0 | 0
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.4 | 12.1 | 11.9 | 11.5 | 11.2 | 11 | 10.8 | 10.7 | 10.5 | 10.1 | 9.7 | 9.6 | 9.5 | 9.4 | 9.3 | 9.2 | 8.2 | 4.9 | 1
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.2 | 15.1 | 15.1 | 15.1 | 15 | 14.9 | 14.7 | 14.6 | 14.5 | 14.3 | 14.1 | 14 | 14 | 14 | 14 | 13.9 | 13.9 | 11.8 | 11.3
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.2 | 15 | 14.8 | 14.6 | 14.5 | 14.4 | 14.2 | 14.1 | 14 | 13.9 | 13.8 | 11.9 | 11.8 | 11.5 | 11.3 | 11 | 10.7 | 8.9 | 6.5
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.2 | 14.9 | 14.6 | 14.4 | 14.3 | 14.1 | 13.9 | 13.8 | 11.9 | 11.8 | 11.5 | 11.2 | 11 | 10.7 | 10.4 | 10.1 | 9.7 | 7.8 | 6
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.2 | 15.1 | 15 | 14.7 | 14.6 | 14.6 | 14.4 | 14.3 | 14.2 | 14 | 13.9 | 13.9 | 13.8 | 13.8 | 11.9 | 11.8 | 11.7 | 10.6 | 9.1
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.1 | 15 | 15 | 14.9 | 14.8 | 14.8 | 14.5 | 14.3 | 13.9 | 11.8 | 11.4 | 11 | 10.6 | 10.4 | 10.2 | 9.9 | 9.6 | 7.5 | 5.2
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.1 | 14.9 | 14.7 | 14.6 | 14.5 | 14.4 | 14 | 13.8 | 11.7 | 10.8 | 9.6 | 8.2 | 7 | 5.8 | 4.8 | 3.8 | 2.8 | 0 | 0
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.1 | 14.9 | 14.6 | 14.5 | 14.4 | 14.3 | 13.9 | 11.8 | 10.6 | 9.5 | 8 | 7 | 6 | 5 | 4.2 | 3.4 | 2.5 | 0 | 0
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.1 | 15 | 14.8 | 14.8 | 14.7 | 14.6 | 14.3 | 14.1 | 13.8 | 11.7 | 10.9 | 10.2 | 9.6 | 9 | 8.5 | 8 | 7.4 | 3.6 | 0
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 17.7 | 17.7 | 17.6 | 17.6 | 17.6 | 17.6 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 17.7 | 17.7 | 17.6 | 17.6 | 17.6 | 17.6 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.3 | 17.2 | 17.1
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 17.7 | 17.7 | 17.6 | 17.6 | 17.6 | 17.6 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.2 | 17.1 | 17
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 17.7 | 17.7 | 17.6 | 17.6 | 17.6 | 17.6 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.3 | 17.3
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.3 | 19.3 | 19.2 | 19.1 | 18.9 | 18.8 | 18.5 | 18.3 | 18.2 | 18 | 17.9 | 18 | 18 | 18.1 | 18.2 | 18.3 | 18.2 | 17.6 | 17
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.3 | 19.1 | 18.9 | 18.7 | 18.4 | 18 | 17.6 | 17.3 | 17.3 | 17.3 | 17.3 | 17.2 | 17 | 16.9 | 14.9 | 14.9 | 14.7 | 13.3 | 11.5
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.3 | 19 | 18.7 | 18.4 | 17.9 | 17.6 | 17.2 | 17 | 16.9 | 15 | 14.9 | 14.8 | 14.6 | 14.4 | 14.2 | 13.9 | 13.5 | 11.5 | 9.4
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.3 | 19.3 | 19.1 | 19 | 18.7 | 18.3 | 17.9 | 17.7 | 17.7 | 17.7 | 17.8 | 17.6 | 17.5 | 17.4 | 17.3 | 17.1 | 17 | 14.6 | 13.4
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 15.1 | 15.1 | 15 | 15 | 15 | 14.9 | 14.9 | 14.8 | 14.8 | 14.8 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.5 | 14.4
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 15.1 | 15.1 | 15 | 14.9 | 14.8 | 14.8 | 14.7 | 14.7 | 14.6 | 14.6 | 14.5 | 14.5 | 14.4 | 14.4 | 14.3 | 14.3 | 14.2 | 14.1 | 12.8
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 15.1 | 15 | 14.9 | 14.8 | 14.7 | 14.7 | 14.6 | 14.5 | 14.4 | 14.4 | 14.3 | 14.3 | 14.2 | 14.2 | 14.1 | 14.1 | 14.1 | 12.8 | 12.5
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 15.1 | 15.1 | 15 | 15 | 14.9 | 14.9 | 14.8 | 14.8 | 14.7 | 14.7 | 14.7 | 14.6 | 14.6 | 14.6 | 14.6 | 14.5 | 14.5 | 14.3 | 14.1
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 77.1 | 77.1 | 76.9 | 76.7 | 76.4 | 75.9 | 77.2 | 76.7 | 76.3 | 75.7 | 75 | 74.5 | 74.2 | 73.8 | 73.3 | 73.1 | 72.7 | 71 | 68.9
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 77.1 | 77 | 76.5 | 76 | 75.2 | 73.8 | 73.5 | 72.2 | 71.3 | 70.4 | 69 | 67.9 | 66.8 | 65.6 | 64.4 | 63.3 | 62.1 | 57.1 | 51.8
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 77.1 | 76.8 | 76 | 75.1 | 74.1 | 70.9 | 70.5 | 69.2 | 67.7 | 66.6 | 65.2 | 64.1 | 62.9 | 61.7 | 60.6 | 59.4 | 58.1 | 52 | 45.6
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 77.1 | 77.1 | 76.7 | 76.4 | 75.9 | 74.4 | 74 | 72.9 | 72.1 | 71.4 | 70.2 | 69.6 | 69 | 67.9 | 67.4 | 66.8 | 66 | 62.2 | 58.1
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 66.4 | 66.4 | 66 | 65.7 | 65.3 | 64.9 | 64.3 | 63.8 | 63.1 | 62.1 | 60.6 | 59.8 | 59.2 | 58.8 | 58.4 | 58.1 | 57.8 | 55.5 | 53.2
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 66.4 | 66.1 | 65.5 | 65 | 64.4 | 63.5 | 60.8 | 59.4 | 57.8 | 56 | 54.4 | 52.5 | 51 | 49.6 | 48.5 | 47.4 | 46.3 | 40.7 | 35.7
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 66.4 | 65.9 | 65.1 | 64.4 | 63.2 | 61.4 | 59.2 | 57 | 54.6 | 52.5 | 50.5 | 48.8 | 47.4 | 46.1 | 45.1 | 43.9 | 42.7 | 36.7 | 31.6
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 66.4 | 66.3 | 65.9 | 65.4 | 64.8 | 64.1 | 61.7 | 60.2 | 58.6 | 56.9 | 55.2 | 53.9 | 53 | 52.2 | 51.6 | 41.1 | 40.3 | 35.8 | 31.7
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 72.7 | 72.5 | 72.2 | 71.9 | 71.9 | 71.4 | 82.7 | 82.3 | 81.6 | 80.8 | 79.6 | 78.7 | 78.1 | 77.6 | 76.3 | 75.4 | 74.8 | 71.3 | 61.8
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 72.7 | 72.1 | 71.3 | 70.2 | 69.3 | 67.8 | 78.7 | 77.7 | 76.1 | 74.2 | 71.2 | 62.4 | 60.7 | 58.7 | 56.9 | 55.2 | 53.3 | 42.7 | 34
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 72.7 | 71.9 | 70.8 | 69.8 | 68.8 | 66.1 | 75.6 | 73.5 | 71.3 | 62.7 | 60 | 58.3 | 56.4 | 54.5 | 53 | 51.3 | 49.4 | 39.4 | 32.8
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 72.7 | 72.4 | 71.8 | 70.9 | 70 | 69.1 | 79.7 | 78.7 | 77.2 | 75.7 | 72.4 | 63.4 | 63.1 | 62.6 | 62.1 | 61.3 | 60.4 | 53.5 | 46
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 18.1 | 18 | 17.9 | 18 | 18.1 | 18 | 17.8 | 17.7 | 17.5 | 17.3 | 17.1 | 15.3 | 15 | 14.7 | 13.6 | 13 | 12.7 | 11.1 | 9.7
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 18.1 | 17.9 | 17.6 | 17 | 15.4 | 15.2 | 14.9 | 14.3 | 13.4 | 12.2 | 10.5 | 9.6 | 8.8 | 8 | 7.5 | 6.9 | 6.2 | 2.9 | 0
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 18.1 | 17.8 | 17.5 | 17.2 | 17.1 | 13.7 | 13 | 11.8 | 10.7 | 9.6 | 8.8 | 8.2 | 7.5 | 6.9 | 6.4 | 5.9 | 5.3 | 2.1 | 0
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 18.1 | 18 | 17.7 | 17.4 | 17.1 | 17 | 15.2 | 14.7 | 13.8 | 12.9 | 10.5 | 9.8 | 9.4 | 9 | 8.6 | 8.2 | 7.7 | 5.1 | 2.7
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 16.8 | 16.8 | 16.8 | 16.8 | 16.7 | 16.7 | 16.2 | 16.2 | 16.2 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 16.8 | 16.8 | 16.8 | 16.8 | 16.7 | 16.7 | 16.2 | 16.2 | 16.2 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16 | 15.8 | 15.6
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 16.8 | 16.8 | 16.8 | 16.8 | 16.7 | 16.7 | 16.2 | 16.2 | 16.2 | 16.1 | 16.1 | 16.1 | 16 | 16 | 15.9 | 15.9 | 15.8 | 15.6 | 15.3
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 16.8 | 16.8 | 16.8 | 16.8 | 16.7 | 16.7 | 16.2 | 16.2 | 16.2 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 15.9
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.5 | 16.5 | 16.5 | 16.4 | 16.3 | 16.1 | 16 | 15.9 | 15.5 | 15.1 | 14.5 | 14.1 | 13.9 | 13.6 | 13.6 | 13.6 | 13.5 | 12.8 | 11.9
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.5 | 16.5 | 16.2 | 16 | 15.7 | 15.4 | 15.1 | 14.4 | 13.7 | 13.1 | 12.5 | 11.5 | 10.7 | 10.1 | 9.7 | 9.4 | 9 | 7.2 | 5.3
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.5 | 16.4 | 16 | 15.7 | 15.3 | 14.5 | 14.2 | 13.4 | 12.5 | 11.8 | 11 | 9.9 | 9.2 | 8.5 | 8.2 | 7.9 | 7.5 | 5.4 | 3.4
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.5 | 16.5 | 16.4 | 16.2 | 15.8 | 15.5 | 15.3 | 14.5 | 13.9 | 13.2 | 12.7 | 11.8 | 11.2 | 10.8 | 10.6 | 10.4 | 10.2 | 8.7 | 7.2
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 16.6 | 16.6 | 16.5 | 16.4 | 16.4 | 16.4 | 16.2 | 16.2 | 16.1 | 16.1 | 16 | 16 | 16 | 15.9 | 15.8 | 15.7 | 15.7 | 15.5 | 15.2
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 16.6 | 16.5 | 16.4 | 16.3 | 16.2 | 16.2 | 16 | 15.9 | 15.9 | 15.8 | 15.4 | 15.3 | 15.2 | 15.1 | 14.6 | 14.6 | 14.5 | 13.9 | 13.2
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 16.6 | 16.4 | 16.3 | 16.1 | 16.1 | 15.7 | 15.5 | 15.4 | 15.2 | 15.1 | 14.6 | 14.6 | 14.5 | 14.4 | 14.3 | 14.2 | 14 | 13.3 | 12.5
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 16.6 | 16.5 | 16.4 | 16.4 | 16.3 | 16.3 | 16.1 | 16.1 | 16 | 16 | 15.6 | 15.5 | 15.5 | 15.4 | 15.4 | 15.3 | 15.2 | 14.5 | 14
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.7 | 14.5 | 14.5 | 14.4 | 14.3 | 14.2 | 13.9 | 13.7 | 13.3 | 12.9 | 12.4 | 12 | 11.7 | 11.4 | 11.2 | 11 | 10.9 | 10.1 | 9.2
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.7 | 14.5 | 14.3 | 13.9 | 13.7 | 13.5 | 12.9 | 12.4 | 11.7 | 10.9 | 10.1 | 9.2 | 8.4 | 7.6 | 7 | 6.5 | 4.5 | 2.2 | 0.7
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.7 | 14.4 | 14.2 | 13.8 | 13.6 | 13.3 | 12.8 | 12 | 11.2 | 10.3 | 9.5 | 5.7 | 4.9 | 4.3 | 3.7 | 3.3 | 2.9 | 0.9 | 0
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.7 | 14.5 | 14.3 | 14 | 13.8 | 13.5 | 13 | 12.6 | 12 | 11.4 | 10.6 | 10 | 9.4 | 8.9 | 8.4 | 8.1 | 6.3 | 4.9 | 3.4
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.5 | 15.5 | 15.5 | 15.4 | 15.4 | 15.3 | 15.2 | 15.1 | 14.8 | 14.4 | 13.8 | 13.4 | 13.2 | 13 | 12.8 | 12.6 | 12.4 | 10.9 | 10.3
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.5 | 15.5 | 15.3 | 15.2 | 15.1 | 15 | 14.7 | 14.4 | 13.8 | 13.1 | 12.3 | 11.5 | 10.7 | 9.9 | 9.3 | 8.7 | 8.1 | 4.8 | 2.9
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.5 | 15.4 | 15.3 | 15.1 | 15 | 14.8 | 14.4 | 13.8 | 12.7 | 11.9 | 10.9 | 10.2 | 9.5 | 8.8 | 8.3 | 7.8 | 7.2 | 4.2 | 3.4
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.5 | 15.5 | 15.4 | 15.3 | 15.2 | 15.1 | 14.8 | 14.6 | 14.1 | 13.6 | 12.8 | 12.3 | 11.8 | 11.3 | 11 | 10.6 | 10.2 | 7.7 | 6
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 70.7 | 70.5 | 70.5 | 70.3 | 69.5 | 69.2 | 69.4 | 68.9 | 67.9 | 66.7 | 55.1 | 54.1 | 53.3 | 52.7 | 52.1 | 51.6 | 51.1 | 47.8 | 45.2
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 70.7 | 70.2 | 60.8 | 59.8 | 59.3 | 58.6 | 57.2 | 56 | 54.2 | 52.2 | 50 | 47.7 | 45.6 | 43.5 | 41.8 | 40.2 | 37.1 | 27.2 | 21.6
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 70.7 | 61.2 | 60.3 | 59.6 | 58.7 | 57.8 | 56.4 | 54.4 | 51.8 | 49.5 | 47 | 42 | 38.6 | 35 | 33.5 | 32 | 30.6 | 23 | 19.1
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 70.7 | 70.3 | 61 | 60.1 | 59.6 | 58.9 | 57.7 | 56.6 | 55.1 | 53.5 | 51.5 | 49.9 | 48.5 | 47.2 | 46.1 | 45 | 42.5 | 34.9 | 29.7
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 9.4 | 9.4 | 9.4 | 9.4 | 9.3 | 9.3 | 17.4 | 17.3 | 17.3 | 17.2 | 16.9 | 16.9 | 15.4 | 15.3 | 15.2 | 15.1 | 15 | 13.9 | 12.7
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 9.4 | 9.4 | 9.3 | 9.2 | 9.2 | 9.1 | 16.8 | 16.7 | 15.5 | 15 | 14.3 | 13.5 | 12.8 | 12 | 11.4 | 10.8 | 10.3 | 7 | 4.7
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 9.4 | 9.3 | 9.3 | 9.2 | 8.8 | 8.8 | 16.8 | 15.5 | 14.9 | 14.1 | 13.2 | 12.6 | 11.9 | 11.2 | 10.7 | 10.3 | 9.8 | 7 | 5.6
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 9.4 | 9.4 | 9.3 | 9.3 | 9.2 | 9.2 | 16.9 | 16.8 | 16.7 | 15.4 | 15 | 14.5 | 14.1 | 13.7 | 13.4 | 13.1 | 12.8 | 10.6 | 8.5
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 22.3 | 22.3 | 22.3 | 22.3 | 22.3 | 22.1 | 21.6 | 21.4 | 21.3 | 21 | 20.8 | 20.6 | 20.3 | 20.1 | 19.8 | 19.6 | 19.4 | 18.9 | 18.2
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 22.3 | 22.3 | 22 | 21.8 | 21.4 | 21 | 20.3 | 19.8 | 19.4 | 19.1 | 18.4 | 18 | 17.6 | 17.1 | 16.6 | 16.1 | 15.7 | 14.3 | 12.8
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 22.3 | 22.2 | 21.8 | 21.5 | 21 | 20.2 | 19.3 | 18.7 | 18.2 | 17.8 | 17.3 | 16.8 | 16.4 | 15.9 | 15.5 | 15 | 14.6 | 12.9 | 11.3
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 22.3 | 22.3 | 22.2 | 22 | 21.7 | 21.3 | 20.4 | 19.9 | 19.6 | 19.2 | 18.7 | 18.4 | 18.1 | 17.8 | 17.5 | 17.1 | 16.8 | 15.7 | 14.6
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.1 | 19 | 18.9 | 18.8 | 18.7 | 18.6 | 18.1 | 18 | 17.9 | 17.8 | 17.7 | 17.6 | 17.6 | 17.6 | 17.6 | 17.5 | 17.5 | 17.1 | 15.3
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.1 | 18.8 | 18.7 | 18.5 | 18.3 | 18.2 | 17.6 | 17.5 | 17.4 | 17.3 | 17.1 | 17 | 16.9 | 15.3 | 15.2 | 15.1 | 14.9 | 13.7 | 12.3
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.1 | 18.7 | 18.4 | 18.2 | 17.9 | 17.7 | 17.1 | 16.9 | 16.8 | 15.3 | 15.2 | 15 | 14.9 | 14.7 | 14.5 | 14.2 | 13.9 | 12.3 | 10.7
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.1 | 19 | 18.8 | 18.7 | 18.6 | 18.4 | 17.8 | 17.7 | 17.6 | 17.6 | 17.5 | 17.4 | 17.3 | 17.2 | 17.1 | 17 | 16.9 | 14.9 | 13.9
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.3 | 18.3 | 18.3 | 18.2 | 18.4 | 18.3 | 18.1 | 17.9 | 17.7 | 17.3 | 17 | 16.9 | 15.4 | 15.3 | 15.2 | 15.1 | 15 | 13.9 | 12.7
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.3 | 18.3 | 18.2 | 18.1 | 18 | 17.7 | 17.2 | 17 | 15.4 | 15 | 14.3 | 13.5 | 12.8 | 12 | 11.4 | 10.8 | 10.3 | 7 | 4.7
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.3 | 18.3 | 18.1 | 18.1 | 17.7 | 17.5 | 17 | 15.4 | 14.8 | 14.1 | 13.2 | 12.5 | 11.9 | 11.2 | 10.7 | 10.2 | 9.7 | 7 | 5.6
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.3 | 18.3 | 18.3 | 18.2 | 18 | 17.9 | 17.4 | 17.2 | 16.9 | 15.4 | 15 | 14.5 | 14.1 | 13.7 | 13.3 | 13.1 | 12.7 | 10.6 | 8.5
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.3 | 17.2 | 17.1 | 17 | 17 | 16.9 | 17 | 17 | 16.9 | 16.9 | 15.5 | 15.1 | 15 | 15 | 14.9 | 14.5 | 13.9 | 12.6 | 11.2
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.3 | 17.1 | 17.1 | 16.9 | 15.6 | 15.1 | 15.1 | 15 | 14.7 | 14.1 | 12.6 | 10.7 | 9.9 | 9.1 | 8.5 | 7.9 | 7.2 | 3.5 | 0.6
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.3 | 17.2 | 17 | 16.8 | 15.1 | 14.8 | 14.5 | 13.8 | 12.8 | 11.3 | 9.2 | 8.4 | 7.7 | 7.1 | 6.6 | 6.1 | 5.5 | 2.3 | 0
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.3 | 17.2 | 17.1 | 17 | 16.8 | 15.5 | 15.2 | 15.1 | 14.9 | 14.5 | 13.5 | 12.4 | 11.7 | 11.5 | 11.3 | 11 | 10.6 | 8.2 | 5.8
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.8 | 16.8 | 16.7 | 16.7 | 16.6 | 16.5 | 16.5 | 16.4 | 16.4 | 15.9 | 15.9 | 15.8 | 15.8 | 15.8 | 15.8 | 15.7 | 15.7 | 15.6 | 15.4
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.8 | 16.7 | 16.6 | 16.4 | 16.3 | 15.9 | 15.8 | 15.6 | 15.5 | 15.3 | 15.2 | 15 | 14.9 | 14.9 | 14.8 | 14.4 | 14.3 | 13.9 | 13.5
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.8 | 16.7 | 16.5 | 16.3 | 15.9 | 15.8 | 15.6 | 15.4 | 15.3 | 15.1 | 14.3 | 14.1 | 14.1 | 14 | 13.9 | 13.8 | 13.7 | 13.2 | 12.7
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.8 | 16.8 | 16.7 | 16.5 | 16.3 | 15.9 | 15.8 | 15.7 | 15.6 | 15.4 | 15.3 | 15.2 | 15.2 | 15.1 | 15.1 | 14.8 | 14.7 | 14.4 | 14.1
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 20.2 | 20.2 | 20.2 | 20.1 | 20.1 | 20.1 | 20.3 | 20.3 | 20.2 | 20 | 19.7 | 19.4 | 19.2 | 19 | 18.8 | 18.8 | 18.7 | 18.3 | 15.7
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 20.2 | 20.2 | 20.2 | 20 | 19.8 | 19.6 | 19.6 | 19.2 | 18.8 | 18.5 | 18.2 | 18 | 15.6 | 15.4 | 15.1 | 14.9 | 14.7 | 13.2 | 11.6
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 20.2 | 20.2 | 20 | 19.7 | 19.3 | 18.7 | 18.5 | 18.2 | 18 | 15.6 | 15.4 | 15.1 | 14.8 | 14.4 | 14.1 | 13.8 | 13.5 | 11.6 | 9.6
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 20.2 | 20.2 | 20.2 | 20.1 | 20.1 | 19.8 | 19.6 | 19.3 | 19 | 18.7 | 18.4 | 18.2 | 18.1 | 15.7 | 15.6 | 15.6 | 15.5 | 14.8 | 13.6
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.9 | 12.1 | 12.2 | 12.1 | 12 | 11.9 | 11.7 | 11.6 | 11.3 | 11 | 10.3 | 10 | 9.8 | 9.7 | 9.5 | 9.4 | 9.2 | 8.2 | 7
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.9 | 11.8 | 11.7 | 11.1 | 10.9 | 10.6 | 10.1 | 9.7 | 9.2 | 8.7 | 8.1 | 7.5 | 7 | 6.4 | 6 | 5.5 | 5 | 1.6 | 0
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.9 | 11.7 | 11.3 | 11.1 | 10.6 | 10.2 | 9.7 | 9.1 | 8.4 | 7.8 | 7.1 | 6.6 | 4.6 | 4.1 | 3.6 | 3.1 | 2.6 | 0 | 0
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.9 | 11.9 | 11.8 | 11.2 | 11.1 | 10.8 | 10.3 | 9.9 | 9.5 | 9.1 | 8.6 | 8.2 | 7.8 | 7.5 | 7.2 | 6.9 | 6.5 | 3.7 | 1.6
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 19.1 | 19.1 | 19.1 | 19 | 19 | 19 | 19.3 | 19.2 | 19.1 | 19 | 18.8 | 18.7 | 18.5 | 18.3 | 18.1 | 17.9 | 17.8 | 16.6 | 16.5
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 19.1 | 19.1 | 19 | 19 | 19 | 18.8 | 18.8 | 18.6 | 18.3 | 17.9 | 17.5 | 16.6 | 16.4 | 16.2 | 15.9 | 15.6 | 15.3 | 13.9 | 13.2
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 19.1 | 19.1 | 19 | 19 | 18.8 | 18.5 | 18.5 | 18 | 17.6 | 16.6 | 16.4 | 16.2 | 15.9 | 15.6 | 15.3 | 15 | 14.7 | 13.1 | 12.2
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 19.1 | 19.1 | 19.1 | 19 | 19 | 19 | 19 | 18.8 | 18.4 | 18.1 | 17.5 | 17.3 | 16.6 | 16.5 | 16.3 | 16.1 | 15.9 | 14.7 | 14.1
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.2 | 17.2 | 17.1 | 17 | 16.9 | 16.8 | 21.5 | 21.4 | 21.3 | 21.2 | 21.1 | 21 | 21 | 21 | 20.9 | 20.9 | 20.9 | 20.4 | 19.9
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.2 | 17.1 | 16.8 | 16.6 | 16.5 | 16.3 | 21 | 20.9 | 20.8 | 20.7 | 20.5 | 20.3 | 20.1 | 19.9 | 19.7 | 19.6 | 19.5 | 16.8 | 15.5
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.2 | 16.9 | 16.6 | 16.3 | 16 | 15.8 | 20.4 | 20.2 | 20 | 19.8 | 19.6 | 19.5 | 17.5 | 17.4 | 17.3 | 17.2 | 16.9 | 15.4 | 13.7
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.2 | 17.2 | 17 | 16.9 | 16.7 | 16.6 | 21.3 | 21.2 | 21.1 | 21 | 20.8 | 20.8 | 20.7 | 20.6 | 20.5 | 20.3 | 20.1 | 19.5 | 17.1
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.3 | 16.2 | 16.3 | 16.3 | 16.2 | 16.2 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.8 | 15.7
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.3 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.7 | 15.7 | 15.6 | 15.6 | 15.3 | 14.9
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.3 | 15.9 | 15.9 | 15.9 | 15.9 | 15.8 | 15.8 | 15.8 | 15.7 | 15.7 | 15.6 | 15.6 | 15.6 | 15.5 | 15.5 | 15.4 | 15.4 | 15 | 14.7
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.3 | 16.2 | 16.2 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.6 | 15.3
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 22.9 | 22.8 | 22.7 | 22.5 | 22.4 | 22.3 | 22.2 | 21.9 | 21.6 | 21.3 | 20.5 | 20.2 | 20.1 | 20 | 19.9 | 19.8 | 19.7 | 19.1 | 18.5
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 22.9 | 22.7 | 22.5 | 22.3 | 22.1 | 21.7 | 20.2 | 19.7 | 19.1 | 18.3 | 17.7 | 17.2 | 16.9 | 16.5 | 16.3 | 16 | 15.8 | 14.3 | 12.9
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 22.9 | 22.6 | 22.4 | 22.1 | 21.6 | 20.6 | 20.1 | 19.3 | 18.4 | 17.5 | 16.9 | 16.4 | 16.2 | 15.9 | 15.6 | 15.4 | 15.1 | 13.9 | 12.6
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 22.9 | 22.8 | 22.6 | 22.5 | 22.2 | 21.9 | 20.4 | 19.9 | 19.3 | 18.6 | 18 | 17.6 | 17.5 | 17.3 | 17.2 | 17.1 | 16.9 | 15.8 | 14.6
Berkswell 132kV | WARWICK 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.7 | 29.4 | 29.2 | 28.9 | 28.8 | 28.6 | 29.1 | 29 | 28.9 | 28.8 | 28.4 | 28.3 | 28.3 | 28.3 | 28.3 | 28.2 | 28.2 | 27.8 | 26.4
Berkswell 132kV | WARWICK 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.7 | 29.2 | 28.7 | 28.3 | 28.1 | 27.8 | 28.1 | 27.9 | 27.8 | 27.6 | 27.4 | 26.5 | 26.1 | 25.7 | 25.3 | 24.8 | 24.4 | 22 | 19.6
Berkswell 132kV | WARWICK 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.7 | 29 | 28.4 | 27.9 | 26.7 | 26.3 | 27.9 | 27.5 | 26.5 | 26.1 | 25.5 | 25.2 | 24.9 | 24.5 | 24.1 | 23.6 | 23.1 | 20.4 | 17.8
Berkswell 132kV | WARWICK 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.7 | 29.3 | 29 | 28.6 | 28.4 | 28.1 | 28.2 | 28.2 | 28.1 | 27.9 | 27.8 | 27.7 | 27.5 | 27.4 | 26.6 | 26.5 | 26.2 | 24.4 | 22.4
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 60.2 | 60 | 59.7 | 59.3 | 58.9 | 58.5 | 59.3 | 58.8 | 57.9 | 56.8 | 55.7 | 52.1 | 52 | 51.8 | 51.6 | 51.3 | 50.9 | 47.3 | 42.8
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 60.2 | 59.5 | 58.6 | 57.6 | 56.9 | 56.2 | 57.2 | 56.3 | 54.7 | 51.4 | 49.2 | 46.5 | 44.4 | 42.2 | 40.4 | 38.2 | 36.1 | 25.1 | 16.6
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 60.2 | 59.2 | 57.9 | 56.9 | 55.9 | 55 | 55.7 | 51.8 | 49.8 | 47.3 | 43.6 | 41.3 | 39.3 | 37.4 | 35.9 | 34.3 | 32.5 | 22.6 | 16.6
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 60.2 | 59.8 | 59.1 | 58.2 | 57.5 | 56.9 | 57.8 | 57.3 | 56.1 | 54.8 | 51.4 | 50.1 | 49 | 48 | 47.2 | 46 | 44.7 | 37.2 | 29.6
Berkswell 132kV | Wellesbourne | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.4 | 17.4 | 17.4 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3
Berkswell 132kV | Wellesbourne | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.4 | 17.4 | 17.4 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3
Berkswell 132kV | Wellesbourne | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.4 | 17.4 | 17.4 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3
Berkswell 132kV | Wellesbourne | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.4 | 17.4 | 17.4 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 23.2 | 23.1 | 22.9 | 22.8 | 22.7 | 22.6 | 22 | 21.8 | 21.7 | 21.6 | 21.5 | 21.4 | 21.4 | 21.4 | 21.4 | 21.3 | 21.3 | 20.7 | 20.1
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 23.2 | 22.9 | 22.7 | 22.5 | 22.3 | 22.1 | 21.3 | 21.1 | 20.9 | 20.8 | 20.7 | 20.6 | 20.4 | 20.2 | 19.9 | 19.7 | 19.6 | 16.3 | 15.1
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 23.2 | 22.8 | 22.5 | 22.2 | 21.9 | 21.6 | 20.7 | 20.5 | 20.3 | 20 | 19.8 | 19.7 | 19.6 | 19.5 | 16.7 | 16.6 | 16.5 | 15.2 | 13.5
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 23.2 | 23.1 | 22.8 | 22.7 | 22.5 | 22.3 | 21.6 | 21.4 | 21.3 | 21.2 | 21.1 | 21.1 | 21 | 20.9 | 20.8 | 20.6 | 20.4 | 19.6 | 16.5
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.9 | 4.8 | 4.8 | 4.8 | 4.8 | 4.6 | 4.6 | 4.4 | 4.2 | 4 | 3.9 | 3.7 | 3.6 | 3.5 | 3.4 | 3.3 | 1.4 | 0
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 4.8 | 4.8 | 4.8 | 4.7 | 4.7 | 4.3 | 4.1 | 3.7 | 2.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 4.8 | 4.8 | 4.7 | 4.6 | 4.5 | 4.1 | 3.6 | 2.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.9 | 4.8 | 4.8 | 4.8 | 4.7 | 4.6 | 4.4 | 4.2 | 3.8 | 3.5 | 3.3 | 3 | 2.5 | 1.8 | 1.1 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6 | 5.7 | 5.2 | 5.1 | 5.1 | 4.8 | 4.9 | 4.6 | 3.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6 | 5.3 | 4.7 | 4.5 | 2.6 | 2.4 | 1.8 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6 | 5.2 | 4.5 | 4.2 | 4 | 3.8 | 3.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6 | 5.4 | 5.1 | 4.8 | 4.6 | 4.5 | 4.1 | 3.8 | 2.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.9 | 8.9 | 8.8 | 8.8 | 8.8 | 8.8 | 8.7 | 7.5 | 7.3 | 7 | 6.5 | 5.8 | 5.4 | 5 | 4.7 | 4.3 | 4 | 1.4 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.9 | 8.8 | 8.8 | 8.7 | 8.7 | 8.7 | 6.2 | 5.3 | 4.1 | 2.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.9 | 8.8 | 8.7 | 8.7 | 8.7 | 7.5 | 5.9 | 4.4 | 2.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.9 | 8.9 | 8.8 | 8.8 | 8.8 | 8.7 | 7.5 | 7.4 | 7.1 | 6.1 | 4.9 | 4 | 3.2 | 2.5 | 1.8 | 1.1 | 0 | 0 | 0
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.6 | 11.6 | 11.5 | 11.5 | 11.4 | 11.4 | 11.3 | 11.2 | 10.9 | 10.5 | 10.1 | 9.8 | 9.6 | 9.4 | 9.5 | 9.3 | 9.2 | 0 | 0
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.6 | 11.5 | 11.4 | 11.4 | 11.3 | 11.2 | 11 | 10.8 | 10.3 | 9.6 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.6 | 11.5 | 11.4 | 11.3 | 11.2 | 11.1 | 10.9 | 10.3 | 9.5 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.6 | 11.6 | 11.5 | 11.4 | 11.4 | 11.3 | 11.2 | 11 | 10.7 | 10.3 | 9.7 | 9.3 | 8.9 | 7 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.6 | 15.6 | 15.5 | 15.5 | 15.5 | 15.5 | 12.2 | 12.2 | 11.8 | 11.4 | 9.9 | 8.8 | 8 | 7.4 | 6.8 | 6.1 | 5.5 | 0 | 0
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.6 | 15.5 | 15.4 | 15.3 | 15.2 | 15.1 | 14.9 | 14.6 | 13 | 10.7 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.6 | 15.5 | 15.4 | 15.3 | 15.2 | 15.2 | 15 | 14.1 | 11.4 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.6 | 15.5 | 15.4 | 15.3 | 15.4 | 15.4 | 15.3 | 15.2 | 14.8 | 13.9 | 11.9 | 10.3 | 7.4 | 2.7 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 20 | 17.7 | 14.2 | 13.4 | 12.6 | 11 | 5.7 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 20 | 14.2 | 10.3 | 8.6 | 4.5 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 20 | 13.6 | 9 | 6.9 | 4.5 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 20 | 14.8 | 13.2 | 10.2 | 8.9 | 7.5 | 4.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.4 | 9.4 | 9.3 | 9.3 | 9.3 | 9.3 | 9.2 | 9.2 | 8.9 | 8.2 | 6.2 | 4.8 | 3.9 | 3.3 | 2.8 | 2.2 | 1.6 | 0 | 0
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.4 | 9.3 | 9.2 | 9.2 | 9.1 | 9.1 | 9 | 8.5 | 6.6 | 4.1 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.4 | 9.3 | 9.1 | 9.1 | 9 | 8.9 | 8.8 | 8.2 | 4.8 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.4 | 9.4 | 9.3 | 9.3 | 9.2 | 9.2 | 9.1 | 9.1 | 8.7 | 7.8 | 5.3 | 3.4 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.7 | 13.6 | 13.5 | 13.3 | 13.1 | 12.9 | 11 | 10.6 | 10.1 | 9.6 | 8.7 | 8.1 | 7.8 | 7.5 | 7.2 | 6.9 | 6.6 | 4.5 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.7 | 13.5 | 13.1 | 12.9 | 12.6 | 12.3 | 8.4 | 7.7 | 6.7 | 5.5 | 4.2 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.7 | 13.4 | 12.9 | 12.5 | 12.2 | 11.7 | 8.3 | 7.1 | 5.5 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.7 | 13.6 | 13.3 | 13.1 | 12.9 | 12.7 | 10.5 | 10.1 | 9.4 | 8.6 | 7.5 | 6.8 | 6.1 | 5.5 | 5 | 4.4 | 0.8 | 0 | 0
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6 | 6 | 5.9 | 5.8 | 5.8 | 5.7 | 5.5 | 5.3 | 4.7 | 4.1 | 3.3 | 2.6 | 2.3 | 2 | 2.2 | 1.9 | 1.6 | 0 | 0
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6 | 5.9 | 5.7 | 5.6 | 5.5 | 5.4 | 5 | 4.6 | 3.6 | 2.4 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6 | 5.9 | 5.6 | 5.5 | 5.3 | 5.2 | 4.7 | 3.7 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6 | 6 | 5.8 | 5.7 | 5.7 | 5.6 | 5.3 | 5.1 | 4.4 | 3.6 | 2.5 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.9 | 9.8 | 9.8 | 9.8 | 9.8 | 9.7 | 9.6 | 9.6 | 9.2 | 8.4 | 7.5 | 6.7 | 6.3 | 5.9 | 5.6 | 5.2 | 4.8 | 0 | 0
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.9 | 9.8 | 9.8 | 9.7 | 9.7 | 9.6 | 9.4 | 8.9 | 7.8 | 6.3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.9 | 9.8 | 9.7 | 9.7 | 9.6 | 9.5 | 9.3 | 8.1 | 6.4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.9 | 9.8 | 9.8 | 9.8 | 9.7 | 9.7 | 9.6 | 9.4 | 8.8 | 7.9 | 6.6 | 5.7 | 4.8 | 2.6 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.9 | 10.9 | 8.3 | 8.2 | 8.2 | 7.2 | 7.1 | 6.9 | 6.6 | 6.1 | 5.5 | 5.1 | 4.8 | 4.6 | 4.4 | 4.2 | 4 | 0 | 0
Bicker Fen 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.9 | 8.3 | 8.1 | 8 | 7.1 | 7 | 6.6 | 6.3 | 5.6 | 4.7 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.9 | 8.2 | 8.1 | 7.9 | 7.7 | 7.6 | 7.2 | 6.5 | 5.4 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.9 | 8.3 | 8.2 | 8.2 | 8.1 | 8 | 7.8 | 7.7 | 7.2 | 6.7 | 5.9 | 5.4 | 4.8 | 4.4 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.8 | 18.6 | 18.5 | 18.4 | 18.2 | 18 | 17.6 | 17.1 | 16.5 | 15.8 | 14.8 | 14 | 12.9 | 11.9 | 10.5 | 9.1 | 7.5 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.8 | 18.4 | 18.1 | 17.9 | 17.5 | 17 | 16.2 | 15 | 14 | 12 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.8 | 18.3 | 17.9 | 17.6 | 17.1 | 16.3 | 14.9 | 13.4 | 10.8 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.8 | 18.5 | 18.3 | 18.1 | 17.7 | 17.2 | 16.5 | 15.8 | 14.5 | 13.4 | 11.3 | 8.8 | 6.4 | 2.5 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.4 | 13.2 | 13.1 | 13 | 13 | 12.9 | 12.8 | 12.6 | 12.2 | 11.6 | 10.9 | 10.4 | 10.1 | 9.9 | 9.7 | 9.5 | 9.3 | 0 | 0
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.4 | 13.1 | 11.1 | 11 | 10.9 | 10.8 | 10.5 | 10.3 | 9.6 | 8.6 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.4 | 13.1 | 11 | 10.8 | 10.6 | 10.5 | 10.2 | 9.4 | 8.1 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.4 | 13.2 | 13 | 11.1 | 11 | 11 | 10.8 | 10.7 | 10.1 | 9.5 | 8.6 | 7.9 | 7.3 | 6.8 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 15.3 | 14.7 | 13.9 | 13.4 | 12.8 | 12.2 | 9.2 | 8 | 6.1 | 3.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 15.3 | 13.9 | 12.6 | 11.6 | 10.5 | 9.4 | 3.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 15.3 | 13.5 | 11.8 | 10.4 | 9 | 7.4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 15.3 | 14.3 | 13.3 | 12.7 | 12 | 11.1 | 7.6 | 5.9 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.1 | 10.1 | 10 | 10 | 10 | 9.9 | 9.6 | 9.4 | 8.7 | 8 | 7.1 | 6.3 | 5.9 | 5.5 | 5.2 | 4.8 | 4.4 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.1 | 10 | 9.9 | 9.8 | 9.7 | 9.6 | 9.1 | 8.5 | 7.4 | 5.9 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.1 | 10 | 9.8 | 9.7 | 9.6 | 9.4 | 8.9 | 7.7 | 6 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.1 | 10.1 | 10 | 9.9 | 9.9 | 9.8 | 9.5 | 9.2 | 8.3 | 7.5 | 6.2 | 5.3 | 4.4 | 2.6 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.3 | 18.3 | 18.1 | 17.9 | 17.8 | 17.6 | 17.5 | 17.3 | 16.8 | 15.8 | 15.1 | 14.5 | 14.2 | 13.9 | 13.4 | 13.1 | 12.9 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.3 | 18.1 | 17.7 | 17.3 | 17 | 16.8 | 16.6 | 15.8 | 15.2 | 14.1 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.3 | 18 | 17.4 | 17 | 16.7 | 15.9 | 15.6 | 14.5 | 12.9 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.3 | 18.2 | 17.9 | 17.6 | 17.3 | 17.1 | 16.9 | 16.7 | 15.7 | 15 | 13.3 | 12.5 | 11.9 | 6.9 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.6 | 17.3 | 17.1 | 15.2 | 15.2 | 15.1 | 15 | 14.9 | 14.8 | 14.5 | 14.2 | 14 | 13.8 | 13.7 | 13.6 | 13.6 | 13.5 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.6 | 17.1 | 15.2 | 15.2 | 15 | 14.8 | 14.5 | 14.2 | 13.9 | 13.3 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.6 | 15.3 | 15.2 | 15 | 14.8 | 14.5 | 14.2 | 13.7 | 13.1 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.6 | 17.1 | 15.2 | 15.2 | 15.1 | 15 | 14.9 | 14.7 | 14.4 | 14.1 | 13.7 | 13.4 | 13.1 | 7.4 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.9 | 11.8 | 11.7 | 11.5 | 11.4 | 11.3 | 9.2 | 8.9 | 8.3 | 7.5 | 6.6 | 5.9 | 5.5 | 5.1 | 4.7 | 4.4 | 4 | 1.4 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.9 | 11.6 | 11.3 | 11.1 | 10.9 | 10.6 | 6.3 | 5.4 | 4.2 | 2.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.9 | 11.5 | 11.1 | 10.7 | 10.4 | 9.8 | 6 | 4.5 | 2.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.9 | 11.8 | 11.5 | 11.4 | 11.2 | 11 | 8.8 | 8.2 | 7.3 | 6.2 | 5 | 4.1 | 3.3 | 2.5 | 1.8 | 1.1 | 0 | 0 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11 | 11 | 10.9 | 10.8 | 10.7 | 10.6 | 10.4 | 10.1 | 9.7 | 9.1 | 8.5 | 8.3 | 8 | 7.8 | 7.5 | 7.2 | 6.9 | 4.9 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11 | 11 | 10.8 | 10.6 | 10.4 | 10.2 | 9.6 | 9 | 8.2 | 7.1 | 5.8 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11 | 10.9 | 10.6 | 10.3 | 10 | 9.7 | 9 | 8 | 6.6 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11 | 11 | 10.9 | 10.7 | 10.6 | 10.4 | 10.1 | 9.7 | 9.1 | 8.4 | 7.5 | 7.1 | 6.4 | 5.8 | 5.3 | 4.4 | 0.8 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.9 | 7.3 | 7.3 | 7.2 | 7 | 6.9 | 6.7 | 6.5 | 6.3 | 6 | 5.7 | 5.5 | 5.3 | 5.2 | 5.1 | 4.9 | 4.8 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.9 | 7.3 | 6.9 | 6.6 | 6.3 | 6 | 5.7 | 5.5 | 5.1 | 4.6 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.9 | 7.2 | 6.7 | 6.3 | 6 | 5.6 | 5.2 | 4.7 | 4 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.9 | 7.4 | 7.1 | 6.9 | 6.6 | 6.4 | 6.2 | 6 | 5.7 | 5.4 | 4.9 | 4.6 | 4.3 | 4.1 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.2 | 6.2 | 6.2 | 6.2 | 6.1 | 6.1 | 6 | 5.9 | 5.8 | 5.7 | 5.6 | 5.5 | 5.4 | 5.3 | 5.2 | 5.1 | 5.1 | 4.6 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.2 | 6.2 | 6.1 | 6 | 5.9 | 5.7 | 5.5 | 5.1 | 4.8 | 4.4 | 4 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.2 | 6.2 | 6.1 | 6 | 5.9 | 5.8 | 5.5 | 5.2 | 5 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.2 | 6.2 | 6.2 | 6.1 | 6.1 | 6.1 | 5.9 | 5.8 | 5.6 | 5.5 | 5.3 | 5.1 | 5 | 4.8 | 4.7 | 4.4 | 0.8 | 0 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8 | 3.3 | 1.5
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 4.7 | 4.4 | 4 | 0 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 55.7 | 55.5 | 55.2 | 49 | 48.5 | 48.1 | 47.4 | 46.8 | 45.5 | 43.9 | 42 | 40 | 38.5 | 37.2 | 36.1 | 35.5 | 34.9 | 30 | 24.5
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 55.7 | 55.2 | 54.5 | 47.8 | 46.9 | 45.9 | 44.6 | 42.8 | 39.8 | 35.3 | 31.8 | 28.3 | 25.2 | 22.1 | 19.7 | 17.4 | 15.3 | 1.6 | 0
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 55.7 | 55 | 54.1 | 46.7 | 45.5 | 44.3 | 42.3 | 38.6 | 33.8 | 30 | 26.1 | 23.3 | 18.9 | 16.3 | 14.4 | 12.3 | 10.3 | 0 | 0
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 55.7 | 55.4 | 54.9 | 48.4 | 47.6 | 46.6 | 45.4 | 44.2 | 41.8 | 38.2 | 34.8 | 32.5 | 30.6 | 29 | 27.8 | 26.6 | 25.4 | 0 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.3 | 11.3 | 11.1 | 11 | 10.9 | 10.8 | 10.6 | 10.4 | 9.5 | 8.4 | 7.1 | 5.9 | 5.1 | 4.5 | 3.9 | 3.4 | 3 | 0 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.3 | 11.2 | 10.9 | 10.7 | 10.5 | 10.2 | 9.9 | 9.1 | 7.5 | 5.3 | 3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.3 | 11.1 | 10.7 | 10.3 | 10 | 9.7 | 9.2 | 7.4 | 4.7 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 11.2 | 11 | 10.8 | 10.7 | 10.5 | 10.2 | 9.8 | 8.6 | 7 | 4.9 | 3.3 | 2 | 0.8 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.9 | 20.5 | 20.3 | 20.2 | 20.1 | 20 | 19.8 | 19.6 | 19.4 | 19 | 18.6 | 18.3 | 18 | 17.8 | 17.7 | 17.5 | 17.3 | 16 | 14.5
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.9 | 20.3 | 20 | 19.8 | 19.6 | 19.4 | 19.1 | 18.7 | 18.2 | 17.5 | 16.8 | 16 | 15.3 | 14.5 | 13.9 | 13.3 | 12.6 | 7.7 | 5
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.9 | 20.1 | 19.7 | 19.4 | 19.1 | 18.7 | 18.2 | 17.5 | 16.7 | 16 | 15.1 | 14.5 | 13.9 | 13.2 | 12.7 | 11.7 | 11.1 | 5.7 | 3.1
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.9 | 20.4 | 20.2 | 20.1 | 19.9 | 19.8 | 19.5 | 19.2 | 18.8 | 18.3 | 17.6 | 17.2 | 16.8 | 16.5 | 16.2 | 15.8 | 15.3 | 9.1 | 6.6
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 28 | 27.5 | 27.1 | 26.8 | 26.5 | 26.2 | 46.4 | 45.6 | 44.1 | 41.4 | 38.1 | 35.5 | 33.9 | 32.7 | 31.6 | 30.6 | 29.5 | 21.4 | 12.3
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 28 | 27 | 26.1 | 25.4 | 24.6 | 23.5 | 42.7 | 40.9 | 37.9 | 33.1 | 28.3 | 23.1 | 18.4 | 13.6 | 9.1 | 5.6 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 28 | 26.6 | 25.3 | 24.2 | 22.9 | 21.5 | 40.1 | 35.6 | 29.9 | 24.9 | 19.2 | 11.6 | 7.7 | 2.5 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 28 | 27.4 | 26.7 | 26.2 | 25.4 | 24.4 | 44 | 42.7 | 40.5 | 37 | 32.6 | 29.5 | 26.8 | 24.5 | 22.4 | 20.5 | 14 | 0 | 0
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.1 | 12 | 11.9 | 11.8 | 11.8 | 11.7 | 11.6 | 11.5 | 11.3 | 10.9 | 10.4 | 9.7 | 9.2 | 8.9 | 8.6 | 8.3 | 8 | 6.7 | 5.5
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.1 | 11.9 | 11.7 | 11.5 | 11.4 | 11.2 | 11 | 10.3 | 9.4 | 8.2 | 7.2 | 6.2 | 5.5 | 4.8 | 4.2 | 3.6 | 2.9 | 0 | 0
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.1 | 11.8 | 11.4 | 11.2 | 10.6 | 9.9 | 9.9 | 8.9 | 7.8 | 6.7 | 5.7 | 5 | 1.9 | 1.3 | 0.8 | 0 | 0 | 0 | 0
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.1 | 12 | 11.8 | 11.6 | 11.5 | 11.4 | 11.2 | 10.7 | 9.9 | 9 | 8.1 | 7.4 | 7 | 6.6 | 6.3 | 6 | 5.6 | 2.2 | 0
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.8 | 18.7 | 18.7 | 9.2 | 9.1 | 9 | 11.2 | 11.1 | 10.8 | 10.5 | 10.2 | 10 | 9.8 | 9.7 | 9.6 | 9.5 | 9.4 | 8.5 | 7.5
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.8 | 18.6 | 18.5 | 8.9 | 8.7 | 8.5 | 10.6 | 10.4 | 10 | 9.5 | 9 | 8.5 | 7.9 | 7.4 | 6.9 | 6.5 | 6.1 | 3.8 | 2
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.8 | 18.5 | 18.3 | 8.6 | 8.4 | 8.1 | 10.1 | 9.7 | 9 | 8.4 | 7.8 | 7.3 | 6.9 | 6.5 | 6.2 | 5.8 | 5.4 | 3.3 | 1.4
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.8 | 18.7 | 18.6 | 9.1 | 9 | 8.8 | 10.9 | 10.7 | 10.4 | 10 | 9.6 | 9.3 | 9 | 8.8 | 8.6 | 8.3 | 8 | 1.8 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.6 | 2.5 | 2.4 | 2.3 | 2.3 | 2.2 | 2.9 | 2.7 | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.6 | 2.4 | 2.2 | 2 | 1.9 | 1.8 | 1.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.6 | 2.3 | 2 | 1.8 | 1.6 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.6 | 2.5 | 2.3 | 2.2 | 2.1 | 2 | 2.2 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.8 | 7.6 | 7.5 | 7.4 | 7.3 | 7.4 | 7.3 | 7 | 6.5 | 5.6 | 5.3 | 7.2 | 6.7 | 6.3 | 6 | 5.8 | 5.7 | 4.7 | 3.6
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.8 | 7.5 | 7.2 | 7 | 6 | 4.3 | 3.7 | 3.2 | 2.4 | 0.6 | 0 | 1.7 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.8 | 7.4 | 7 | 6.1 | 4.7 | 4.2 | 3.6 | 2.5 | 1 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.8 | 7.6 | 7.4 | 7.1 | 6.3 | 4.8 | 3.9 | 3.5 | 2.8 | 1.3 | 0 | 2.5 | 2.2 | 1.9 | 1.7 | 1.5 | 1.2 | 0 | 0
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 3.4 | 3.2 | 2.9 | 2.5 | 2.2 | 2 | 1.9 | 1.8 | 1.7 | 1.6 | 0.8 | 0
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 3.3 | 2.9 | 2.5 | 2 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 2.9 | 2.2 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 3.4 | 3.1 | 2.8 | 2.3 | 1.9 | 1.6 | 1.4 | 1.2 | 1.1 | 0.9 | 0 | 0
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.9 | 3.7 | 3.6 | 3.4 | 3.3 | 3 | 2.7 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.7 | 3.3 | 2.9 | 2.7 | 2.4 | 1.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.5 | 3 | 2.6 | 2.2 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.8 | 3.5 | 3.2 | 3 | 2.8 | 2.3 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 49.3 | 48.8 | 48.3 | 47.1 | 46.6 | 46.4 | 49.8 | 49 | 47.7 | 45.4 | 43.2 | 43.5 | 42.4 | 41.5 | 40.8 | 40.2 | 39.4 | 35 | 30.1
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 49.3 | 48.2 | 46.4 | 45.5 | 43.9 | 41.6 | 44.1 | 42 | 38.6 | 34.4 | 31.3 | 30.8 | 28.3 | 25.8 | 23.8 | 21.8 | 19.7 | 3.5 | 0
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 49.3 | 47.1 | 45.4 | 43.4 | 41 | 39.3 | 41.4 | 37.9 | 33.5 | 29.8 | 26.3 | 26.7 | 15.1 | 13 | 11.4 | 9.6 | 7.6 | 0 | 0
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 49.3 | 48.7 | 47 | 46.1 | 44.8 | 42.6 | 44.8 | 43.1 | 40.7 | 37.4 | 34.6 | 35.3 | 33.9 | 32.8 | 31.9 | 30.9 | 29.6 | 16.9 | 7.1
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 17.4 | 17.5 | 17.4 | 16.7 | 16.7 | 16.3 | 16 | 15.7 | 15.5 | 15.5 | 15.4 | 15.1 | 14.6
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.9 | 13.9 | 13.9 | 13 | 13 | 12.9 | 16.2 | 15.6 | 15.1 | 14.4 | 14.2 | 14 | 13.8 | 13.6 | 13.4 | 13.3 | 13.1 | 12.1 | 11.3
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.9 | 13.9 | 13.1 | 13.1 | 13 | 12.1 | 15.3 | 14.9 | 14.4 | 14.1 | 13.9 | 13.7 | 13.5 | 13.4 | 13.2 | 13.1 | 12.9 | 12 | 11.4
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.9 | 13.9 | 13.9 | 13.1 | 13 | 13 | 15.8 | 15.5 | 15.2 | 14.7 | 14.4 | 14.3 | 14.2 | 14.2 | 14.1 | 14 | 13.9 | 13.2 | 12.5
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 28.1 | 27.9 | 27.5 | 27.1 | 27 | 26.6 | 33.4 | 32.6 | 30.5 | 27.6 | 24.6 | 22.2 | 20.6 | 19.4 | 18.1 | 17 | 16 | 9.3 | 1.7
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 28.1 | 27.5 | 26.5 | 25.3 | 23.7 | 22 | 27.1 | 24.9 | 21.3 | 16.6 | 12.4 | 7.8 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 28.1 | 27.3 | 25.9 | 24.7 | 22.5 | 19.7 | 24.7 | 20.5 | 14.8 | 10 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 28.1 | 27.7 | 27 | 25.9 | 24.8 | 23.5 | 28.3 | 27 | 24.2 | 21.1 | 17.1 | 14.3 | 11.8 | 9.6 | 8 | 6.6 | 0 | 0 | 0
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.4 | 9 | 8.9 | 8.9 | 8.8 | 8.7 | 8.5 | 8.3 | 8 | 7.5 | 7 | 6.5 | 6.3 | 6 | 5.8 | 5.6 | 5.4 | 3.7 | 1.8
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.4 | 8.8 | 8.6 | 8.4 | 8.2 | 8.1 | 7.7 | 7.3 | 6.7 | 5.8 | 4.9 | 3.8 | 2.8 | 1.8 | 1 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.4 | 8.7 | 8.4 | 8.1 | 7.8 | 7.6 | 7.1 | 6.3 | 5.2 | 4.3 | 3.2 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.4 | 8.9 | 8.8 | 8.7 | 8.5 | 8.4 | 8.1 | 7.8 | 7.4 | 6.8 | 6.1 | 5.5 | 5 | 4.5 | 4 | 3.6 | 3.1 | 0 | 0
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.3 | 6.2 | 6.2 | 6.1 | 6.1 | 6.1 | 5.9 | 5.7 | 5.5 | 5.3 | 5 | 4.8 | 4.7 | 4.6 | 4.6 | 4.5 | 4.4 | 3.8 | 3.1
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.3 | 6.2 | 6 | 6 | 5.7 | 5.5 | 5.1 | 4.8 | 4.5 | 4.2 | 3.8 | 3.5 | 3.1 | 2.8 | 2.5 | 2.2 | 0 | 0 | 0
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.3 | 6.1 | 5.9 | 5.7 | 5.4 | 5.2 | 4.8 | 4.4 | 4 | 3.6 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.3 | 6.2 | 6.1 | 6.1 | 5.9 | 5.7 | 5.4 | 5.2 | 4.9 | 4.6 | 4.3 | 4 | 3.9 | 3.7 | 3.6 | 3.4 | 0 | 0 | 0
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.6 | 17.7 | 17.6 | 17.5 | 17.5 | 17.4 | 17.2 | 17.2 | 17 | 16.9 | 16.9 | 16.9 | 15.5 | 15.5 | 15.3 | 15.1 | 15 | 14.7 | 14.2
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.6 | 17.7 | 17.6 | 17.3 | 17 | 16.8 | 15.5 | 15.3 | 15.1 | 14.7 | 14.2 | 13.6 | 12.9 | 12.2 | 11.7 | 11.4 | 11.1 | 9.7 | 8.4
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.6 | 17.7 | 17.4 | 17.1 | 16.9 | 16.7 | 15.3 | 15 | 14.5 | 14 | 13.3 | 12.9 | 12.5 | 12.1 | 11.9 | 11.7 | 11.4 | 10 | 8.7
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.6 | 17.7 | 17.6 | 17.5 | 17.5 | 17.4 | 17.1 | 17 | 16.9 | 15.5 | 15.4 | 15.1 | 14.7 | 14.4 | 14.2 | 14.1 | 14 | 13.2 | 12.4
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.3 | 9.2 | 9.2 | 9.1 | 9.1 | 9 | 11.4 | 11.4 | 11.2 | 10.8 | 10.3 | 9.7 | 9.2 | 8.9 | 8.6 | 8.3 | 8 | 6.7 | 5.4
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.3 | 9.2 | 9 | 8.9 | 8.8 | 8.7 | 11 | 10.3 | 9.3 | 8.2 | 7.2 | 6.2 | 5.5 | 4.8 | 4.2 | 3.6 | 2.9 | 0 | 0
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.3 | 9.1 | 8.9 | 8.6 | 8.5 | 8.3 | 9.9 | 8.9 | 7.8 | 6.7 | 5.6 | 5 | 1.9 | 1.3 | 0.8 | 0 | 0 | 0 | 0
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.3 | 9.2 | 9.1 | 8.9 | 8.9 | 8.8 | 11 | 10.7 | 9.9 | 8.9 | 8.1 | 7.4 | 7 | 6.6 | 6.3 | 5.9 | 5.6 | 2.2 | 0
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11 | 11 | 10.9 | 11.1 | 11 | 10.9 | 18.8 | 18.7 | 18.7 | 18.3 | 15.4 | 15.2 | 15.1 | 15 | 15 | 14.8 | 14.6 | 13.7 | 10.8
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11 | 10.9 | 10.7 | 9.9 | 9.8 | 9.8 | 16.2 | 16.2 | 14.2 | 13.8 | 13.1 | 12.4 | 11.6 | 10.6 | 9.8 | 8.9 | 8 | 2.6 | 0
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11 | 10.8 | 10.6 | 10.7 | 7.9 | 7.8 | 15.8 | 15.4 | 12.7 | 11.8 | 9.8 | 8.6 | 6.2 | 5.2 | 4.6 | 3.7 | 2.9 | 0 | 0
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11 | 11 | 10.8 | 10 | 9.9 | 9.9 | 17.7 | 17.7 | 14.5 | 14.2 | 13.7 | 13.2 | 12.9 | 12.4 | 12.1 | 11.6 | 8.1 | 3.7 | 0
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 27.6 | 27.6 | 27.5 | 27.5 | 27.4 | 27.4 | 27.3 | 27.2 | 27.1 | 27 | 26.4 | 26.3 | 26.2 | 26 | 25.7 | 25.4 | 25.3 | 25 | 24.6
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 27.6 | 27.5 | 27.4 | 27.3 | 27.3 | 27.2 | 27.1 | 27 | 26.3 | 26.1 | 25.7 | 24.9 | 24.4 | 23.9 | 23.7 | 23.5 | 23.1 | 22.2 | 21.3
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 27.6 | 27.5 | 27.3 | 27.2 | 27.1 | 26.5 | 26.1 | 25.7 | 25.2 | 24.8 | 24.3 | 24 | 23.7 | 23.5 | 23.4 | 23.2 | 22.8 | 21.9 | 21.4
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 27.6 | 27.6 | 27.5 | 27.4 | 27.4 | 27.3 | 27.2 | 27.1 | 26.3 | 26 | 25.4 | 25 | 24.7 | 24.4 | 24.3 | 24.3 | 24 | 23.4 | 22.7
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.7 | 16.7 | 16.6 | 16.6 | 16.6 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.4 | 16.4 | 16.3 | 16.3 | 16.3 | 16.2 | 16.2 | 15.7 | 15.1
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.7 | 16.6 | 16.6 | 16.5 | 16.4 | 16.2 | 16.2 | 16 | 15.7 | 15.4 | 15 | 14.7 | 14.3 | 13.9 | 13.6 | 13.3 | 12.9 | 11.1 | 9.6
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.7 | 16.6 | 16.5 | 16.4 | 16.2 | 15.9 | 15.9 | 15.6 | 15.2 | 14.9 | 14.5 | 14.3 | 14 | 13.8 | 13.5 | 13.2 | 12.9 | 11.2 | 9.8
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.7 | 16.7 | 16.6 | 16.6 | 16.5 | 16.5 | 16.5 | 16.5 | 16.4 | 16.4 | 16.4 | 16.3 | 16.2 | 16.1 | 16 | 15.9 | 15.7 | 14.7 | 13.6
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.6 | 2.6 | 2.5 | 2.4 | 2.3 | 2.2 | 3 | 2.7 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.6 | 2.5 | 2.2 | 2.1 | 2 | 1.8 | 1.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.6 | 2.4 | 2.1 | 1.9 | 1.7 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.6 | 2.5 | 2.4 | 2.3 | 2.2 | 2.1 | 2.3 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 84.8 | 83.8 | 83.5 | 83.2 | 83 | 82.8 | 84.2 | 83.9 | 83.6 | 83.2 | 82.7 | 82.2 | 81.9 | 75.9 | 75.9 | 75.7 | 75.5 | 74.6 | 72.6
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 84.8 | 83.5 | 82.9 | 82.4 | 81.9 | 81.6 | 82.5 | 81.9 | 75.8 | 75.4 | 74.3 | 72.2 | 70.7 | 69.6 | 68.5 | 67.4 | 66.3 | 60.4 | 54.8
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 84.8 | 83.2 | 82.3 | 81.7 | 80 | 79.3 | 75.1 | 74.4 | 73.3 | 71.7 | 69.6 | 68.7 | 67.9 | 66.9 | 66 | 64.9 | 63.7 | 57.3 | 51.8
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 84.8 | 83.7 | 83.3 | 83 | 82.6 | 82.3 | 83.6 | 83 | 82.2 | 75.8 | 75.5 | 74.8 | 74.3 | 74.1 | 73.9 | 73.6 | 73.2 | 69.3 | 65.3
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 17.7 | 17.6 | 17.5 | 17.4 | 17.3 | 17.2 | 18 | 17.9 | 17.8 | 17.6 | 17.5 | 17.5 | 17.4 | 16.8 | 16.8 | 16.6 | 16.4 | 15.9 | 15.3
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 17.7 | 17.4 | 17.2 | 17 | 16.9 | 16.7 | 17.5 | 17.4 | 16.8 | 16.7 | 16.1 | 15.2 | 14.9 | 14.7 | 14.4 | 14.1 | 13.8 | 12.1 | 10.6
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 17.7 | 17.3 | 16.9 | 16.6 | 16.5 | 15.7 | 16.3 | 15.8 | 15.3 | 14.8 | 14.1 | 14 | 13.8 | 13.6 | 13.3 | 13 | 12.7 | 10.9 | 9.3
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 17.7 | 17.6 | 17.4 | 17.3 | 17.2 | 17 | 17.8 | 17.6 | 17.4 | 16.8 | 16.3 | 16 | 15.9 | 15.9 | 15.8 | 15.7 | 15.5 | 14.4 | 13.3
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.2 | 11 | 10.9 | 10.7 | 10.6 | 10.4 | 24.8 | 24.6 | 24.2 | 23.4 | 22.3 | 21.4 | 21.2 | 21.1 | 21 | 20.8 | 20.5 | 18.9 | 17
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.2 | 10.8 | 10.5 | 10.2 | 10 | 9.8 | 23.7 | 22.9 | 21.4 | 20.3 | 19.2 | 18 | 17.2 | 16.2 | 15.5 | 14.8 | 14 | 8.8 | 5.2
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.2 | 10.6 | 10.1 | 9.6 | 9.1 | 8.5 | 22.3 | 21.1 | 19.7 | 18.5 | 17.1 | 16.4 | 14 | 13.2 | 12.6 | 12 | 11.3 | 7.2 | 4.6
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.2 | 11 | 10.7 | 10.4 | 10.2 | 9.8 | 23.8 | 23.1 | 22.2 | 21.5 | 20.7 | 20 | 19.5 | 19.1 | 18.9 | 18.5 | 18.1 | 14.2 | 11.1
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.8 | 11.5 | 11.5 | 11.5 | 11.4 | 11.3 | 11.6 | 11.5 | 11.4 | 11.3 | 11.2 | 10.9 | 10.6 | 10.6 | 10.5 | 10.2 | 9.9 | 9.1 | 9
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.8 | 11.5 | 11.4 | 11.2 | 10.5 | 10.3 | 10.9 | 10.5 | 9.8 | 9.3 | 8.4 | 7.4 | 6.9 | 6.4 | 6.1 | 6 | 5.8 | 2.6 | 0
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.8 | 11.4 | 11.2 | 11.1 | 10.8 | 10.6 | 11 | 10.4 | 9.5 | 8.5 | 7.4 | 7.3 | 5.6 | 5.2 | 4.7 | 3.8 | 3 | 0 | 0
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.8 | 11.5 | 11.4 | 11.2 | 11.2 | 11.1 | 11.3 | 11.2 | 10.9 | 10.5 | 9.9 | 9.2 | 8.7 | 8.5 | 8.4 | 8.4 | 5.8 | 3.7 | 0
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.5 | 10.5 | 10.4 | 10.3 | 10.3 | 10.2 | 18.2 | 18.1 | 18 | 17.9 | 17.8 | 17.7 | 17.7 | 17.7 | 17.7 | 17.6 | 17.6 | 17.5 | 16.4
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.5 | 10.4 | 10.2 | 10.1 | 10 | 9.9 | 17.8 | 17.7 | 17.6 | 17.5 | 16.5 | 16.5 | 16.4 | 16.3 | 16.2 | 16.1 | 16 | 15.2 | 14.6
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.5 | 10.4 | 10.2 | 10 | 9.9 | 9.8 | 17.7 | 17.5 | 17.5 | 16.5 | 16.4 | 16.3 | 16.2 | 16 | 16 | 15.8 | 15.7 | 15 | 14.5
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.5 | 10.4 | 10.3 | 10.2 | 10.1 | 10 | 17.9 | 17.8 | 17.7 | 17.6 | 17.5 | 17.5 | 17.5 | 16.5 | 16.5 | 16.5 | 16.4 | 16.1 | 15.6
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 24.4 | 24.2 | 24 | 23.8 | 23.7 | 23.6 | 24.9 | 24.5 | 23.7 | 22.6 | 21.9 | 21.2 | 20.6 | 20.1 | 19.7 | 19.4 | 19.2 | 17.2 | 14.9
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 24.4 | 23.9 | 23.4 | 22.9 | 22.3 | 21.3 | 21.7 | 20.5 | 19.2 | 17.3 | 16 | 14.7 | 13.5 | 12.2 | 11.1 | 10.1 | 9.2 | 3.8 | 1.6
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 24.4 | 23.7 | 23.1 | 22.2 | 21.2 | 20.1 | 20.3 | 18.5 | 16.5 | 14.9 | 13.5 | 12.5 | 11.5 | 10.6 | 9.6 | 9 | 8.1 | 2.2 | 0.9
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 24.4 | 24.1 | 23.7 | 23.3 | 22.6 | 21.7 | 22 | 21.1 | 20 | 18.5 | 17.3 | 16.5 | 15.8 | 15.2 | 14.7 | 14.1 | 12.2 | 8.2 | 6.4
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 1.8 | 1.7 | 1.4 | 1 | 0.7 | 0.5 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 2.2 | 0 | 0
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 30.9 | 30.8 | 30.7 | 30.5 | 30.4 | 30.3 | 30 | 29.9 | 29.9 | 30.1 | 30.3 | 29.6 | 28.9 | 25 | 23.8 | 23.3 | 23.2 | 22.7 | 22
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 30.9 | 30.6 | 30.3 | 30.1 | 29.8 | 29.6 | 29.2 | 28.8 | 25.1 | 22 | 19.9 | 18.4 | 17.2 | 16 | 14.8 | 14.4 | 14.1 | 12.3 | 10.8
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 30.9 | 30.5 | 30.1 | 29.8 | 29.5 | 29.2 | 25.3 | 24.2 | 21.9 | 19.1 | 17 | 15.8 | 14.7 | 13.5 | 13.2 | 12.8 | 12.4 | 10.4 | 8.7
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 30.9 | 30.8 | 30.5 | 30.3 | 30.1 | 29.9 | 29.5 | 29.1 | 28.7 | 23.1 | 20.7 | 19.4 | 18.2 | 17.3 | 16.3 | 16.1 | 15.9 | 14.7 | 13.5
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.9 | 20.6 | 20.9 | 20.8 | 20.6 | 20.3 | 20.2 | 19.9 | 19.6 | 19.3 | 19 | 18.8 | 18.7 | 18.6 | 18.5 | 18.4 | 18.3 | 17.4 | 16.4
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.9 | 20.2 | 20 | 19.5 | 18.2 | 17.7 | 17.2 | 16.7 | 16.2 | 15.6 | 15 | 14.4 | 13.9 | 13.5 | 13 | 12.5 | 12 | 8.7 | 6.4
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.9 | 20 | 19.6 | 19 | 18.3 | 17.5 | 16.7 | 15.9 | 15.3 | 14.6 | 13.9 | 13.4 | 11.8 | 11.4 | 11 | 10.4 | 9.8 | 6.8 | 4.1
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.9 | 20.4 | 20.3 | 19.9 | 19.5 | 19 | 18.6 | 18.1 | 17.7 | 17.2 | 16.7 | 16.5 | 16.3 | 16.2 | 16 | 15.8 | 15.4 | 11.6 | 9.8
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 17.3 | 16.7 | 16.5 | 16 | 15.3 | 14.7 | 12.6 | 11.8 | 11.1 | 10.3 | 9.5 | 6.3 | 4.6 | 2.5 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 17.3 | 15.7 | 14.5 | 13.3 | 11.1 | 9.8 | 7 | 4.9 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 17.3 | 15.2 | 13.5 | 11.7 | 9.8 | 7.9 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 17.3 | 16.3 | 15.5 | 14.4 | 13.2 | 12 | 9.4 | 7.7 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.7 | 18.7 | 18.5 | 18.4 | 18.3 | 18.2 | 28.9 | 28.8 | 28.8 | 28.7 | 28.6 | 28.3 | 28.1 | 25.8 | 25.7 | 25.7 | 25.6 | 25.4 | 25
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.7 | 18.5 | 18.3 | 18.2 | 18 | 17.9 | 28.5 | 28.2 | 25.9 | 24.9 | 24.3 | 23.8 | 23.5 | 23.2 | 23.1 | 22.9 | 22.7 | 21.7 | 20.7
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.7 | 18.5 | 18.2 | 18 | 17.8 | 17.6 | 28.1 | 25.7 | 24.8 | 23.9 | 23.4 | 23.1 | 22.8 | 22.6 | 22.4 | 22.3 | 22.1 | 21 | 20
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.7 | 18.6 | 18.4 | 18.3 | 18.2 | 18 | 28.6 | 28.4 | 28.1 | 25.3 | 24.6 | 24.3 | 24.1 | 23.9 | 23.9 | 23.8 | 23.7 | 23 | 22.2
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 14.7 | 14.6 | 12.6 | 12.3 | 11.6 | 11 | 10.6 | 10.3 | 10.1 | 9.9 | 9.6 | 7.7 | 5.5
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 12.6 | 12.5 | 11.8 | 10.8 | 9.6 | 8.4 | 7.3 | 6.1 | 5.4 | 4.6 | 2.1 | 0 | 0
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 12.4 | 11.6 | 10.1 | 8.9 | 7.4 | 2.9 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 12.6 | 12.3 | 11.6 | 10.6 | 9.9 | 9.2 | 8.7 | 8.4 | 8 | 7.1 | 2.5 | 0
Chesterfield 132kV | PINXTON 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 18.5 | 18.5 | 18.3 | 18.3 | 18.2 | 18.2 | 17.6 | 17.5 | 17.2 | 16.6 | 16.4 | 16.3 | 16.3 | 16.2 | 16.1 | 16.1 | 16 | 15.6 | 15.1
Chesterfield 132kV | PINXTON 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 18.5 | 18.4 | 18.2 | 18.1 | 17.7 | 17 | 15.8 | 15.5 | 15.2 | 15 | 14.7 | 14.4 | 14.2 | 13.9 | 13.7 | 13.5 | 13.3 | 11.3 | 10.4
Chesterfield 132kV | PINXTON 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 18.5 | 18.4 | 18.2 | 17.8 | 17.2 | 16.5 | 15.7 | 15.5 | 15.1 | 14.8 | 14.4 | 14.2 | 12.8 | 12.6 | 12.4 | 12.2 | 12 | 10.6 | 9.8
Chesterfield 132kV | PINXTON 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 18.5 | 18.4 | 18.3 | 18.2 | 17.9 | 17.3 | 15.9 | 15.6 | 15.4 | 15.2 | 15 | 14.8 | 14.7 | 14.6 | 14.5 | 14.3 | 14.2 | 8.2 | 7.3
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 30.1 | 29.4 | 29.4 | 29.3 | 29.3 | 29.2 | 28.2 | 28.2 | 28.2 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 27.6
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 30.1 | 29.4 | 29.3 | 29.3 | 29.3 | 29.2 | 28.2 | 28.2 | 28.1 | 28.1 | 28.1 | 27.8 | 27.7 | 27.6 | 27.5 | 27.4 | 27.3 | 26.8 | 26.5
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 30.1 | 29.4 | 29.3 | 29.3 | 29.3 | 29.2 | 28 | 27.9 | 27.7 | 27.6 | 27.4 | 27.4 | 27.3 | 27.2 | 27.1 | 27 | 26.9 | 26.5 | 23.5
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 30.1 | 29.4 | 29.3 | 29.3 | 29.3 | 29.2 | 28.2 | 28.2 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28 | 27.2 | 26.9
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 6.8 | 6.7 | 6.7 | 6.7 | 6.6 | 6.5 | 6.4 | 5.9 | 5.3 | 4.6 | 4.1 | 3.8 | 3.6 | 3.3 | 3.1 | 2.9 | 0 | 0
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 6.8 | 6.7 | 6.6 | 6.6 | 6.5 | 6.3 | 6 | 5.3 | 4.3 | 3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 6.7 | 6.6 | 6.6 | 6.5 | 6.4 | 6.2 | 5.4 | 4.2 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.8 | 6.7 | 6.7 | 6.6 | 6.6 | 6.5 | 6.3 | 5.7 | 5.1 | 4.2 | 3.4 | 2 | 0.9 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.1 | 16.1 | 16 | 16 | 16 | 15.9 | 15.8 | 15.8 | 15.8 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.1 | 16.1 | 16 | 16 | 16 | 15.9 | 15.8 | 15.8 | 15.8 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.1 | 16.1 | 16 | 16 | 16 | 15.9 | 15.8 | 15.8 | 15.8 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.1 | 16.1 | 16 | 16 | 16 | 15.9 | 15.8 | 15.8 | 15.8 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 3 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.8 | 2.8 | 2.7 | 2.7 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.4 | 2.2
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 3 | 2.9 | 2.8 | 2.6 | 2.5 | 2.3 | 2.2 | 2.1 | 1.9 | 1.7 | 1.5 | 1.3 | 1.1 | 1 | 0.9 | 0.8 | 0 | 0
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 2.9 | 2.9 | 2.7 | 2.6 | 2.5 | 2.4 | 2.3 | 2.1 | 2 | 1.9 | 1.8 | 1.7 | 1.6 | 1.5 | 1.5 | 1.4 | 0.8 | 0
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 3 | 2.9 | 2.9 | 2.9 | 2.9 | 2.8 | 2.8 | 2.8 | 2.7 | 2.7 | 2.6 | 2.6 | 2.5 | 2.5 | 2.5 | 2.4 | 2.1 | 1.8
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.6 | 15.6 | 15.5 | 15.4 | 15.3 | 15.2 | 21.7 | 21.5 | 21.2 | 20.7 | 20.2 | 19.8 | 19.6 | 19.4 | 19.3 | 19.1 | 19 | 17.8 | 16.8
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.6 | 15.5 | 15.3 | 15.2 | 15 | 14.9 | 21.2 | 21 | 20.4 | 19.7 | 18.9 | 18.2 | 17.5 | 16.9 | 15.2 | 14.8 | 14.3 | 10.7 | 8.2
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.6 | 15.5 | 15.2 | 15 | 14.9 | 14.7 | 21 | 20.4 | 19.4 | 18.6 | 17.8 | 17.2 | 16.8 | 15.4 | 14.6 | 14.2 | 13.7 | 10.7 | 9.4
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.6 | 15.5 | 15.4 | 15.3 | 15.1 | 15 | 21.4 | 21.3 | 20.8 | 20.3 | 19.6 | 19.2 | 18.8 | 18.4 | 17.9 | 17.6 | 17.4 | 14.7 | 12.5
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.6 | 4.5 | 4.4 | 3.6 | 3.5 | 3.4 | 3.3 | 3.1 | 2.9 | 2.6 | 2.3 | 2.1 | 2 | 2 | 1.9 | 1.8 | 1.7 | 0.9 | 0
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.6 | 4.4 | 3.4 | 3.2 | 3.1 | 2.9 | 2.6 | 2.4 | 2 | 1.6 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.6 | 3.6 | 3.3 | 3 | 2.8 | 2.5 | 2.2 | 1.8 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.6 | 4.5 | 3.6 | 3.4 | 3.3 | 3.1 | 3 | 2.8 | 2.4 | 2.1 | 1.8 | 1.6 | 1.4 | 1.2 | 1 | 0.9 | 0.7 | 0 | 0
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 17.4 | 17.3 | 17.3 | 17.2 | 17.2 | 17.2 | 17.1 | 17.1 | 17.1 | 17 | 16.9 | 16.9 | 16.9 | 16.8 | 16.8 | 16.7 | 15.7 | 15.7 | 15.5
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 17.4 | 17.3 | 17.2 | 17.1 | 17 | 17 | 16.9 | 16.9 | 16.8 | 16.8 | 15.7 | 15.5 | 15.2 | 15.1 | 15 | 14.9 | 14.8 | 14.3 | 13.7
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 17.4 | 17.2 | 17.1 | 17 | 16.9 | 16.8 | 16.7 | 15.7 | 15.7 | 15.4 | 15 | 14.9 | 14.8 | 14.7 | 14.7 | 14.6 | 14.5 | 13.8 | 12.8
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 17.4 | 17.3 | 17.2 | 17.2 | 17.1 | 17.1 | 17 | 17 | 16.9 | 16.8 | 16.7 | 15.6 | 15.5 | 15.5 | 15.5 | 15.4 | 15.4 | 15.1 | 14.7
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.4 | 17.3 | 17.3 | 17.2 | 17.2 | 17.2 | 17.1 | 17.1 | 17 | 17 | 16.9 | 16.9 | 16.9 | 16.8 | 16.8 | 16.7 | 15.7 | 15.7 | 15.5
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.4 | 17.3 | 17.2 | 17.1 | 17 | 17 | 16.9 | 16.9 | 16.8 | 16.8 | 15.7 | 15.5 | 15.2 | 15.1 | 15 | 14.9 | 14.8 | 14.3 | 13.7
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.4 | 17.2 | 17.1 | 17 | 16.9 | 16.8 | 16.7 | 15.7 | 15.7 | 15.4 | 15 | 14.9 | 14.8 | 14.8 | 14.7 | 14.6 | 14.5 | 13.8 | 12.8
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.4 | 17.3 | 17.2 | 17.2 | 17.1 | 17.1 | 17 | 16.9 | 16.9 | 16.8 | 16.7 | 15.6 | 15.5 | 15.5 | 15.5 | 15.4 | 15.4 | 15.1 | 14.7
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.2 | 17.2 | 17.2 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17 | 16.9
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.2 | 17.2 | 17.1 | 17.1 | 17 | 17 | 17 | 17 | 16.9 | 16.8 | 16.8 | 16.5 | 15.9
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.2 | 17.2 | 17.1 | 17.1 | 17.1 | 17 | 17 | 16.9 | 16.9 | 16.6 | 16.6 | 16.5 | 16.5
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.2 | 17.2 | 17.2 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17 | 17 | 17 | 16.7 | 16.5
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.8 | 3.5 | 3.4 | 3.4 | 3.4 | 3.3 | 3.2 | 3.1 | 3 | 2.8 | 2.5 | 2.4 | 2.2 | 2.2 | 2.1 | 2 | 1.9 | 1.2 | 0
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.8 | 3.4 | 3.3 | 3.3 | 3.1 | 3 | 2.8 | 2.7 | 2.4 | 2.1 | 1.7 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.8 | 3.3 | 3.2 | 3.1 | 2.9 | 2.8 | 2.6 | 2.3 | 1.9 | 1.5 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.8 | 3.4 | 3.4 | 3.3 | 3.3 | 3.2 | 3 | 2.9 | 2.7 | 2.5 | 2.2 | 1.9 | 1.7 | 1.5 | 1.3 | 1.1 | 0.9 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.9 | 3.8 | 3.7 | 3.6 | 3.5 | 3.4 | 3.3 | 3.2 | 3 | 2.9 | 1 | 0.9 | 0.8 | 0.6 | 0.5 | 0 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.8 | 3.6 | 3.4 | 3.1 | 3 | 2.8 | 2.6 | 2.3 | 2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.7 | 3.4 | 3.1 | 2.8 | 2.5 | 2.1 | 1.5 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.9 | 3.7 | 3.5 | 3.3 | 3.2 | 3 | 2.8 | 2.4 | 2 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7 | 6.8 | 6.7 | 6.6 | 6.5 | 6.4 | 6.2 | 6.1 | 6.1 | 6 | 5.8 | 5.7 | 5.5 | 5.5 | 5.4 | 5.3 | 5.3 | 5 | 4.7
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7 | 6.7 | 6.5 | 6.3 | 6 | 5.6 | 5.3 | 4.9 | 4.7 | 4.5 | 4.3 | 4.1 | 3.9 | 3.7 | 3.5 | 3.3 | 3.2 | 2.2 | 1.4
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7 | 6.7 | 6.4 | 6.1 | 5.7 | 5.2 | 4.7 | 4.4 | 4.1 | 4 | 3.8 | 3.6 | 3.5 | 3.3 | 3.1 | 2.9 | 2.8 | 1.6 | 0.7
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7 | 6.8 | 6.6 | 6.4 | 6.1 | 5.7 | 5.4 | 5.1 | 4.9 | 4.7 | 4.6 | 4.4 | 4.3 | 4.2 | 4.2 | 4 | 4 | 0 | 0
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.9 | 2.8 | 2.7 | 2.6 | 2.6 | 2.5 | 2.2 | 2.1 | 2 | 1.9 | 1.8 | 1.8 | 1.7 | 1.7 | 1.6 | 1.4 | 1.1 | 0.6 | 9.6
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.9 | 2.6 | 2.4 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.9 | 2.5 | 2.1 | 1.8 | 1.5 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.9 | 2.7 | 2.6 | 2.4 | 2.3 | 2.1 | 1.8 | 1.7 | 1.6 | 1.4 | 1.1 | 0.5 | 0 | 0 | 0 | 2 | 1.8 | 0.9 | 7.6
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 38.9 | 25.2 | 24.8 | 24.9 | 24.6 | 24.3 | 24.4 | 24.1 | 23.9 | 23.1 | 20.3 | 19.8 | 19.2 | 18.7 | 18.2 | 17.3 | 16.6 | 14.4 | 21.6
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 38.9 | 24.7 | 24 | 22.6 | 11.3 | 10.8 | 10.8 | 10.4 | 7.2 | 5.9 | 3.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 38.9 | 24.4 | 23.3 | 22.8 | 20.4 | 19.5 | 19.1 | 17.6 | 13.6 | 11.4 | 8.6 | 7.3 | 4.7 | 3.5 | 2.7 | 3.6 | 2.2 | 0 | 0
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 38.9 | 25 | 24.5 | 23.2 | 22.7 | 22.3 | 22.3 | 21.8 | 18.8 | 17.7 | 15.8 | 14 | 12.9 | 12.3 | 11.9 | 13.3 | 10.9 | 5.9 | 6.1
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.9 | 8.8 | 8.6 | 8.5 | 8.3 | 8.1 | 7.9 | 7.7 | 7.4 | 7 | 6.7 | 4.7 | 4.5 | 4.2 | 4 | 3.8 | 3.7 | 2.6 | 1.4
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.9 | 8.6 | 8.2 | 7.9 | 7.5 | 7.2 | 6.8 | 6.4 | 5.9 | 5.2 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.9 | 8.4 | 7.9 | 7.5 | 7 | 6.5 | 5.8 | 4.9 | 4 | 3.3 | 2.6 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.9 | 8.7 | 8.4 | 8.1 | 7.8 | 7.5 | 7.2 | 6.8 | 6.2 | 5.6 | 4.9 | 2.9 | 2.6 | 2.3 | 2.1 | 1.8 | 1.4 | 0 | 0
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 4.4 | 4.1 | 3.9 | 3.5 | 3.3 | 3.1 | 3 | 2.9 | 2.8 | 2.7 | 1.9 | 1
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 4.4 | 3.9 | 3.3 | 2.9 | 2.3 | 1.9 | 1.4 | 1.1 | 0.8 | 0 | 0 | 0
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 3.9 | 3.1 | 2.4 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 4.6 | 4.1 | 3.7 | 3.2 | 2.9 | 2.6 | 2.4 | 2.3 | 2.1 | 0 | 0 | 0
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9 | 8.9 | 8.9 | 8.8 | 8.8 | 8.8 | 8.7 | 8.7 | 8.7 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.5 | 8.5 | 8.5 | 7.6 | 7.4
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9 | 8.8 | 8.8 | 8.7 | 8.7 | 8.7 | 8.6 | 8.6 | 8.5 | 8.5 | 7.6 | 7.6 | 7.5 | 7.4 | 7.3 | 7.1 | 7 | 6.2 | 5.5
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9 | 8.8 | 8.7 | 8.6 | 8.6 | 8.6 | 8.5 | 7.7 | 7.6 | 7.5 | 7.3 | 7.2 | 7.1 | 7 | 6.9 | 6.8 | 6.6 | 5.8 | 5.2
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9 | 8.9 | 8.8 | 8.8 | 8.8 | 8.8 | 8.7 | 8.7 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.5 | 7.7 | 7.6 | 7.6 | 7.2 | 6.7
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 4.6 | 4.4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3.9 | 3.4
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 2.5 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.9 | 1.5 | 1 | 0 | 0 | 0
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 2.6 | 2.6 | 2.5 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 0 | 0 | 0
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.4 | 11.4 | 11.2 | 11.1 | 11 | 10.9 | 10.7 | 10.5 | 9.6 | 8.5 | 7.1 | 6 | 5.2 | 4.6 | 3.9 | 3.5 | 3 | 0 | 0
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.4 | 11.3 | 11 | 10.8 | 10.6 | 10.3 | 10 | 9.2 | 7.6 | 5.3 | 3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.4 | 11.2 | 10.8 | 10.4 | 10.1 | 9.8 | 9.3 | 7.5 | 4.8 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.4 | 11.4 | 11.1 | 10.9 | 10.8 | 10.6 | 10.3 | 9.9 | 8.6 | 7.1 | 4.9 | 3.3 | 2 | 0.9 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.7 | 12.1 | 12 | 11.9 | 11.8 | 11.7 | 12.4 | 12.3 | 12.1 | 11.8 | 11.2 | 10.8 | 10.6 | 10.5 | 10.4 | 10.2 | 9.8 | 9.1 | 9
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.7 | 12 | 11.7 | 11.4 | 10.4 | 10.3 | 10.9 | 10.5 | 9.8 | 9.3 | 8.4 | 7.4 | 6.9 | 6.4 | 6.1 | 5.9 | 5.8 | 2.6 | 0
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.7 | 11.9 | 11.5 | 11.2 | 10.8 | 10.5 | 10.9 | 10.3 | 9.4 | 8.5 | 7.3 | 7.2 | 5.5 | 5.2 | 4.7 | 3.8 | 2.9 | 0 | 0
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.7 | 12.1 | 11.9 | 11.6 | 11.4 | 11.3 | 11.8 | 11.5 | 10.9 | 10.5 | 9.9 | 9.1 | 8.7 | 8.5 | 8.4 | 8.4 | 5.8 | 3.7 | 0
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 36.9 | 30.8 | 30.5 | 30.2 | 29.9 | 29.7 | 57.1 | 56.6 | 55.8 | 54.6 | 53.2 | 52.2 | 51.6 | 51.2 | 50.8 | 50.3 | 49.7 | 46.4 | 43
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 36.9 | 30.4 | 29.6 | 29 | 27.9 | 27.2 | 54 | 52.9 | 51.2 | 49.5 | 47.3 | 44.9 | 43 | 41 | 39.4 | 37.9 | 34.6 | 23.9 | 17.4
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 36.9 | 30.1 | 29 | 28.1 | 27.1 | 26.2 | 52.8 | 50.9 | 48.5 | 46.2 | 43.5 | 38.3 | 35.5 | 32.6 | 31.4 | 30.1 | 28.5 | 19.2 | 14.5
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 36.9 | 30.6 | 30.1 | 29.5 | 29 | 28.4 | 55.4 | 54.5 | 53.2 | 52 | 50.2 | 48.7 | 47.5 | 46.6 | 45.9 | 45.2 | 38.8 | 28.6 | 22.8
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.2 | 9.1 | 9.1 | 9 | 9 | 9 | 8.9 | 8.8 | 8.8 | 8.7 | 8.7 | 7.4 | 7.3 | 7.1 | 6.9 | 6.8 | 6.8 | 6.4 | 6
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.2 | 9.1 | 9 | 8.9 | 8.8 | 8.8 | 8.6 | 7.5 | 7.1 | 6.6 | 6.2 | 5.9 | 5.6 | 5.3 | 5 | 4.7 | 4.6 | 3.5 | 2.5
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.2 | 9 | 8.8 | 8.7 | 8.7 | 7.5 | 7.2 | 6.8 | 6.3 | 5.9 | 5.6 | 5.3 | 5 | 4.8 | 4.6 | 4.3 | 4.1 | 3.1 | 2.3
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.2 | 9.1 | 9 | 8.9 | 8.9 | 8.8 | 8.6 | 7.6 | 7.3 | 6.9 | 6.5 | 6.3 | 6.1 | 6 | 5.9 | 5.7 | 5.6 | 4.9 | 4.1
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.4 | 12.5 | 12.5 | 12.5 | 12.4 | 12.4 | 12.2 | 12.1 | 11.7 | 11.1 | 10.4 | 9.9 | 9.6 | 9.4 | 9.1 | 8.9 | 8.6 | 6.9 | 5
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.4 | 12.5 | 12.4 | 12.3 | 12.1 | 12 | 11.6 | 11.4 | 10.7 | 9.4 | 8.1 | 6.7 | 5.5 | 4.1 | 3.5 | 2.8 | 2.1 | 0 | 0
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.4 | 12.5 | 12.3 | 12.2 | 12 | 11.9 | 11.6 | 10.5 | 9 | 7.7 | 6.3 | 5.1 | 4.4 | 3.6 | 3.1 | 2.6 | 2 | 0 | 0
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.4 | 12.5 | 12.5 | 12.4 | 12.3 | 12.2 | 12 | 11.8 | 11.3 | 10.7 | 9.7 | 9.1 | 8.4 | 7.9 | 7.5 | 7.1 | 6.7 | 3.8 | 0
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.9 | 8.9 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.7 | 8.5 | 8.1 | 7.7 | 7.4 | 7.2 | 7.1 | 6.9 | 6.8 | 6.6 | 5.6 | 4.5
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.9 | 8.8 | 8.8 | 8.7 | 8.7 | 8.6 | 8.5 | 8.3 | 7.8 | 7.2 | 6.5 | 5.8 | 5.2 | 4.6 | 4.1 | 3.6 | 3.1 | 0 | 0
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.9 | 8.8 | 8.7 | 8.6 | 8.6 | 8.5 | 8.4 | 7.8 | 7.1 | 6.5 | 5.8 | 5.3 | 4.8 | 4.3 | 3.9 | 3.5 | 2.7 | 0 | 0
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.9 | 8.8 | 8.8 | 8.8 | 8.7 | 8.7 | 8.7 | 8.5 | 8.2 | 7.8 | 7.3 | 6.9 | 6.5 | 6.2 | 5.9 | 5.7 | 5.4 | 3.5 | 1.3
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10 | 9.9 | 9.8 | 9.7 | 9.7 | 9.6 | 9.4 | 9.3 | 9.1 | 9 | 7.3 | 7.2 | 7 | 7 | 6.8 | 6.7 | 6.6 | 5.6 | 3.7
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10 | 9.8 | 9.6 | 9.5 | 9.4 | 9.3 | 9 | 8.9 | 7.2 | 6.9 | 6.4 | 5.8 | 5 | 4 | 3.3 | 2.5 | 1.6 | 0 | 0
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10 | 9.7 | 9.4 | 9.3 | 9.2 | 9 | 7.3 | 7.1 | 6.4 | 5.8 | 4.7 | 3.6 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10 | 9.8 | 9.7 | 9.6 | 9.5 | 9.4 | 9.2 | 9 | 8.9 | 7.2 | 6.9 | 6.6 | 6.2 | 5.9 | 5.7 | 5.3 | 4.7 | 1.4 | 0
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.3 | 18.2 | 18.1 | 18 | 17.9 | 18 | 17.9 | 17.6 | 17.2 | 15.2 | 14.8 | 11.3 | 7.8 | 3.9 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.3 | 18.1 | 17.9 | 17.7 | 17.1 | 15 | 14.1 | 13.1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.3 | 18.1 | 17.7 | 16.9 | 14.9 | 14.1 | 13.3 | 10.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.3 | 18.2 | 18 | 17.7 | 17.1 | 15 | 14.3 | 13 | 12.2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.4 | 19.1 | 19 | 18.9 | 18.8 | 18.7 | 18.5 | 18.4 | 18.3 | 18.2 | 18.1 | 18 | 18 | 18 | 18 | 17.9 | 17.9 | 17.5 | 17.2
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.4 | 19 | 18.8 | 18.6 | 18.5 | 18.3 | 18.1 | 18 | 17.9 | 17.8 | 17.6 | 17.5 | 17.4 | 17.2 | 17.2 | 14.9 | 14.8 | 14 | 12.7
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.4 | 18.9 | 18.6 | 18.4 | 18.2 | 18 | 17.7 | 17.6 | 17.4 | 17.2 | 17.1 | 14.9 | 14.8 | 14.8 | 14.7 | 14.5 | 14.3 | 12.9 | 11.3
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.4 | 19 | 18.9 | 18.8 | 18.7 | 18.5 | 18.3 | 18.2 | 18.1 | 18 | 17.9 | 17.8 | 17.7 | 17.6 | 17.6 | 17.5 | 17.4 | 14.8 | 14.2
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.8 | 17.7 | 17.6 | 17.5 | 17.4 | 17.8 | 18.2 | 18.3 | 18.7 | 18.3 | 18.8 | 18.8 | 18.6 | 18.2 | 17.9 | 17.9 | 17.9 | 17.7 | 17.3
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.8 | 17.6 | 17.2 | 17 | 16.8 | 16.1 | 15.8 | 13.5 | 13.2 | 12.1 | 11.3 | 10.9 | 10.6 | 10.4 | 10.1 | 10 | 9.8 | 8.8 | 7.8
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.8 | 17.5 | 17 | 16.8 | 16.3 | 16.1 | 13.5 | 13.1 | 12.4 | 11.5 | 10.7 | 10.5 | 10.2 | 10 | 9.8 | 9.7 | 9.4 | 8.2 | 6.9
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.8 | 17.6 | 17.3 | 17.2 | 17.1 | 16.4 | 15.8 | 13.5 | 13.3 | 12.3 | 11.5 | 11.2 | 11.1 | 11 | 10.9 | 10.9 | 10.8 | 10.2 | 9.5
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.9 | 17.6 | 17.6 | 17.5 | 17.5 | 17.5 | 17.4 | 17.4 | 17.3 | 17.1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15.4 | 15.3
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.9 | 17.6 | 17.5 | 17.3 | 17.1 | 17 | 15.3 | 14.8 | 14.6 | 14.4 | 14.1 | 14 | 13.9 | 13.8 | 13.7 | 13.6 | 13.5 | 12.8 | 12.2
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.9 | 17.6 | 17.4 | 17.2 | 17 | 15.3 | 15.1 | 14.7 | 14.4 | 14.2 | 13.9 | 13.8 | 13.7 | 13.6 | 13.5 | 13.4 | 13.3 | 12.6 | 11.9
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.9 | 17.6 | 17.5 | 17.4 | 17.2 | 17 | 15.4 | 15.1 | 14.9 | 14.7 | 14.4 | 14.2 | 14.1 | 14 | 14 | 14 | 13.9 | 13.5 | 13
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 32 | 31.7 | 31.6 | 31.4 | 31.2 | 31 | 30.6 | 30.5 | 30.4 | 30.2 | 30 | 29.8 | 29.6 | 29.5 | 29.4 | 29.3 | 29.2 | 29 | 28.7
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 32 | 31.6 | 31 | 30.7 | 30.4 | 30.2 | 29.7 | 29.4 | 29.2 | 28.8 | 25.2 | 25.1 | 25 | 24.9 | 24.7 | 24.6 | 24.4 | 23.2 | 21.8
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 32 | 31.5 | 30.9 | 30.4 | 30 | 29.8 | 29.3 | 28.9 | 28.7 | 25.1 | 24.9 | 24.7 | 24.6 | 24.4 | 24.2 | 24 | 23.7 | 22.3 | 20.9
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 32 | 31.7 | 31.2 | 30.9 | 30.6 | 30.3 | 29.8 | 29.6 | 29.4 | 29 | 28.8 | 28.7 | 25.2 | 25.2 | 25.1 | 25.1 | 25.1 | 24.5 | 23.6
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 82.5 | 81.7 | 81.5 | 81.3 | 79.8 | 79.8 | 85.1 | 84.8 | 84.1 | 83.1 | 79.3 | 78.9 | 78.4 | 77.9 | 77.3 | 76.7 | 76.2 | 73 | 69
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 82.5 | 81.5 | 79.7 | 79.3 | 79 | 78.4 | 79.4 | 78.4 | 76.8 | 73.9 | 70.8 | 67.9 | 65.5 | 62.9 | 61.4 | 59.8 | 58.1 | 48.6 | 39.2
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 82.5 | 81.4 | 79.5 | 79 | 78.3 | 77.3 | 78.3 | 75.5 | 72.3 | 68.6 | 65.1 | 62.9 | 61.2 | 59.6 | 58.3 | 56.8 | 55.2 | 44.6 | 37.1
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 82.5 | 81.7 | 81.3 | 79.6 | 79.4 | 78.9 | 82.3 | 79.3 | 78.2 | 76.4 | 73.8 | 72.3 | 70.9 | 69.7 | 68.9 | 68 | 66.9 | 60 | 52.5
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 31.6 | 31.6 | 31.6 | 31.5 | 31.4 | 31.4 | 30.6 | 30.5 | 30.5 | 30.4 | 30.4 | 30.4 | 30.4 | 30.3 | 30.3 | 30.3 | 30.2 | 29.8 | 29.2
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 31.6 | 31.6 | 31.6 | 31.5 | 31.3 | 31.2 | 30.3 | 30.3 | 30.2 | 30 | 29.8 | 29.6 | 29.4 | 29.1 | 28.9 | 28.7 | 28.4 | 27.3 | 26
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 31.6 | 31.6 | 31.6 | 31.3 | 31 | 30.8 | 29.8 | 29.5 | 29.3 | 29 | 28.7 | 28.5 | 28.3 | 28.1 | 27.9 | 27.6 | 27.3 | 25.9 | 24.4
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 31.6 | 31.6 | 31.6 | 31.5 | 31.4 | 31.4 | 30.6 | 30.5 | 30.4 | 30.2 | 30.1 | 30 | 29.9 | 29.8 | 29.7 | 29.6 | 29.4 | 28.5 | 27.5
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.6 | 20.5 | 20.4 | 20.3 | 20.2 | 20.1 | 19.9 | 19.8 | 17.9 | 17.8 | 15.5 | 11.3 | 7.8 | 3.9 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.6 | 20.4 | 20.3 | 20.1 | 19.9 | 17.8 | 17.5 | 16.4 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.6 | 20.4 | 20.1 | 19.9 | 17.8 | 17.4 | 16.4 | 10.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.6 | 20.5 | 20.3 | 20.1 | 20 | 17.8 | 17.5 | 16.6 | 13.4 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 28.4 | 27.3 | 26.7 | 26.2 | 25.7 | 25.4 | 24.9 | 23.9 | 21.9 | 19 | 15.5 | 11.3 | 7.7 | 3.9 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 28.4 | 26.6 | 25.5 | 24.3 | 22.7 | 20.8 | 20.1 | 16.4 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 28.4 | 26.3 | 24.7 | 22.9 | 20.4 | 18.3 | 17 | 10.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 28.4 | 27 | 26.1 | 25 | 23.5 | 21.5 | 21.3 | 18.1 | 13.4 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.4 | 15.4 | 15.4 | 15.4 | 15.3 | 15.3 | 15.2 | 15.1 | 15 | 15 | 14.4 | 14.1 | 13.9 | 13.6 | 13.6 | 13.6 | 13.5 | 12.8 | 11.9
Coventry 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.4 | 15.4 | 15.3 | 15.3 | 15.2 | 15.1 | 15 | 14.4 | 13.7 | 13.1 | 12.5 | 11.5 | 10.7 | 10.1 | 9.7 | 9.4 | 9 | 7.2 | 5.3
Coventry 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.4 | 15.4 | 15.3 | 15.2 | 15.1 | 15 | 14.2 | 13.4 | 12.5 | 11.8 | 11 | 9.9 | 9.2 | 8.5 | 8.2 | 7.9 | 7.5 | 5.4 | 3.4
Coventry 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.4 | 15.4 | 15.4 | 15.3 | 15.2 | 15.1 | 15 | 14.4 | 13.9 | 13.2 | 12.7 | 11.8 | 11.2 | 10.8 | 10.6 | 10.4 | 10.2 | 8.7 | 7.2
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.1 | 19 | 18.9 | 18.7 | 18.6 | 18.4 | 18.2 | 18.1 | 18 | 17.7 | 17.4 | 17.1 | 17 | 17 | 16.9 | 16.9 | 16.8 | 15 | 14.5
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.1 | 18.7 | 18.2 | 17.7 | 17.3 | 16.9 | 15.1 | 15 | 14.8 | 14.6 | 14.3 | 13.9 | 13.6 | 13.4 | 13.1 | 12.8 | 12.5 | 10.9 | 9.3
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.1 | 18.6 | 17.9 | 17.3 | 16.8 | 15.2 | 14.9 | 14.7 | 14.4 | 14 | 13.6 | 13.3 | 13.1 | 12.8 | 12.6 | 12.3 | 12 | 10.2 | 8.8
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.1 | 18.8 | 18.4 | 18 | 17.7 | 17.3 | 16.9 | 16.8 | 15.1 | 15 | 14.8 | 14.6 | 14.4 | 14.3 | 14.2 | 14 | 13.8 | 12.8 | 11.6
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 19.4 | 19.4 | 19.4 | 19.4 | 19.3 | 19.3 | 18.8 | 18.8 | 18.8 | 18.7 | 18.5 | 18.4 | 18.3 | 18.2 | 18.2 | 18.2 | 18.1 | 17.8 | 17.4
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 19.4 | 19.4 | 19.4 | 19.4 | 19.3 | 19.2 | 18.5 | 18.2 | 18 | 17.7 | 17.4 | 17.2 | 17 | 17 | 17 | 15.2 | 15.1 | 14.5 | 13.6
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 19.4 | 19.4 | 19.4 | 19.4 | 19.2 | 18.9 | 18.1 | 17.7 | 17.4 | 17.2 | 17 | 15.2 | 15 | 15 | 14.9 | 14.8 | 14.6 | 13.6 | 12.2
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 19.4 | 19.4 | 19.4 | 19.4 | 19.3 | 19.3 | 18.7 | 18.3 | 18.1 | 17.8 | 17.6 | 17.4 | 17.2 | 17.1 | 17.1 | 17 | 17 | 15 | 14.3
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.4 | 13 | 12.8 | 12.5 | 12.2 | 12.1 | 12.4 | 12.2 | 11.6 | 10.9 | 10.1 | 7.7 | 5 | 1.6 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.4 | 12.6 | 11.7 | 10.9 | 10.3 | 10 | 10.3 | 8.9 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.4 | 12.4 | 11.5 | 10.8 | 10.1 | 9.8 | 8.7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.4 | 12.8 | 12.3 | 11.7 | 11.1 | 10.9 | 11.2 | 10.2 | 7.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 47.5 | 46.7 | 46.3 | 46 | 42.1 | 41.7 | 44.3 | 43.4 | 42.2 | 40.7 | 37.7 | 35.9 | 34.6 | 33.3 | 32.1 | 30.9 | 30.2 | 11.7 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 47.5 | 46.3 | 45.3 | 40.9 | 40.1 | 39 | 38.9 | 36 | 32.3 | 28.2 | 24.1 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 47.5 | 46 | 41.2 | 40.2 | 39.1 | 37.8 | 35.7 | 31.2 | 26 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 47.5 | 46.5 | 45.8 | 41.5 | 40.8 | 39.9 | 40.3 | 37.7 | 34.4 | 31 | 27.2 | 24.4 | 16.8 | 4.6 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.4 | 18.7 | 18.5 | 18.2 | 17.9 | 17.6 | 17.3 | 16.9 | 16.7 | 14.9 | 14.1 | 13.5 | 12.9 | 12.3 | 11.7 | 11.2 | 11.2 | 10.8 | 10.2
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.4 | 18.5 | 17.8 | 17 | 15.5 | 14.6 | 13.6 | 11.6 | 9.6 | 7.7 | 6.4 | 5.2 | 4.1 | 2.9 | 2 | 1.8 | 1.6 | 0 | 0
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.4 | 18.4 | 17.6 | 16.7 | 15 | 14.4 | 12.1 | 9.9 | 7.9 | 6.1 | 4.7 | 3.6 | 2.5 | 1.4 | 1.1 | 0 | 0 | 0 | 0
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.4 | 18.6 | 17.9 | 17.1 | 16.4 | 14.8 | 13.8 | 12 | 10.1 | 8.3 | 6.9 | 5.9 | 5 | 4 | 3.1 | 2.8 | 2.7 | 1.9 | 0
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 5.2 | 5.2 | 5.1 | 5 | 4.9 | 7.5 | 7.3 | 8.9 | 8.5 | 7.8 | 7.1 | 6.6 | 6.2 | 5.8 | 4.2 | 1.8 | 0 | 0
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 5 | 4.7 | 4.6 | 4.4 | 4.2 | 6.8 | 6.6 | 8 | 5.7 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 4.9 | 4.5 | 4.2 | 3.9 | 3.7 | 6.2 | 3.7 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 5.2 | 4.9 | 4.8 | 4.7 | 4.6 | 7.1 | 7 | 8.5 | 7.4 | 5.6 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 18 | 18 | 17.9 | 17.9 | 17.9 | 17.9 | 17.4 | 17.5 | 17.4 | 17.4 | 17.4 | 17.3 | 17.1 | 16.9 | 16.7 | 16.5 | 16.5 | 16.5 | 16.4
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 18 | 18 | 17.9 | 17.9 | 17.9 | 17.9 | 17.4 | 17.4 | 17.2 | 16.7 | 16.3 | 15.8 | 15.8 | 15.7 | 15.7 | 15.7 | 15.7 | 15.5 | 15.4
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 18 | 18 | 17.9 | 17.9 | 17.9 | 17.9 | 17.2 | 16.9 | 16.6 | 15.8 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.6 | 15.6 | 15.5 | 15.3
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 18 | 18 | 17.9 | 17.9 | 17.9 | 17.9 | 17.4 | 17.3 | 17 | 16.7 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.7 | 15.7 | 15.6
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.6 | 12.4 | 12.4 | 12.5 | 12.6 | 12.5 | 12.6 | 12.6 | 12.2 | 11.6 | 11 | 10.4 | 10.1 | 9.7 | 9.4 | 7.9 | 6.2 | 3.8 | 2.2
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.6 | 12.4 | 12.4 | 12.2 | 12.1 | 12.2 | 12.3 | 12 | 11.3 | 10.3 | 7.4 | 4 | 2.8 | 1.6 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.6 | 12.3 | 12.3 | 12.1 | 12.1 | 12 | 11.8 | 11.1 | 10 | 7.1 | 2.9 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.6 | 12.4 | 12.5 | 12.5 | 12.4 | 12.5 | 12.7 | 12.5 | 12 | 11.3 | 9.5 | 6.4 | 4.6 | 3.8 | 3.1 | 2.4 | 1.6 | 0 | 0
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.2 | 15.6 | 15.7 | 16.2 | 16.4 | 16.3 | 16.6 | 16.5 | 16.2 | 15.8 | 15.3 | 14.8 | 14.5 | 14.2 | 9.7 | 7.4 | 4.5 | 3.5 | 2.5
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.2 | 15.4 | 15.3 | 15.1 | 14.8 | 15 | 15.1 | 14.7 | 14.1 | 13.1 | 8.8 | 3.8 | 3 | 2.3 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.2 | 15.3 | 15.2 | 15 | 15.4 | 15.1 | 15.2 | 14.2 | 13.2 | 8.7 | 2.1 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.2 | 15.4 | 15.3 | 15.6 | 15.4 | 15.7 | 15.9 | 15.7 | 15.2 | 14.5 | 12.1 | 7.1 | 4.6 | 4.1 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10 | 9.6 | 9.5 | 9.3 | 9.2 | 9.1 | 8.9 | 8.8 | 8.4 | 7.9 | 7.3 | 6.9 | 6.6 | 6.4 | 6.1 | 5.9 | 5.7 | 4 | 2.1
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10 | 9.4 | 9 | 8.8 | 8.6 | 8.3 | 7.9 | 7.6 | 6.9 | 6.1 | 5.2 | 4.2 | 3.3 | 2.3 | 1.6 | 0.8 | 0 | 0 | 0
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10 | 9.3 | 8.7 | 8.4 | 8 | 7.6 | 7.1 | 6.2 | 5 | 4 | 2.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10 | 9.6 | 9.3 | 9.1 | 8.9 | 8.7 | 8.4 | 8.1 | 7.5 | 6.9 | 6 | 5.5 | 4.9 | 4.4 | 4 | 3.6 | 2.8 | 0 | 0
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.9 | 13.3 | 13.3 | 13.3 | 13.3 | 13.7 | 18.6 | 18.7 | 18.7 | 18.1 | 17.4 | 16.7 | 16.3 | 16 | 15.2 | 14.5 | 13.9 | 11.5 | 9.3
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.9 | 13.2 | 13.1 | 12.6 | 12.5 | 12.2 | 17.5 | 17 | 16 | 14.2 | 12.2 | 10.2 | 8.8 | 7.3 | 6.1 | 5.1 | 4.1 | 0 | 0
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.9 | 13.2 | 12.8 | 12.5 | 12.3 | 11.4 | 16.6 | 14.9 | 13.1 | 11.1 | 8.8 | 7.5 | 6.5 | 5.4 | 4.6 | 3.7 | 2.7 | 0 | 0
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.9 | 13.3 | 13.3 | 13 | 13 | 12.6 | 17.8 | 17.5 | 17 | 15.9 | 13.9 | 12.6 | 11.7 | 11 | 10.4 | 9.8 | 9 | 4.7 | 1.3
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.5 | 19.5 | 19.6 | 19.6 | 19.6 | 19.9 | 19.9 | 20 | 19.9 | 19.3 | 18.8 | 18.5 | 18.5 | 18.5 | 18.5 | 18.3 | 18.1 | 18 | 17.8
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.5 | 19.5 | 19.4 | 19.2 | 19.1 | 18.7 | 18 | 17.6 | 14.7 | 13.8 | 13.2 | 12.7 | 12.6 | 12.4 | 12.3 | 12.2 | 12 | 11.2 | 10.3
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.5 | 19.5 | 19.2 | 19 | 18.5 | 18 | 17.5 | 14.8 | 14.3 | 13.4 | 12.5 | 12.5 | 12.4 | 12.3 | 12.1 | 12 | 11.8 | 10.7 | 9.6
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.5 | 19.5 | 19.5 | 19.3 | 19.2 | 18.8 | 17.9 | 17.5 | 14.7 | 14.2 | 13.7 | 13.3 | 13.1 | 13.1 | 13.1 | 13.1 | 13 | 12.5 | 11.9
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 80.3 | 79.9 | 79.9 | 79.7 | 79.5 | 79.8 | 85.5 | 85.6 | 85.3 | 84 | 83.3 | 82.5 | 79.7 | 79.3 | 78.3 | 77.9 | 77.1 | 73.4 | 68.8
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 80.3 | 79.6 | 78.8 | 77.9 | 77.3 | 76 | 78 | 75.6 | 72.3 | 66.1 | 60.9 | 56.6 | 53.8 | 50.8 | 51.2 | 49.1 | 47 | 35.7 | 26.6
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 80.3 | 79.3 | 78.1 | 77.1 | 75.6 | 73.9 | 74.6 | 70.1 | 65.1 | 59.5 | 53.7 | 51.2 | 49 | 49.4 | 47.7 | 45.7 | 43.5 | 32.1 | 21
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 80.3 | 79.8 | 79.3 | 78.6 | 78.2 | 76.9 | 78.7 | 76.9 | 74.3 | 69.5 | 64.7 | 61.8 | 59.9 | 58.6 | 57.5 | 56.5 | 55 | 46.9 | 39
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 34.6 | 32.9 | 32.9 | 33.5 | 33.6 | 33.1 | 32.3 | 31.6 | 30.2 | 28.6 | 27.3 | 26.4 | 25.7 | 22.4 | 15.7 | 11.2 | 5.8 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 34.6 | 32.6 | 32.3 | 31.7 | 30.6 | 29.8 | 27.4 | 25.2 | 22.4 | 16.6 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 34.6 | 32.4 | 32 | 30.9 | 30.5 | 27.9 | 26.1 | 22.8 | 17.9 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 34.6 | 32.7 | 32.6 | 32.7 | 32.1 | 32 | 31.7 | 29.6 | 27.6 | 25.1 | 16.7 | 6.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.8 | 10.8 | 10.8 | 10.7 | 10.7 | 10.7 | 10.7 | 10.4 | 10.4 | 10.3 | 10.2 | 10 | 9.9 | 9.7 | 9.5 | 9.3 | 9.1 | 8.1 | 7.5
Coventry 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.8 | 10.8 | 10.7 | 10.7 | 8.8 | 8.8 | 8.6 | 8.4 | 8.1 | 6.8 | 5.5 | 4.2 | 3 | 1.7 | 2.2 | 1.6 | 1 | 0 | 0
Coventry 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.8 | 10.7 | 10.7 | 10.7 | 10.4 | 10.4 | 10.3 | 9.9 | 9.4 | 9 | 7.8 | 6.6 | 6.1 | 5.5 | 6.2 | 5.6 | 5 | 2.1 | 2.2
Coventry 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.8 | 10.8 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.4 | 10.4 | 10.1 | 9.7 | 9.4 | 9 | 8.7 | 8.4 | 8 | 7.6 | 5.8 | 5.1
Coventry 132kV | RUGBY 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 17.4 | 17.4 | 17.4 | 17.2 | 17 | 16.9 | 16 | 15.8 | 15.6 | 15.4 | 15.1 | 14.9 | 14.8 | 19.1 | 19 | 19 | 20.7 | 20.1 | 19.5
Coventry 132kV | RUGBY 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 17.4 | 17.3 | 17 | 16.8 | 16.5 | 16.2 | 15.3 | 15.1 | 14.9 | 14.1 | 13.2 | 12.4 | 11.8 | 15.6 | 8.4 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 17.4 | 17.2 | 16.8 | 16.5 | 16.1 | 15.8 | 14.9 | 14 | 13 | 12.2 | 11.4 | 10.8 | 10.6 | 14.2 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 17.4 | 17.4 | 17.1 | 17 | 16.7 | 16.5 | 15.6 | 15.4 | 15.2 | 14.8 | 14.4 | 14.1 | 13.9 | 18.2 | 18.1 | 17.9 | 19.6 | 11.3 | 0
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 67.1 | 66 | 62.2 | 61.6 | 61 | 60.6 | 63.5 | 63 | 63.7 | 62.4 | 60.6 | 57.2 | 53.9 | 49.9 | 45.6 | 41.9 | 36 | 30.7 | 26.3
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 67.1 | 61.7 | 60.2 | 59.1 | 57.7 | 56.5 | 58.9 | 56.7 | 54.7 | 44.6 | 35.1 | 25.8 | 17.2 | 10 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 67.1 | 61.3 | 59.5 | 57.9 | 56.1 | 54.9 | 55.8 | 48 | 40.5 | 30.3 | 19.4 | 12.7 | 7 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 67.1 | 62.3 | 61.2 | 60.4 | 59.3 | 58.6 | 61.3 | 59.8 | 58.6 | 50.9 | 43 | 36.3 | 29.7 | 25 | 20.5 | 19.5 | 14.5 | 0 | 0
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.4 | 14.9 | 14.7 | 14.6 | 14.5 | 14.5 | 15 | 14.9 | 14.9 | 14.8 | 14.7 | 14.5 | 14.3 | 14.1 | 9.8 | 7.4 | 4.5 | 3.5 | 2.5
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.4 | 14.7 | 14.6 | 14.5 | 14.4 | 14.2 | 14.5 | 14.3 | 14.1 | 13.2 | 8.9 | 3.9 | 3 | 2.3 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.4 | 14.7 | 14.6 | 14.4 | 14.2 | 14 | 14.3 | 13.8 | 13.3 | 8.8 | 2.2 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.4 | 14.7 | 14.6 | 14.6 | 14.5 | 14.3 | 14.8 | 14.7 | 14.6 | 14.2 | 12.2 | 7.2 | 4.6 | 4.1 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.9 | 13.6 | 13.6 | 13.5 | 13.5 | 13.5 | 13.4 | 13.4 | 13.2 | 13 | 12.7 | 12.3 | 11.9 | 11.6 | 12.4 | 12.1 | 11.8 | 10 | 9.8
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.9 | 13.6 | 13.5 | 13.4 | 8.8 | 8.7 | 8.6 | 8.4 | 8.1 | 6.8 | 5.5 | 4.2 | 2.9 | 1.7 | 2.2 | 1.6 | 1 | 0 | 0
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.9 | 13.6 | 13.5 | 13.4 | 13.3 | 13.2 | 12.9 | 11.7 | 10.3 | 9.1 | 7.8 | 6.6 | 6.1 | 5.5 | 6.2 | 5.6 | 5 | 2 | 2.2
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.9 | 13.6 | 13.6 | 13.5 | 13.5 | 13.4 | 13.4 | 13.3 | 13.1 | 12.4 | 11.7 | 11.1 | 10.5 | 9.9 | 10.5 | 9.9 | 9.3 | 6.1 | 5.3
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.2 | 12.1 | 12 | 11.9 | 11.7 | 11.6 | 12.3 | 12.1 | 11.6 | 10.9 | 10.1 | 9.6 | 9.2 | 7.4 | 7.2 | 6.9 | 6.7 | 4.9 | 2.7
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.2 | 12 | 11.7 | 11.4 | 11.1 | 10.8 | 11.1 | 10.8 | 10 | 8.9 | 7.5 | 6.1 | 5 | 0.6 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.2 | 11.8 | 11.4 | 11.1 | 10.8 | 10.5 | 10.5 | 9.4 | 7.8 | 6.5 | 4.9 | 3.9 | 3 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.2 | 12.1 | 11.9 | 11.6 | 11.4 | 11.2 | 11.7 | 11.5 | 10.8 | 10.1 | 8.7 | 7.9 | 7.3 | 5.2 | 4.9 | 4.5 | 4.1 | 0 | 0
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.6 | 19.5 | 14.7 | 14.6 | 14.5 | 14.4 | 14.4 | 14.2 | 14 | 13.9 | 13.6 | 13.4 | 13.3 | 13.1 | 13 | 12.9 | 12.8 | 11.9 | 11
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.6 | 14.7 | 14.5 | 14.4 | 14 | 13.5 | 13 | 12.5 | 12 | 11 | 10.1 | 9.2 | 8.4 | 7.5 | 7.3 | 7 | 6.7 | 5 | 3.3
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.6 | 14.6 | 14.4 | 13.9 | 13.4 | 12.9 | 12.2 | 10.8 | 9.7 | 8.8 | 8 | 7.2 | 7 | 6.9 | 6.7 | 6.4 | 6 | 4 | 2
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.6 | 14.7 | 14.6 | 14.5 | 14.3 | 14.1 | 13.9 | 13.6 | 13.3 | 12.9 | 12.5 | 12.2 | 12 | 11.8 | 11.5 | 11.3 | 10.9 | 9.2 | 7.9
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.9 | 17.8 | 17.7 | 17.7 | 17.6 | 17.6 | 17.7 | 17.7 | 17.6 | 17.5 | 17.4 | 17.4 | 17.4 | 17.3 | 17.3 | 17.3 | 17.3 | 17 | 16.3
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.9 | 17.7 | 17.6 | 17.5 | 17.4 | 17.3 | 17.5 | 17.4 | 17.3 | 17.2 | 17.1 | 16.9 | 16.3 | 16.3 | 16.2 | 15.5 | 15.5 | 14.9 | 13.7
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.9 | 17.7 | 17.5 | 17.4 | 17.2 | 17 | 17.2 | 17.1 | 16.4 | 16.3 | 16.2 | 15.5 | 15.5 | 15.4 | 15.3 | 15.2 | 15.1 | 13.8 | 12.4
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.9 | 17.8 | 17.7 | 17.6 | 17.5 | 17.4 | 17.6 | 17.5 | 17.4 | 17.3 | 17.3 | 17.2 | 17.1 | 17.1 | 17 | 16.8 | 16.3 | 15.5 | 15
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17 | 17 | 17 | 16.9 | 16.9 | 16.9 | 16.8 | 16.8 | 15.6 | 15.3 | 14.8 | 11.3 | 7.7 | 3.9 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17 | 16.9 | 16.9 | 16.8 | 16.8 | 16.8 | 15.7 | 15.6 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17 | 16.9 | 16.9 | 16.8 | 16.8 | 16.8 | 15.6 | 10.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17 | 17 | 16.9 | 16.9 | 16.9 | 16.8 | 16.7 | 15.7 | 13.4 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 22.2 | 21.8 | 21.4 | 21 | 20.4 | 19.6 | 18.6 | 17.7 | 16.4 | 16.2 | 15.8 | 15.6 | 15.5 | 15.4 | 13.8 | 13.2 | 18.5 | 17.8 | 16.9
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 22.2 | 21.3 | 20.1 | 18.5 | 16.4 | 13.7 | 15.7 | 12.8 | 9.7 | 8.3 | 3.3 | 2.9 | 2.5 | 2.1 | 1.7 | 1.4 | 1 | 0 | 0
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 22.2 | 21.2 | 19.9 | 18.1 | 15.9 | 13.3 | 15.2 | 11.9 | 8.5 | 2.2 | 1.6 | 1.3 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 22.2 | 21.4 | 20.3 | 18.7 | 16.7 | 13.9 | 15.6 | 12.6 | 9.6 | 9.5 | 3.6 | 3.4 | 3.3 | 3.1 | 2.9 | 2.7 | 2.4 | 0.9 | 0
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 72 | 71 | 70.3 | 69.6 | 68.8 | 67.7 | 59.9 | 58.7 | 57.2 | 56.5 | 55.6 | 54.8 | 54.1 | 53.5 | 52.6 | 51.6 | 56.5 | 64.6 | 62.8
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 72 | 70.3 | 68.6 | 66.7 | 59.6 | 56.5 | 51.5 | 48.1 | 55.5 | 52.3 | 45.4 | 43.1 | 41 | 39 | 39 | 37.8 | 36.5 | 28.5 | 22.8
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 72 | 70 | 68.1 | 65.9 | 63.1 | 59.8 | 54.7 | 49.5 | 55.4 | 47.1 | 44.7 | 42.7 | 41.5 | 40.3 | 40.3 | 38.7 | 36.9 | 28.1 | 22.3
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 72 | 70.5 | 69.1 | 67.2 | 64.8 | 61.9 | 56.5 | 53 | 60.5 | 59.3 | 52.1 | 50.9 | 49.8 | 48.9 | 49.2 | 48.3 | 47.2 | 41.3 | 36.5
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.8 | 14.8 | 14.7 | 14.7 | 14.6 | 14.6 | 14.9 | 14.8 | 14.8 | 14.6 | 14.5 | 14 | 13.8 | 13.4 | 13.2 | 13.1 | 13 | 12.2 | 11.2
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.8 | 14.7 | 14.5 | 14.3 | 14.2 | 13.9 | 13.7 | 13.2 | 12.6 | 11.4 | 10.2 | 9.3 | 8.5 | 7.7 | 9.8 | 9.3 | 8.9 | 6.4 | 4.1
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.8 | 14.6 | 14.4 | 14.1 | 13.7 | 13.2 | 12.8 | 11.8 | 10.8 | 9.6 | 8.5 | 7.8 | 7.2 | 9.1 | 8.8 | 8.3 | 7.9 | 5.1 | 0
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.8 | 14.8 | 14.6 | 14.5 | 14.4 | 14.1 | 13.8 | 13.4 | 12.9 | 11.9 | 10.9 | 10.3 | 9.9 | 9.5 | 9.2 | 9 | 8.7 | 6.9 | 5.1
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7 | 7 | 7 | 6.9 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2 | 3.2
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7 | 7 | 6.9 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 0 | 0
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7 | 7 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 2.4 | 0 | 0 | 0 | 0
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7 | 7 | 6.9 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 0
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.3 | 7.3 | 7.2 | 7.2 | 7.1 | 7 | 7 | 6.9 | 3.9 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.4 | 7.4 | 7.3 | 7.3 | 7.3 | 7.2 | 7.1 | 7 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.4 | 7.4 | 7.3 | 7.2 | 7.2 | 7.1 | 7 | 6.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.4 | 7.4 | 7.4 | 7.4 | 7.3 | 7.3 | 7.3 | 7.2 | 7.1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.7 | 5.4 | 4.9 | 4.3 | 3.7 | 3.1 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.7 | 5.1 | 4.3 | 3.5 | 2.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.7 | 5 | 3.9 | 2.9 | 1.9 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.7 | 5.3 | 4.6 | 3.9 | 3.1 | 2.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.3 | 16.3 | 15.7 | 15.7 | 15.7 | 15.6 | 15.6 | 15.4 | 15.1 | 14.6 | 14 | 13.6 | 13.2 | 13.1 | 13 | 12.9 | 12.9 | 12.1 | 11.4
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.3 | 15.7 | 15.7 | 15.7 | 15.5 | 14.7 | 14 | 13.3 | 12.4 | 11.3 | 10.3 | 9.3 | 8.9 | 8.5 | 8.2 | 8 | 7.7 | 5.7 | 4.2
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.3 | 15.7 | 15.7 | 15.5 | 15.1 | 14.4 | 13.7 | 12.7 | 11.5 | 10.4 | 9.2 | 8.8 | 7 | 6.6 | 6.4 | 6.2 | 5.9 | 4.6 | 4
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.3 | 16.2 | 15.7 | 15.7 | 15.6 | 14.8 | 14.1 | 13.4 | 12.5 | 11.6 | 10.6 | 9.8 | 9.6 | 9.4 | 9.3 | 9.1 | 9 | 7.4 | 6.1
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10 | 9.8 | 9.7 | 9.7 | 9.6 | 9.5 | 9.3 | 9.2 | 9.1 | 9 | 9 | 7.2 | 7.2 | 7.2 | 7.2 | 7.1 | 7.1 | 6.3 | 5.2
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10 | 9.7 | 9.5 | 9.4 | 9.3 | 9.2 | 9 | 8.9 | 7.3 | 7.1 | 6.8 | 6.3 | 5.8 | 5.3 | 4.7 | 4 | 3.1 | 0 | 0
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10 | 9.6 | 9.4 | 9.2 | 9.1 | 9 | 7.3 | 7.1 | 6.6 | 6.2 | 5.6 | 5.2 | 3.4 | 2.4 | 1.6 | 0.8 | 0 | 0 | 0
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10 | 9.8 | 9.7 | 9.6 | 9.5 | 9.4 | 9.1 | 9 | 9 | 7.3 | 7.2 | 7.1 | 7 | 6.8 | 6.7 | 6.6 | 6.3 | 3.3 | 0
Drakelow 132kV | Burton 11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 61.3 | 61.4 | 61 | 60.7 | 60.4 | 60.1 | 59.2 | 58.5 | 57.6 | 55.9 | 55.5 | 52.3 | 51.7 | 51.5 | 51.3 | 51.1 | 50.9 | 49.2 | 47.2
Drakelow 132kV | Burton 11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 61.3 | 61 | 60.4 | 59.9 | 58.7 | 57 | 52.6 | 51.5 | 49.2 | 46.8 | 44.8 | 42.9 | 41.9 | 40.7 | 39.8 | 38.9 | 36.4 | 1.6 | 0
Drakelow 132kV | Burton 11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 61.3 | 60.7 | 59.9 | 58.7 | 57 | 55.7 | 51.8 | 49.7 | 46.9 | 44.3 | 42 | 41 | 32.7 | 26.4 | 21.6 | 16.3 | 10.2 | 0 | 0
Drakelow 132kV | Burton 11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 61.3 | 61.2 | 60.8 | 60.4 | 59.4 | 57.8 | 55.6 | 52.1 | 50 | 47.8 | 45.8 | 44.4 | 43.8 | 43.2 | 42.8 | 42.2 | 41.5 | 28.5 | 2.5
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 65.7 | 59.6 | 59 | 58.6 | 47 | 46.3 | 45.5 | 44.6 | 43 | 41 | 37.4 | 35.7 | 34.6 | 33.8 | 33.3 | 32.8 | 32.2 | 27.3 | 21.6
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 65.7 | 59 | 53.8 | 49.7 | 48.1 | 45.9 | 42.9 | 40.3 | 36.9 | 33.6 | 30.1 | 26.9 | 23.8 | 20.6 | 18.5 | 16.4 | 9.1 | 0 | 0
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 65.7 | 54.5 | 49.7 | 47.8 | 45.8 | 43.3 | 40.3 | 36.5 | 31.7 | 27.9 | 23.8 | 10.9 | 6.6 | 4.3 | 2.6 | 0.6 | 0 | 0 | 0
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 65.7 | 59.4 | 54.4 | 50.5 | 49.2 | 47.6 | 45.3 | 43.1 | 39.8 | 37.1 | 33.8 | 31.6 | 29.8 | 28.1 | 26.8 | 25.8 | 19.5 | 5.8 | 0
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 55.5 | 55 | 54.9 | 54.7 | 54.3 | 53.4 | 53.6 | 53.2 | 52.3 | 51.1 | 44.3 | 42.4 | 41 | 39.9 | 39.8 | 39.6 | 39.4 | 37.9 | 35.9
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 55.5 | 54.9 | 54.4 | 53.9 | 53.1 | 50.7 | 46.2 | 41.9 | 36.6 | 32 | 27.8 | 24.5 | 21.8 | 19.1 | 18.3 | 17.5 | 16.3 | 10.7 | 6.7
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 55.5 | 54.7 | 54.1 | 53 | 51.7 | 47.7 | 43.9 | 39 | 33.2 | 28.3 | 24 | 20.7 | 16 | 15.1 | 14.5 | 13.8 | 13.1 | 8.6 | 6
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 55.5 | 55 | 54.6 | 54.2 | 53.5 | 51.8 | 48.6 | 44.3 | 39.1 | 34.7 | 30.6 | 27.8 | 25.8 | 23.7 | 21.8 | 21.4 | 20.6 | 12.6 | 9
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.2 | 10.9 | 10.7 | 10.5 | 10.3 | 10.1 | 10.6 | 10.2 | 9.7 | 9.1 | 8.4 | 8 | 7.6 | 7.4 | 7.1 | 6.9 | 6.7 | 5.3 | 4.8
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.2 | 10.7 | 10.3 | 9.9 | 9.5 | 8.9 | 9 | 8.5 | 7.7 | 6.8 | 5.8 | 4.8 | 3.8 | 2.8 | 1.9 | 1.1 | 0 | 0 | 0
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.2 | 10.6 | 10.1 | 9.6 | 9 | 8.4 | 8.5 | 7.6 | 6.3 | 5.2 | 3.9 | 3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.2 | 10.8 | 10.5 | 10.2 | 9.7 | 9.3 | 9.5 | 8.9 | 8.1 | 7.4 | 6.5 | 5.9 | 5.3 | 4.7 | 4.3 | 3.8 | 3.5 | 0 | 0
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 50.7 | 50 | 49.3 | 48.6 | 47.7 | 46.8 | 45.5 | 44.4 | 42.6 | 40.6 | 38.6 | 37.1 | 36.2 | 35.5 | 34.8 | 33.4 | 31.9 | 31.1 | 26.9
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 50.7 | 49.6 | 48.2 | 47.1 | 45.6 | 43.9 | 41.7 | 40 | 37.4 | 34.2 | 30.9 | 24.9 | 21.7 | 18.5 | 16 | 13.5 | 8.5 | 0 | 0
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 50.7 | 49.3 | 47.6 | 46.1 | 44.3 | 42.5 | 40.2 | 36.9 | 32.8 | 29.1 | 25 | 14.3 | 7.2 | 3.3 | 1.2 | 0 | 0 | 0 | 0
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 50.7 | 49.9 | 48.8 | 47.7 | 46.4 | 45 | 43 | 41.3 | 38.9 | 36.5 | 33.6 | 29.8 | 27.1 | 25.5 | 24.1 | 22.7 | 18.5 | 7.2 | 0
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 25.6 | 20 | 19.8 | 19.6 | 8.3 | 8 | 7.8 | 7.5 | 6.7 | 5.8 | 4.9 | 4.3 | 3.9 | 3.6 | 3.4 | 3.1 | 2.8 | 0.7 | 0
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 25.6 | 19.8 | 15.3 | 11.7 | 11.1 | 10.3 | 9.6 | 8.7 | 7.7 | 6.7 | 5.5 | 4.3 | 3.2 | 2 | 1.2 | 0 | 0 | 0 | 0
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 25.6 | 15.5 | 11.7 | 11 | 10.2 | 9.4 | 8.6 | 7.4 | 5.8 | 4.6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 25.6 | 19.9 | 15.5 | 11.9 | 11.4 | 10.9 | 10.3 | 9.7 | 8.7 | 7.9 | 6.6 | 5.8 | 5.1 | 4.5 | 4.1 | 3.7 | 0 | 0 | 0
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.9 | 0.9 | 0.8 | 0.7 | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.9 | 0.8 | 0.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.9 | 0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.9 | 3.6 | 3.6 | 3.5 | 3 | 3 | 4.1 | 4 | 3.9 | 3.7 | 3.6 | 3.5 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3 | 2.6
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.9 | 3.6 | 3.3 | 3 | 2.8 | 2.5 | 3.5 | 3.5 | 3.2 | 3 | 2.9 | 2.7 | 2.6 | 2.4 | 2.2 | 2.1 | 1 | 0 | 0
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.9 | 3.4 | 3.1 | 2.9 | 2.6 | 2.4 | 3.4 | 3.2 | 3 | 2.7 | 2.5 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.9 | 3.6 | 3.4 | 3.1 | 2.9 | 2.7 | 3.6 | 3.6 | 3.4 | 3.2 | 3.1 | 3 | 2.9 | 2.9 | 2.8 | 2.7 | 2.4 | 0.5 | 0
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.4 | 9.4 | 9.3 | 9.3 | 9.3 | 9.3 | 8.7 | 8.7 | 8.6 | 8.5 | 8.3 | 8.1 | 8 | 7.9 | 7.8 | 7.8 | 7.7 | 7.1 | 6.5
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.4 | 9.3 | 9.3 | 9.3 | 8.7 | 8.6 | 8.6 | 8.6 | 8.4 | 8.1 | 7.7 | 7.4 | 7.1 | 6.7 | 6.5 | 6.3 | 6.1 | 4.7 | 3.3
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.4 | 9.3 | 9.3 | 8.7 | 8.6 | 8.6 | 8.6 | 8.3 | 7.8 | 7.4 | 7 | 6.7 | 6.4 | 6.1 | 5.9 | 5.7 | 5.5 | 4.3 | 3.6
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.4 | 9.4 | 9.3 | 9.3 | 9.3 | 8.7 | 8.7 | 8.7 | 8.5 | 8.4 | 8 | 7.8 | 7.6 | 7.5 | 7.4 | 7.3 | 7.2 | 6.1 | 5
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.8 | 12.5 | 12.4 | 12.3 | 12.2 | 11.4 | 14.1 | 14.1 | 13.9 | 13.8 | 12.1 | 10.9 | 9.8 | 8.9 | 8.8 | 8.7 | 8.7 | 8.1 | 7.5
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.8 | 12.4 | 12.2 | 11.9 | 11.5 | 10.3 | 12.6 | 10.6 | 6.5 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.8 | 12.3 | 12 | 11.5 | 10.9 | 7.7 | 12.1 | 8.5 | 4.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.8 | 12.4 | 12.3 | 12.1 | 11.8 | 11.2 | 13.3 | 12.3 | 8.7 | 5.4 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.7 | 5.4 | 4.9 | 4.3 | 3.7 | 3.1 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.7 | 5.1 | 4.3 | 3.5 | 2.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.7 | 5 | 3.9 | 2.9 | 1.9 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.7 | 5.3 | 4.6 | 3.9 | 3.1 | 2.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.2 | 13.1 | 13 | 12.9 | 12.9 | 12.7 | 12.5 | 12.3 | 12 | 11.7 | 11.4 | 11.1 | 11 | 10.9 | 10.8 | 10.7 | 10.6 | 8.9 | 6.6
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.2 | 13 | 12.7 | 12.6 | 12.2 | 11.7 | 11.3 | 10.9 | 10.4 | 9.9 | 9.2 | 8.1 | 7.1 | 6 | 5.1 | 4.2 | 3.2 | 0 | 0
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.2 | 12.9 | 12.6 | 12.1 | 11.7 | 11.3 | 10.8 | 10.2 | 9.1 | 8.1 | 6.9 | 6 | 3.4 | 2.5 | 1.7 | 0.8 | 0 | 0 | 0
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.2 | 13.1 | 12.9 | 12.8 | 12.5 | 12.2 | 11.7 | 11.4 | 11 | 10.7 | 10.2 | 9.9 | 9.7 | 9.3 | 9 | 8.6 | 8 | 3.3 | 0
East Claydon 132kV | Banbury 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 54.5 | 54.4 | 54.3 | 53.4 | 53.2 | 53.1 | 48.4 | 48.4 | 48.3 | 48.2 | 47.8 | 47.6 | 47 | 46.1 | 45.6 | 45.4 | 45.3 | 44.6 | 43.4
East Claydon 132kV | Banbury 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 54.5 | 54.4 | 53.3 | 52.3 | 51.7 | 51.2 | 48 | 47.5 | 44.6 | 42.3 | 39.9 | 38.3 | 37.5 | 36.7 | 38.3 | 37.7 | 37.2 | 34.2 | 31.5
East Claydon 132kV | Banbury 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 54.5 | 54.3 | 52.5 | 52 | 51.4 | 50.3 | 47.5 | 44.1 | 41.2 | 39.5 | 37.7 | 37.1 | 36.1 | 37.7 | 37.3 | 36.8 | 36.3 | 33.5 | 31.1
East Claydon 132kV | Banbury 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 54.5 | 54.4 | 54.3 | 53.3 | 53.1 | 52 | 48.3 | 47.9 | 46.7 | 44.5 | 42.1 | 40.7 | 39.7 | 39.2 | 38.8 | 35.1 | 34.9 | 32.7 | 30.5
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 23.5 | 23.4 | 23.3 | 23.2 | 23.1 | 22.9 | 22.8 | 22.7 | 22.6 | 22.5 | 22.3 | 22.3 | 22.3 | 22.3 | 22.3 | 22.3 | 22.3 | 21.9 | 21.3
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 23.5 | 23.3 | 23 | 22.7 | 22.5 | 22.3 | 22.1 | 22 | 21.9 | 21.8 | 21.7 | 21.5 | 21.3 | 21.1 | 20.9 | 20.7 | 20.5 | 19.2 | 17.9
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 23.5 | 23.1 | 22.7 | 22.4 | 22.1 | 21.8 | 21.4 | 21.2 | 21 | 20.7 | 20.5 | 20.3 | 20.1 | 20 | 19.8 | 19.6 | 19.4 | 18.5 | 17.1
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 23.5 | 23.4 | 23.2 | 23 | 22.8 | 22.6 | 22.5 | 22.4 | 22.3 | 22.2 | 22.1 | 22.1 | 22 | 22 | 22 | 22 | 21.9 | 19.1 | 18.1
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 60.1 | 58.5 | 57.9 | 57.3 | 56.4 | 55.5 | 53.2 | 52.6 | 51.8 | 50.8 | 49.8 | 49.2 | 48.8 | 52.4 | 52.2 | 51.9 | 51.7 | 51 | 47.9
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 60.1 | 58 | 56.5 | 54.8 | 53.1 | 51.5 | 49.2 | 48.1 | 47 | 45.5 | 43.9 | 42.3 | 40.8 | 43.1 | 41.8 | 40.6 | 39.3 | 35.2 | 29.1
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 60.1 | 57.6 | 55.5 | 53.5 | 51.3 | 49.1 | 46.8 | 44.9 | 42.9 | 41.2 | 39.3 | 38.1 | 36.8 | 39.5 | 38.5 | 37.4 | 36.3 | 33 | 24.9
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 60.1 | 58.4 | 57.3 | 55.8 | 54.2 | 52.7 | 50.5 | 49.6 | 48.6 | 47.4 | 46.2 | 45.5 | 44.9 | 48.3 | 47.9 | 47.4 | 46.7 | 43.1 | 38
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.8 | 9.8 | 9.8 | 9.7 | 9.7 | 9.7 | 9.6 | 9.5 | 9.4 | 9.2 | 9 | 8.9 | 8.8 | 8.8 | 8.7 | 8.7 | 8.6 | 8.1 | 7.4
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.8 | 9.7 | 9.7 | 9.6 | 9.5 | 9.5 | 9.4 | 9.3 | 9.1 | 8.8 | 8.5 | 8.2 | 7.9 | 7.6 | 7.4 | 7.2 | 6.1 | 3.7 | 2.6
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.8 | 9.7 | 9.6 | 9.5 | 9.4 | 9.3 | 9.2 | 9 | 8.6 | 8.3 | 7.9 | 6 | 5.7 | 5.5 | 3.5 | 3.3 | 3.1 | 1.8 | 1.1
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.8 | 9.8 | 9.7 | 9.6 | 9.6 | 9.6 | 9.5 | 9.5 | 9.3 | 9.1 | 8.9 | 8.7 | 8.6 | 8.4 | 8.3 | 8.2 | 7.2 | 5.4 | 4.3
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 57.3 | 55.4 | 55.1 | 53.2 | 52.6 | 51.8 | 51.7 | 51.5 | 49.9 | 48 | 44.8 | 42.8 | 41.6 | 40.6 | 39.7 | 38.8 | 37.9 | 31.9 | 25.7
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 57.3 | 54.7 | 51.4 | 48.8 | 46.8 | 44.9 | 42.1 | 38.9 | 35.4 | 32 | 28.6 | 24.9 | 21.5 | 17.9 | 14.4 | 9 | 4.4 | 0 | 0
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 57.3 | 53 | 50.7 | 48.4 | 45.6 | 42.9 | 40.6 | 36.1 | 31.3 | 26.3 | 17.1 | 11.1 | 6.6 | 3.7 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 57.3 | 54.9 | 51.8 | 49.2 | 47.2 | 45.3 | 42.2 | 39.8 | 37.2 | 35.1 | 32.2 | 30 | 28.1 | 26.4 | 24.3 | 20.3 | 17 | 5 | 0
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.1 | 17.7 | 17.6 | 17.5 | 17.4 | 17.3 | 17.2 | 17.3 | 17 | 16.7 | 16.4 | 15.5 | 15.4 | 15.3 | 15.3 | 15.2 | 15.1 | 14.3 | 13.4
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.1 | 17.6 | 17.4 | 17.2 | 17 | 16.8 | 16.6 | 16.7 | 16.4 | 15.4 | 15 | 14.5 | 14 | 13.4 | 13 | 12.7 | 12.3 | 10 | 8.1
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.1 | 17.6 | 17.3 | 17 | 16.8 | 16.6 | 16.4 | 15.5 | 15.1 | 14.5 | 13.9 | 13.4 | 13 | 12.6 | 12.3 | 11.9 | 11.6 | 9.6 | 8.7
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.1 | 17.7 | 17.5 | 17.3 | 17.1 | 17 | 16.8 | 16.9 | 16.6 | 16.4 | 15.4 | 15.2 | 14.9 | 14.7 | 14.6 | 14.4 | 14.2 | 12.7 | 11.1
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 65.2 | 65.3 | 64.8 | 64.4 | 63.8 | 63.1 | 62.4 | 61.5 | 60.3 | 59.3 | 58.1 | 56.9 | 53.4 | 52.4 | 51.7 | 50.9 | 50.3 | 47.4 | 44.8
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 65.2 | 64.8 | 63.5 | 61.8 | 60.6 | 58.9 | 57.1 | 55.1 | 52.8 | 49.9 | 47 | 44.1 | 37.3 | 35.6 | 34.3 | 33.1 | 29.8 | 21.5 | 0
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 65.2 | 64.3 | 62.5 | 60.9 | 58.9 | 55.4 | 52.7 | 49.2 | 45.7 | 42.6 | 39.3 | 34 | 27.2 | 25.9 | 24.9 | 23.7 | 24.4 | 0 | 0
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 65.2 | 65.2 | 64.2 | 62.8 | 61.6 | 60.2 | 58 | 56.1 | 53.8 | 51.3 | 48.7 | 47.1 | 43.6 | 43 | 42.7 | 42.2 | 39.5 | 33.3 | 33.5
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.7 | 5.6 | 5.4 | 5.2 | 5 | 4.9 | 11.4 | 10.9 | 9.2 | 6.8 | 3.9 | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 8.2 | 6.2
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.7 | 5.4 | 5 | 4.6 | 4.2 | 3.7 | 9 | 8.2 | 5.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.7 | 5.3 | 4.7 | 4.3 | 3.7 | 3.2 | 8.1 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.7 | 5.5 | 5.2 | 4.8 | 4.5 | 4.1 | 9.7 | 9.2 | 7 | 4.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.4 | 17.9 | 17.9 | 17.8 | 17.7 | 17.5 | 17.3 | 17.1 | 16.9 | 16.9 | 16.8 | 16.8 | 16.7 | 16.6 | 16.4 | 16.3 | 16.3 | 15.8 | 15.8
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.4 | 17.9 | 17.7 | 17.4 | 17.1 | 16.7 | 16.4 | 15.8 | 15.6 | 15.4 | 15.1 | 14.8 | 14.7 | 14.6 | 14.5 | 14.5 | 14.4 | 14.1 | 13.7
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.4 | 17.9 | 17.6 | 17.3 | 17 | 16.5 | 15.7 | 15.2 | 14.7 | 14.6 | 14.5 | 14.5 | 14.4 | 14.3 | 14.3 | 14.2 | 14.2 | 13.8 | 13.4
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.4 | 17.9 | 17.7 | 17.5 | 17.2 | 16.8 | 16.4 | 15.8 | 15.5 | 15.2 | 14.9 | 14.9 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.5 | 14.2
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.1 | 13.1 | 13 | 12.9 | 12.9 | 12.8 | 12.9 | 12.8 | 12.7 | 12.6 | 12.5 | 12.5 | 12.3 | 12.2 | 12.1 | 12.1 | 12.1 | 11.8 | 11.4
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.1 | 13 | 12.8 | 12.7 | 12.6 | 12.5 | 12.5 | 12.4 | 12.2 | 11.9 | 11.6 | 11.3 | 11 | 10.8 | 10.7 | 10.5 | 10.3 | 9.3 | 13.7
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.1 | 13 | 12.7 | 12.6 | 12.4 | 12.1 | 11.7 | 11.4 | 11.1 | 10.9 | 10.6 | 10.4 | 10 | 9.9 | 9.8 | 9.6 | 14.5 | 13.6 | 12.9
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.1 | 13.1 | 12.9 | 12.8 | 12.8 | 12.7 | 12.7 | 12.5 | 12.3 | 12 | 11.7 | 11.7 | 11.5 | 11.5 | 11.5 | 11.5 | 11.4 | 10.7 | 10.2
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.3 | 18.4 | 18.4 | 18.4 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 17.9
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.3 | 18.4 | 18.4 | 18.4 | 18.3 | 18.3 | 18.3 | 18.3 | 18 | 17.9 | 17.7 | 17.5 | 15.5 | 14.7
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.4 | 17.4 | 17.4 | 17.4 | 17.3 | 17.2 | 18.4 | 18.4 | 18.4 | 18.1 | 17.8 | 17.7 | 17.5 | 17.4 | 17.3 | 17.2 | 17.1 | 15 | 13.9
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.3 | 18.4 | 18.4 | 18.4 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 17.8 | 17.1
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17 | 16.7 | 16.7 | 16.7 | 16.6 | 16.6 | 16.6 | 16.5 | 16.5 | 16.5 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17 | 16.8 | 16.7 | 16.7 | 16.6 | 16.6 | 16.6 | 16.5 | 16.5 | 16.5 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 17.3 | 17.3
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17 | 16.8 | 16.7 | 16.6 | 16.6 | 16.5 | 16.6 | 16.5 | 16.5 | 16.5 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 17.3 | 17.3
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17 | 16.8 | 16.7 | 16.7 | 16.6 | 16.6 | 16.6 | 16.5 | 16.5 | 16.5 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 17.4 | 17.4
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.8 | 16.8 | 16.7 | 16.7 | 16.7 | 16.7 | 16.4 | 15 | 15 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.7
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.8 | 16.7 | 16.5 | 15.4 | 14.8 | 14.8 | 14.9 | 14.9 | 14.8 | 14.7 | 14.6 | 14.3 | 13.9 | 13.7 | 13.5 | 13.4 | 13.2 | 11.9 | 10.9
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.8 | 16.6 | 15.4 | 14.8 | 14.8 | 14.7 | 14.8 | 14.6 | 14.3 | 14 | 13.6 | 13.3 | 12.9 | 12.7 | 12.5 | 12.4 | 12.2 | 13 | 12.3
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.8 | 16.8 | 16.6 | 16.6 | 15.4 | 15.4 | 15 | 14.9 | 14.9 | 14.8 | 14.6 | 14.6 | 14.5 | 14.4 | 14.4 | 14.4 | 14.3 | 13.3 | 12.6
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.5 | 7.5 | 7.4 | 7.4 | 7.3 | 7.3 | 7.2 | 7.2 | 6.9 | 6.6 | 6.3 | 6 | 5.9 | 5.8 | 5.7 | 5.6 | 5.5 | 4.7 | 3.8
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.5 | 7.4 | 7.3 | 7.3 | 7.2 | 7.2 | 7 | 6.9 | 6.5 | 6.1 | 5.6 | 5.1 | 4.6 | 4.2 | 3.8 | 3.5 | 1.2 | 0 | 0
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.5 | 7.4 | 7.3 | 7.2 | 7.1 | 7.1 | 6.9 | 6.5 | 5.9 | 5.4 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.5 | 7.5 | 7.4 | 7.3 | 7.3 | 7.2 | 7.1 | 7 | 6.7 | 6.4 | 6 | 5.7 | 5.4 | 5.2 | 5 | 4.8 | 2.7 | 1.3 | 0
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.6 | 19.3 | 19.3 | 19.2 | 19.2 | 19.1 | 19 | 18.9 | 18.8 | 18.8 | 18.6 | 18.6 | 18.5 | 18.5 | 18.5 | 18.4 | 18.4 | 18.1 | 17.7
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.6 | 19.2 | 19 | 18.9 | 18.8 | 18.7 | 18.4 | 18.3 | 18.2 | 18 | 17.9 | 17.7 | 17.6 | 17.5 | 17.4 | 17.4 | 14.7 | 14.2 | 13.3
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.6 | 19.2 | 18.8 | 18.6 | 18.5 | 18.3 | 18 | 17.8 | 17.6 | 17.5 | 17.4 | 17.4 | 14.7 | 14.7 | 14.7 | 14.6 | 14.5 | 13.5 | 12.6
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.6 | 19.3 | 19.2 | 19.1 | 19 | 18.9 | 18.6 | 18.5 | 18.4 | 18.3 | 18.1 | 18.1 | 18 | 18 | 17.9 | 17.9 | 17.8 | 17.4 | 14.6
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.8 | 19.8 | 19.7 | 19.6 | 19.5 | 19.5 | 19.3 | 19.3 | 19.2 | 19.2 | 19.1 | 19.1 | 19.1 | 19 | 18.9 | 18.9 | 18.9 | 18.8 | 18.7
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.8 | 19.7 | 19.6 | 19.5 | 19.5 | 19.4 | 19.2 | 19.1 | 19.1 | 19 | 18.9 | 18.8 | 18.8 | 18.8 | 18.8 | 18.7 | 18.7 | 18.2 | 17.6
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.8 | 19.7 | 19.6 | 19.5 | 19.3 | 19.2 | 19 | 18.9 | 18.8 | 18.7 | 18.6 | 18.5 | 18.5 | 18.5 | 18.4 | 18.4 | 18.2 | 17.7 | 17.3
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.8 | 19.8 | 19.7 | 19.6 | 19.5 | 19.4 | 19.3 | 19.2 | 19.2 | 19.1 | 19.1 | 19.1 | 19 | 18.9 | 18.9 | 18.8 | 18.8 | 18.7 | 18.5
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.7 | 19.7 | 19.5 | 19.4 | 19.3 | 19.3 | 19.1 | 19 | 18.9 | 18.8 | 18.7 | 18.6 | 18.6 | 18.6 | 18.6 | 18.5 | 18.6 | 18.2 | 17.8
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.7 | 19.5 | 19.3 | 19.2 | 19 | 18.9 | 18.7 | 18.7 | 18.6 | 18.4 | 18.2 | 18 | 17.9 | 17.7 | 17.6 | 17.5 | 17.4 | 14.5 | 13.8
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.7 | 19.4 | 19.1 | 18.9 | 18.7 | 18.5 | 18.2 | 18 | 17.8 | 17.6 | 17.5 | 17.4 | 17.4 | 17.3 | 14.7 | 14.7 | 14.6 | 13.9 | 12.9
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.7 | 19.6 | 19.5 | 19.3 | 19.2 | 19.1 | 19 | 18.9 | 18.7 | 18.6 | 18.4 | 18.4 | 18.4 | 18.3 | 18.3 | 18.3 | 18.2 | 17.6 | 14.7
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.2 | 4.1 | 4 | 4 | 3.8 | 3.5 | 3.4 | 3.1 | 2.8 | 2.6 | 2.4 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.2 | 4 | 3.7 | 3.3 | 2.9 | 2.4 | 2.1 | 1.6 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.2 | 3.9 | 3.4 | 2.9 | 2.4 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.2 | 4.1 | 3.9 | 3.6 | 3.3 | 2.8 | 2.5 | 2 | 1.5 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.9 | 10.2 | 10.1 | 9.9 | 9.8 | 9.7 | 9.8 | 9.6 | 9.3 | 8.9 | 8.3 | 8 | 7.7 | 11.4 | 11.3 | 11.1 | 11 | 11.4 | 9.7
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.9 | 10 | 9.6 | 9.3 | 9.1 | 8.9 | 8.9 | 8.7 | 8.2 | 7.5 | 6.8 | 5.9 | 5.1 | 8 | 7.4 | 6.8 | 6.1 | 4.1 | 1.1
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.9 | 9.9 | 9.4 | 9 | 8.7 | 8.4 | 8.4 | 7.7 | 6.7 | 5.9 | 4.9 | 4.2 | 3.5 | 6.6 | 6.1 | 5.6 | 5 | 3.4 | 1.5
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.9 | 10.1 | 9.8 | 9.6 | 9.3 | 9.2 | 9.3 | 9.1 | 8.7 | 8.3 | 7.6 | 7.2 | 6.7 | 10.2 | 9.9 | 9.6 | 9.2 | 8.5 | 5.8
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.7 | 19.7 | 19.7 | 19.6 | 19.6 | 19.6 | 19 | 19 | 18.9 | 18.9 | 18.8 | 18.9 | 18.9 | 18.7 | 18.7 | 18.6 | 18.6 | 18.5 | 18.3
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.7 | 19.7 | 19.7 | 19.6 | 19.6 | 19.3 | 18.4 | 18.3 | 18.3 | 18.1 | 17.9 | 17.8 | 17.7 | 17.6 | 17.5 | 17.4 | 17.4 | 17 | 16.7
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.7 | 19.7 | 19.7 | 19.6 | 19.4 | 19 | 17.9 | 17.7 | 17.6 | 17.5 | 17.4 | 17.3 | 17.3 | 17.2 | 17.2 | 17.1 | 17 | 16.7 | 14.9
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.7 | 19.7 | 19.7 | 19.6 | 19.6 | 19.4 | 18.6 | 18.5 | 18.3 | 18.1 | 18 | 18 | 18 | 18 | 17.9 | 17.9 | 17.9 | 17.6 | 17.3
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.1 | 10.5 | 10.5 | 10.5 | 10.4 | 10.4 | 10.3 | 10.3 | 10.3 | 10.3 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.1 | 10.1 | 10.1 | 10.1
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.1 | 10.5 | 10.5 | 10.5 | 10.4 | 10.4 | 10.3 | 10.3 | 10.3 | 10.2 | 10 | 9.9 | 9.8 | 9.8 | 9.8 | 9.8 | 9.7 | 11.3 | 11.2
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.1 | 10.5 | 10.5 | 10.5 | 10.4 | 10.4 | 10 | 9.9 | 9.8 | 9.8 | 9.7 | 9.7 | 9.7 | 11.3 | 11.3 | 11.3 | 11.3 | 11.4 | 11.3
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.1 | 10.5 | 10.5 | 10.5 | 10.4 | 10.4 | 10.3 | 10.3 | 10.2 | 10.1 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.3 | 9.2
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.1 | 18.1 | 18 | 17.9 | 17.9 | 17.8 | 17.7 | 17.6 | 17.6 | 17.5 | 17.4 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.2 | 15.1
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.1 | 18 | 17.8 | 17.7 | 17.7 | 17.6 | 17.4 | 17.4 | 17.3 | 17.2 | 17.2 | 17.2 | 15.2 | 15.1 | 15.1 | 14.9 | 14.8 | 13.8 | 12.7
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.1 | 17.9 | 17.7 | 17.6 | 17.5 | 17.4 | 17.2 | 17.1 | 15.2 | 15.2 | 15 | 14.9 | 14.8 | 14.6 | 14.5 | 14.3 | 14.1 | 13 | 11.9
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.1 | 18 | 17.9 | 17.9 | 17.8 | 17.7 | 17.6 | 17.5 | 17.5 | 17.4 | 17.3 | 17.3 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 15 | 14.3
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.3 | 16.2 | 16 | 14.3 | 13.9 | 13.4 | 12.9 | 12.9 | 12.5 | 12 | 10.5 | 9.9 | 9.6 | 9.3 | 8.9 | 8.6 | 8.2 | 6.3 | 4.6
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.3 | 15.8 | 13.2 | 11.4 | 10 | 8.8 | 6.4 | 4.5 | 3 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.3 | 14.3 | 12.9 | 11.4 | 9.4 | 8.1 | 6.3 | 4.2 | 2.5 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.3 | 15.8 | 13.2 | 11.3 | 9.9 | 8.5 | 6 | 4.4 | 3.2 | 2.8 | 2 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.7 | 4.6 | 4.5 | 4.3 | 4.2 | 4.1 | 5.6 | 5.3 | 4.3 | 2.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8 | 4.5
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.7 | 4.5 | 4.2 | 3.9 | 3.7 | 3.4 | 4.6 | 4.2 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.7 | 4.4 | 4 | 3.7 | 3.4 | 3.1 | 4.2 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.7 | 4.6 | 4.4 | 4.2 | 3.9 | 3.7 | 5.1 | 4.8 | 3.5 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 48.6 | 47.6 | 47 | 46.4 | 45.7 | 44.9 | 45.2 | 44.2 | 41.1 | 37 | 32.3 | 28.7 | 26.4 | 24.7 | 23.2 | 22 | 20.8 | 25.8 | 14.4
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 48.6 | 46.7 | 45 | 42.7 | 40.6 | 37.8 | 35.4 | 31.9 | 26.7 | 20.1 | 13.7 | 7.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 48.6 | 46.2 | 43.7 | 41.5 | 38.4 | 34.2 | 32.1 | 25.2 | 16.4 | 8.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 48.6 | 47.2 | 45.9 | 43.8 | 41.7 | 39.3 | 36.5 | 33.7 | 29.4 | 24.9 | 18.6 | 14.7 | 11.4 | 8.5 | 6.1 | 4 | 0 | 0 | 0
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 26.5 | 26.4 | 26.4 | 26.3 | 26.2 | 26.1 | 26 | 25.7 | 25.2 | 24.7 | 24.1 | 23.8 | 23.7 | 23.6 | 23.5 | 23.4 | 23.3 | 22.9 | 21.7
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 26.5 | 26.4 | 26.2 | 26 | 25.3 | 24.9 | 24.2 | 23.4 | 22.4 | 21.5 | 20.6 | 20 | 19.4 | 18.8 | 17.9 | 17.5 | 17 | 14.7 | 12.2
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 26.5 | 26.3 | 26.2 | 25.8 | 25.2 | 24.5 | 23.9 | 22.7 | 21.4 | 19.4 | 18.4 | 17.6 | 17.1 | 16.5 | 16.2 | 15.9 | 15.3 | 13.2 | 11.9
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 26.5 | 26.4 | 26.3 | 26.1 | 25.3 | 25.1 | 24.4 | 23.7 | 22.7 | 22 | 21.2 | 20.8 | 20.5 | 20.3 | 19.7 | 19.5 | 19.1 | 17.8 | 15.8
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.5 | 5.2 | 5.2 | 5.1 | 5.1 | 5.1 | 4.6 | 4.5 | 4.2 | 3.6 | 2.8 | 2.3 | 1.9 | 1.7 | 1.4 | 1.2 | 0.9 | 0 | 0
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.5 | 5.2 | 5 | 5 | 4.9 | 4.8 | 4.4 | 4.1 | 3.3 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.5 | 5.1 | 4.9 | 4.8 | 4.7 | 4.6 | 4.3 | 3.4 | 2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.5 | 5.2 | 5.1 | 5.1 | 5 | 5 | 4.5 | 4.4 | 3.9 | 3.3 | 2.3 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.6 | 13.7 | 13.8 | 14 | 14 | 13.9 | 14.5 | 14.5 | 14.3 | 14 | 13.8 | 13.3 | 12.9 | 12.5 | 12.3 | 12.3 | 12.2 | 10.7 | 9.2
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.6 | 13.6 | 13.7 | 13.2 | 13 | 12.7 | 12.7 | 10.5 | 9.3 | 7.7 | 6.9 | 6.1 | 5.3 | 4.5 | 3.8 | 3 | 0 | 0 | 0
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.6 | 13.7 | 13.5 | 13.4 | 13.1 | 11.9 | 11.1 | 8.8 | 7.4 | 6.2 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.6 | 13.6 | 13.8 | 13.3 | 13 | 12.8 | 12 | 10.4 | 9.6 | 8.6 | 7.8 | 7.3 | 7 | 6.6 | 6.2 | 5.8 | 3.2 | 0 | 0
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.4 | 18.1 | 18 | 17.9 | 17.9 | 17.9 | 15.8 | 15.7 | 15.6 | 15.6 | 15.4 | 15.4 | 15.3 | 15.3 | 15.3 | 15.2 | 15.2 | 14.8 | 14.3
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.4 | 18 | 17.8 | 15.5 | 15.4 | 15.3 | 15.2 | 15.1 | 14.9 | 14.6 | 14.3 | 13.9 | 13.6 | 13.3 | 13 | 12.7 | 12.5 | 12.1 | 10.8
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.4 | 18 | 16.4 | 15.5 | 15.3 | 15 | 14.6 | 14.3 | 14 | 13.7 | 13.4 | 13.1 | 12.9 | 12.7 | 12.4 | 12.2 | 11.9 | 11.6 | 10.2
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.4 | 18.1 | 17.9 | 17.8 | 15.5 | 15.5 | 15.6 | 15.5 | 15.3 | 15.1 | 14.9 | 14.8 | 14.8 | 14.7 | 14.7 | 14.6 | 14.5 | 14.8 | 13.9
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.1 | 18.2 | 18.1 | 18.1 | 17.9 | 17.7 | 17.6 | 17.5 | 17.4 | 17.3 | 17.2 | 17.2 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17 | 16.9
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.1 | 18.1 | 17.9 | 17.5 | 17 | 16.5 | 16.8 | 15.2 | 15 | 14.8 | 14.5 | 14.4 | 14.3 | 14.1 | 14 | 13.9 | 13.8 | 13.2 | 12.4
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.1 | 18.1 | 17.8 | 17.3 | 16.8 | 15.8 | 16.7 | 15 | 14.7 | 14.3 | 14.1 | 14 | 13.9 | 13.7 | 13.6 | 13.5 | 13.5 | 12.5 | 11.7
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.1 | 18.2 | 18 | 17.6 | 17 | 16.5 | 16.8 | 15.7 | 15.1 | 14.8 | 14.6 | 14.6 | 14.6 | 14.4 | 14.4 | 14.4 | 14.3 | 14 | 13.6
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.1 | 6.1 | 6.1 | 6 | 6 | 6 | 5.6 | 5.5 | 5 | 4.1 | 3.5 | 2.9 | 2.6 | 2.4 | 2.1 | 2 | 1.8 | 0.6 | 0
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.1 | 6 | 5.9 | 5.6 | 5.3 | 4.4 | 3.2 | 2.5 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.1 | 6 | 5.7 | 5.4 | 4.7 | 3.7 | 2.9 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.1 | 6.1 | 6 | 5.7 | 5.4 | 4.7 | 3.1 | 2.6 | 2.1 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.6 | 7.3 | 7.2 | 7.1 | 7 | 6.9 | 6.8 | 6.6 | 5.9 | 5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.6 | 7.2 | 7 | 6.8 | 6.5 | 6.4 | 6.1 | 5.7 | 4.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.6 | 7.2 | 6.9 | 6.6 | 6.4 | 6.2 | 5.8 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.6 | 7.3 | 7.1 | 6.9 | 6.7 | 6.6 | 6.3 | 6.2 | 5.3 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.8 | 11.8 | 11.8 | 11.7 | 11.7 | 11.6 | 11.4 | 11.4 | 11.2 | 11 | 10.8 | 10.1 | 9.5 | 9 | 8.7 | 8.6 | 8.6 | 7.9 | 8.2
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.8 | 11.7 | 11.5 | 11 | 10.8 | 10.7 | 10.1 | 9.4 | 8.6 | 7.2 | 6.8 | 6.4 | 6 | 5.7 | 5.4 | 5.2 | 5 | 3.4 | 8
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.8 | 11.6 | 11.2 | 11 | 10.7 | 9.5 | 9 | 8.2 | 7.1 | 6.2 | 5.7 | 5.4 | 5.1 | 4.8 | 4.6 | 4.4 | 4.1 | 2.5 | 7.6
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.8 | 11.8 | 11.7 | 11.1 | 11 | 10.9 | 9.8 | 9.4 | 8.8 | 7.7 | 7.1 | 6.9 | 6.8 | 6.6 | 6.6 | 6.5 | 6.4 | 5.2 | 10.1
East Claydon 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.5 | 7.5 | 7.5 | 7.5 | 7.4 | 7.4 | 6.8 | 6.8 | 6.8 | 6.9 | 7 | 7.1 | 7 | 7 | 7 | 6.9 | 6.9 | 6.6 | 6
East Claydon 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.5 | 7.5 | 7.4 | 7.4 | 7.3 | 7.3 | 7.1 | 7.1 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 5.2 | 4.1 | 2.3 | 0 | 0
East Claydon 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.5 | 7.4 | 7.4 | 7.3 | 7.3 | 7.2 | 7.1 | 7 | 6.8 | 6.7 | 6.5 | 6.3 | 5.5 | 4.4 | 3.6 | 2.7 | 1.7 | 0 | 0
East Claydon 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.5 | 7.5 | 7.5 | 7.4 | 7.4 | 7.4 | 7.3 | 7.3 | 7.2 | 7.1 | 7 | 7 | 6.9 | 6.8 | 6.7 | 6.7 | 6.5 | 3.7 | 0
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.9 | 13.8 | 13.7 | 13.8 | 13.8 | 13.8 | 13.6 | 13.2 | 12.7 | 12 | 11.8 | 11.7 | 12.9 | 12.8 | 12.8 | 12.8 | 12.7 | 12.3 | 11.7
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.9 | 13.7 | 13.5 | 12.9 | 12.4 | 11.1 | 9.8 | 9.6 | 9.3 | 9 | 8.6 | 8.3 | 10.5 | 10.1 | 9.7 | 9.3 | 9 | 7.3 | 5.8
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.9 | 13.6 | 13.4 | 12.9 | 11.9 | 10.9 | 9.7 | 9.3 | 8.9 | 8.6 | 8.2 | 7.9 | 10.3 | 10 | 9.7 | 9.3 | 9 | 7.2 | 5.8
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.9 | 13.8 | 13.6 | 13.2 | 12.7 | 11.7 | 10.4 | 10.2 | 10 | 9.8 | 9.6 | 9.5 | 10.6 | 10.5 | 10.4 | 10.1 | 9.9 | 8.8 | 7.6
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 30.9 | 30.9 | 30.8 | 30.8 | 30.7 | 30.5 | 30.4 | 30.2 | 30 | 29.8 | 27.3 | 24.9 | 23.3 | 21.8 | 20.4 | 19 | 17.6 | 8.2 | 0
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 30.9 | 30.9 | 30.6 | 30.4 | 30.2 | 28.9 | 28.1 | 25.9 | 22.2 | 18.2 | 13.2 | 7.8 | 3 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 30.9 | 30.8 | 30.4 | 30.1 | 29.2 | 26.4 | 25.3 | 20.9 | 15.1 | 10.5 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 30.9 | 30.9 | 30.8 | 30.6 | 30.4 | 29.6 | 29.3 | 27.2 | 24.2 | 21.4 | 16.8 | 13.5 | 10.6 | 7.8 | 5.5 | 3 | 0 | 0 | 0
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.7 | 17.7 | 17.7 | 17 | 16.9 | 16.9 | 15.1 | 15.1 | 15 | 14.9 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.6
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.7 | 17.7 | 16.9 | 16.8 | 16.7 | 16.7 | 15.7 | 15.6 | 15.1 | 15 | 14.9 | 14.8 | 14.7 | 14.7 | 14.6 | 14.6 | 14.6 | 14.1 | 13.4
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.7 | 17 | 16.8 | 16.7 | 16.7 | 15.7 | 15.5 | 15 | 14.8 | 14.5 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.1 | 13.4 | 10.9
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.7 | 17.7 | 17 | 16.9 | 16.8 | 16.7 | 15.7 | 15.7 | 15.5 | 15 | 15 | 14.9 | 14.9 | 14.9 | 14.9 | 15 | 15 | 14.7 | 14.3
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.1 | 17 | 16.9 | 16.8 | 16.7 | 16.6 | 16.5 | 15.4 | 15.4 | 15.3 | 15.1 | 15 | 14.8 | 14.6 | 14.6 | 14.5 | 14.4 | 13.7 | 12.7
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.1 | 16.8 | 16.6 | 15.5 | 15.4 | 15.2 | 14.8 | 14.5 | 14.1 | 13.5 | 12.9 | 11.9 | 11.1 | 10.3 | 9.9 | 9.7 | 9.4 | 8 | 6.5
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.1 | 16.7 | 16.4 | 15.4 | 15.1 | 14.7 | 14.2 | 13.6 | 12.8 | 11.9 | 10.9 | 10.2 | 9.6 | 9.2 | 9 | 8.7 | 8.4 | 6.8 | 5.2
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.1 | 16.9 | 16.7 | 16.5 | 15.4 | 15.3 | 15.1 | 14.7 | 14.4 | 13.9 | 13.3 | 12.8 | 12.3 | 12 | 11.9 | 11.7 | 11.4 | 10 | 8.5
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.4 | 20.3 | 20.2 | 20.2 | 20.1 | 20 | 19.9 | 19.7 | 19.5 | 19.3 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 18.9 | 18.5
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.4 | 20.1 | 20 | 19.5 | 19.2 | 18.9 | 18.6 | 18.5 | 18.4 | 18.3 | 18.2 | 18.1 | 18 | 17.9 | 14.4 | 14.4 | 14.3 | 13.7 | 12.5
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.4 | 20 | 19.7 | 19.2 | 18.8 | 18.5 | 18.3 | 18.1 | 17.9 | 17.9 | 14.4 | 14.3 | 14.3 | 14.2 | 14.1 | 13.9 | 13.7 | 12.5 | 10.8
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.4 | 20.2 | 20.2 | 19.8 | 19.5 | 19.2 | 18.9 | 18.8 | 18.6 | 18.5 | 18.4 | 18.4 | 18.4 | 18.3 | 18.3 | 18.3 | 18.2 | 14.4 | 14
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.2 | 14 | 13.8 | 13.7 | 13.6 | 13.7 | 13.5 | 13.2 | 12.6 | 11.8 | 10.9 | 10.4 | 10 | 9.6 | 9.2 | 8.8 | 8.6 | 6.9 | 5.1
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.2 | 13.9 | 13.6 | 13.4 | 12.6 | 11.8 | 10.7 | 10.3 | 9.5 | 8.5 | 7.2 | 5.7 | 4.6 | 3.6 | 2.8 | 2 | 0 | 0 | 0
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.2 | 13.8 | 13.4 | 12.7 | 12.1 | 11.4 | 10.7 | 9.7 | 8.2 | 7.1 | 5.7 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.2 | 13.9 | 13.7 | 13.5 | 12.8 | 12.1 | 11.5 | 10.6 | 9.9 | 9.1 | 7.5 | 6.9 | 6.3 | 5.8 | 5.3 | 4.9 | 4.5 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 37.7 | 37 | 36.7 | 36.3 | 35.8 | 35.3 | 36.3 | 35.2 | 33 | 30.5 | 27.4 | 25 | 23.3 | 21.9 | 20.5 | 19 | 17.6 | 8.2 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 37.7 | 36.4 | 34.9 | 33.2 | 31.3 | 29 | 28.1 | 26 | 22.3 | 18.2 | 13.2 | 7.8 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 37.7 | 36.1 | 33.8 | 31.7 | 29.3 | 26.4 | 25.3 | 21 | 15.2 | 10.5 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 37.7 | 36.7 | 35.7 | 33.8 | 32 | 29.7 | 29.3 | 27.3 | 24.3 | 21.5 | 16.9 | 13.6 | 10.6 | 7.8 | 5.6 | 3 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.2 | 2.1 | 2 | 1.8 | 1.6 | 1.4 | 3.2 | 2.8 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.2 | 1.8 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.2 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.2 | 2 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.5 | 20.3 | 20.2 | 20 | 19.9 | 19.7 | 19.5 | 19.4 | 19.2 | 19 | 18.8 | 18.7 | 18.6 | 18.4 | 18.3 | 18.2 | 18.1 | 17.7 | 17
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.5 | 20.1 | 19.8 | 19.6 | 19.3 | 19.1 | 18.8 | 18.6 | 18.3 | 18 | 17.5 | 16.9 | 16.6 | 16.3 | 15.9 | 15.7 | 15.5 | 14.2 | 12.6
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.5 | 20 | 19.5 | 19.2 | 18.8 | 18.4 | 17.9 | 17.4 | 16.7 | 15.9 | 15.7 | 15.6 | 15.4 | 15.2 | 14.9 | 14.7 | 14.4 | 12.8 | 10.9
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.5 | 20.3 | 20.1 | 19.9 | 19.7 | 19.4 | 19.2 | 18.9 | 18.6 | 18.2 | 17.6 | 17.5 | 17.4 | 17.3 | 17.2 | 17.1 | 16.9 | 15.8 | 14.7
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.1 | 20.2 | 20.1 | 20 | 19.9 | 19.7 | 19.5 | 19.3 | 19 | 18.7 | 18.4 | 18.1 | 17.8 | 17.5 | 17.3 | 17 | 16.8 | 14.9 | 14.9
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.1 | 20.2 | 20 | 19.7 | 19.3 | 18.9 | 18.4 | 17.9 | 17.4 | 16.9 | 16.5 | 14.8 | 14.6 | 14.2 | 13.8 | 13.4 | 12.9 | 11.4 | 11.1
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.1 | 20.2 | 19.9 | 19.5 | 19.1 | 18.7 | 18.1 | 17.6 | 17.1 | 16.6 | 14.9 | 14.7 | 14.4 | 14 | 13.6 | 13.1 | 12.6 | 11.1 | 10.6
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.1 | 20.2 | 20 | 19.7 | 19.4 | 19 | 18.5 | 18 | 17.5 | 17 | 16.5 | 14.9 | 14.7 | 14.5 | 14.1 | 13.7 | 13.2 | 11.9 | 11.6
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17 | 17 | 17 | 17 | 15.1 | 15.1 | 15.1 | 15 | 15 | 15 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.8 | 14.7
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17 | 17 | 15.1 | 15.1 | 15.1 | 15 | 14.9 | 14.7 | 14.6 | 14.5 | 14.4 | 14.4 | 14.3 | 14.2 | 14.1 | 14.1 | 14 | 13.6 | 13
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17 | 17 | 15.1 | 15.1 | 14.9 | 14.8 | 14.6 | 14.4 | 14.3 | 14.2 | 14.1 | 14 | 13.9 | 13.8 | 13.7 | 13.6 | 13.5 | 15 | 12.1
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17 | 17 | 17 | 15.1 | 15.1 | 15 | 15 | 14.9 | 14.8 | 14.7 | 14.6 | 14.6 | 14.6 | 14.6 | 14.6 | 14.5 | 14.5 | 14.2 | 13.9
Enderby 132kV | HINCKLEY 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 7 | 6.7 | 6.3 | 6.1 | 5.9 | 5.8 | 5.5 | 5.3 | 4.9 | 4.4 | 3.8 | 3.3 | 3 | 2.7 | 2.4 | 2.2 | 1.9 | 0 | 0
Enderby 132kV | HINCKLEY 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 7 | 6.2 | 5.7 | 5.4 | 5 | 4.6 | 4 | 3.5 | 2.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | HINCKLEY 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 7 | 6 | 5.4 | 4.8 | 4.3 | 3.7 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | HINCKLEY 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 7 | 6.3 | 6 | 5.8 | 5.5 | 5.1 | 4.6 | 4.2 | 3.6 | 2.9 | 2 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 23.3 | 23.3 | 23.2 | 23.1 | 23 | 22.9 | 22.8 | 22.7 | 22.5 | 22.3 | 22.1 | 21.8 | 21.5 | 21.6 | 21.7 | 21.6 | 21.3 | 20.8 | 20.4
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 23.3 | 23.1 | 23 | 22.8 | 22.6 | 22.4 | 22.1 | 21.7 | 21.3 | 20.9 | 20.4 | 19.7 | 18.9 | 18.4 | 18.2 | 17.9 | 17.7 | 16.6 | 15.4
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 23.3 | 23.1 | 22.9 | 22.6 | 22.3 | 21.9 | 21.4 | 21 | 20.3 | 19.7 | 18.5 | 18 | 17.6 | 17.4 | 17.2 | 16.9 | 16.6 | 15.2 | 13.9
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 23.3 | 23.2 | 23.2 | 23 | 22.8 | 22.6 | 22.2 | 21.8 | 21.5 | 21.2 | 20.7 | 20.2 | 19.8 | 19.7 | 19.2 | 19.1 | 18.9 | 18.1 | 17.2
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.6 | 17.3 | 17.2 | 17.2 | 17.2 | 17.2 | 17.1 | 17.1 | 17.1 | 17 | 17 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 8.2 | 0
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.6 | 17.3 | 17.2 | 17.2 | 17.2 | 17.1 | 17.1 | 17.1 | 17 | 16.9 | 13.2 | 7.8 | 3 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.6 | 17.3 | 17.2 | 17.2 | 17.1 | 17.1 | 17.1 | 17 | 15.1 | 10.5 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.6 | 17.3 | 17.2 | 17.2 | 17.2 | 17.1 | 17.1 | 17.1 | 17 | 17 | 16.8 | 13.6 | 10.6 | 7.8 | 5.6 | 3 | 0 | 0 | 0
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 25.2 | 25.2 | 25.1 | 25 | 24.9 | 24.8 | 24.7 | 24.6 | 24.5 | 24.4 | 24.3 | 24.3 | 24.3 | 24.3 | 24.3 | 24.2 | 24.3 | 24.1 | 23.9
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 25.2 | 25.1 | 24.9 | 24.7 | 24.6 | 24.4 | 24.3 | 24.2 | 24 | 23.9 | 23.9 | 23.8 | 23.7 | 23.6 | 23.6 | 23.5 | 23.5 | 23.3 | 19.7
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 25.2 | 25 | 24.7 | 24.5 | 24.3 | 24.1 | 23.9 | 23.7 | 23.6 | 23.5 | 23.5 | 23.4 | 23.4 | 23.4 | 23.4 | 23.3 | 23.3 | 19.6 | 19.1
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 25.2 | 25.2 | 25 | 24.9 | 24.8 | 24.6 | 24.5 | 24.3 | 24.2 | 24.1 | 24.1 | 24 | 24 | 24 | 24 | 23.9 | 23.9 | 23.6 | 23.4
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 42 | 42 | 42 | 41.9 | 41.8 | 41.8 | 41.4 | 41.2 | 41 | 40.9 | 40.7 | 40.6 | 40.6 | 40.5 | 40.5 | 40.5 | 41 | 40.7 | 40.2
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 42 | 42 | 41.7 | 41.4 | 41.1 | 40.8 | 40.5 | 40.3 | 40.1 | 39.8 | 39.7 | 39.5 | 39.3 | 39.1 | 39 | 38.8 | 39.1 | 38.4 | 34
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 42 | 42 | 41.4 | 41 | 40.6 | 40.2 | 39.8 | 39.4 | 39.1 | 38.9 | 38.7 | 38.6 | 38.5 | 38.4 | 38.3 | 38.2 | 38.3 | 33.9 | 33.2
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 42 | 42 | 42 | 41.9 | 41.5 | 41.2 | 40.9 | 40.7 | 40.5 | 40.3 | 40.1 | 40.1 | 40 | 40 | 39.9 | 39.9 | 40.2 | 39.5 | 38.9
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 90.5 | 90.4 | 90 | 89.7 | 89.4 | 89.1 | 88.5 | 88 | 87.5 | 86.9 | 86.4 | 86.2 | 86 | 86 | 86 | 85.9 | 86.2 | 84.9 | 83.4
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 90.5 | 90.2 | 89.4 | 88.6 | 87.8 | 86.9 | 86.1 | 85.3 | 84.7 | 84 | 83.3 | 82.7 | 79.1 | 78.5 | 76.5 | 76 | 75.2 | 68.2 | 63
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 90.5 | 90 | 88.7 | 87.6 | 86.5 | 85.4 | 84.4 | 83.2 | 82.5 | 78.9 | 77.7 | 76.4 | 75.7 | 74.8 | 72 | 71.8 | 71 | 62.6 | 56.2
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 90.5 | 90.4 | 89.9 | 89.4 | 88.6 | 87.8 | 87 | 86.3 | 85.6 | 85 | 84.6 | 84.1 | 83.8 | 83.5 | 83.3 | 83.1 | 83 | 78.5 | 75.1
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 84.7 | 84.4 | 83.8 | 83.4 | 82.9 | 82.4 | 81.8 | 80.6 | 79.9 | 78.5 | 77.4 | 76.5 | 75.7 | 75 | 74.4 | 74 | 73.6 | 71.1 | 68.2
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 84.7 | 83.8 | 82.8 | 81.9 | 80.1 | 79 | 77.2 | 75.4 | 73.5 | 71.4 | 69.4 | 67.3 | 65.6 | 63.8 | 61.8 | 60.2 | 58.2 | 48.6 | 40.6
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 84.7 | 83.4 | 82.1 | 80 | 78.6 | 76.8 | 74.2 | 71.7 | 69.3 | 66.1 | 64 | 62.5 | 60.1 | 58 | 56.2 | 54.1 | 51.8 | 44.3 | 32.3
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 84.7 | 84.2 | 83.5 | 82.6 | 81.8 | 80.2 | 78.4 | 76.8 | 75.1 | 73.3 | 71.6 | 70.5 | 69.5 | 68.5 | 67.2 | 66.2 | 65 | 59.2 | 53.4
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 26.9 | 26.9 | 26.9 | 26.8 | 26.8 | 26.7 | 26.6 | 26.6 | 26.5 | 26.4 | 26.2 | 26.1 | 26.1 | 26 | 26 | 26 | 26 | 25.7 | 25.4
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 26.9 | 26.9 | 26.9 | 26.8 | 26.6 | 26.4 | 26.1 | 25.9 | 25.6 | 25.4 | 25.2 | 25 | 24.9 | 24.7 | 24.5 | 24.4 | 24.2 | 23.5 | 22.6
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 26.9 | 26.9 | 26.9 | 26.6 | 26.2 | 25.8 | 25.5 | 25.1 | 24.8 | 24.5 | 24.3 | 24.1 | 24 | 23.9 | 23.7 | 23.6 | 23.3 | 22.4 | 20.5
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 26.9 | 26.9 | 26.9 | 26.8 | 26.8 | 26.7 | 26.5 | 26.2 | 26 | 25.8 | 25.7 | 25.6 | 25.6 | 25.5 | 25.5 | 25.4 | 25.3 | 24.7 | 24.1
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.2 | 17.2 | 17.1 | 17.1 | 17 | 17 | 16.9 | 16.9 | 16.9 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 15.5
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.2 | 17.1 | 16.9 | 16.9 | 16.8 | 16.8 | 16.8 | 15.6 | 15.6 | 15.5 | 15.5 | 15.5 | 15.4 | 15.3 | 15.2 | 15.1 | 15 | 14.5 | 13.8
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.2 | 17 | 16.8 | 16.8 | 15.6 | 15.6 | 15.5 | 15.3 | 15.2 | 15.1 | 15 | 15 | 14.9 | 14.8 | 14.7 | 14.6 | 14.5 | 13.7 | 11
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.2 | 17.1 | 17.1 | 17 | 16.9 | 16.9 | 16.8 | 16.8 | 16.8 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.5 | 15.3 | 14.9
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 46.9 | 46.6 | 46.1 | 44.7 | 44.2 | 43.6 | 41.5 | 40.9 | 40.3 | 39.6 | 38.9 | 38.4 | 38 | 37.7 | 37.6 | 37.4 | 37.3 | 35.7 | 33.4
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 46.9 | 46 | 43.9 | 42.9 | 41.8 | 40.7 | 39.4 | 38.2 | 37.1 | 35.7 | 34.2 | 32.2 | 30.7 | 29.3 | 28.4 | 27.6 | 26.8 | 22.5 | 17.5
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 46.9 | 44.6 | 42.9 | 41.5 | 40 | 38.4 | 36.6 | 34.7 | 32.5 | 30.4 | 28.5 | 27.3 | 26.2 | 25.4 | 24.8 | 24 | 23 | 19 | 11
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 46.9 | 46.4 | 44.7 | 43.9 | 42.9 | 41.8 | 40.6 | 39.5 | 38.3 | 37 | 35.6 | 34.7 | 34 | 33.5 | 33.3 | 33.1 | 32.5 | 28.7 | 24.9
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 21.5 | 21.4 | 21.4 | 21.3 | 21.3 | 21.2 | 21.1 | 21.1 | 21 | 21 | 20.9 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.6 | 20.4
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 21.5 | 21.4 | 21.2 | 21.1 | 21 | 20.8 | 20.7 | 20.6 | 20.5 | 20.3 | 20.3 | 20.2 | 20.1 | 19.9 | 19.8 | 19.7 | 19.6 | 19 | 17.5
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 21.5 | 21.3 | 21.1 | 20.9 | 20.7 | 20.5 | 20.3 | 20 | 19.9 | 19.8 | 19.6 | 19.5 | 19.4 | 19.3 | 19.2 | 19.1 | 18.9 | 19 | 11
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 21.5 | 21.4 | 21.3 | 21.2 | 21.2 | 21.1 | 20.9 | 20.8 | 20.7 | 20.7 | 20.6 | 20.6 | 20.6 | 20.6 | 20.5 | 20.5 | 20.4 | 20 | 19.5
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 31.2 | 31.2 | 31.1 | 31.1 | 31 | 31 | 30.9 | 30.9 | 30.8 | 30.7 | 30.6 | 30.6 | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 30.4 | 30.3
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 31.2 | 31.2 | 31 | 30.9 | 30.8 | 30.7 | 30.5 | 30.4 | 30.3 | 30.2 | 30.1 | 30.1 | 30 | 30 | 29.9 | 29.9 | 29.8 | 29.5 | 29.2
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 31.2 | 31.2 | 30.9 | 30.8 | 30.6 | 30.5 | 30.3 | 30.2 | 30.1 | 30 | 29.9 | 29.8 | 29.8 | 29.7 | 29.6 | 29.6 | 29.5 | 29.1 | 28.7
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 31.2 | 31.2 | 31.1 | 31 | 30.9 | 30.8 | 30.7 | 30.6 | 30.5 | 30.4 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.2 | 30.2 | 30 | 29.8
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 21.2 | 21 | 21 | 21 | 20.9 | 20.8 | 20.7 | 16.2 | 15.8 | 15.3 | 14 | 13 | 12.4 | 11.9 | 11.4 | 10.8 | 10.3 | 6.3 | 1.9
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 21.2 | 20.8 | 20.6 | 16.3 | 16.1 | 15.9 | 15.3 | 14.7 | 13.3 | 12.4 | 10.2 | 7.9 | 5.8 | 3.5 | 1.8 | 0 | 0 | 0 | 0
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 21.2 | 20.7 | 16.3 | 16.2 | 15.8 | 15.4 | 14.6 | 12.9 | 10.3 | 9 | 6.3 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 21.2 | 20.9 | 20.8 | 16.3 | 16.2 | 16.1 | 15.7 | 15.3 | 14.2 | 13.9 | 12 | 10.6 | 9.3 | 8.1 | 7.2 | 6.2 | 5.1 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 5.2 | 5.2 | 5.1 | 5.1 | 5 | 4.7 | 4.6 | 4.2 | 3.7 | 3.2 | 2.9 | 2.6 | 2.4 | 2.2 | 2 | 1.8 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 5 | 4.8 | 4.4 | 3.9 | 3.3 | 2.4 | 2 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 5 | 4.7 | 4.3 | 3.7 | 3.1 | 2.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 5.1 | 4.9 | 4.5 | 4.1 | 3.5 | 2.6 | 2.4 | 1.9 | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.2 | 2.1 | 2 | 1.8 | 1.6 | 1.4 | 3.2 | 2.8 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.2 | 1.8 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.2 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.2 | 2 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 35.1 | 35.1 | 35.1 | 35 | 34.9 | 34.9 | 34.8 | 34.7 | 34.7 | 34.6 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.3 | 33.3 | 32.1
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 35.1 | 35.1 | 35.1 | 35 | 34.9 | 34.9 | 34.8 | 34.7 | 34.6 | 34.4 | 33.8 | 33 | 32.1 | 31.2 | 30.4 | 29.7 | 24.8 | 21.3 | 19.5
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 35.1 | 35.1 | 35.1 | 35 | 34.9 | 34.9 | 34.8 | 34.4 | 33.4 | 32.4 | 31.5 | 30.7 | 30.1 | 29.5 | 24.8 | 24.5 | 23.8 | 19.4 | 18.3
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 35.1 | 35.1 | 35.1 | 35 | 34.9 | 34.9 | 34.8 | 34.7 | 34.7 | 34.6 | 34.5 | 34.1 | 33.8 | 33.5 | 33.2 | 32.9 | 32.6 | 31 | 29.8
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 25.3 | 25.2 | 25 | 24.9 | 24.8 | 24.7 | 24.5 | 24.4 | 24.3 | 24.2 | 24.1 | 24.1 | 24 | 24 | 24 | 24 | 24 | 23.8 | 23.5
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 25.3 | 25 | 24.7 | 24.5 | 24.2 | 24 | 23.8 | 23.7 | 23.6 | 23.5 | 23.5 | 23.4 | 23.4 | 19.7 | 19.7 | 19.6 | 19.6 | 19 | 17.9
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 25.3 | 24.8 | 24.4 | 24.1 | 23.8 | 23.6 | 23.4 | 23.3 | 19.7 | 19.6 | 19.5 | 19.5 | 19.4 | 19.3 | 19.2 | 19 | 18.8 | 17.6 | 16
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 25.3 | 25.1 | 24.9 | 24.7 | 24.6 | 24.4 | 24.2 | 24 | 23.9 | 23.8 | 23.7 | 23.7 | 23.6 | 23.6 | 23.6 | 23.6 | 23.5 | 19.7 | 19.5
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 21.3 | 21.2 | 21.1 | 21 | 20.9 | 20.8 | 20.7 | 20.6 | 20.5 | 20.4 | 20.3 | 20.2 | 20.2 | 20.1 | 20.1 | 20.1 | 20.1 | 19.9 | 19.7
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 21.3 | 21 | 20.8 | 20.6 | 20.4 | 20.3 | 20.1 | 20 | 19.9 | 19.8 | 19.7 | 19.7 | 17.2 | 17.2 | 17.1 | 17 | 16.9 | 16.1 | 15.1
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 21.3 | 20.9 | 20.6 | 20.3 | 20.1 | 19.9 | 19.7 | 19.6 | 17.3 | 17.1 | 17 | 16.9 | 16.9 | 16.7 | 16.6 | 16.5 | 16.2 | 15.1 | 13.7
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 21.3 | 21.1 | 21 | 20.8 | 20.7 | 20.5 | 20.4 | 20.2 | 20.1 | 20 | 19.9 | 19.9 | 19.8 | 19.8 | 19.8 | 19.8 | 19.7 | 17.1 | 16.7
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.6 | 14.6 | 14.5 | 14.4 | 14.4 | 14.3 | 14.3 | 14.1 | 13.9 | 13.3 | 13.3 | 13.3 | 13.2 | 13.1 | 13 | 12.9 | 12.9 | 12.7 | 12.4
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.6 | 14.5 | 14.3 | 14.1 | 13.9 | 13.4 | 12.4 | 11.9 | 11.5 | 10.9 | 10.6 | 10.4 | 10.2 | 10.1 | 9.2 | 9.1 | 8.9 | 8.3 | 7.5
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.6 | 14.4 | 14.2 | 14 | 13.6 | 13 | 11.8 | 11.1 | 10.6 | 8.4 | 8.3 | 8.2 | 8.1 | 8 | 7.9 | 7.8 | 7.6 | 6.8 | 5.9
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.6 | 14.5 | 14.4 | 14.2 | 14.1 | 13.6 | 12.5 | 12.1 | 11.6 | 10.9 | 10.7 | 10.7 | 10.6 | 10.6 | 9.8 | 9.7 | 9.6 | 9.2 | 8.6
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.3 | 14.2 | 12.1 | 12.1 | 12 | 12 | 11.9 | 11.8 | 11.5 | 11.1 | 10.6 | 10.1 | 9.7 | 9.3 | 9 | 8.7 | 8.5 | 7.3 | 5.7
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.3 | 12.1 | 12.1 | 12 | 11.8 | 11.7 | 11.4 | 10.8 | 10 | 9 | 8 | 6.9 | 6 | 5 | 4.1 | 3.3 | 2.5 | 0 | 0
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.3 | 12.1 | 12 | 11.9 | 11.7 | 11.4 | 10.8 | 9.9 | 8.8 | 7.8 | 6.7 | 5.8 | 4.3 | 3.5 | 2.8 | 2 | 1.3 | 0 | 0
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.3 | 14.2 | 12.1 | 12 | 11.9 | 11.8 | 11.5 | 11.1 | 10.5 | 9.8 | 9 | 8.2 | 7.6 | 7 | 6.5 | 6 | 5.5 | 2.7 | 0
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.7 | 18.6 | 18.6 | 18.5 | 18.4 | 18.3 | 18.2 | 18.1 | 18 | 17.8 | 17.7 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 14.6 | 14.5 | 14.1
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.7 | 18.5 | 18.4 | 18.1 | 18 | 17.9 | 17.8 | 17.7 | 17.6 | 17.6 | 14.5 | 14.4 | 14.3 | 14.1 | 13.9 | 13.7 | 13.5 | 12.7 | 11
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.7 | 18.5 | 18.2 | 18 | 17.9 | 17.7 | 17.6 | 17.6 | 14.5 | 14.4 | 14.1 | 13.9 | 13.6 | 13.4 | 13.2 | 12.9 | 12.6 | 11.6 | 10.2
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.7 | 18.6 | 18.5 | 18.3 | 18.2 | 18 | 17.9 | 17.9 | 17.7 | 17.7 | 17.6 | 14.6 | 14.5 | 14.5 | 14.5 | 14.4 | 14.4 | 14.1 | 12.9
Enderby 132kV | WIGSTON 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.1 | 28.5 | 28.3 | 28.1 | 28 | 27.8 | 27.6 | 27.5 | 27.4 | 26.5 | 26.4 | 26.3 | 26.3 | 26.2 | 26.2 | 26.2 | 26.1 | 25.7 | 24.9
Enderby 132kV | WIGSTON 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.1 | 28.3 | 27.9 | 27.7 | 27.4 | 26.5 | 26.4 | 26.1 | 25.8 | 25.5 | 25.2 | 25 | 24.7 | 24.4 | 24.1 | 23.8 | 23.4 | 21.3 | 19.4
Enderby 132kV | WIGSTON 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.1 | 28.1 | 27.7 | 27.4 | 26.5 | 26.1 | 25.7 | 25.2 | 24.7 | 24.3 | 23.9 | 23.7 | 22.4 | 22.1 | 21.7 | 21.4 | 21 | 18.9 | 16.6
Enderby 132kV | WIGSTON 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.1 | 28.4 | 28.2 | 28 | 27.7 | 27.5 | 26.5 | 26.4 | 26.3 | 26.1 | 25.9 | 25.8 | 25.7 | 25.5 | 25.4 | 25.3 | 25 | 23.4 | 21.9
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 27 | 27 | 27 | 27.1 | 27.2 | 27.3 | 27.3 | 27.3 | 27 | 26.8 | 26.5 | 26.3 | 26.6 | 26.5 | 26.5 | 26.4 | 26.4 | 25.6 | 24.4
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 27 | 27 | 27.1 | 27.1 | 27 | 26.6 | 26.2 | 26 | 25.6 | 24.9 | 24.2 | 23.5 | 24.4 | 23.7 | 23.2 | 22.7 | 22.2 | 20.2 | 16.9
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 27 | 27.1 | 27.2 | 27.2 | 27 | 26.6 | 25.9 | 25.3 | 24.4 | 23.6 | 22.8 | 22.3 | 23 | 22.4 | 21.9 | 21.3 | 20.8 | 18.4 | 15.7
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 27 | 27 | 27.1 | 27 | 27 | 26.7 | 26.2 | 26.3 | 26.2 | 25.8 | 25.3 | 25 | 25.3 | 25.1 | 24.9 | 24.6 | 24.3 | 23.1 | 20.5
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 28 | 27.8 | 27.6 | 27.4 | 27.2 | 27.1 | 26.9 | 26.7 | 26.6 | 26.4 | 26.2 | 25.9 | 25.7 | 25.5 | 25.4 | 25.4 | 25.4 | 19.6 | 19.1
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 28 | 27.5 | 27.1 | 26.8 | 26.5 | 26.2 | 26 | 25.6 | 25.3 | 19.5 | 19.1 | 18.6 | 18.1 | 17.5 | 17.1 | 16.6 | 16.1 | 13.4 | 10.6
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 28 | 27.3 | 26.7 | 26.3 | 25.9 | 25.6 | 25.2 | 19.6 | 18.8 | 17.9 | 17.2 | 16.6 | 16.2 | 15.8 | 15.4 | 14.9 | 14.3 | 11.1 | 8.2
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 28 | 27.7 | 27.4 | 27.2 | 26.9 | 26.6 | 26.4 | 26 | 25.6 | 25.3 | 19.5 | 19.5 | 19.4 | 19.3 | 19.2 | 19.1 | 18.9 | 17.3 | 15.3
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.7 | 6.7 | 6.6 | 6.6 | 6.5 | 6.5 | 6.4 | 6.3 | 5.8 | 6.1 | 5.3 | 4.7 | 4.4 | 4.1 | 3.9 | 3.6 | 3.4 | 1.4 | 0
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.7 | 6.6 | 6.5 | 6.4 | 6.4 | 6.3 | 6 | 5.8 | 5.1 | 5 | 3.9 | 2.8 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.7 | 6.6 | 6.4 | 6.3 | 6.2 | 6.1 | 5.9 | 5 | 3.6 | 3.4 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.7 | 6.7 | 6.6 | 6.5 | 6.5 | 6.4 | 6.2 | 6.1 | 5.5 | 5.8 | 4.7 | 4 | 3.3 | 2.7 | 2.3 | 1.9 | 1.5 | 0 | 0
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.1 | 17 | 17 | 16.9 | 16.9 | 16.9 | 16.8 | 16.8 | 16.8 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.8 | 16.8 | 16.7 | 16.6 | 15.5
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.1 | 16.9 | 16.8 | 16.7 | 16.6 | 16.6 | 16.5 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 15.5 | 15.5 | 15.5 | 15.2 | 15.2 | 14.5 | 13.3
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.1 | 16.8 | 16.6 | 16.5 | 15.9 | 15.8 | 15.6 | 15.5 | 15.5 | 15.2 | 15.2 | 15.2 | 15.1 | 14.9 | 14.8 | 14.7 | 14.4 | 13.1 | 11.6
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.1 | 17 | 16.9 | 16.9 | 16.8 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.8 | 16.8 | 16.8 | 16.8 | 16.6 | 15.5 | 15
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.6 | 14.6 | 14.5 | 14.4 | 14.3 | 14.2 | 14.1 | 14 | 13.9 | 13.8 | 13.6 | 13.5 | 13.4 | 13.4 | 13.3 | 13.3 | 13.4 | 13.1 | 12.7
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.6 | 14.5 | 14.3 | 14 | 13.9 | 13.6 | 13.5 | 13.3 | 13.1 | 12.9 | 12.7 | 12.5 | 12.2 | 12 | 11.9 | 11.8 | 11.8 | 10.3 | 9.3
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.6 | 14.4 | 14.2 | 13.9 | 13.7 | 13.4 | 13.2 | 12.9 | 12.6 | 12.3 | 12 | 11.9 | 11.7 | 10.2 | 10.1 | 10 | 9.7 | 8.8 | 8.1
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.6 | 14.6 | 14.4 | 14.1 | 13.9 | 13.7 | 13.6 | 13.4 | 13.2 | 13.1 | 12.9 | 12.7 | 12.6 | 12.5 | 12.5 | 12.4 | 12.5 | 11.3 | 10.5
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 31.5 | 31.4 | 31.1 | 29.7 | 29.5 | 29.3 | 29.1 | 28.9 | 28.8 | 24.6 | 24.5 | 24.4 | 24.3 | 24.3 | 24.2 | 24.2 | 24.1 | 23.4 | 22.7
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 31.5 | 31.2 | 29.4 | 29 | 28.7 | 24.7 | 24.3 | 23.8 | 23.2 | 22.5 | 21.8 | 21.3 | 20.9 | 20.4 | 20 | 19.5 | 19 | 16.2 | 14.5
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 31.5 | 29.9 | 29.3 | 28.8 | 24.7 | 24.5 | 23.9 | 23.2 | 22.4 | 21.6 | 20.8 | 20.4 | 19.9 | 19.5 | 19.1 | 18.6 | 18.1 | 15 | 13.1
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 31.5 | 31.3 | 29.6 | 29.2 | 28.8 | 24.7 | 24.5 | 24 | 23.5 | 22.9 | 22.3 | 22 | 21.8 | 21.6 | 21.3 | 21 | 20.6 | 18.5 | 17.1
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.1 | 11.9 | 11.9 | 11.9 | 11.5 | 11.4 | 11.3 | 11.2 | 11 | 10 | 8.2 | 6.8 | 6 | 5.5 | 5 | 4.5 | 3.9 | 0 | 0
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.1 | 11.9 | 11.5 | 11.3 | 10.9 | 10.5 | 9.7 | 9.4 | 7.9 | 5.5 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.1 | 11.5 | 11.4 | 11.2 | 10.9 | 10.5 | 9.6 | 7.9 | 4.6 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.1 | 11.9 | 11.5 | 11.3 | 11 | 10.5 | 9.8 | 9.5 | 9.1 | 7.5 | 5.1 | 3.4 | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.6 | 4.6 | 4.5 | 4.5 | 4.5 | 4.5 | 4.3 | 4.2 | 3.9 | 3.5 | 3.1 | 2.7 | 2.5 | 2.3 | 2.1 | 2 | 1.8 | 0 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.6 | 4.6 | 4.5 | 4.4 | 4.4 | 4.3 | 4 | 3.7 | 3.1 | 2.3 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.6 | 4.5 | 4.5 | 4.4 | 4.3 | 4.3 | 3.9 | 3.4 | 2.5 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.6 | 4.6 | 4.5 | 4.5 | 4.5 | 4.4 | 4.2 | 4.1 | 3.7 | 3.3 | 2.7 | 2.2 | 1.8 | 1.3 | 0.7 | 0 | 0 | 0 | 0
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.4 | 9.4 | 9.3 | 9.3 | 9.3 | 9.2 | 9.2 | 9.2 | 9.1 | 9 | 8.9 | 8.8 | 8.8 | 7.4 | 7.4 | 7.3 | 7.3 | 7.1 | 6.7
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.4 | 9.3 | 9.3 | 9.2 | 9.2 | 9.2 | 9.1 | 9.1 | 9 | 8.9 | 8.8 | 7.3 | 7.2 | 7 | 6.9 | 6.7 | 6.6 | 5.6 | 4.5
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.4 | 9.3 | 9.2 | 9.2 | 9.1 | 9.1 | 9 | 8.9 | 8.8 | 7.3 | 7.1 | 6.9 | 6.7 | 6.6 | 6.4 | 6.3 | 6.1 | 5.3 | 4.7
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.4 | 9.4 | 9.3 | 9.3 | 9.2 | 9.2 | 9.2 | 9.2 | 9 | 8.9 | 8.8 | 7.4 | 7.3 | 7.3 | 7.3 | 7.2 | 7.2 | 6.6 | 5.7
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.1 | 10.3 | 10.1 | 9.8 | 9.5 | 9.5 | 9.3 | 5.4 | 5.1 | 4.8 | 4.5 | 4.3 | 4.2 | 4.2 | 4.3 | 4.2 | 4.2 | 1.7 | 0.7
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.1 | 10.1 | 9.5 | 8.5 | 8 | 7.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.1 | 10 | 9.4 | 9 | 8.5 | 8.1 | 7.7 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.1 | 10.1 | 9.6 | 8.9 | 8.7 | 8.5 | 8.3 | 4.3 | 4 | 3.7 | 3.3 | 3.1 | 2.8 | 2.7 | 2.8 | 2.5 | 2.6 | 0 | 0
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 32.7 | 32.7 | 32.7 | 32.6 | 32.6 | 32.7 | 32.7 | 32.6 | 32.5 | 32.2 | 32 | 31.9 | 31.8 | 31.7 | 31.7 | 31.7 | 31.7 | 31.3 | 30.7
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 32.7 | 32.7 | 32.7 | 32.3 | 32.1 | 31.6 | 31.2 | 31 | 30.9 | 30.6 | 30.3 | 30 | 29.7 | 29.4 | 29.3 | 29.1 | 28.9 | 26.4 | 25.3
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 32.7 | 32.7 | 32.5 | 32.1 | 31.6 | 31.1 | 30.6 | 30.3 | 30.1 | 29.7 | 29.4 | 29.1 | 28.9 | 28.6 | 28.5 | 28.4 | 28.3 | 25.3 | 23.9
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 32.7 | 32.7 | 32.7 | 32.6 | 32.5 | 32 | 31.6 | 31.4 | 31.3 | 31.1 | 30.8 | 30.7 | 30.5 | 30.4 | 30.4 | 30.3 | 30.2 | 29.4 | 28.5
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 28 | 27.6 | 27.6 | 27.5 | 27.3 | 27.1 | 29.6 | 29.3 | 29 | 28.6 | 28.3 | 28.1 | 27.8 | 27.7 | 27.6 | 27.6 | 27.5 | 27.1 | 24.4
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 28 | 27.5 | 27.1 | 26.8 | 24.5 | 24 | 27.1 | 24.4 | 24.1 | 23.7 | 23 | 22.3 | 21.6 | 21.1 | 20.8 | 20.5 | 20.2 | 18.4 | 16.4
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 28 | 27.4 | 26.9 | 26.7 | 24.3 | 23.4 | 24.5 | 23.7 | 22.9 | 22.2 | 21.5 | 21 | 20.4 | 19.9 | 19.6 | 19.3 | 18.9 | 16.7 | 14.5
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 28 | 27.7 | 27.3 | 26.9 | 24.5 | 24.2 | 27.2 | 24.5 | 24.2 | 23.7 | 23.1 | 22.8 | 22.4 | 22.2 | 22.1 | 22 | 21.8 | 20.5 | 19
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.3 | 9.3 | 8.4 | 8.1 | 7.9 | 7.7 | 7.5 | 7.1 | 6.4 | 5.5 | 4.1 | 3.2 | 2.6 | 2.2 | 1.7 | 1 | 0 | 0 | 0
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.3 | 9.2 | 8 | 7.4 | 6.8 | 6.2 | 4.4 | 3.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.3 | 9.1 | 8.8 | 8.1 | 7.4 | 5.9 | 4.7 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.3 | 9.3 | 8.1 | 7.5 | 7 | 6.4 | 5.4 | 3.6 | 2.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.4 | 20.4 | 20.3 | 20.1 | 19.9 | 19.7 | 19.5 | 19.1 | 19 | 18.9 | 18.8 | 18.6 | 18.5 | 15.4 | 15.4 | 15.4 | 15.4 | 15.3 | 15.3
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.4 | 20.3 | 19.9 | 19.5 | 18.5 | 15.4 | 14.6 | 14 | 13.4 | 12.4 | 11.8 | 11.4 | 11.1 | 10.9 | 10.6 | 10.4 | 10.4 | 0 | 0
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.4 | 20.3 | 19.9 | 18.7 | 15.5 | 15 | 14.5 | 13.7 | 13 | 12.3 | 11.7 | 11.5 | 11.2 | 11 | 10.7 | 10.5 | 10.5 | 0 | 0
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.4 | 20.3 | 19.9 | 19.5 | 18.5 | 15.4 | 14.6 | 14.1 | 13.5 | 12.5 | 11.9 | 11.5 | 11.3 | 11 | 10.8 | 10.6 | 10.6 | 10.5 | 0
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 24.6 | 23.9 | 24 | 23.8 | 23.5 | 23.6 | 23.4 | 22.8 | 21.7 | 19 | 18.1 | 17.3 | 16.6 | 16.3 | 16.1 | 15.9 | 15.8 | 14.5 | 13
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 24.6 | 23.7 | 22.9 | 22.3 | 20.4 | 16.8 | 14.2 | 11.8 | 9.4 | 7.4 | 5.7 | 4.2 | 3.6 | 2.8 | 2.3 | 1.7 | 1.2 | 0 | 0
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 24.6 | 23.6 | 22.7 | 21 | 18 | 16.6 | 14 | 11.3 | 8.8 | 6.8 | 4.9 | 4.3 | 3.8 | 3.3 | 2.9 | 2.5 | 2 | 0 | 0
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 24.6 | 23.8 | 23 | 22.4 | 20.7 | 17.5 | 14.3 | 11.9 | 9.5 | 7.4 | 5.7 | 4.5 | 4.1 | 3.8 | 3.5 | 3.2 | 2.9 | 0 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.8 | 6.6 | 6 | 4.4 | 3.3 | 2.6 | 2.2 | 1.8 | 1.3 | 0.9 | 0 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.6 | 6.4 | 5.6 | 3.6 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.9 | 6.9 | 6.9 | 6.9 | 6.8 | 6.6 | 6.3 | 5.3 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.7 | 6.2 | 5.3 | 3.3 | 1.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.4 | 4.8 | 4.7 | 4.6 | 4.4 | 4.3 | 4 | 3.6 | 2.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.4 | 4.7 | 4.4 | 4 | 3.1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.4 | 4.6 | 4.2 | 3.4 | 2.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.4 | 4.8 | 4.5 | 4.2 | 3.4 | 2.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.5 | 7.5 | 7.4 | 7.3 | 7.3 | 7.2 | 7 | 6.9 | 6.5 | 5.9 | 4.3 | 3.2 | 2.6 | 2.2 | 1.7 | 1.3 | 0.9 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.5 | 7.4 | 7.2 | 7.1 | 6.9 | 6.8 | 6.5 | 6.3 | 5.5 | 3.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.5 | 7.3 | 7.1 | 6.9 | 6.7 | 6.5 | 6.2 | 5.2 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.5 | 7.4 | 7.3 | 7.2 | 7.1 | 7 | 6.8 | 6.6 | 6.1 | 5.2 | 3.2 | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.7 | 20.7 | 20.8 | 20.7 | 20.7 | 20.7 | 20.6 | 20.3 | 20 | 19.6 | 19.4 | 19.3 | 19.3 | 19.2 | 19.1 | 19.1 | 19.1 | 18.8 | 18.4
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.7 | 20.7 | 20.3 | 19.8 | 19.1 | 18 | 17.5 | 17.5 | 14.8 | 14.7 | 14.5 | 14.4 | 14.2 | 14 | 13.9 | 13.8 | 13.6 | 0 | 0
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.7 | 20.7 | 20.3 | 19 | 18.1 | 17.7 | 17.6 | 17.5 | 14.8 | 14.7 | 14.5 | 14.4 | 14.3 | 14.1 | 14 | 13.9 | 13.8 | 0 | 0
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.7 | 20.7 | 20.3 | 19.8 | 19.2 | 18.2 | 17.5 | 17.5 | 14.8 | 14.7 | 14.6 | 14.6 | 14.5 | 14.4 | 14.4 | 14.3 | 14.3 | 13.7 | 0
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.6 | 19.5 | 19.3 | 19.1 | 18.9 | 18.6 | 18.4 | 18 | 17.6 | 14.6 | 14.5 | 14.5 | 14.5 | 14.5 | 14.4 | 14.4 | 14.4 | 14.2 | 13.8
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.6 | 19.3 | 18.8 | 18.3 | 17.8 | 14.9 | 13.8 | 12.6 | 11.5 | 11.1 | 10.9 | 10.7 | 10.5 | 10.3 | 10.1 | 10 | 9.7 | 8.4 | 6.9
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.6 | 19.2 | 18.6 | 18.1 | 17.5 | 14.4 | 13.3 | 11.9 | 10.7 | 10.2 | 10 | 9.8 | 9.7 | 9.5 | 9.3 | 9.1 | 8.8 | 7.2 | 5.6
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.6 | 19.4 | 19 | 18.5 | 17.9 | 14.6 | 14.1 | 13 | 11.9 | 11.5 | 11.4 | 11.3 | 11.3 | 11.3 | 11.3 | 11.2 | 11.1 | 10.1 | 9
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.5 | 16.5 | 16.5 | 16.4 | 16.3 | 16.2 | 15 | 15 | 14.9 | 14.8 | 14.6 | 14.4 | 14.3 | 14.1 | 13.7 | 12.7 | 11.8 | 11 | 10.2
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.5 | 16.5 | 16.4 | 16.3 | 15.9 | 15.1 | 15 | 14.9 | 14.6 | 14.2 | 12.9 | 10.8 | 9.8 | 8.9 | 8.1 | 7.7 | 7.4 | 5.1 | 3.8
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.5 | 16.5 | 16.3 | 16.2 | 15.1 | 15 | 14.8 | 14.4 | 13.7 | 12.4 | 9.9 | 9.2 | 8.5 | 8 | 7.6 | 7.3 | 6.9 | 5.1 | 4.3
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.5 | 16.5 | 16.4 | 16.3 | 16.3 | 15.1 | 15 | 15 | 14.8 | 14.4 | 13.5 | 11.7 | 10.5 | 9.8 | 9.4 | 9.2 | 9 | 7.6 | 6.3
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.8 | 8.8 | 8.7 | 8.7 | 8.7 | 8.7 | 8.6 | 8.5 | 8.4 | 7.8 | 7.7 | 7.5 | 7.5 | 7.4 | 7.3 | 7.2 | 7.1 | 6.5 | 5.8
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.8 | 8.7 | 8.7 | 8.6 | 8.6 | 8.5 | 8.4 | 7.8 | 7.6 | 7.3 | 6.9 | 6.5 | 6.1 | 5.7 | 5.4 | 5 | 4.6 | 2.4 | 1.4
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.8 | 8.7 | 8.6 | 8.6 | 8.5 | 8.5 | 8.3 | 7.7 | 7.4 | 7.1 | 6.7 | 6.3 | 6 | 5.7 | 5.4 | 5.1 | 4.8 | 3 | 2.2
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.8 | 8.7 | 8.7 | 8.7 | 8.6 | 8.6 | 8.5 | 8.4 | 7.8 | 7.7 | 7.5 | 7.3 | 7.1 | 7 | 6.8 | 6.6 | 6.4 | 5.1 | 4
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.1 | 17.1 | 17 | 17 | 16.9 | 16.9 | 16.8 | 16.7 | 15.6 | 15.5 | 15.1 | 15 | 15 | 15 | 15 | 14.5 | 13.8 | 13.2 | 11.3
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.1 | 17 | 16.8 | 16.7 | 15.7 | 15.6 | 15.1 | 14.9 | 14.4 | 13.9 | 12.4 | 10.6 | 10.2 | 9.7 | 8.6 | 7.1 | 5.6 | 0 | 0
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.1 | 16.9 | 16.8 | 16.7 | 15.6 | 15.2 | 14.9 | 14.4 | 13.6 | 11.9 | 9.4 | 9.1 | 8.8 | 5.8 | 4.5 | 3.3 | 1.9 | 0 | 0
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.1 | 17 | 16.9 | 16.8 | 16.7 | 15.6 | 15.5 | 15.1 | 14.8 | 14.4 | 13.6 | 12.1 | 11.3 | 11.1 | 11 | 10.9 | 10.7 | 6.2 | 0
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.5 | 17.5 | 17.3 | 17.1 | 16.9 | 16.8 | 16.6 | 16.5 | 16.3 | 16.1 | 16 | 16 | 14.3 | 16 | 16 | 14.2 | 10.7 | 10.5 | 9.9
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.5 | 17.2 | 16.9 | 16.5 | 16.3 | 16 | 15.9 | 14.3 | 14.1 | 10.8 | 10.5 | 9.9 | 9.3 | 9.3 | 8.7 | 8 | 7.1 | 3.6 | 0
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.5 | 17.1 | 16.6 | 16.2 | 15.9 | 14.4 | 11.1 | 10.9 | 10.6 | 10 | 8.8 | 8.2 | 7.5 | 7.7 | 6.9 | 5.9 | 5.2 | 0 | 0
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.5 | 17.5 | 17.1 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 14.3 | 14.2 | 10.7 | 10.6 | 10.3 | 10.3 | 10.1 | 9.8 | 9.4 | 7.8 | 5.1
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2 | 1.9 | 1.8 | 1.6 | 1.4 | 1.3 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2 | 1.7 | 1.3 | 0.9 | 0.5 | 0 | 16 | 15.8 | 15.4 | 14.9 | 13.8 | 12.5 | 11.3 | 10.1 | 9.2 | 8.4 | 7.5 | 1.8 | 0
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2 | 1.6 | 1 | 0.6 | 0 | 0 | 15.9 | 15.4 | 14.4 | 13.2 | 11.6 | 10.6 | 8.3 | 7.2 | 6.5 | 5.8 | 5 | 0.7 | 0
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2 | 1.8 | 1.5 | 1.3 | 1 | 0.7 | 16 | 15.9 | 15.6 | 15.2 | 14.7 | 13.9 | 13.2 | 12.5 | 12.1 | 11.6 | 11.1 | 6.8 | 2.9
Grendon 132kV | Hayfield | Primary Substation | 11 | Counterfactual | Headroom (MW) | 37 | 37 | 36.9 | 36.9 | 36.8 | 36.6 | 36.5 | 36.4 | 35.4 | 35.3 | 35.1 | 34.9 | 34.6 | 34.3 | 34 | 33.7 | 33.5 | 32.1 | 32.1
Grendon 132kV | Hayfield | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 37 | 37 | 36.9 | 36.7 | 36.4 | 35.4 | 35 | 34.6 | 34.1 | 33.5 | 33 | 32.5 | 32 | 31.4 | 30.9 | 30.4 | 29.8 | 27.4 | 27.4
Grendon 132kV | Hayfield | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 37 | 37 | 36.9 | 36.7 | 36.4 | 35.4 | 35 | 34.6 | 34.1 | 33.5 | 33 | 32.5 | 31.9 | 31.4 | 30.9 | 30.4 | 29.8 | 27.4 | 27.4
Grendon 132kV | Hayfield | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 37 | 37 | 36.9 | 36.7 | 36.4 | 35.4 | 35 | 34.6 | 34.1 | 33.5 | 33 | 32.5 | 32 | 31.4 | 30.9 | 30.4 | 29.9 | 27.4 | 27.4
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 27.7 | 27.5 | 27.4 | 27.3 | 27.1 | 27.1 | 26.9 | 26.8 | 26.5 | 26.2 | 25.9 | 25.7 | 25.5 | 25.4 | 25.3 | 25.2 | 25.2 | 21.5 | 20.8
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 27.7 | 27.3 | 26.9 | 26.7 | 26.5 | 26.3 | 26.1 | 26 | 25.7 | 25.3 | 25 | 21.5 | 21.2 | 20.9 | 18.6 | 16.3 | 13.9 | 1.1 | 0
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 27.7 | 27.2 | 26.6 | 26.4 | 26 | 25.8 | 25.4 | 24.9 | 21.5 | 21.2 | 20.8 | 20.5 | 20.2 | 18.9 | 17 | 14.9 | 12.7 | 1 | 0
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 27.7 | 27.5 | 27.1 | 27 | 26.9 | 26.7 | 26.5 | 26.3 | 25.9 | 25.5 | 25.1 | 25 | 25 | 21.5 | 21.5 | 21.5 | 21.4 | 11 | 1.4
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.9 | 9.5 | 9.5 | 9.3 | 9.1 | 8.9 | 8.7 | 8.5 | 7.9 | 7 | 6 | 5.3 | 4.9 | 4.6 | 3.8 | 3.3 | 3 | 0.6 | 0
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.9 | 9.3 | 8.6 | 8.3 | 8 | 7.8 | 7.4 | 7 | 5.9 | 4.6 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.9 | 9.3 | 8.5 | 8.1 | 7.8 | 7.2 | 6.8 | 5.5 | 3.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.9 | 9.4 | 8.8 | 8.6 | 8.3 | 8.2 | 7.9 | 7.6 | 6.8 | 5.9 | 3.4 | 2.5 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 21.7 | 21.7 | 21.5 | 21.4 | 21.3 | 21.2 | 21.1 | 21 | 20.7 | 20.2 | 19.5 | 18.2 | 16.9 | 16.8 | 16.7 | 15.7 | 14.4 | 13.2 | 12
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 21.7 | 21.5 | 21.3 | 21.1 | 20.9 | 20.8 | 20.2 | 19.3 | 17.7 | 16.2 | 13.8 | 10.4 | 8.8 | 8.2 | 7.6 | 7 | 6.4 | 4 | 1.8
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 21.7 | 21.4 | 21 | 20.6 | 20 | 19.3 | 17.9 | 16.6 | 15.2 | 13.1 | 9.6 | 8.2 | 7.5 | 7 | 6.5 | 5.9 | 5.5 | 3.1 | 1.4
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 21.7 | 21.6 | 21.4 | 21.1 | 21 | 20.6 | 19.9 | 19.1 | 17.8 | 16.6 | 15 | 12.7 | 11 | 10.6 | 10.2 | 9.8 | 9.3 | 7.2 | 5.1
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.6 | 17.3 | 17.3 | 17.2 | 17.2 | 17.2 | 17.1 | 17.1 | 17.1 | 17 | 16.9 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.7 | 15.5
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.6 | 17.3 | 17.2 | 17.2 | 17.1 | 17.1 | 17.1 | 17 | 17 | 16.9 | 16.8 | 16.7 | 16.7 | 15.7 | 15.5 | 15.5 | 15.5 | 15.1 | 14.5
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.6 | 17.3 | 17.2 | 17.1 | 17.1 | 17 | 17 | 16.9 | 16.7 | 16.7 | 15.7 | 15.5 | 15.5 | 15.5 | 15.4 | 15.4 | 15.3 | 14.9 | 14.5
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.6 | 17.3 | 17.3 | 17.2 | 17.2 | 17.2 | 17.1 | 17.1 | 17 | 16.9 | 16.8 | 16.8 | 16.8 | 16.7 | 16.7 | 16.7 | 16.7 | 15.5 | 15.2
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18 | 10.7 | 10.6 | 10.5 | 10.4 | 10.3 | 10.2 | 10 | 9.3 | 8.2 | 6.9 | 5.9 | 5.4 | 5 | 4.7 | 4.2 | 3.7 | 0.9 | 0
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18 | 10.6 | 10.4 | 10.3 | 10.1 | 10 | 9.6 | 9.1 | 7.8 | 6.3 | 4.4 | 2.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18 | 10.5 | 10.2 | 10 | 9.8 | 9.5 | 9 | 7.6 | 5.4 | 3.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18 | 10.6 | 10.5 | 10.4 | 10.3 | 10.1 | 9.8 | 9.5 | 8.5 | 7.4 | 5.7 | 4.4 | 3.3 | 2.5 | 2 | 1.5 | 0.9 | 0 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.3 | 19 | 18.4 | 18.2 | 18 | 17.8 | 17.6 | 17.3 | 16.9 | 16.5 | 15.8 | 15.3 | 15 | 14.7 | 14.5 | 14.1 | 13.9 | 12.5 | 11
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.3 | 18.8 | 17.9 | 17.3 | 16.8 | 16.2 | 15.3 | 14.7 | 13.9 | 13 | 12 | 11 | 10.1 | 9.1 | 8.4 | 7.6 | 6.8 | 3.2 | 0
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.3 | 18.7 | 18.2 | 17.3 | 16.6 | 15.7 | 14.9 | 13.9 | 12.7 | 11.8 | 10.7 | 9.6 | 8.9 | 8.2 | 7.6 | 6.7 | 6.1 | 2.4 | 0
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.3 | 18.9 | 18.1 | 17.5 | 17 | 16.5 | 15.9 | 15 | 14.4 | 13.8 | 13 | 12.5 | 12 | 11.6 | 11.2 | 10.7 | 10.1 | 7.1 | 4.6
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.5 | 1.4 | 1.2 | 1 | 0.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.5 | 1.1 | 0.6 | 0 | 0 | 0 | 4.4 | 4.3 | 4.1 | 3.8 | 3.5 | 3.2 | 2.9 | 2.7 | 2.5 | 2.2 | 2 | 0.7 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 3.9 | 3.6 | 3.2 | 2.9 | 2.5 | 2.3 | 2.1 | 1.9 | 1.7 | 1.5 | 1.2 | 0 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.5 | 1.2 | 0.9 | 0.6 | 0 | 0 | 4.6 | 4.5 | 4.3 | 4.1 | 3.8 | 3.7 | 3.6 | 3.5 | 3.4 | 3.3 | 3.2 | 2.3 | 1.1
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.4 | 15.4 | 15.2 | 15.2 | 15.1 | 15 | 14.3 | 12.1 | 11.9 | 11.3 | 10.2 | 9.4 | 8.9 | 8.5 | 8 | 7.6 | 7.2 | 4.4 | 1.2
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.4 | 15.3 | 15 | 14.8 | 14.7 | 14.5 | 12.2 | 12 | 11.1 | 9.5 | 7.6 | 5.7 | 4 | 2.2 | 1 | 0 | 0 | 0 | 0
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.4 | 15.2 | 14.8 | 14.6 | 14.4 | 14.3 | 12 | 10.9 | 8.8 | 7 | 4.8 | 3.3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.4 | 15.3 | 15.2 | 15 | 14.9 | 14.7 | 14.4 | 14.3 | 11.8 | 10.8 | 9.3 | 8.1 | 7.1 | 6.2 | 5.6 | 5 | 4.3 | 0 | 0
Grendon 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.3 | 10.3 | 10.3 | 10.1 | 10.1 | 10.1 | 10 | 9.8 | 9.8 | 9.6 | 9.4 | 9.2 | 9.1 | 9 | 8.9 | 8.8 | 8.7 | 8.1 | 7.4
Grendon 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.3 | 10.3 | 10.1 | 10 | 10 | 10 | 9.8 | 9.8 | 9.6 | 9.2 | 8.8 | 8.4 | 8.1 | 7.7 | 7.4 | 7.2 | 6.9 | 5.2 | 4.1
Grendon 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.3 | 10.3 | 10 | 10 | 9.8 | 9.8 | 9.8 | 9.6 | 9.1 | 8.8 | 8.4 | 8 | 7.7 | 7.4 | 7.2 | 7 | 6.8 | 5.4 | 4.9
Grendon 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.3 | 10.3 | 10.1 | 10.1 | 10 | 10 | 9.8 | 9.8 | 9.7 | 9.5 | 9.2 | 8.9 | 8.7 | 8.5 | 8.4 | 8.3 | 8.1 | 7.1 | 6
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.5 | 18.3 | 18.2 | 18.1 | 18.1 | 14.3 | 14.1 | 13.9 | 12.8 | 11.1 | 8.8 | 7.1 | 6 | 5.1 | 2.3 | 0.7 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.5 | 18.2 | 18 | 14.1 | 6.4 | 5.7 | 4.2 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.5 | 18.1 | 14.4 | 14 | 13.6 | 11.4 | 9.7 | 6.7 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.5 | 18.3 | 18 | 14.3 | 14.1 | 13.8 | 12.8 | 11.7 | 9.6 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 31.8 | 31.8 | 31.8 | 31.7 | 31.6 | 31.6 | 31.6 | 31.5 | 31.3 | 30.8 | 30.6 | 30.5 | 30.5 | 30.5 | 30.4 | 30.4 | 30.4 | 30.1 | 29.6
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 31.8 | 31.8 | 31.8 | 31.7 | 31.3 | 30.6 | 29.8 | 29.5 | 29.3 | 29.1 | 28.8 | 28.7 | 28.5 | 28.3 | 28.1 | 27.9 | 27.8 | 26.6 | 25.5
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 31.8 | 31.8 | 31.7 | 31.4 | 30.6 | 29.9 | 29.5 | 29.2 | 28.8 | 28.5 | 28.3 | 28.1 | 28 | 27.8 | 27.7 | 27.6 | 26.9 | 25.8 | 26.1
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 31.8 | 31.8 | 31.8 | 31.7 | 31.6 | 30.9 | 30.1 | 29.7 | 29.5 | 29.3 | 29.1 | 29.1 | 29 | 29 | 28.9 | 28.8 | 28.7 | 28 | 26.9
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.8 | 5.8 | 5.7 | 5.7 | 5.6 | 5.6 | 5.5 | 5.4 | 5.4 | 5.3 | 5.3 | 5.2 | 5.2 | 5.2 | 5.3 | 5.2 | 5 | 4.6
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.7 | 5.6 | 5.5 | 5.4 | 5.3 | 5.2 | 5.2 | 5.1 | 5.1 | 5 | 4.9 | 4.7 | 4.6 | 4.5 | 4.4 | 4.3 | 3.5 | 2.6
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.6 | 5.5 | 5.3 | 5.1 | 5 | 4.9 | 4.7 | 4.6 | 4.4 | 4.3 | 4.2 | 4.1 | 4 | 3.9 | 3.8 | 3.6 | 2.7 | 1.7
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.8 | 5.7 | 5.6 | 5.5 | 5.4 | 5.4 | 5.3 | 5.3 | 5.2 | 5.2 | 5.2 | 5.2 | 5.1 | 5.1 | 5.1 | 5 | 4.5 | 3.8
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 23.5 | 23.5 | 23.5 | 23.5 | 23.4 | 23.4 | 23.4 | 23.3 | 23.3 | 23.3 | 23.3 | 23.4 | 23 | 22.8 | 22.5 | 22.5 | 22.6 | 22.6 | 22.2
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 23.5 | 23.5 | 23.3 | 23.1 | 22.9 | 22.8 | 22.6 | 22.3 | 22 | 21.3 | 21 | 20.8 | 20.6 | 20.5 | 20.4 | 20.4 | 20.4 | 17.1 | 16.4
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 23.5 | 23.5 | 23.1 | 22.9 | 22.6 | 22.4 | 22 | 21.5 | 21 | 20.6 | 20.5 | 20.4 | 20.4 | 17.2 | 17.2 | 17.2 | 17.1 | 16.4 | 15.4
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 23.5 | 23.5 | 23.5 | 23.3 | 23.2 | 23 | 22.9 | 22.6 | 22.3 | 21.7 | 21.3 | 21.1 | 21 | 20.9 | 20.8 | 20.8 | 20.7 | 20.4 | 17.2
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19 | 19 | 18.9 | 18.7 | 18.5 | 18.4 | 18 | 17.7 | 17 | 15.9 | 14.9 | 14.2 | 13.7 | 13.3 | 12.9 | 12.3 | 11.8 | 9 | 6
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19 | 18.9 | 18.3 | 18.1 | 17.8 | 17.5 | 16.9 | 16.4 | 15.1 | 13.6 | 11.5 | 9.3 | 7.8 | 6.3 | 5.1 | 3.9 | 2.6 | 0 | 0
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19 | 18.8 | 18.1 | 17.7 | 17.4 | 17 | 16.4 | 14.9 | 12.9 | 11.1 | 8.7 | 7.4 | 6.2 | 4.9 | 3.9 | 2.9 | 1.8 | 0 | 0
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19 | 18.9 | 18.5 | 18.3 | 18.1 | 17.8 | 17.4 | 17 | 15.9 | 14.9 | 13.2 | 11.9 | 10.9 | 10.2 | 9.7 | 9 | 8.3 | 3.4 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.3 | 17.3 | 17.2 | 17.2 | 17.2 | 17.1 | 17.1 | 17 | 16.9 | 16.8 | 16.6 | 16.6 | 15.5 | 15.5 | 15.4 | 15.2 | 15 | 13.5 | 11.9
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.3 | 17.2 | 17.1 | 17.1 | 17 | 16.8 | 16.7 | 16.6 | 15.8 | 15.5 | 15.2 | 14.8 | 14.2 | 13.6 | 13.1 | 12.5 | 11.9 | 0 | 0
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.3 | 17.2 | 17.1 | 16.9 | 16.8 | 16.7 | 16.6 | 15.4 | 15 | 14.5 | 13.9 | 13.4 | 12.9 | 12.4 | 11.9 | 11.4 | 10.9 | 0 | 0
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.3 | 17.3 | 17.2 | 17.2 | 17.1 | 16.9 | 16.8 | 16.7 | 16.6 | 15.5 | 15.1 | 14.7 | 14.3 | 13.8 | 13.4 | 12.9 | 12.4 | 10.2 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.7 | 8.5 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 7.8 | 7.6 | 7 | 5.9 | 5.3 | 4.8 | 4.6 | 3.8 | 3.3 | 3 | 0.5 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.7 | 8.5 | 8.4 | 8.2 | 7.8 | 7.7 | 7.3 | 6.9 | 5.8 | 4.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.7 | 8.4 | 8.4 | 7.8 | 7.7 | 7.2 | 6.7 | 5.5 | 3.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.7 | 8.5 | 8.4 | 8.4 | 7.8 | 7.8 | 7.7 | 7.5 | 6.7 | 5.9 | 3.4 | 2.4 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.8 | 5.7 | 5.6 | 5.5 | 5.4 | 5.1 | 4.9 | 3.8 | 2.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.7 | 5.4 | 5.2 | 5.1 | 4.9 | 4.4 | 3.8 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.6 | 5.2 | 5 | 4.7 | 4.5 | 3.9 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.8 | 5.6 | 5.5 | 5.4 | 5.3 | 4.9 | 4.6 | 3.3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.8 | 9.6 | 9.5 | 9.5 | 9.4 | 9.3 | 9.1 | 8.7 | 8.2 | 7.5 | 6.6 | 5.9 | 5.4 | 5.2 | 4.4 | 4 | 3.3 | 1 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.8 | 9.5 | 9.4 | 9.2 | 9.2 | 9.2 | 8.6 | 7.8 | 6.8 | 5.5 | 4 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.8 | 9.5 | 9.2 | 9 | 8.9 | 8.7 | 8.2 | 6.7 | 5 | 3.5 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.8 | 9.6 | 9.5 | 9.4 | 9.3 | 9.3 | 9.1 | 8.5 | 7.8 | 7 | 5.8 | 4.9 | 4.1 | 3.3 | 2.3 | 1.8 | 0 | 0 | 0
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 7 | 7 | 6.9 | 6.6 | 6.5 | 6.3 | 6 | 5.4 | 4.6 | 4.4 | 4.2 | 4.2 | 4.1 | 4.1 | 4 | 4 | 3.5 | 2.8
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 6.9 | 6.5 | 6 | 5 | 3.7 | 2.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 6.8 | 6.4 | 5.6 | 4.6 | 3.5 | 2.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 7 | 6.6 | 6.1 | 5.2 | 3.9 | 2.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.7 | 9.7 | 9.6 | 9.6 | 9.5 | 9.4 | 9.4 | 9.3 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.7 | 9.7 | 9.5 | 9.4 | 9.3 | 9.2 | 9 | 8.9 | 8.8 | 8.7 | 8.7 | 8.7 | 8.7 | 8.6 | 8.6 | 8.4 | 8.6 | 8.3 | 8.2
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.7 | 9.7 | 9.5 | 9.4 | 9.3 | 9.2 | 9 | 8.9 | 8.8 | 8.7 | 8.3 | 8.4 | 8.4 | 8.3 | 7.9 | 7.9 | 7.8 | 7.7 | 7.8
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.7 | 9.7 | 9.5 | 9.4 | 9.3 | 9.2 | 9 | 8.9 | 8.8 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.6 | 8.4 | 8.6 | 8.3 | 8.3
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.8 | 9.4 | 9.4 | 9.4 | 7.7 | 7.6 | 7.6 | 7.6 | 7.4 | 7.1 | 6.6 | 6.4 | 6.2 | 7 | 7 | 6.9 | 6.8 | 5.7 | 4.4
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.8 | 9.3 | 7.7 | 7.7 | 7.6 | 7.5 | 7.3 | 7.4 | 7 | 6.4 | 5.7 | 5 | 4.4 | 4.8 | 4.7 | 3.9 | 3.3 | 0 | 0
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.8 | 9.3 | 7.7 | 7.7 | 7.5 | 7.4 | 7.1 | 6.7 | 6 | 5.3 | 4.5 | 4.2 | 3.6 | 4 | 4 | 3.2 | 2.6 | 0 | 0
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.8 | 9.4 | 9.4 | 7.7 | 7.7 | 7.6 | 7.5 | 7.4 | 7.1 | 6.7 | 6.1 | 5.8 | 5.4 | 6.1 | 6.1 | 5.7 | 5.4 | 3.2 | 1
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.7 | 12 | 12 | 11.9 | 11.8 | 11.7 | 11.5 | 11.4 | 11.2 | 11 | 10.8 | 10.6 | 10.5 | 10.4 | 4.4 | 4.4 | 4.3 | 3.7 | 3
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.7 | 12 | 11.8 | 11.6 | 11.4 | 11.2 | 10.9 | 10.6 | 10.3 | 10 | 9.5 | 9.1 | 8.7 | 8.3 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.7 | 11.9 | 11.7 | 11.5 | 11.3 | 11 | 10.7 | 10.2 | 9.7 | 9.3 | 8.9 | 8.6 | 8.2 | 7.9 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.7 | 12 | 11.9 | 11.7 | 11.6 | 11.4 | 11.1 | 10.8 | 10.6 | 10.3 | 10 | 9.7 | 9.5 | 9.3 | 3.3 | 3.1 | 2.9 | 1.7 | 0.6
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.3 | 3.2 | 3.2 | 3.1 | 3.1 | 3.1 | 3 | 2.9 | 2.6 | 2.2 | 1.7 | 1.3 | 1.1 | 1 | 0.8 | 0.7 | 0 | 0 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.3 | 3.2 | 3.1 | 3 | 2.9 | 2.9 | 2.7 | 2.5 | 2.1 | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.3 | 3.1 | 3 | 2.9 | 2.8 | 2.7 | 2.5 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.3 | 3.2 | 3.1 | 3.1 | 3 | 3 | 2.9 | 2.8 | 2.4 | 2 | 1.3 | 0.9 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.1 | 6.2 | 6.2 | 6.4 | 6.5 | 6.2 | 6.2 | 6.2 | 6.2 | 5.9 | 5.4 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 4.7 | 3.9
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.1 | 6 | 5.8 | 5.6 | 5.2 | 4.8 | 4.2 | 3.5 | 2.7 | 2.5 | 2.2 | 1.9 | 1.7 | 1.4 | 1.1 | 0.8 | 0 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.1 | 5.8 | 5.4 | 5 | 4.4 | 3.8 | 2.9 | 2.2 | 1.6 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.1 | 6.1 | 5.9 | 5.8 | 5.3 | 4.9 | 4.2 | 3.6 | 3.1 | 2.9 | 2.6 | 2.6 | 2.6 | 2.6 | 2.5 | 2.5 | 0 | 0 | 0
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.8 | 0.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 11.6 | 11.1 | 10.5 | 9.8 | 9 | 8.2 | 7.6 | 7 | 6.4 | 6 | 5.5 | 1.4 | 0
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 11.2 | 10.6 | 9.9 | 9.5 | 9 | 8.6 | 8.2 | 7.7 | 7.3 | 6.9 | 6.4 | 1.6 | 0
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 12.1 | 11.8 | 11.3 | 10.8 | 10.2 | 9.9 | 9.6 | 9.3 | 9 | 8.7 | 8.5 | 6.7 | 4.7
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.1 | 14.4 | 14.3 | 14.2 | 14.2 | 14.1 | 14 | 13.9 | 13.4 | 12.7 | 11.9 | 11.3 | 11 | 10.8 | 10.6 | 10.4 | 10.1 | 8.2 | 6.2
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.1 | 14.3 | 14.2 | 14.1 | 14 | 13.9 | 13.7 | 13.6 | 12.9 | 11.9 | 10.8 | 9.7 | 8.7 | 6.8 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.1 | 14.3 | 14.1 | 13.9 | 13.8 | 13.6 | 13.4 | 12.5 | 9.3 | 8.2 | 6.9 | 6 | 5.1 | 4.2 | 2.8 | 1.4 | 0 | 0 | 0
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.1 | 14.4 | 14.3 | 14.2 | 14.1 | 14 | 13.9 | 13.8 | 13.2 | 12.5 | 11.4 | 10.7 | 10.1 | 8.8 | 8.5 | 8.1 | 7.7 | 4.5 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.2 | 6.2 | 6.1 | 6.1 | 6 | 6 | 5.8 | 5.6 | 5 | 4.2 | 3.2 | 2.5 | 2.1 | 1.8 | 1.5 | 1.2 | 0.9 | 0 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.2 | 6.1 | 6 | 5.9 | 5.8 | 5.7 | 5.3 | 4.9 | 3.9 | 2.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.2 | 6.1 | 5.9 | 5.8 | 5.6 | 5.5 | 5.1 | 4.1 | 2.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.2 | 6.2 | 6.1 | 6 | 5.9 | 5.8 | 5.6 | 5.3 | 4.6 | 3.8 | 2.6 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.8 | 20.7 | 20.6 | 20.5 | 20.4 | 20.3 | 20.3 | 20.2 | 20.2 | 20.1 | 20.1 | 20.1 | 20.1 | 20.1 | 20.1 | 20.1 | 20.2 | 19.9 | 19.6
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.8 | 20.5 | 20.3 | 20.2 | 20.1 | 20 | 19.9 | 19.9 | 19.8 | 19.8 | 19.7 | 19.7 | 19.6 | 19.5 | 19.5 | 19.4 | 19.4 | 16.9 | 16
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.8 | 20.4 | 20.1 | 19.9 | 19.8 | 19.6 | 19.5 | 19.4 | 19.4 | 19.4 | 17.3 | 17.3 | 17.3 | 17.2 | 17.2 | 17.1 | 17 | 16 | 14.6
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.8 | 20.6 | 20.5 | 20.4 | 20.3 | 20.2 | 20.1 | 20.1 | 20 | 20 | 20 | 20 | 20 | 20 | 20.1 | 20 | 19.9 | 19.5 | 17.2
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.7 | 18.6 | 18.5 | 18.3 | 18.1 | 17.9 | 17.6 | 17.5 | 17.3 | 17.2 | 17.2 | 14.7 | 14.6 | 14.6 | 14.6 | 14.6 | 14.6 | 14.2 | 13.5
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.7 | 18.5 | 18 | 17.6 | 17.2 | 14.8 | 14.5 | 14.3 | 14 | 13.5 | 13.2 | 12.8 | 12.4 | 12 | 11.7 | 11.4 | 11.1 | 9.1 | 7.2
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.7 | 18.4 | 17.9 | 17.4 | 17.1 | 14.7 | 14.2 | 13.7 | 13 | 12.5 | 12 | 11.7 | 11.4 | 11.1 | 10.8 | 10.6 | 10.2 | 8.3 | 6.8
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.7 | 18.6 | 18.1 | 17.7 | 17.3 | 17.1 | 14.6 | 14.5 | 14.2 | 13.9 | 13.6 | 13.4 | 13.3 | 13.2 | 13.1 | 12.9 | 12.8 | 11.5 | 9.9
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.7 | 16.7 | 16.6 | 16.5 | 14.4 | 14.3 | 14.1 | 14 | 13.9 | 13.7 | 13.6 | 13.6 | 13.6 | 13.6 | 13.7 | 13.7 | 13.7 | 13.4 | 12.9
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.7 | 16.6 | 16.3 | 14.2 | 13.9 | 13.6 | 13.4 | 13.3 | 13.2 | 13.1 | 13 | 12.9 | 12.8 | 12.6 | 12.5 | 12.3 | 12.2 | 6.7 | 0
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.7 | 16.5 | 14.1 | 13.8 | 13.5 | 13.2 | 12.9 | 12.7 | 12.5 | 12.3 | 12.1 | 12 | 11.9 | 11.8 | 11.7 | 11.3 | 9.5 | 0 | 0
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.7 | 16.7 | 16.5 | 14.4 | 14.2 | 14 | 13.8 | 13.6 | 13.5 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.3 | 13.2 | 12.5 | 9.7
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.7 | 15.5 | 15.4 | 15.3 | 15.2 | 15.1 | 14.8 | 14.5 | 14 | 13.2 | 12.3 | 11.2 | 10.2 | 9.4 | 8.7 | 8.2 | 8 | 6.2 | 4.4
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.7 | 15.4 | 15.1 | 14.9 | 14.6 | 14.4 | 13.8 | 12.4 | 10.6 | 8 | 6.3 | 4.6 | 2.9 | 1.3 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.7 | 15.3 | 14.9 | 14.5 | 14.1 | 13.7 | 12.6 | 10.5 | 7.9 | 5.9 | 4 | 2.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.7 | 15.5 | 15.2 | 15 | 14.8 | 14.5 | 14 | 13 | 11.5 | 9.2 | 7.4 | 6.3 | 5.2 | 4.3 | 3.5 | 2.7 | 2.2 | 0 | 0
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 32.8 | 32.9 | 32.8 | 32.7 | 32.7 | 32.6 | 32.6 | 32.5 | 32.5 | 32.4 | 32.4 | 32.2 | 32.1 | 31.9 | 31.6 | 31.5 | 31.5 | 31 | 30.4
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 32.8 | 32.9 | 32.8 | 32.7 | 32.5 | 32.3 | 32.2 | 32 | 31.9 | 31.5 | 31 | 30.5 | 30.2 | 30.1 | 29.9 | 29.7 | 29.6 | 25.4 | 24.7
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 32.8 | 32.8 | 32.5 | 32.3 | 32 | 31.7 | 31.4 | 30.9 | 30.4 | 30 | 29.9 | 29.8 | 29.7 | 29.6 | 29.4 | 29.3 | 29.2 | 25 | 23.6
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 32.8 | 32.9 | 32.8 | 32.7 | 32.7 | 32.6 | 32.6 | 32.3 | 32 | 31.5 | 31 | 31 | 30.9 | 30.9 | 30.8 | 30.7 | 30.5 | 29.7 | 29.1
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 29.3 | 29.3 | 29.3 | 29.2 | 29.1 | 28.9 | 28.7 | 28.5 | 28.4 | 28.4 | 28.3 | 28 | 27.7 | 27.4 | 27.2 | 27.2 | 27.2 | 27.1 | 26.9
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 29.3 | 29.3 | 29.3 | 28.9 | 28.5 | 28.1 | 27.7 | 26.9 | 26.3 | 25.5 | 25.3 | 25.3 | 25.3 | 25.3 | 22.4 | 22.4 | 22.4 | 0 | 0
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 29.3 | 29.3 | 29 | 28.7 | 28.3 | 27.8 | 26.7 | 25.9 | 25.3 | 22.5 | 22.4 | 22.4 | 22.4 | 22.4 | 22.4 | 17.6 | 10.2 | 0 | 0
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 29.3 | 29.3 | 29.3 | 29.1 | 28.6 | 28.3 | 27.9 | 27.2 | 26.7 | 25.8 | 25.5 | 25.5 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.3 | 11.1
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.1 | 9.9 | 9.9 | 9.8 | 9.8 | 9.7 | 9.6 | 9.6 | 9.5 | 9.4 | 9.2 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 8.8 | 8.3
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.1 | 9.8 | 9.7 | 9.5 | 9.4 | 9.2 | 9.1 | 8.9 | 8.6 | 8.6 | 8.5 | 8.3 | 8.2 | 8 | 7.9 | 7.8 | 7.7 | 6.8 | 5.8
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.1 | 9.7 | 9.5 | 9.2 | 9 | 8.6 | 8.4 | 8.2 | 8.1 | 7.9 | 7.7 | 7.6 | 7.5 | 7.4 | 7.3 | 7.2 | 7 | 5.9 | 4.8
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.1 | 9.9 | 9.8 | 9.7 | 9.6 | 9.4 | 9.2 | 9 | 8.9 | 8.8 | 8.8 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 5.5 | 4.8 | 4
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 30.5 | 30.3 | 30.1 | 30 | 29.7 | 29.5 | 29.3 | 29.1 | 28.9 | 28.7 | 28.6 | 28.2 | 24.9 | 24.7 | 24.4 | 24.3 | 24.2 | 23.6 | 22.8
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 30.5 | 30.1 | 29.7 | 29.3 | 28.9 | 28.5 | 28.1 | 25 | 24.7 | 23 | 21.9 | 21.2 | 20.4 | 19 | 18.3 | 16.8 | 15.2 | 6.7 | 0
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 30.5 | 29.9 | 29.2 | 28.7 | 28.2 | 27.9 | 24.8 | 23.8 | 22.2 | 20.6 | 18.6 | 16.6 | 14.5 | 13.7 | 12.7 | 11.3 | 9.5 | 0 | 0
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 30.5 | 30.3 | 29.9 | 29.6 | 29.3 | 28.9 | 28.6 | 28.2 | 24.9 | 23.8 | 22.5 | 22 | 21.5 | 21 | 20.8 | 20.6 | 20.4 | 15.9 | 9.7
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8 | 6.9 | 6.8 | 6.7 | 6.7 | 6.6 | 6.5 | 6.3 | 6 | 5.4 | 4.8 | 4.3 | 3.9 | 3.7 | 3.5 | 3.3 | 3.2 | 1.8 | 0
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8 | 6.8 | 6.7 | 6.4 | 6 | 5.5 | 5.2 | 4.7 | 3.8 | 2.8 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8 | 6.7 | 6.5 | 6.1 | 5.6 | 5.2 | 4.6 | 3.6 | 2.5 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8 | 6.9 | 6.8 | 6.6 | 6.3 | 5.9 | 5.5 | 5 | 4.4 | 3.7 | 2.9 | 2.4 | 2 | 1.6 | 1.5 | 1.2 | 0.9 | 0 | 0
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.2 | 17.2 | 17.1 | 17.1 | 17 | 17 | 16.9 | 16.9 | 16.8 | 16.7 | 15.6 | 15.6 | 15.5 | 15.1 | 15.1 | 15.1 | 15.1 | 14.7 | 14
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.2 | 17.1 | 17 | 16.9 | 16.8 | 16.7 | 16.7 | 16.7 | 15.6 | 15.1 | 15 | 14.7 | 14.5 | 14.1 | 13.9 | 13.6 | 13.2 | 11.4 | 9.8
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.2 | 17.1 | 16.9 | 16.8 | 16.7 | 16.7 | 15.7 | 15.6 | 15.1 | 14.8 | 14.4 | 14.2 | 13.9 | 13.6 | 13.4 | 13.1 | 12.8 | 11.1 | 10.1
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.2 | 17.1 | 17.1 | 17 | 16.9 | 16.8 | 16.8 | 16.7 | 15.6 | 15.6 | 15.1 | 15 | 15 | 14.9 | 14.8 | 14.7 | 14.5 | 13.4 | 12
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.3 | 7.3 | 7.3 | 7.2 | 7.2 | 7.1 | 7.1 | 6.9 | 6.6 | 6.1 | 5.5 | 4.9 | 4.5 | 4.1 | 3.8 | 3.4 | 3.2 | 1.9 | 0.7
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.3 | 7.3 | 7.2 | 7.1 | 7.1 | 7 | 6.8 | 6.3 | 5.4 | 4.5 | 3.4 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.3 | 7.3 | 7.1 | 7 | 7 | 6.9 | 6.5 | 5.7 | 4.4 | 3.2 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.3 | 7.3 | 7.2 | 7.2 | 7.1 | 7.1 | 6.9 | 6.5 | 5.7 | 4.9 | 3.9 | 3.1 | 2.3 | 1.6 | 0.9 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10 | 10 | 10 | 9.9 | 9.8 | 9.8 | 9.7 | 9.7 | 9.6 | 9.6 | 9.6 | 9.5 | 9.5 | 9.4 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10 | 10 | 10 | 9.8 | 9.8 | 9.7 | 9.7 | 9.5 | 9.4 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 12.2 | 12.2 | 12.2 | 0 | 0
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10 | 10 | 9.9 | 9.8 | 9.7 | 9.7 | 9.4 | 9.3 | 9.1 | 9 | 9 | 9 | 9.1 | 12.2 | 12.2 | 12.2 | 10.9 | 0 | 0
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10 | 10 | 10 | 9.8 | 9.8 | 9.7 | 9.7 | 9.6 | 9.4 | 9.2 | 9.1 | 9.1 | 9.1 | 9.1 | 12.2 | 12.2 | 12.2 | 7.5 | 7.5
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 33.1 | 33 | 32.8 | 32.6 | 32.4 | 32.3 | 32.1 | 32 | 31.9 | 31.7 | 31.5 | 31.3 | 31.3 | 31.3 | 31.2 | 31.2 | 31.1 | 30.5 | 29.9
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 33.1 | 32.7 | 32.3 | 32.1 | 31.9 | 31.2 | 31 | 30.8 | 30.7 | 30.5 | 30.3 | 30.1 | 29.9 | 29.7 | 29.5 | 29.4 | 29.4 | 23.3 | 21.7
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 33.1 | 32.6 | 32 | 31.6 | 31.3 | 30.9 | 30.6 | 30.3 | 30.1 | 29.9 | 29.7 | 29.6 | 29.5 | 29.4 | 23.9 | 23.8 | 23.8 | 22.3 | 20.3
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 33.1 | 32.9 | 32.6 | 32.4 | 32.3 | 32.1 | 31.8 | 31.7 | 31.6 | 31.5 | 31.3 | 31.2 | 31.2 | 31.1 | 31 | 30.9 | 30.7 | 29.7 | 23.8
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 32.3 | 32.1 | 31.9 | 31.8 | 31.7 | 31.5 | 31.3 | 31.1 | 30.8 | 30.4 | 30.2 | 30.1 | 30 | 29.9 | 29.9 | 29.9 | 29.8 | 29.2 | 28.8
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 32.3 | 31.9 | 31.6 | 31.2 | 30.9 | 30.5 | 30.3 | 30.1 | 29.9 | 29.6 | 29.3 | 27.7 | 24.2 | 21.5 | 14.6 | 13.2 | 11.7 | 2.5 | 0
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 32.3 | 31.8 | 31.3 | 30.9 | 30.4 | 30 | 29.7 | 29.4 | 29 | 20.3 | 15.7 | 13.3 | 10.5 | 8.5 | 6.7 | 5.4 | 3.7 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 32.3 | 32 | 31.8 | 31.4 | 31.2 | 30.8 | 30.5 | 30.4 | 30.2 | 30 | 29.7 | 29.6 | 28 | 26.5 | 20.6 | 20 | 19.1 | 11.2 | 3.5
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 54.7 | 54.4 | 54 | 53.6 | 53.1 | 52.5 | 51.6 | 50.6 | 49.1 | 47 | 45.1 | 43.9 | 42.3 | 40.7 | 39.4 | 38.6 | 38.3 | 35.4 | 31.8
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 54.7 | 54 | 53.1 | 51.8 | 50.4 | 48.5 | 46.3 | 43.8 | 40.6 | 36.8 | 31.9 | 27.1 | 23.9 | 21.4 | 14.6 | 13.2 | 11.8 | 2.5 | 0
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 54.7 | 53.8 | 52.3 | 50.9 | 49.1 | 46.4 | 43.2 | 38.9 | 34.3 | 20.2 | 15.8 | 13.4 | 10.6 | 8.5 | 6.7 | 5.4 | 3.7 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 54.7 | 54.3 | 53.5 | 52.4 | 51 | 49.3 | 47.2 | 44.4 | 40.9 | 36.8 | 31.3 | 28.9 | 26.8 | 25.3 | 19.5 | 19 | 18.4 | 11.3 | 3.5
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.2 | 14.1 | 14 | 13.8 | 13.7 | 13.5 | 13.4 | 13.2 | 12.9 | 12.5 | 12.1 | 11.9 | 11.7 | 11.5 | 11.3 | 11.2 | 10.6 | 9.8 | 7.2
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.2 | 13.9 | 13.6 | 13.3 | 13 | 12.6 | 12.4 | 12.2 | 11.8 | 11.2 | 10.2 | 7.4 | 6 | 4.6 | 3.8 | 1 | 0 | 0 | 0
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.2 | 13.8 | 13.2 | 12.8 | 12.4 | 11.8 | 11.3 | 10.5 | 8.7 | 6.6 | 5.2 | 4.1 | 3.3 | 2.2 | 1.5 | 0 | 0 | 0 | 0
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.2 | 14.1 | 13.8 | 13.6 | 13.4 | 13.2 | 12.9 | 12.6 | 12 | 11.3 | 10.4 | 8.8 | 7.8 | 7.1 | 6.9 | 5.6 | 5 | 1.1 | 0
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 34.2 | 34.3 | 34.2 | 34.1 | 33.9 | 33.8 | 33.7 | 33.7 | 33.7 | 33.5 | 33.5 | 32.9 | 32.2 | 31.4 | 30.9 | 30.9 | 30.9 | 30.7 | 30.4
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 34.2 | 34.3 | 34.2 | 33.9 | 33.6 | 33.4 | 33.2 | 32.6 | 31.7 | 30.1 | 29.7 | 29.6 | 24.8 | 24.7 | 24.6 | 24.6 | 24.5 | 0 | 0
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 34.2 | 34.2 | 34 | 33.6 | 33.3 | 33.1 | 32.3 | 31.1 | 30 | 29.6 | 24.8 | 24.6 | 24.4 | 24.3 | 23.5 | 17.6 | 10.2 | 0 | 0
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 34.2 | 34.3 | 34.2 | 33.9 | 33.9 | 33.8 | 33.4 | 32.9 | 32.1 | 30.5 | 29.8 | 29.7 | 24.9 | 24.8 | 24.8 | 24.8 | 24.8 | 24.6 | 11.1
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 42.5 | 42.7 | 42.6 | 42.5 | 41.9 | 41.8 | 41.7 | 41.6 | 41.6 | 41.1 | 40.1 | 38.6 | 36.9 | 35.1 | 33.7 | 33.3 | 33 | 30.6 | 27.6
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 42.5 | 42.6 | 42.3 | 41.6 | 41.4 | 40.2 | 38.6 | 36.6 | 34.1 | 28.8 | 25.7 | 23.4 | 21.3 | 19.1 | 18.3 | 16.9 | 15.2 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 42.5 | 42.5 | 41.6 | 41.2 | 39.4 | 37.5 | 34.3 | 29.8 | 25.3 | 21.4 | 18.7 | 16.7 | 14.5 | 13.8 | 12.8 | 11.3 | 6.7 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 42.5 | 42.7 | 42.5 | 41.9 | 41.7 | 41.6 | 40.3 | 38.4 | 35.9 | 30.8 | 27.4 | 26.2 | 25.1 | 24.2 | 24.4 | 23.8 | 22.9 | 16 | 7.3
Ratcliffe 132kV | NOTTINGHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 30.4 | 30.2 | 30.1 | 30 | 29.8 | 29.7 | 29.6 | 29.5 | 29.5 | 29.5 | 29.4 | 29.3 | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 24.8 | 24.5
Ratcliffe 132kV | NOTTINGHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 30.4 | 30 | 29.7 | 29.5 | 29.3 | 29.2 | 29.1 | 24.9 | 24.8 | 24.5 | 24.4 | 24.1 | 23.9 | 23.5 | 23.2 | 22.8 | 22.5 | 20.6 | 18.6
Ratcliffe 132kV | NOTTINGHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 30.4 | 29.8 | 29.4 | 29.2 | 29 | 24.9 | 24.6 | 24.1 | 23.5 | 23.1 | 22.8 | 22.5 | 22.1 | 21.8 | 21.5 | 21.1 | 20.6 | 17.9 | 15.5
Ratcliffe 132kV | NOTTINGHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 30.4 | 30.2 | 29.9 | 29.8 | 29.6 | 29.4 | 29.4 | 29.2 | 29.1 | 24.8 | 24.7 | 24.7 | 24.6 | 24.6 | 24.5 | 24.4 | 24.3 | 23.3 | 22
Ratcliffe 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.2 | 16.1 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 14.9 | 14.5 | 13.9 | 13.2 | 12.9 | 12.5 | 12 | 11.5 | 11.1 | 10.8 | 9.1 | 7.1
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.2 | 15.9 | 15.6 | 15.3 | 15 | 14.6 | 14.2 | 13.8 | 13 | 11.7 | 10.1 | 8.3 | 7.3 | 6.5 | 1 | 0 | 0 | 0 | 0
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.2 | 15.8 | 15.3 | 14.9 | 14.4 | 13.7 | 12.7 | 11.4 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.2 | 16.1 | 15.8 | 15.6 | 15.3 | 15 | 14.6 | 14.1 | 13.1 | 11.9 | 10.1 | 9.4 | 9 | 8.7 | 3.5 | 3.2 | 2.7 | 0 | 0
Ratcliffe 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.9 | 9 | 9 | 9.1 | 9.1 | 8.9 | 8.8 | 8.6 | 7.8 | 7.5 | 6.9 | 6.4 | 6 | 5.6 | 5.2 | 5.1 | 5 | 4.3 | 3.5
Ratcliffe 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.9 | 8.9 | 8.9 | 8.8 | 8.6 | 8.4 | 7.4 | 6.8 | 6 | 5.2 | 4.3 | 3.4 | 2.6 | 1.7 | 0.9 | 0.6 | 0 | 0 | 0
Ratcliffe 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.9 | 8.9 | 8.9 | 8.7 | 8.5 | 7.7 | 7.2 | 6.4 | 5.4 | 4.5 | 3.5 | 2.7 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.9 | 9 | 9 | 8.9 | 8.6 | 7.8 | 7.4 | 6.9 | 6.2 | 5.5 | 4.6 | 3.9 | 3.2 | 2.5 | 1.9 | 1.7 | 1.6 | 0 | 0
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.2 | 17.2 | 17 | 16.9 | 14.7 | 14.6 | 14.4 | 13.9 | 13 | 11.5 | 10.2 | 9 | 7.7 | 6.3 | 5.3 | 4.8 | 4.6 | 3.2 | 1.7
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.2 | 17 | 14.7 | 14.5 | 13.8 | 12.5 | 10.8 | 8.6 | 6.1 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.2 | 17 | 14.7 | 14.3 | 13.3 | 11.7 | 9.5 | 6.4 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.2 | 17.1 | 16.8 | 14.6 | 14 | 12.8 | 11.1 | 8.8 | 6.1 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.3 | 13.2 | 13.1 | 13 | 12.8 | 12.7 | 12.6 | 12.5 | 12.5 | 12.4 | 12.2 | 12 | 11.7 | 11.4 | 11.1 | 11 | 10.9 | 10.7 | 10.4
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.3 | 13 | 12.7 | 12.1 | 12 | 11.9 | 11.5 | 11.3 | 11.1 | 10.3 | 9.8 | 9.4 | 9.2 | 9.1 | 8.9 | 8.8 | 8.6 | 6.7 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.3 | 12.9 | 12.3 | 12 | 11.6 | 11.3 | 10.7 | 9.8 | 9.3 | 9 | 8.8 | 8.7 | 8.7 | 8.6 | 8.5 | 8.3 | 8.1 | 0 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.3 | 13.1 | 12.8 | 12.3 | 12.2 | 12.1 | 11.7 | 11.4 | 11 | 10.2 | 9.7 | 9.7 | 9.6 | 9.6 | 9.6 | 9.5 | 9.4 | 9 | 8.5
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.6 | 4.6 | 4.6 | 4.6 | 4.5 | 4.5 | 4.3 | 4.2 | 3.5 | 2.7 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.6 | 4.6 | 4.5 | 4.5 | 4.4 | 4.4 | 4 | 3.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.6 | 4.6 | 4.5 | 4.4 | 4.3 | 4 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.6 | 4.6 | 4.6 | 4.5 | 4.5 | 4.5 | 4.3 | 3.7 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.9 | 17.9 | 17.9 | 17.9 | 17.9 | 17.8 | 17.8 | 17.8 | 17.7 | 17.6 | 17.6 | 17.5 | 17.4 | 17.3 | 17.1 | 17.1 | 17.1 | 17 | 16.9
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.9 | 17.9 | 17.9 | 17.9 | 17.8 | 17.6 | 17.5 | 17.3 | 17.1 | 16.9 | 16.7 | 15.7 | 15.6 | 15.5 | 15.5 | 15.4 | 15.4 | 15.1 | 14.9
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.9 | 17.9 | 17.9 | 17.8 | 17.6 | 17.5 | 17.2 | 16.9 | 16.7 | 15.7 | 15.6 | 15.5 | 15.4 | 15.3 | 15.2 | 15.2 | 15.1 | 14.8 | 0
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.9 | 17.9 | 17.9 | 17.9 | 17.9 | 17.7 | 17.6 | 17.4 | 17.2 | 16.9 | 16.7 | 15.7 | 15.7 | 15.7 | 15.6 | 15.6 | 15.6 | 15.5 | 15.4
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.5 | 7.4 | 7.3 | 7.4 | 7.3 | 7.2 | 6.8 | 6.4 | 5.2 | 3.4 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.5 | 7.1 | 6.8 | 6.1 | 5.7 | 5.2 | 4.1 | 3.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.5 | 7 | 6.2 | 5.7 | 5 | 4 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.5 | 7.3 | 7.2 | 6.5 | 6.2 | 5.7 | 4.7 | 3.7 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.5 | 20.5 | 20.4 | 20.4 | 20.3 | 20.3 | 20.3 | 20.2 | 20.2 | 20.2 | 20.2 | 20.2 | 20.2 | 20.2 | 20.2 | 20.2 | 20.2 | 20.2 | 20
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.5 | 20.5 | 20.4 | 20.4 | 20.3 | 20.3 | 20.3 | 20.2 | 20.2 | 20 | 19.7 | 19.5 | 19.4 | 19.4 | 19.3 | 19.3 | 19.2 | 19 | 15.1
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.5 | 20.5 | 20.4 | 20.4 | 20.3 | 20.3 | 20.3 | 19.9 | 19.6 | 19.4 | 19.3 | 19.2 | 19.2 | 19.2 | 19.1 | 19.1 | 19 | 17.9 | 0
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.5 | 20.5 | 20.4 | 20.4 | 20.3 | 20.3 | 20.3 | 20.2 | 20.2 | 19.9 | 19.6 | 19.6 | 19.6 | 19.5 | 19.5 | 19.5 | 19.5 | 19.3 | 19.2
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.1 | 18.9 | 18.8 | 18.7 | 18.5 | 18.4 | 18.2 | 18.1 | 18.2 | 18 | 17.8 | 17.2 | 16.7 | 15.6 | 15.1 | 14.9 | 14.6 | 13.7 | 13
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.1 | 18.7 | 18.4 | 18.1 | 17.9 | 17.7 | 17.3 | 16.6 | 15.3 | 14.2 | 13.5 | 12.8 | 12 | 11.3 | 10.6 | 10 | 9.3 | 7.4 | 6
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.1 | 18.6 | 18.1 | 17.7 | 17.3 | 16.7 | 15.2 | 14.2 | 13.3 | 12.4 | 11.7 | 11.1 | 10.5 | 9.9 | 9.3 | 8.7 | 8.1 | 6 | 4.2
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.1 | 18.9 | 18.6 | 18.4 | 18.2 | 17.8 | 17.2 | 16.6 | 15.3 | 14.3 | 13.6 | 13.1 | 12.6 | 12.1 | 11.7 | 11.2 | 10.7 | 9.3 | 8.2
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 51.2 | 51.1 | 51 | 50.8 | 50.7 | 50.5 | 50.3 | 50.1 | 49.9 | 49.6 | 49 | 48.3 | 47.8 | 47.2 | 46.7 | 46.5 | 46.3 | 45 | 43.5
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 51.2 | 50.8 | 50.4 | 50.1 | 49.8 | 49 | 48.3 | 47.3 | 46.2 | 45.1 | 44 | 43 | 41.9 | 40.6 | 38.9 | 36.9 | 35 | 26.5 | 18.6
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 51.2 | 50.6 | 50 | 49.5 | 48.8 | 47.8 | 46.6 | 45.3 | 44.1 | 42.9 | 41.6 | 40.8 | 38.8 | 36.3 | 34.3 | 32.4 | 30.5 | 21.8 | 14.9
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 51.2 | 51 | 50.7 | 50.5 | 50.2 | 49.6 | 48.8 | 47.9 | 47.1 | 46.1 | 45.1 | 44.5 | 43.8 | 43.1 | 42.4 | 41.9 | 39.1 | 24.9 | 18.5
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 29.1 | 28.7 | 28.5 | 28.3 | 28.1 | 28 | 27.8 | 27.5 | 27.4 | 27.3 | 27.3 | 26.7 | 26 | 25.3 | 24.7 | 24.7 | 24.6 | 22.9 | 22.4
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 29.1 | 28.5 | 28.1 | 27.8 | 27.4 | 27 | 26.7 | 26 | 25 | 22 | 21.1 | 20.8 | 20.4 | 18.9 | 18.2 | 16.8 | 15.1 | 6.7 | 0
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 29.1 | 28.4 | 27.9 | 27.3 | 26.8 | 26.4 | 25.4 | 22.9 | 21.6 | 20.3 | 18.5 | 16.6 | 14.4 | 13.7 | 12.7 | 11.2 | 9.5 | 0 | 0
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 29.1 | 28.7 | 28.4 | 28 | 27.7 | 27.5 | 27.2 | 26.5 | 25.5 | 22.6 | 21.5 | 21.4 | 21.2 | 21 | 20.9 | 20.9 | 20.5 | 15.9 | 9.7
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.7 | 13.7 | 13.6 | 13.6 | 13.5 | 13.5 | 13.2 | 13 | 12.3 | 11.4 | 10.2 | 9.4 | 8.9 | 8.5 | 8.1 | 7.7 | 7.3 | 4.4 | 1.3
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.7 | 13.6 | 13.5 | 13.4 | 13.3 | 13.2 | 12.8 | 12.3 | 11.2 | 9.7 | 8.1 | 6.3 | 4.7 | 3.2 | 2.1 | 0.8 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.7 | 13.6 | 13.4 | 13.3 | 13.2 | 13.1 | 12.5 | 11.3 | 9.4 | 7.9 | 6 | 4.8 | 2.9 | 1.5 | 0.5 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.7 | 13.7 | 13.6 | 13.5 | 13.5 | 13.4 | 13.1 | 12.9 | 11.9 | 10.9 | 9.5 | 8.2 | 7.3 | 6.4 | 5.8 | 5.1 | 4.4 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 42.4 | 41.7 | 41.2 | 40.8 | 40.4 | 39.9 | 38.7 | 37.5 | 34.4 | 30.1 | 25.6 | 22 | 19.3 | 16.7 | 14.3 | 11.8 | 9.9 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 42.4 | 41 | 39.7 | 38.2 | 36.9 | 35.6 | 33 | 29.8 | 24.1 | 16.3 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 42.4 | 40.5 | 38.3 | 36.6 | 34.7 | 32.6 | 28.4 | 21.1 | 11.7 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 42.4 | 41.5 | 40.6 | 39.3 | 38.3 | 37.2 | 34.8 | 32 | 26.7 | 20.2 | 13.7 | 7.9 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.1 | 17.1 | 17.2 | 16.9 | 16.5 | 16.3 | 16 | 15.9 | 15.7 | 15.5 | 15.3 | 15.3 | 15.2 | 15.2 | 15.1 | 15.1 | 15.1 | 14.6 | 14
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.1 | 17.2 | 16.6 | 16.1 | 15.6 | 15.2 | 14.8 | 14.6 | 14.4 | 14.1 | 13.8 | 13.6 | 13.3 | 12.9 | 12.6 | 12.2 | 11.9 | 0 | 0
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.1 | 17 | 16.1 | 15.5 | 15 | 14.3 | 13.6 | 13.2 | 12.9 | 12.5 | 12.1 | 11.8 | 11.7 | 11.4 | 11.1 | 10.8 | 10.3 | 0 | 0
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.1 | 17.1 | 16.9 | 16.4 | 16.1 | 15.7 | 15.3 | 15.1 | 14.9 | 14.7 | 14.5 | 14.4 | 14.3 | 14.2 | 14.2 | 14 | 13.8 | 12.8 | 11.2
Stalybridge 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.7 | 16.7 | 16.6 | 16.6 | 16.5 | 16.5 | 16.6 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.3 | 16.1
Stalybridge 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.7 | 16.6 | 16.5 | 16.4 | 16.3 | 16.3 | 16.4 | 16.4 | 16.4 | 16.3 | 16.3 | 16.1 | 16.1 | 16 | 15.9 | 15.8 | 15.7 | 15.1 | 14.4
Stalybridge 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.7 | 16.6 | 16.4 | 16.3 | 16 | 15.9 | 16.3 | 16.1 | 16 | 15.9 | 15.8 | 15.7 | 15.6 | 15.5 | 15.4 | 15.3 | 15.2 | 14.4 | 13.6
Stalybridge 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.7 | 16.7 | 16.6 | 16.5 | 16.4 | 16.4 | 16.5 | 16.5 | 16.5 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.3 | 15.9 | 15.5
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.7 | 12.7 | 12.7 | 12.7 | 12.6 | 12.6 | 15 | 15.1 | 15.2 | 15.3 | 15.2 | 15.1 | 15 | 14.9 | 14.8 | 14.8 | 14.7 | 14 | 13.2
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.7 | 12.7 | 12.6 | 12.6 | 11.7 | 11.4 | 13.5 | 13.1 | 12.7 | 12.2 | 11.7 | 11.2 | 10.7 | 10.2 | 9.9 | 9.5 | 9.1 | 7.1 | 5.6
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.7 | 12.7 | 12.6 | 12.6 | 12.5 | 12.5 | 15.1 | 15.1 | 14.6 | 14.2 | 13.7 | 13.3 | 12.9 | 12.6 | 12.3 | 12 | 11.7 | 9.8 | 8.9
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.7 | 12.7 | 12.7 | 12.6 | 12.6 | 12.6 | 15.2 | 15.3 | 15.3 | 15.1 | 14.8 | 14.6 | 14.4 | 14.2 | 14.1 | 13.9 | 13.4 | 12.1 | 10.7
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.3 | 15.3 | 15.3 | 15.2 | 15 | 14.9 | 17.3 | 17.2 | 17.1 | 15.3 | 15.1 | 15 | 14.9 | 14.8 | 14.8 | 14.7 | 14.6 | 13.9 | 13.2
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.3 | 15.3 | 15.1 | 14.8 | 11.7 | 11.4 | 13.4 | 13.1 | 12.6 | 12.1 | 11.6 | 11.1 | 10.7 | 10.2 | 9.8 | 9.4 | 9.1 | 7.1 | 5.6
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.3 | 15.3 | 15 | 14.8 | 14.6 | 14.5 | 15.3 | 15 | 14.6 | 14.1 | 13.6 | 13.2 | 12.9 | 12.5 | 12.2 | 11.9 | 11.6 | 9.7 | 8.8
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.3 | 15.3 | 15.2 | 15 | 14.9 | 14.7 | 17.1 | 17.1 | 15.2 | 15.1 | 14.7 | 14.5 | 14.3 | 14.1 | 14 | 13.8 | 13.3 | 12 | 10.7
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.4 | 7.4 | 7.3 | 7.2 | 7.2 | 7.1 | 6.9 | 6.8 | 6.5 | 6 | 5.5 | 5.1 | 4.9 | 4.7 | 4.5 | 4.3 | 4.1 | 2.7 | 1.3
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.4 | 7.3 | 7.2 | 7.1 | 7 | 7 | 6.7 | 6.5 | 6 | 5.3 | 4.6 | 3.8 | 3.1 | 2.3 | 6.5 | 6 | 5.4 | 2.2 | 0
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.4 | 7.3 | 7.1 | 7 | 6.9 | 6.8 | 6.5 | 5.9 | 5.1 | 4.4 | 3.5 | 2.9 | 2.3 | 6.4 | 6 | 5.5 | 5 | 0 | 0
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.4 | 7.4 | 7.3 | 7.2 | 7.2 | 7.1 | 7 | 6.9 | 6.5 | 6 | 5.4 | 2.5 | 2.1 | 1.7 | 1.5 | 1.2 | 0.9 | 0 | 0
Staythorpe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.5 | 13.3 | 13.1 | 12.9 | 12.7 | 12.5 | 12.1 | 11.8 | 10.3 | 8.4 | 5.9 | 3.8 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.5 | 13.1 | 11.3 | 10.9 | 10.5 | 9.7 | 8.9 | 7.8 | 5.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.5 | 13 | 12.2 | 10.4 | 9.7 | 9.1 | 7.9 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.5 | 13.2 | 12.8 | 11.2 | 10.8 | 10.3 | 9.7 | 9.1 | 6.9 | 4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.1 | 10 | 10 | 9.9 | 9.9 | 9.8 | 9.6 | 9.5 | 9 | 8.2 | 6 | 3.9 | 2.5 | 1.3 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.1 | 10 | 9.8 | 9.7 | 9.5 | 9.3 | 9 | 7.9 | 5.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.1 | 10 | 9.7 | 9.6 | 9.4 | 9.2 | 8 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.1 | 10 | 9.9 | 9.8 | 9.6 | 9.4 | 9.2 | 9 | 7 | 4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.1 | 13 | 12.8 | 12.6 | 12.4 | 12.2 | 11.9 | 11.6 | 10.2 | 8.4 | 5.9 | 3.8 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.1 | 12.8 | 11.1 | 10.7 | 10.4 | 9.6 | 8.9 | 7.8 | 5.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.1 | 12.7 | 12 | 10.3 | 9.7 | 9.1 | 7.9 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.1 | 12.9 | 12.6 | 11 | 10.7 | 10.3 | 9.7 | 9 | 6.9 | 4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.3 | 7.3 | 7 | 6.6 | 6.1 | 5.7 | 5.5 | 5.2 | 5 | 4.8 | 4.7 | 3.7 | 2.7
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.4 | 7.4 | 7.4 | 7.4 | 7.3 | 7.3 | 7.2 | 7.1 | 6.7 | 6 | 5.1 | 4.3 | 3.7 | 3.2 | 2.9 | 2.4 | 2.1 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.4 | 7.4 | 7.4 | 7.3 | 7.3 | 7.2 | 7.1 | 6.5 | 5.6 | 4.9 | 4.2 | 3.8 | 3.4 | 2.9 | 2.7 | 2.3 | 2 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.3 | 7.3 | 7.2 | 6.8 | 6.2 | 5.3 | 4.8 | 4.5 | 4.2 | 4.1 | 3.8 | 3.7 | 2.3 | 0.6
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 14.3 | 14.1 | 13.3 | 12.9 | 12.5 | 12.1 | 11.1 | 11.2 | 7.9 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 14.3 | 13.4 | 12.2 | 11.1 | 10.3 | 9.6 | 7.9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 14.3 | 13.1 | 11.4 | 10.4 | 9.2 | 7.8 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 14.3 | 13.7 | 12.9 | 12.4 | 11.8 | 11.2 | 9.9 | 9.6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.8 | 14.2 | 14.1 | 14.1 | 14 | 13.8 | 13.5 | 13.1 | 11.6 | 9.5 | 7.4 | 5.9 | 5 | 4.4 | 3.8 | 3.3 | 2.7 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.8 | 14 | 13.4 | 12.7 | 12.2 | 11.4 | 10.3 | 9.3 | 6.9 | 4.3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.8 | 13.9 | 13.1 | 12.7 | 11.9 | 10.8 | 9.7 | 7 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.8 | 14.1 | 13.6 | 12.9 | 12.4 | 11.7 | 10.5 | 9.6 | 7.5 | 5.7 | 3.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 21.8 | 21.8 | 21.7 | 21.6 | 20.9 | 20 | 18.4 | 17.7 | 13.4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 21.8 | 21.7 | 20.5 | 18.3 | 16.2 | 13.8 | 9.3 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 21.8 | 21.6 | 19.3 | 17 | 14.4 | 10.7 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 21.8 | 21.8 | 21.5 | 20 | 18.1 | 15.9 | 12.5 | 9.7 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 24.1 | 23.7 | 22.5 | 21.7 | 20.8 | 19.9 | 18.3 | 17.6 | 13.3 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 24.1 | 22.6 | 20.4 | 18.2 | 16.1 | 13.7 | 9.2 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 24.1 | 22.1 | 19.2 | 17 | 14.4 | 10.6 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 24.1 | 23.1 | 21.4 | 19.9 | 18 | 15.8 | 12.4 | 9.7 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 7.2 | 7.1 | 7.1 | 7 | 7 | 6.9 | 8 | 7 | 5.8 | 4.2 | 3.4 | 2.7 | 2.2 | 1.7 | 1.3 | 0.9 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 7.1 | 7 | 6.9 | 6.8 | 6.7 | 6.1 | 6.5 | 5 | 3.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 7.1 | 6.9 | 6.8 | 6.4 | 5.9 | 5.2 | 4.4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 7.2 | 7.1 | 7 | 7 | 6.9 | 6.7 | 7.1 | 5.9 | 4.6 | 2.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.7 | 10.4 | 10.2 | 10 | 9.7 | 9.4 | 8.9 | 8.4 | 7.6 | 6.6 | 5.5 | 4.8 | 4.5 | 4.2 | 3.9 | 3.7 | 3.4 | 1.7 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.7 | 10 | 9.4 | 8.6 | 7.5 | 6.1 | 4.4 | 2.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.7 | 9.9 | 9.1 | 8.2 | 7 | 5.5 | 3.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.7 | 10.2 | 9.6 | 8.9 | 7.8 | 6.5 | 4.9 | 3.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 22.9 | 15.8 | 15.3 | 14.8 | 14 | 12.9 | 11.3 | 9.5 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 22.9 | 14.8 | 11.3 | 7.6 | 5.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 22.9 | 14.3 | 10.5 | 6.9 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 22.9 | 15.4 | 13.7 | 8.9 | 6.7 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 22.4 | 22.3 | 22.3 | 22.3 | 22.1 | 21.9 | 21.6 | 21.3 | 20.5 | 19.5 | 18.4 | 17.3 | 16.5 | 15.8 | 15.3 | 15 | 14.8 | 13 | 10.8
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 22.4 | 22.1 | 21.8 | 20.5 | 20.3 | 19.8 | 19.2 | 18.5 | 17.2 | 15.7 | 14.3 | 13 | 11.7 | 10.4 | 9.5 | 8.8 | 8.2 | 4.2 | 0
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 22.4 | 22 | 21.1 | 20.8 | 20.3 | 19 | 18.3 | 16.9 | 15 | 13.4 | 11.7 | 10.7 | 9.6 | 8.5 | 7.7 | 7 | 6.4 | 9.9 | 7.4
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 22.4 | 22.2 | 22.1 | 20.8 | 20.6 | 20.2 | 19.5 | 18.9 | 17.8 | 16.6 | 15.3 | 14.4 | 13.6 | 12.9 | 12.4 | 12.1 | 11.8 | 8.8 | 5
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.2 | 6.2 | 6.2 | 6.1 | 6.1 | 6.1 | 5.9 | 5.8 | 5.2 | 4.4 | 3.5 | 2.7 | 2.3 | 2 | 1.7 | 1.4 | 1.1 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.2 | 6.2 | 6.1 | 6 | 5.9 | 5.8 | 5.6 | 5.3 | 4.3 | 3.1 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.2 | 6.2 | 6 | 5.9 | 5.8 | 5.7 | 5.5 | 4.4 | 2.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.2 | 6.2 | 6.1 | 6.1 | 6 | 6 | 5.8 | 5.6 | 4.9 | 4.1 | 2.8 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.9 | 3.9 | 3.8 | 3.7 | 3.6 | 3.5 | 3.4 | 3.2 | 2.8 | 2.2 | 1.4 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.9 | 3.7 | 3.5 | 3.4 | 3.2 | 3.1 | 2.8 | 2.5 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.9 | 3.7 | 3.3 | 3.1 | 2.9 | 2.6 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.9 | 3.8 | 3.7 | 3.6 | 3.5 | 3.3 | 3.1 | 2.9 | 2.3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.4 | 5.4 | 5.4 | 5.1 | 4.7 | 4.2 | 3.8 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.5 | 5.5 | 5.4 | 5.4 | 5.4 | 5.4 | 5.3 | 5.2 | 4.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.5 | 5.5 | 5.4 | 5.4 | 5.3 | 5.3 | 5.2 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.5 | 5.5 | 5.5 | 5.5 | 5.4 | 5.4 | 5.4 | 5.3 | 5 | 4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3.1 | 3 | 2.7 | 2.3 | 1.7 | 1.2 | 0.9 | 0.7 | 4.4 | 4.2 | 4.1 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3.4 | 3.3 | 2.9 | 2.8 | 2.6 | 2.4 | 2.2 | 1.8 | 1.2 | 0.6 | 3.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.3 | 3 | 2.9 | 2.8 | 2.3 | 2.1 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.4 | 3.4 | 3 | 2.9 | 2.8 | 2.6 | 2.5 | 2.1 | 1.7 | 1.1 | 4.1 | 3.7 | 2.6 | 1.9 | 1 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.4 | 1.8 | 1.6 | 1.5 | 1.4 | 1.3 | 1.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.4 | 1.6 | 1.1 | 1 | 0.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.4 | 1.5 | 0.9 | 0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.4 | 1.7 | 1.2 | 1.1 | 1.1 | 1 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.1 | 1.1 | 0.9 | 0.8 | 0.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.1 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.1 | 1 | 0.8 | 0.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.4 | 1.8 | 1.6 | 1.5 | 1.4 | 1.4 | 1.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.4 | 1.6 | 1.1 | 1 | 0.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.4 | 1.5 | 0.9 | 0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.4 | 1.7 | 1.3 | 1.2 | 1.1 | 1 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.9 | 3.8 | 3.7 | 3.7 | 3.6 | 3.4 | 3.3 | 2.8 | 2.2 | 1.5 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.8 | 3.5 | 3.4 | 3.3 | 3.1 | 2.8 | 2.5 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.7 | 3.3 | 3.1 | 2.9 | 2.6 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.9 | 3.7 | 3.6 | 3.5 | 3.4 | 3.2 | 2.9 | 2.3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.5 | 13.3 | 13.2 | 13.1 | 12.8 | 12.7 | 12.6 | 12.5 | 12.4 | 12.3 | 13.9 | 13.8 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.3 | 12.7
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.5 | 13.2 | 12.9 | 12.6 | 12.4 | 12.2 | 12 | 11.7 | 11.5 | 11.3 | 13.1 | 12.8 | 12.5 | 12.2 | 11.9 | 11.5 | 11.2 | 9.5 | 8
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.5 | 13 | 12.7 | 12.3 | 12 | 11.6 | 11.3 | 10.8 | 10.5 | 10.2 | 12 | 11.6 | 11.2 | 10.9 | 10.7 | 10.3 | 9.9 | 8.1 | 1.6
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.5 | 13.3 | 13.1 | 12.9 | 12.7 | 12.5 | 12.3 | 12.1 | 11.9 | 11.8 | 13.5 | 13.4 | 13.3 | 13.2 | 13.1 | 12.9 | 12.2 | 11.1 | 10
Stoke Bardolph 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.8 | 17.7 | 17.6 | 17.6 | 17.5 | 17.5 | 17.4 | 17.4 | 17.4 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 15.6 | 15.4
Stoke Bardolph 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.8 | 17.5 | 17.5 | 17.4 | 17.3 | 17.3 | 17.3 | 17.2 | 17.2 | 15.6 | 15.5 | 15.5 | 15.4 | 15.3 | 15.1 | 15 | 14.8 | 13.9 | 13.1
Stoke Bardolph 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.8 | 17.5 | 17.3 | 17.2 | 17.2 | 15.6 | 15.6 | 15.5 | 15.4 | 15.2 | 15 | 14.9 | 14.8 | 14.6 | 14.5 | 14.3 | 14.1 | 13 | 12.1
Stoke Bardolph 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.8 | 17.6 | 17.6 | 17.5 | 17.5 | 17.4 | 17.4 | 17.3 | 17.3 | 17.3 | 17.3 | 17.2 | 17.2 | 15.6 | 15.6 | 15.6 | 15.5 | 15.2 | 14.7
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 30.4 | 30.2 | 30.1 | 30 | 29.8 | 29.7 | 29.4 | 29.2 | 29 | 28.6 | 28.6 | 28.2 | 27.6 | 26.9 | 26.3 | 26.2 | 26.2 | 25.8 | 25
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 30.4 | 29.9 | 29.3 | 29 | 28.1 | 27.4 | 27 | 26.6 | 26 | 24.3 | 23 | 21.8 | 21.4 | 21.1 | 20.8 | 20.5 | 20.2 | 18.6 | 17.2
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 30.4 | 29.7 | 29 | 28.1 | 27.3 | 26.6 | 25.4 | 24.4 | 23.1 | 21.6 | 20.7 | 20.4 | 20.1 | 19.9 | 19.6 | 19.3 | 19 | 17.1 | 15.3
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 30.4 | 30.1 | 29.6 | 29.3 | 28.6 | 28 | 27.6 | 27.1 | 26.3 | 24.5 | 22.9 | 22.4 | 22.3 | 22.2 | 22.1 | 22 | 21.8 | 20.7 | 19.7
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.6 | 17.4 | 17.3 | 17.3 | 17.2 | 17.2 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 14.9 | 14.9 | 17.1 | 17.1 | 14.9 | 14.8 | 14.6
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.6 | 17.3 | 17.1 | 17 | 17 | 17 | 15 | 14.9 | 14.9 | 14.9 | 14.8 | 14.8 | 14.7 | 14.5 | 14.3 | 14.1 | 13.9 | 12.7 | 11.5
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.6 | 17.1 | 17 | 15 | 15 | 14.9 | 14.8 | 14.6 | 14.5 | 14.3 | 14.1 | 14 | 13.8 | 13.6 | 13.4 | 13.2 | 12.9 | 11.3 | 9.7
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.6 | 17.4 | 17.3 | 17.2 | 17.1 | 17.1 | 17 | 17 | 17 | 17.1 | 17.1 | 17.1 | 14.9 | 14.9 | 14.9 | 14.9 | 14.8 | 14.3 | 13.6
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.5 | 9.2 | 9.1 | 9 | 8.8 | 8.8 | 8.7 | 8.6 | 8.4 | 8.2 | 8 | 7.9 | 7.8 | 7.7 | 7.6 | 7.6 | 7.5 | 9.6 | 8.8
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.5 | 9 | 8.7 | 8.4 | 8 | 7.6 | 7.5 | 7.3 | 7.1 | 6.9 | 6.6 | 6.2 | 5.8 | 5.4 | 5 | 4.3 | 3.1 | 4 | 2.4
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.5 | 8.8 | 8.5 | 8 | 7.5 | 7.2 | 7 | 6.7 | 6.3 | 5.9 | 5.4 | 3.5 | 3.1 | 2.8 | 2.5 | 1.8 | 1.5 | 2.3 | 0.7
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.5 | 9.1 | 8.9 | 8.6 | 8.2 | 7.9 | 7.7 | 7.6 | 7.4 | 7.2 | 6.9 | 6.7 | 6.6 | 6.4 | 6.3 | 5.9 | 4.9 | 6.3 | 5
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 31.6 | 31.5 | 31.3 | 31.2 | 31 | 31 | 30.9 | 30.9 | 30.8 | 30.6 | 30.4 | 30.2 | 30.1 | 29.9 | 29.7 | 29.7 | 29.6 | 29.4 | 25.9
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 31.6 | 31.2 | 31 | 30.7 | 30.5 | 30 | 29.5 | 29.3 | 26.1 | 25.7 | 25.1 | 24.5 | 24.1 | 23.5 | 23.1 | 22.7 | 22.3 | 16.4 | 8.6
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 31.6 | 31.1 | 30.7 | 30.4 | 29.9 | 29.4 | 26.1 | 25.6 | 24.8 | 23.9 | 23.1 | 22.6 | 22.1 | 21.6 | 21.3 | 19.4 | 17.6 | 10 | 1.5
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 31.6 | 31.4 | 31.2 | 31 | 30.8 | 30.5 | 29.9 | 29.5 | 29.3 | 26 | 25.5 | 25.3 | 25.1 | 24.9 | 24.7 | 24.6 | 24.3 | 20.3 | 14.6
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.8 | 17.7 | 17.6 | 17.5 | 17.4 | 17.3 | 17.2 | 17.1 | 17 | 16.9 | 16.8 | 16.8 | 16.8 | 16.7 | 16.7 | 16.6 | 16.6 | 16.3 | 16
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.8 | 17.5 | 17.3 | 17.1 | 16.9 | 16.8 | 16.7 | 16.6 | 16.5 | 16.4 | 16.3 | 16.1 | 16 | 15.9 | 13.2 | 13.1 | 13 | 12 | 10.8
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.8 | 17.4 | 17 | 16.7 | 16.5 | 16.3 | 16.1 | 16 | 15.9 | 15.9 | 13.2 | 13.1 | 13 | 12.8 | 12.7 | 12.5 | 12.2 | 10.6 | 9
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.8 | 17.7 | 17.5 | 17.3 | 17.2 | 17.1 | 17 | 16.9 | 16.8 | 16.7 | 16.5 | 16.4 | 16.4 | 16.3 | 16.3 | 16.2 | 16.1 | 13.2 | 12.7
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 45.9 | 45.1 | 44.7 | 44.3 | 39.8 | 39.6 | 39.2 | 38.8 | 38.4 | 37.7 | 37.6 | 36.9 | 36.3 | 35.7 | 35.1 | 34.9 | 34.7 | 34.7 | 32.1
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 45.9 | 44.5 | 43.6 | 42.6 | 41.2 | 39.8 | 38.6 | 36.9 | 34.8 | 32.4 | 31.4 | 29.1 | 27.1 | 25.1 | 23.3 | 21.5 | 19 | 11.6 | 3.8
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 45.9 | 44.1 | 42.8 | 41.3 | 39.6 | 38 | 35.2 | 32.1 | 29.3 | 26.8 | 25.5 | 22.3 | 19.3 | 17.8 | 16.5 | 14.7 | 12.9 | 5.2 | 0
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 45.9 | 44.9 | 44.2 | 43.6 | 42.7 | 41.6 | 40.5 | 39.3 | 37.9 | 35.8 | 34.7 | 33.7 | 32.9 | 32.2 | 31.6 | 30.7 | 19.6 | 15.5 | 9.9
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 82.7 | 82.6 | 79.4 | 79.4 | 79.2 | 79.1 | 78.8 | 78.5 | 78.3 | 77.9 | 78.9 | 78.6 | 78.3 | 77.8 | 77.5 | 77.4 | 77.2 | 76 | 74.2
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 82.7 | 79.3 | 78.9 | 78.5 | 77.7 | 77 | 76.5 | 75.9 | 75.3 | 74.1 | 74.4 | 73.3 | 72.4 | 71.5 | 70.6 | 69.7 | 68.7 | 62 | 49.5
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 82.7 | 79.1 | 78.3 | 77.3 | 76.2 | 75.2 | 74 | 72.7 | 71.3 | 69.9 | 70.2 | 69.5 | 68.4 | 67.3 | 66.2 | 64.9 | 63.3 | 50.3 | 27.2
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 82.7 | 79.4 | 79.3 | 79.1 | 78.5 | 78 | 77.5 | 76.9 | 76.3 | 75.1 | 75.5 | 75 | 74.7 | 74.4 | 74.2 | 73.8 | 73 | 70.1 | 64.1
Stoke Bardolph 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.1 | 18.1 | 18.1 | 18 | 18 | 18 | 18 | 17.8 | 17.7 | 17.6 | 17.5 | 17.4 | 17.2 | 17 | 16.8 | 16.7 | 16.7 | 16.7 | 15.6
Stoke Bardolph 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.1 | 18.1 | 18.1 | 18 | 17.8 | 17.6 | 17.3 | 17 | 16.7 | 15.6 | 15.2 | 14.4 | 14.3 | 14.1 | 13.9 | 13.8 | 13.6 | 13 | 8.6
Stoke Bardolph 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.1 | 18.1 | 18.1 | 17.9 | 17.6 | 17.3 | 16.9 | 15.7 | 15.3 | 14.5 | 14.1 | 13.9 | 13.6 | 13.4 | 13.3 | 13.1 | 12.9 | 10 | 1.5
Stoke Bardolph 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.1 | 18.1 | 18.1 | 18 | 18 | 17.7 | 17.5 | 17.1 | 16.8 | 15.7 | 15.1 | 14.5 | 14.5 | 14.4 | 14.4 | 14.3 | 14.3 | 14 | 13.6
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 7 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18 | 18 | 17.8 | 17.7 | 17.6 | 17.5 | 17.2 | 16.7 | 16 | 15 | 13.9 | 13.1 | 12.6 | 12.3 | 12 | 11.6 | 11.3 | 8.7 | 5.8
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18 | 17.8 | 17.4 | 17.1 | 16.9 | 16.5 | 15.9 | 15.5 | 14.3 | 12.8 | 11.2 | 9.6 | 8 | 5.3 | 2.8 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18 | 17.7 | 17.2 | 16.8 | 16.4 | 16 | 15.5 | 14.1 | 12 | 10.6 | 6.9 | 4.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18 | 17.9 | 17.6 | 17.3 | 17 | 16.8 | 16.4 | 16.1 | 15.2 | 14.2 | 12.7 | 11.8 | 11 | 10.2 | 9.7 | 9.1 | 8.5 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 32.7 | 31.4 | 30.3 | 29.1 | 28.2 | 27.9 | 26.1 | 24.1 | 15.6 | 10.9 | 6.4 | 3.5 | 1.6 | 0 | 11.3 | 8.9 | 6.3 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 32.7 | 30.3 | 27.6 | 26 | 23.6 | 20.6 | 16.8 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 32.7 | 29.2 | 26.3 | 23.3 | 20.3 | 17.5 | 13.3 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 32.7 | 31 | 28.9 | 27.6 | 25.4 | 22.8 | 19.4 | 16.7 | 7.1 | 2.8 | 0 | 3.6 | 0 | 0 | 12.2 | 10.2 | 7.3 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.1 | 5 | 4.8 | 4.7 | 4.6 | 4.5 | 4.3 | 4.1 | 3.5 | 2.9 | 2.2 | 1.7 | 1.4 | 1.2 | 1.3 | 1.2 | 1 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.1 | 4.9 | 4.5 | 4.3 | 4 | 3.8 | 3.4 | 2.9 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.1 | 4.8 | 4.4 | 4.1 | 3.7 | 3.5 | 3 | 2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.1 | 5 | 4.7 | 4.5 | 4.3 | 4.1 | 3.7 | 3.4 | 2.6 | 2 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.9 | 4.8 | 4.7 | 4.7 | 4.7 | 4.7 | 4.6 | 4.5 | 4.4 | 4.2 | 3.9 | 3.7 | 3.6 | 3.5 | 3.5 | 3.4 | 3.3 | 2.7 | 1.9
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.9 | 4.8 | 4.7 | 4.6 | 4.6 | 4.5 | 4.4 | 4.3 | 4.1 | 3.7 | 3.3 | 2.9 | 2.5 | 2.2 | 1.9 | 0 | 0 | 0 | 0
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.9 | 4.7 | 4.6 | 4.6 | 4.5 | 4.4 | 4.3 | 4 | 3.5 | 3.1 | 2.6 | 2.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.9 | 4.8 | 4.7 | 4.7 | 4.6 | 4.6 | 4.5 | 4.5 | 4.3 | 4.1 | 3.7 | 3.5 | 3.3 | 3.1 | 3 | 2.8 | 2.7 | 0 | 0
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.1 | 15.5 | 15.4 | 15.4 | 14.6 | 14.6 | 14.5 | 14.3 | 14 | 13.4 | 12.9 | 12.5 | 12.1 | 11.9 | 11.5 | 11.2 | 10.9 | 8.6 | 6.2
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.1 | 15.5 | 14.7 | 14.6 | 14.5 | 14.2 | 13.6 | 12.9 | 11.9 | 10.7 | 9.6 | 8.2 | 6.9 | 5.5 | 2.4 | 0 | 0 | 0 | 0
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.1 | 15.5 | 14.6 | 14.5 | 14.2 | 13.9 | 13.2 | 12.1 | 10.9 | 9.7 | 8.3 | 7 | 5.9 | 4.8 | 1.7 | 0 | 0 | 0 | 0
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.1 | 15.5 | 15.4 | 14.7 | 14.6 | 14.4 | 14 | 13.6 | 13 | 12.2 | 11.4 | 10.7 | 10 | 9.3 | 8.6 | 7.9 | 7.1 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 4.1 | 4 | 4 | 3.9 | 3.9 | 3.8 | 3.7 | 3.7 | 3.6 | 3.5 | 3.4 | 3.3 | 3.2 | 3.1 | 3 | 3 | 2.5 | 2.2
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 4 | 4 | 3.9 | 3.9 | 3.8 | 3.6 | 3.5 | 3.3 | 3.2 | 3 | 2.8 | 2.7 | 2.5 | 2.3 | 2.1 | 0.9 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 4 | 3.9 | 3.9 | 3.8 | 3.7 | 3.5 | 3.3 | 3.1 | 3 | 2.8 | 2.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 4.1 | 4 | 4 | 4 | 3.8 | 3.7 | 3.6 | 3.4 | 3.3 | 3.2 | 3 | 2.9 | 2.8 | 2.7 | 2.5 | 2.4 | 1.6 | 1.2
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.6 | 12.9 | 12.8 | 12.7 | 12.6 | 12.5 | 12.1 | 11.7 | 11.2 | 10.5 | 9.9 | 9.4 | 9 | 8.7 | 8.5 | 8.2 | 7.9 | 5.6 | 3.1
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.6 | 12.8 | 12.5 | 12.3 | 12 | 11.7 | 10.6 | 9.9 | 8.8 | 7.6 | 6.2 | 4.7 | 3.3 | 1.4 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.6 | 12.7 | 12.3 | 11.9 | 11.6 | 11.3 | 10.5 | 9.5 | 7.1 | 5.9 | 4.5 | 3.3 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.6 | 12.9 | 12.7 | 12.5 | 12.2 | 12 | 11.5 | 11.1 | 10.4 | 9.7 | 8.8 | 8 | 7.3 | 6.1 | 5.3 | 4.6 | 3.8 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.5 | 11.3 | 11 | 10.5 | 10.3 | 10.1 | 9.6 | 9.2 | 8.2 | 7.2 | 5.9 | 5.1 | 4.6 | 4 | 4 | 2.8 | 1.7 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.5 | 11.1 | 10.1 | 9.6 | 9 | 8.4 | 7.7 | 6.9 | 5.2 | 3.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.5 | 10.7 | 9.7 | 9 | 8.2 | 7.5 | 6.4 | 4.5 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.5 | 11.2 | 10.5 | 10.1 | 9.6 | 9.1 | 8.4 | 7.7 | 6.4 | 5.1 | 2.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.5 | 14.8 | 14.6 | 14.5 | 14.4 | 14.3 | 14.1 | 14 | 13.9 | 13.8 | 13.2 | 13.1 | 13 | 13 | 12.9 | 12.8 | 12.8 | 12.4 | 11.7
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.5 | 14.6 | 14.4 | 14.2 | 14 | 13.8 | 13.2 | 13 | 12.7 | 12.3 | 11.9 | 11.5 | 11.1 | 10.4 | 8.3 | 4.7 | 0.9 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.5 | 14.5 | 14.2 | 14 | 13.8 | 13.1 | 12.7 | 12.3 | 11.9 | 11.5 | 11.1 | 7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.5 | 14.7 | 14.5 | 14.4 | 14.2 | 14 | 13.8 | 13.2 | 13 | 12.7 | 12.5 | 12.4 | 12.3 | 12.1 | 12 | 11.8 | 11.5 | 10.4 | 5.4
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.6 | 18.5 | 18.4 | 18.3 | 18.2 | 18.1 | 18 | 17.9 | 17.9 | 17.9 | 17.9 | 17.9 | 17.7 | 17.6 | 17.5 | 17.4 | 17.4 | 14.7 | 14.3
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.6 | 18.4 | 18.1 | 17.8 | 17.6 | 17.4 | 17.3 | 17.2 | 14.7 | 14.6 | 14.4 | 14.3 | 12.7 | 10.4 | 8.3 | 4.7 | 0.9 | 0 | 0
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.6 | 18.3 | 17.9 | 17.6 | 17.4 | 17.2 | 14.7 | 14.5 | 14.1 | 13.7 | 12 | 7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.6 | 18.5 | 18.2 | 18 | 17.8 | 17.6 | 17.5 | 17.3 | 17.3 | 14.7 | 14.5 | 14.5 | 14.4 | 14.2 | 14.1 | 14 | 11.6 | 11.1 | 5.4
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 18.2 | 17.4 | 17.3 | 17.3 | 17.2 | 17.1 | 16.8 | 16.4 | 14.8 | 11.7 | 9.2 | 7.5 | 6.3 | 5.3 | 12.2 | 11.9 | 11.6 | 5.7 | 0
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 18.2 | 17.3 | 17.1 | 16.9 | 16.7 | 16.6 | 15.7 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 18.2 | 17.3 | 16.9 | 16.7 | 16.5 | 16.3 | 14 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 18.2 | 17.4 | 17.2 | 17.1 | 17 | 16.9 | 16.5 | 16 | 7.9 | 5.2 | 1.8 | 12.7 | 10.6 | 7.9 | 3 | 0.9 | 0 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 28.6 | 26.9 | 26.1 | 25.4 | 24.8 | 24.6 | 23.2 | 21.8 | 14.5 | 10.8 | 6.4 | 3.4 | 1.6 | 0 | 11.2 | 8.8 | 6.3 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 28.6 | 26.2 | 24.5 | 23.4 | 21.5 | 19.1 | 15.8 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 28.6 | 25.8 | 23.6 | 21.5 | 19.2 | 17.1 | 13.2 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 28.6 | 26.6 | 25.4 | 24.5 | 22.8 | 20.7 | 17.9 | 15.7 | 7.1 | 2.8 | 0 | 3.5 | 0 | 0 | 3 | 0.9 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.6 | 18.5 | 18.4 | 18.4 | 18.3 | 18.3 | 18.2 | 18.1 | 17.8 | 17.5 | 14.9 | 14.9 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.5 | 14
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.6 | 18.4 | 18.2 | 18.1 | 17.7 | 15 | 14.7 | 14.1 | 13.6 | 13.3 | 13 | 12.6 | 12.3 | 12 | 11.7 | 11.4 | 11.1 | 9.4 | 8
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.6 | 18.3 | 18.1 | 17.7 | 17.4 | 14.8 | 14.3 | 13.7 | 13.2 | 12.9 | 12.5 | 12.2 | 11.9 | 11.6 | 11.3 | 11.1 | 10.8 | 9.1 | 7.9
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.6 | 18.5 | 18.3 | 18.2 | 17.8 | 17.4 | 14.8 | 14.3 | 13.8 | 13.6 | 13.4 | 13.2 | 13.1 | 12.9 | 12.8 | 12.7 | 12.5 | 11.4 | 10.3
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 28.6 | 26.9 | 26.1 | 25.4 | 24.8 | 24.6 | 23.2 | 21.8 | 14.5 | 10.8 | 6.4 | 3.4 | 1.6 | 0 | 11.2 | 8.8 | 6.3 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 28.6 | 26.2 | 24.5 | 23.4 | 21.5 | 19.1 | 15.8 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 28.6 | 25.8 | 23.6 | 21.5 | 19.2 | 17.1 | 13.2 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 28.6 | 26.6 | 25.4 | 24.5 | 22.8 | 20.7 | 17.9 | 15.7 | 7.1 | 2.8 | 0 | 3.5 | 0 | 0 | 3 | 0.9 | 0 | 0 | 0
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 31.7 | 31.6 | 31.4 | 31.2 | 31.1 | 31 | 30.8 | 30.5 | 30.2 | 29.9 | 29.5 | 29.3 | 29.1 | 29 | 28.8 | 28.7 | 28.6 | 27.6 | 25.8
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 31.7 | 31.5 | 31.1 | 30.8 | 30.4 | 30 | 29.6 | 29.2 | 28.8 | 28.3 | 27.8 | 27.4 | 25.8 | 25.5 | 25.1 | 24.6 | 24.2 | 21.8 | 19.5
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 31.7 | 31.3 | 30.8 | 30.5 | 30 | 29.5 | 29 | 28.4 | 27.8 | 27.3 | 25.8 | 25.5 | 25.1 | 24.6 | 24.1 | 23.7 | 23.2 | 20.5 | 18.3
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 31.7 | 31.6 | 31.3 | 31 | 30.7 | 30.3 | 29.9 | 29.6 | 29.2 | 28.7 | 28.3 | 27.9 | 27.7 | 27.4 | 25.9 | 25.9 | 25.7 | 24.1 | 22.2
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.3 | 19.2 | 19 | 18.9 | 18.8 | 18.7 | 18.5 | 18.4 | 18.1 | 17.9 | 14.4 | 14.3 | 14.1 | 14.1 | 13.8 | 13.3 | 12.6 | 11.1 | 9.2
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.3 | 19 | 18.6 | 18.4 | 18.3 | 18.1 | 18 | 17.9 | 14.5 | 14 | 12.5 | 10.5 | 9.4 | 8.3 | 7.4 | 6.7 | 6 | 1.9 | 0
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.3 | 18.8 | 18.4 | 18.1 | 17.9 | 17.8 | 14.5 | 14.1 | 12.9 | 11.1 | 8.4 | 7.6 | 6.8 | 5.9 | 5.3 | 4.6 | 3.9 | 0 | 0
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.3 | 19.1 | 18.9 | 18.7 | 18.5 | 18.4 | 18.2 | 18 | 17.9 | 14.4 | 13.6 | 12.2 | 11.3 | 10.8 | 10.5 | 10.2 | 9.8 | 6.9 | 3.8
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 56.6 | 56.5 | 56.2 | 53.7 | 53.5 | 53.4 | 53 | 52.1 | 46.5 | 42.5 | 37.5 | 33.9 | 31.7 | 29.9 | 35.7 | 32.9 | 30 | 18.7 | 4.7
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 56.6 | 56.2 | 53.5 | 53.1 | 51.9 | 49.2 | 46.1 | 43.4 | 29.7 | 22.2 | 12.2 | 13.6 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 56.6 | 54.2 | 53.2 | 52.2 | 49.1 | 46.3 | 42.7 | 36.5 | 19 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 56.6 | 56.4 | 53.7 | 53.5 | 53.2 | 51.2 | 48.7 | 46.7 | 39.9 | 34.7 | 26.5 | 29.5 | 24.6 | 20.9 | 31.5 | 27.9 | 22.9 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.6 | 0.6 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.4 | 8.4 | 8.4 | 7.8 | 7.8 | 7.7 | 7.7 | 7.7 | 7.5 | 7.2 | 6.8 | 6.5 | 6.4 | 6.2 | 6.1 | 6 | 5.8 | 4.8 | 3.6
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.4 | 8.4 | 7.8 | 7.7 | 7.7 | 7.6 | 7.5 | 7.3 | 7 | 6.4 | 5.8 | 5.1 | 4.5 | 3.9 | 3.5 | 3 | 2.6 | 0 | 0
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.4 | 7.8 | 7.7 | 7.7 | 7.6 | 7.5 | 7.3 | 6.9 | 6.2 | 5.6 | 4.7 | 4.3 | 3.8 | 3.3 | 3 | 2.6 | 2.2 | 0 | 0
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.4 | 8.4 | 7.8 | 7.8 | 7.7 | 7.7 | 7.6 | 7.5 | 7.3 | 7 | 6.4 | 6 | 5.7 | 5.4 | 5.2 | 5 | 4.7 | 2.9 | 1.1
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.9 | 13.9 | 13.9 | 13.8 | 13.8 | 13.8 | 13.7 | 13.6 | 13.6 | 13.5 | 13.4 | 13.4 | 13.4 | 13.4 | 13.3 | 12.9 | 12.4 | 11.8 | 6.5
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.9 | 13.9 | 13.8 | 13.8 | 13.6 | 13.4 | 13.4 | 13.3 | 13.3 | 13.2 | 12.2 | 11.1 | 9 | 5.3 | 2.8 | 0 | 0 | 0 | 0
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.9 | 13.9 | 13.8 | 13.6 | 13.5 | 13.4 | 13.4 | 13.3 | 13 | 12 | 7 | 4.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.9 | 13.9 | 13.9 | 13.8 | 13.7 | 13.5 | 13.4 | 13.4 | 13.3 | 13.3 | 13 | 12.1 | 11.6 | 11.5 | 11.3 | 10.2 | 8.9 | 0 | 0
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10 | 9.9 | 9.8 | 9.7 | 9.7 | 9.6 | 9.5 | 9.4 | 9.3 | 9.1 | 8.9 | 8.8 | 8.8 | 8.7 | 16.9 | 16.9 | 16.9 | 16.6 | 15.1
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10 | 9.9 | 9.7 | 9.6 | 9.3 | 9.1 | 9 | 8.9 | 8.7 | 8.5 | 8.3 | 16.5 | 15.1 | 15 | 15 | 14.9 | 14.8 | 14.2 | 13.7
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10 | 9.8 | 9.6 | 9.4 | 9.2 | 9.1 | 9 | 8.8 | 8.5 | 8.3 | 8 | 15.1 | 15 | 15 | 14.9 | 14.8 | 14.7 | 14.2 | 13.8
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10 | 9.9 | 9.7 | 9.6 | 9.4 | 9.2 | 9.1 | 9 | 8.8 | 8.7 | 8.5 | 16.7 | 16.6 | 16.6 | 16.6 | 16.5 | 15.1 | 14.9 | 14.6
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.3 | 10.3 | 10.2 | 10.1 | 10 | 10 | 10 | 9.9 | 9.7 | 9.3 | 8.8 | 8.5 | 8.3 | 8.1 | 7.6 | 6.6 | 5.6 | 3 | 0
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.3 | 10.2 | 10 | 10 | 9.9 | 9.9 | 9.7 | 9.6 | 9.2 | 8.5 | 6.1 | 2.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.3 | 10.1 | 10 | 9.9 | 9.8 | 9.7 | 9.5 | 9 | 6.9 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.3 | 10.3 | 10.1 | 10 | 10 | 9.9 | 9.9 | 9.8 | 9.4 | 9 | 7.4 | 5.1 | 3.5 | 2.6 | 2.1 | 1.5 | 0.9 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.1 | 5 | 4.9 | 4.8 | 4.7 | 4.6 | 4.3 | 4.1 | 3.5 | 2.9 | 2.2 | 1.7 | 1.4 | 1.2 | 1.3 | 1.2 | 1 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.1 | 4.9 | 4.6 | 4.3 | 4.1 | 3.8 | 3.4 | 3 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.1 | 4.9 | 4.4 | 4.1 | 3.8 | 3.5 | 3 | 2.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.1 | 5 | 4.7 | 4.6 | 4.4 | 4.1 | 3.7 | 3.4 | 2.7 | 2.1 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.2 | 14.2 | 14 | 11.9 | 11.8 | 11.7 | 11.4 | 11.2 | 10.6 | 9.8 | 8.8 | 8.2 | 7.8 | 7.4 | 7 | 6.1 | 5.3 | 2.6 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.2 | 14.1 | 11.7 | 11.5 | 11.2 | 10.9 | 10.5 | 10.1 | 9.1 | 7.8 | 5.6 | 2.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.2 | 12 | 11.6 | 11.2 | 10.9 | 10.5 | 9.9 | 8.6 | 6.4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.2 | 14.1 | 11.9 | 11.7 | 11.5 | 11.2 | 10.8 | 10.5 | 9.7 | 8.7 | 6.9 | 4.9 | 3.4 | 2.5 | 2 | 1.4 | 0.7 | 0 | 0
Walpole 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.5 | 5.5 | 5.4 | 5.4 | 5.4 | 5.4 | 5.2 | 5 | 4.9 | 4.8 | 4.6 | 4.5 | 4.4 | 4.2 | 4.1 | 4 | 3.9 | 3.3 | 2.6
Walpole 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.5 | 5.4 | 5.4 | 5.2 | 5 | 4.9 | 4.4 | 4 | 3.5 | 3 | 2.4 | 1.9 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.5 | 5.4 | 5.4 | 5.2 | 5 | 4.9 | 4.5 | 4.1 | 3.8 | 3.4 | 3.1 | 2.7 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.5 | 5.5 | 5.4 | 5.4 | 5.4 | 5.3 | 5.1 | 4.9 | 4.7 | 4.5 | 4.2 | 4 | 3.8 | 3.6 | 3.4 | 3.1 | 2.8 | 1.5 | 0.6
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.4 | 18.9 | 18.8 | 18.6 | 18.5 | 18.4 | 18.3 | 18.2 | 18.1 | 18 | 17.8 | 17.7 | 17.6 | 17.6 | 17.5 | 17.5 | 17.5 | 14.3 | 14.1
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.4 | 18.7 | 18.4 | 18.2 | 18 | 17.8 | 17.6 | 17.5 | 14.5 | 14.4 | 14.2 | 13.9 | 13.6 | 13.2 | 12.9 | 12.6 | 12.3 | 2.9 | 0
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.4 | 18.6 | 18.1 | 17.8 | 17.5 | 17.4 | 14.4 | 14.3 | 13.9 | 13.4 | 13.1 | 12.9 | 12.7 | 12.4 | 12.2 | 12 | 10.9 | 1.8 | 0
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.4 | 18.8 | 18.5 | 18.3 | 18.1 | 17.9 | 17.7 | 17.6 | 17.5 | 17.5 | 14.4 | 14.3 | 14.3 | 14.2 | 14.1 | 14.1 | 14 | 13.2 | 7.6
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.2 | 20.3 | 20.2 | 20.2 | 20.1 | 20.1 | 20 | 20 | 20 | 19.9 | 19.9 | 19.9 | 19.9 | 19.9 | 19.9 | 19.9 | 19.9 | 19.6 | 19.4
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.2 | 20.3 | 20.2 | 20.2 | 20.1 | 20 | 19.9 | 19.8 | 19.8 | 19.7 | 19.6 | 19.5 | 19.4 | 19.3 | 19.2 | 19.1 | 19 | 18.5 | 18
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.2 | 20.3 | 20.2 | 20 | 19.9 | 19.7 | 19.6 | 19.4 | 19.3 | 19.2 | 19 | 19 | 18.9 | 18.8 | 18.8 | 18.7 | 18.6 | 18 | 17.6
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.2 | 20.3 | 20.2 | 20.2 | 20.1 | 20.1 | 20 | 20 | 20 | 19.9 | 19.9 | 19.9 | 19.9 | 19.9 | 19.9 | 19.8 | 19.7 | 19.4 | 19
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.4 | 2.3 | 2.2 | 2 | 1.6 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.4 | 2.2 | 1.9 | 1.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.4 | 2.1 | 1.7 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.4 | 2.3 | 2.1 | 1.9 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.3 | 12.1 | 11.8 | 11.5 | 11.3 | 11 | 10.7 | 10.4 | 10.2 | 9.8 | 9.4 | 9.1 | 9.1 | 9 | 8.8 | 8.7 | 8.8 | 7.6 | 6.3
West Burton 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.3 | 11.7 | 10.9 | 10.5 | 10.1 | 9.7 | 9.2 | 8.7 | 8.3 | 7.9 | 7.5 | 6.9 | 6.3 | 5.7 | 5.1 | 4.6 | 4.1 | 0.9 | 0
West Burton 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.3 | 11.5 | 10.4 | 9.8 | 9.1 | 8.5 | 7.9 | 7.3 | 6.7 | 6 | 5.3 | 4.7 | 4.2 | 3.7 | 3.2 | 2.7 | 1.9 | 0 | 0
West Burton 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.3 | 12 | 11.4 | 11 | 10.7 | 10.3 | 9.9 | 9.5 | 9.2 | 8.9 | 8.6 | 8.3 | 8.1 | 7.9 | 7.8 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 57.6 | 56.3 | 54.6 | 54 | 53.2 | 52.1 | 50.8 | 50 | 46.9 | 45 | 40.3 | 37 | 34.9 | 33.3 | 31.4 | 29.6 | 28.4 | 18.9 | 2.8
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 57.6 | 54.6 | 53.1 | 51.8 | 50.1 | 48.3 | 45.8 | 44.2 | 39.5 | 35.7 | 29.1 | 18.1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 57.6 | 54.1 | 52 | 50.2 | 48 | 45.7 | 42.8 | 37.9 | 29.5 | 22.9 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 57.6 | 55.2 | 54 | 53 | 51.7 | 50.2 | 48.1 | 47.1 | 43.3 | 41.2 | 35.1 | 30.9 | 27.1 | 21.9 | 18.4 | 14.2 | 1.9 | 0 | 0
West Burton 132kV | LINCOLN No 2 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 27.1 | 27.1 | 27.1 | 27.1 | 24.9 | 24.6 | 24.2 | 23.8 | 23.4 | 22.9 | 22.4 | 21.4 | 20.6 | 19.8 | 19.2 | 18.8 | 18.5 | 17.4 | 2.8
West Burton 132kV | LINCOLN No 2 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 27.1 | 25.4 | 24.9 | 24.5 | 24 | 23.3 | 22.4 | 20.8 | 19.1 | 17 | 15.8 | 14.8 | 8 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN No 2 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 27.1 | 25.3 | 24.6 | 24.1 | 23.5 | 22.6 | 20.7 | 18.7 | 16.9 | 15.6 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN No 2 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 27.1 | 27.1 | 27.1 | 24.8 | 24.4 | 23.6 | 22.7 | 21.4 | 19.9 | 17.8 | 16.5 | 15.8 | 15 | 14.4 | 13.7 | 13 | 1.9 | 0 | 0
West Burton 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.9 | 15 | 15 | 15.2 | 15.3 | 15 | 13 | 12.8 | 11.8 | 10.5 | 8.9 | 7.5 | 6.9 | 6.5 | 6.1 | 5.8 | 5.6 | 4.6 | 3.3
West Burton 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.9 | 14.9 | 13.1 | 12.7 | 11.2 | 10.2 | 8.2 | 5.7 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.9 | 14.9 | 13.1 | 12.1 | 11.3 | 9.9 | 7.4 | 4.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.9 | 14.9 | 13.2 | 12.8 | 11.4 | 10.4 | 8.4 | 6 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 5.9 | 3.3 | 3.3 | 3.2 | 2.3 | 2.2 | 2 | 1.7 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 3.3 | 3.2 | 3 | 2.2 | 2 | 1.7 | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 3.3 | 3.1 | 2.9 | 2.8 | 2.6 | 2.3 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 3.3 | 3.3 | 3.2 | 3.1 | 3.1 | 2.9 | 2.7 | 2.3 | 1.8 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.5 | 12.4 | 12.3 | 12.2 | 12.1 | 11.9 | 11.8 | 13 | 12.8 | 12.5 | 12.1 | 11.8 | 11.6 | 11.5 | 11.4 | 11.3 | 11.2 | 10 | 8.6
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.5 | 12.3 | 12 | 11.7 | 11.5 | 11.3 | 11 | 12.4 | 12 | 11.4 | 10.7 | 10 | 9.3 | 8.6 | 8.1 | 7.6 | 7.1 | 4.2 | 1.2
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.5 | 12.2 | 11.8 | 11.4 | 11.1 | 10.8 | 10.5 | 11.4 | 10.5 | 9.7 | 8.8 | 8.3 | 7.7 | 7.1 | 6.7 | 6.3 | 5.8 | 3 | 1.1
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.5 | 12.4 | 12.2 | 12 | 11.8 | 11.7 | 11.5 | 12.8 | 12.5 | 12.1 | 11.6 | 11.2 | 10.9 | 10.6 | 10.4 | 10.2 | 10 | 7.9 | 5.5
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.8 | 15.5 | 15.4 | 15.4 | 15.3 | 15.5 | 15.5 | 15.4 | 15.2 | 14.5 | 14.2 | 14 | 13.9 | 13.9 | 14 | 14 | 14.1 | 13.6 | 12.8
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.8 | 15.3 | 15.1 | 15 | 14.7 | 14 | 13 | 12.5 | 11.9 | 11.2 | 10.6 | 10.1 | 9.9 | 9.6 | 9.4 | 9.2 | 8.9 | 7.6 | 6.3
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.8 | 15.2 | 14.9 | 14.5 | 13.9 | 13 | 12.4 | 11.6 | 10.8 | 10.1 | 9.5 | 9.3 | 9.1 | 8.9 | 8.8 | 8.6 | 8.3 | 6.8 | 5.6
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.8 | 15.5 | 15.3 | 15.2 | 15 | 14.3 | 13.6 | 12.8 | 12.2 | 11.6 | 10.9 | 10.7 | 10.6 | 10.6 | 10.6 | 10.5 | 10.4 | 9.5 | 8.5
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.7 | 16.7 | 16.6 | 16.5 | 16.5 | 16.4 | 16.3 | 16 | 15.8 | 15.4 | 14.9 | 14.4 | 14.2 | 14 | 13.8 | 13.6 | 13.5 | 12 | 10.1
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.7 | 16.6 | 16.4 | 16.4 | 16.3 | 16 | 15.9 | 15.6 | 15.1 | 14.3 | 13.3 | 12.4 | 11.5 | 10.6 | 10 | 9.3 | 8.6 | 4.2 | 0.8
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.7 | 16.5 | 16.3 | 16 | 15.9 | 15.8 | 15.5 | 14.9 | 13.8 | 12.9 | 11.9 | 11.2 | 10.6 | 9.9 | 9.3 | 8.7 | 8 | 4 | 2
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.7 | 16.7 | 16.5 | 16.5 | 16.4 | 16.4 | 16 | 15.9 | 15.6 | 15.2 | 14.4 | 13.9 | 13.4 | 13 | 12.7 | 12.3 | 11.9 | 8.9 | 5.8
West Burton 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 33.5 | 33.8 | 33.6 | 33.8 | 33.6 | 32.9 | 32 | 31.5 | 30.1 | 28.5 | 26.7 | 25.2 | 24.5 | 24 | 23.5 | 23.1 | 22.9 | 21.1 | 19
West Burton 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 33.5 | 33.2 | 32.4 | 31.4 | 29.5 | 28.2 | 25.9 | 23.1 | 20 | 16.8 | 12.6 | 10.3 | 8.2 | 6.2 | 4.1 | 2 | 0 | 0 | 0
West Burton 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 33.5 | 33 | 31.9 | 30.2 | 29 | 27.1 | 24.2 | 20.8 | 17.2 | 14 | 9.5 | 7.6 | 5.7 | 4 | 2 | 0 | 0 | 0 | 0
West Burton 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 33.5 | 33.4 | 32.8 | 31.9 | 30.1 | 28.8 | 26.6 | 23.9 | 20.9 | 18 | 14 | 12.2 | 10.6 | 9.2 | 7.9 | 1.7 | 0 | 0 | 0
West Burton 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.4 | 18.1 | 18 | 17.9 | 17.8 | 17.7 | 19.7 | 19.5 | 19.4 | 19.3 | 19.1 | 19.1 | 19 | 19 | 19 | 19 | 19 | 18.6 | 18.2
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.4 | 18 | 17.8 | 17.6 | 17.4 | 17.3 | 18.8 | 18.6 | 18.5 | 18.3 | 18.2 | 18.1 | 18 | 17.9 | 17.8 | 14.5 | 14.4 | 13.6 | 12.5
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.4 | 17.9 | 17.6 | 17.4 | 17.2 | 17.1 | 18.3 | 18 | 17.9 | 17.8 | 14.5 | 14.4 | 14.4 | 14.3 | 14.2 | 14 | 13.8 | 12.5 | 11.1
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.4 | 18.1 | 17.9 | 17.7 | 17.6 | 17.4 | 19.1 | 18.8 | 18.7 | 18.6 | 18.5 | 18.4 | 18.4 | 18.3 | 18.3 | 18.2 | 18.1 | 17.8 | 14.2
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.4 | 16.3 | 16 | 15.8 | 15.6 | 15.5 | 13.8 | 13.6 | 13.1 | 12.5 | 11.8 | 11.3 | 10.9 | 10.7 | 10.4 | 10.1 | 9.8 | 7.6 | 5.5
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.4 | 15.9 | 15.2 | 14.7 | 14.2 | 13.6 | 11.7 | 11.3 | 10.6 | 9.5 | 8.3 | 7.1 | 5.9 | 4.7 | 3.7 | 2.8 | 1.8 | 0 | 0
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.4 | 15.8 | 15.1 | 14.3 | 13.8 | 13.3 | 11.5 | 10.5 | 9.1 | 7.8 | 6.3 | 5.3 | 3.5 | 2.3 | 1.5 | 0.7 | 0 | 0 | 0
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.4 | 16 | 15.4 | 14.9 | 14.4 | 13.9 | 12 | 11.7 | 11.1 | 10.4 | 9.3 | 8.6 | 7.9 | 7.3 | 6.8 | 6.3 | 5.7 | 1.5 | 0
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9 | 9 | 8.9 | 8.9 | 8.8 | 8.8 | 8.8 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.6 | 8.6
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9 | 8.9 | 8.8 | 8.8 | 8.7 | 8.7 | 8.6 | 8.6 | 8.6 | 8.6 | 8.5 | 8.5 | 7.7 | 7.7 | 7.6 | 7.6 | 7.6 | 7.3 | 7
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9 | 8.9 | 8.7 | 8.7 | 8.6 | 8.6 | 8.5 | 7.7 | 7.7 | 7.6 | 7.6 | 7.6 | 7.5 | 7.5 | 7.5 | 7.4 | 7.4 | 7 | 6.4
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9 | 9 | 8.9 | 8.8 | 8.8 | 8.8 | 8.7 | 8.7 | 8.7 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.5 | 7.6
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.1 | 18.8 | 18.7 | 18.6 | 18.5 | 18.4 | 18.2 | 18.1 | 18 | 17.8 | 17.7 | 17.6 | 17.6 | 17.6 | 14.8 | 14.8 | 14.8 | 14.3 | 13.3
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.1 | 18.6 | 18.4 | 18.2 | 18.1 | 18 | 17.6 | 17.5 | 14.8 | 14.5 | 14.1 | 13.7 | 13.2 | 12.6 | 12.2 | 11.8 | 11.3 | 8.6 | 6
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.1 | 18.5 | 18.1 | 17.9 | 17.8 | 17.7 | 14.8 | 14.5 | 13.9 | 13.3 | 12.6 | 12.2 | 11.8 | 11.3 | 11 | 10.6 | 10 | 7.2 | 5
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.1 | 18.7 | 18.5 | 18.4 | 18.3 | 18.2 | 17.8 | 17.7 | 17.6 | 14.8 | 14.6 | 14.5 | 14.4 | 14.2 | 14.1 | 14 | 13.7 | 12 | 9.9
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.4 | 12.4 | 12.3 | 12.3 | 12.3 | 12.2 | 12.2 | 12 | 11.7 | 11.1 | 10.7 | 10.5 | 10.3 | 10.2 | 10.1 | 10 | 9.9 | 9 | 8
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.4 | 12.4 | 12.2 | 12 | 11.8 | 11.5 | 11.1 | 10.9 | 10.5 | 10.1 | 9.6 | 9 | 8.6 | 6.9 | 6.5 | 6.1 | 5.5 | 1.5 | 0
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.4 | 12.4 | 12.1 | 12 | 11.6 | 11.4 | 11 | 10.6 | 9.9 | 9.4 | 8.8 | 8.4 | 7.6 | 5.9 | 5.4 | 4.8 | 4.2 | 2.1 | 0
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.4 | 12.4 | 12.3 | 12 | 11.8 | 11.6 | 11.2 | 11 | 10.7 | 10.4 | 9.9 | 9.5 | 9.2 | 8.4 | 8.2 | 8 | 7.8 | 5.9 | 3.1
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.7 | 15.6 | 15.5 | 15.4 | 15.2 | 15 | 14 | 13.8 | 13.7 | 13.4 | 13.1 | 12.8 | 12.7 | 12.6 | 12.5 | 11.5 | 11.5 | 11 | 10.4
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.7 | 15.3 | 14.9 | 14.4 | 13.8 | 13 | 11.1 | 10.3 | 9.5 | 9.3 | 8.9 | 8.5 | 8.2 | 7.8 | 7.5 | 5.3 | 5 | 3.5 | 2
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.7 | 15.2 | 14.6 | 13.9 | 13 | 11.9 | 9.7 | 8.7 | 8.2 | 7.9 | 7.6 | 7.3 | 7 | 6.8 | 6.5 | 4.7 | 4.4 | 2.6 | 0.9
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.7 | 15.5 | 15.1 | 14.6 | 14 | 13.1 | 11.2 | 10.4 | 9.9 | 9.6 | 9.3 | 9.2 | 9.2 | 9.1 | 9 | 7.9 | 7.7 | 6.7 | 5.6
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.4 | 14.3 | 13.9 | 13.6 | 13.3 | 13 | 12.5 | 12.4 | 11.4 | 10.2 | 8.7 | 7.7 | 7.2 | 6.9 | 6.5 | 6.9 | 6.4 | 2.8 | 0
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.4 | 13.9 | 13.1 | 12.3 | 11.2 | 9.8 | 9.6 | 9.2 | 7.6 | 5.7 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.4 | 13.8 | 12.8 | 11.5 | 10.5 | 9.9 | 9.6 | 7.8 | 4.8 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.4 | 14 | 13.3 | 12.6 | 11.6 | 10.3 | 9.9 | 9.6 | 8.4 | 7.2 | 5.3 | 4 | 2.9 | 2 | 1.4 | 0.7 | 0 | 0 | 0
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.3 | 4.2 | 4.1 | 4 | 3.9 | 3.9 | 16.3 | 16.2 | 16 | 15.7 | 15.4 | 15.3 | 15.1 | 15 | 14.7 | 14.5 | 14.3 | 11.3 | 7.2
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.3 | 4.1 | 3.9 | 3.8 | 0 | 0 | 15.6 | 15.5 | 15.2 | 13.9 | 10.6 | 8 | 5.6 | 3.1 | 1.3 | 0 | 0 | 0 | 0
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.3 | 4 | 3.8 | 3.4 | 0 | 0 | 15.5 | 15.1 | 13 | 9.6 | 6.5 | 4.2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.3 | 4.2 | 4 | 3.9 | 0.7 | 0 | 15.8 | 15.7 | 15.5 | 14.8 | 12.6 | 10.9 | 9.4 | 8.1 | 7.1 | 1.6 | 0 | 0 | 0
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.5 | 15.8 | 15.8 | 15.7 | 15.7 | 15.7 | 15.6 | 15.6 | 15.5 | 15.3 | 15.1 | 14.9 | 14.9 | 14.8 | 14.8 | 14.8 | 14.8 | 14.2 | 13.6
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.5 | 15.7 | 15.6 | 15.5 | 15.4 | 15.3 | 15.1 | 14.9 | 14.6 | 14.5 | 14.2 | 14 | 13.6 | 13.3 | 13 | 12.7 | 12.4 | 10.7 | 9.3
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.5 | 15.6 | 15.4 | 15.1 | 14.8 | 14.6 | 14.4 | 14.1 | 13.8 | 13.5 | 13.1 | 12.9 | 12.6 | 12.3 | 12.1 | 11.8 | 11.5 | 9.7 | 8.3
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.5 | 15.8 | 15.7 | 15.6 | 15.5 | 15.4 | 15.3 | 15.2 | 15.1 | 14.9 | 14.8 | 14.7 | 14.6 | 14.5 | 14.4 | 14.2 | 14 | 13 | 11.9
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.7 | 15.9 | 15.8 | 15.7 | 15.7 | 15.6 | 15.4 | 15.3 | 15.2 | 15 | 14.6 | 13.9 | 13.3 | 12.8 | 12.5 | 12.4 | 12.4 | 11.7 | 11
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.7 | 15.8 | 15.6 | 15.4 | 15.3 | 15 | 14.8 | 13.8 | 12.7 | 10.8 | 10.1 | 9.6 | 9.3 | 8.9 | 8.7 | 8.4 | 8.2 | 6.6 | 4.8
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.7 | 15.8 | 15.5 | 15.2 | 14.8 | 14.5 | 13.6 | 12.2 | 10.8 | 9.8 | 9.3 | 9 | 8.7 | 8.5 | 8.3 | 8 | 7.8 | 5.6 | 4.7
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.7 | 15.9 | 15.7 | 15.5 | 15.4 | 15.1 | 14.7 | 14 | 13 | 11.3 | 10.4 | 10.1 | 10 | 9.9 | 9.8 | 9.7 | 9.5 | 8.4 | 6.8
Willington 132kV | DERBY 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 63.7 | 63.8 | 63.7 | 63.1 | 62.8 | 62.4 | 61.7 | 61.4 | 61.3 | 61 | 60.8 | 60.7 | 60.6 | 60.5 | 60.2 | 60.1 | 60 | 59.4 | 58.6
Willington 132kV | DERBY 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 63.7 | 63.4 | 62.7 | 62.2 | 61.7 | 61.4 | 60.6 | 60.3 | 60 | 59.7 | 59 | 58.6 | 58.2 | 57.9 | 57.7 | 57.5 | 57.4 | 49.8 | 48.1
Willington 132kV | DERBY 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 63.7 | 63.2 | 62.3 | 61.6 | 60.9 | 60.3 | 59.2 | 58.7 | 58.3 | 57.8 | 57.6 | 57.5 | 57.4 | 50.5 | 50.4 | 50.2 | 50 | 47.9 | 45.5
Willington 132kV | DERBY 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 63.7 | 63.8 | 63.1 | 62.7 | 62.3 | 62 | 61.2 | 60.9 | 60.6 | 60.2 | 59.6 | 59.4 | 59.3 | 59.2 | 59.1 | 58.9 | 58.7 | 57.7 | 50.4
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 77.6 | 76.8 | 75 | 74.6 | 74.7 | 74.7 | 94.1 | 93.6 | 92.9 | 91.9 | 90.7 | 89.7 | 89.1 | 88.7 | 88.3 | 87.4 | 87.1 | 74.1 | 73.2
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 77.6 | 74.5 | 74.5 | 73.9 | 72.5 | 70.8 | 88.5 | 87.1 | 86.1 | 85.9 | 73.9 | 73.2 | 72.2 | 70.8 | 69.5 | 66.6 | 65 | 56.6 | 50
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 77.6 | 74.5 | 74.2 | 72.4 | 70.4 | 67.9 | 86.3 | 74.2 | 73.7 | 72.9 | 71.5 | 70.3 | 69 | 67.6 | 66.5 | 63.8 | 62.2 | 53.5 | 47.7
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 77.6 | 74.9 | 74.6 | 74.5 | 73.6 | 72 | 89.5 | 88.3 | 87.3 | 86.5 | 86 | 74.1 | 74 | 73.8 | 73.5 | 72.5 | 71.8 | 66.2 | 60.9
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 58.8 | 58.2 | 57.8 | 57.5 | 57.2 | 56.8 | 59.8 | 59.4 | 59 | 58.6 | 58.1 | 58 | 57.8 | 57.7 | 57.5 | 57.3 | 57.1 | 55.5 | 53.8
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 58.8 | 57.8 | 57.1 | 56.6 | 55.9 | 55.1 | 57.5 | 56.6 | 55.4 | 54.5 | 52.9 | 52 | 51 | 50.1 | 49.4 | 39.6 | 31.6 | 0 | 0
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 58.8 | 57.5 | 56.7 | 55.8 | 54.9 | 51.3 | 55.9 | 54.2 | 52.8 | 50.8 | 49.5 | 48.6 | 44.5 | 33.4 | 26.8 | 16.8 | 8.6 | 0 | 0
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 58.8 | 58 | 57.5 | 57.1 | 56.5 | 55.8 | 58.4 | 57.7 | 57.2 | 56.5 | 55.2 | 54.7 | 54.2 | 53.7 | 53.2 | 52.7 | 52 | 21.6 | 3.7
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.3 | 18.3 | 18.3 | 18.2 | 18.1 | 18 | 17.5 | 17.4 | 17.4 | 17.3 | 17.2 | 17.2 | 17.2 | 17.1 | 17.1 | 17.1 | 17.1 | 16.9 | 16.7
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.3 | 18.3 | 18.1 | 17.8 | 17.6 | 17.5 | 17 | 16.9 | 16.8 | 16.7 | 16.6 | 16.5 | 16.4 | 16.3 | 16.2 | 16.1 | 16 | 15.6 | 14.8
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.3 | 18.3 | 18 | 17.7 | 17.4 | 17.3 | 16.7 | 16.6 | 16.4 | 16.3 | 16.2 | 16.1 | 16 | 15.9 | 15.8 | 15.7 | 15.7 | 14.7 | 14.2
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.3 | 18.3 | 18.1 | 17.9 | 17.7 | 17.6 | 17.1 | 17 | 17 | 16.9 | 16.8 | 16.8 | 16.7 | 16.7 | 16.7 | 16.6 | 16.5 | 16.2 | 15.9
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.2 | 13 | 12.8 | 12.7 | 12.6 | 12.4 | 12.4 | 12.3 | 12.1 | 11.7 | 11.3 | 10.8 | 10.6 | 10.4 | 10.2 | 10.1 | 10.1 | 9.3 | 8.3
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.2 | 12.7 | 12.4 | 12.2 | 11.9 | 11.6 | 11.4 | 10.9 | 10.2 | 9.6 | 9 | 8.5 | 7.9 | 7.3 | 6.9 | 6.5 | 6.2 | 4.2 | 1.7
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.2 | 12.6 | 12.1 | 11.7 | 11.2 | 10.6 | 10.1 | 9.4 | 8.6 | 8 | 7.4 | 7 | 6.6 | 6.2 | 5.8 | 5.4 | 5 | 2.1 | 0
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.2 | 12.9 | 12.7 | 12.5 | 12.3 | 11.9 | 11.6 | 11.1 | 10.5 | 10 | 9.6 | 9.3 | 9 | 8.7 | 8.6 | 8.4 | 8.2 | 3.4 | 1.3
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 58.7 | 54.4 | 52.6 | 51 | 49.3 | 47.3 | 62.3 | 61.7 | 60.7 | 59 | 57.1 | 54.2 | 52.2 | 50.2 | 48.8 | 48.2 | 47.8 | 43.5 | 38.1
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 58.7 | 51.8 | 47.6 | 43.2 | 37.8 | 32.8 | 58.1 | 54.9 | 50.6 | 44.3 | 40 | 36.8 | 33.9 | 31.1 | 28.7 | 24.8 | 22.8 | 0 | 0
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 58.7 | 50.2 | 44.2 | 37.7 | 30.3 | 24 | 52.4 | 47.2 | 41.4 | 36.3 | 32.7 | 30.4 | 28.1 | 24.9 | 20 | 12.5 | 6.4 | 0 | 0
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 58.7 | 53.5 | 50.3 | 46.2 | 41.6 | 37.1 | 59.1 | 56.4 | 52.8 | 47.3 | 42.9 | 41 | 39.5 | 38.2 | 37.2 | 35.3 | 34.1 | 16.1 | 2.7
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.2 | 4.2 | 4.1 | 4 | 3.9 | 3.9 | 3.9 | 3.8 | 3.6 | 3.2 | 2.5 | 2.1 | 1.8 | 1.6 | 1.4 | 0 | 0 | 0 | 0
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.2 | 4.1 | 3.9 | 3.7 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.2 | 4 | 3.7 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.2 | 4.2 | 4 | 3.9 | 0.7 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.2 | 17.2 | 17.1 | 17 | 17 | 17 | 14.7 | 14.7 | 14.5 | 14.2 | 13.9 | 13.7 | 13.6 | 13.5 | 13.4 | 13.3 | 13.3 | 12.5 | 11.7
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.2 | 17.1 | 17 | 16.9 | 16.8 | 16.8 | 14.5 | 14.5 | 14.2 | 13.8 | 13.4 | 13 | 12.6 | 12.1 | 11.9 | 11.6 | 11.3 | 9.7 | 8
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.2 | 17 | 16.9 | 16.8 | 16.7 | 16.6 | 14.3 | 13.9 | 13.4 | 12.9 | 12.4 | 12 | 11.7 | 11.3 | 11.1 | 10.8 | 10.6 | 9.1 | 8.2
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.2 | 17.1 | 17.1 | 17 | 16.9 | 16.9 | 14.7 | 14.6 | 14.4 | 14.1 | 13.7 | 13.4 | 13.2 | 13 | 12.9 | 12.8 | 12.6 | 11.4 | 10
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 22.1 | 21.7 | 21.5 | 21.4 | 21.3 | 21.1 | 19.8 | 19.7 | 19.5 | 19.4 | 19.2 | 19.1 | 19 | 18.8 | 18.8 | 18.8 | 18.8 | 15.4 | 15
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 22.1 | 21.5 | 21.2 | 21 | 20.7 | 20.4 | 19 | 18.8 | 18.7 | 15.3 | 15 | 14.5 | 13.9 | 13.3 | 13 | 12.7 | 12.4 | 10.5 | 8.8
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 22.1 | 21.4 | 21 | 20.7 | 20.3 | 20.1 | 18.7 | 15.4 | 15 | 14.4 | 13.8 | 13.2 | 12.8 | 12.4 | 12.1 | 11.8 | 11.5 | 9.5 | 7.9
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 22.1 | 21.6 | 21.4 | 21.2 | 20.9 | 20.7 | 19.2 | 18.9 | 18.8 | 15.4 | 15.3 | 15.1 | 14.9 | 14.6 | 14.5 | 14.4 | 14.2 | 12.9 | 11.5
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.3 | 15.2 | 15.2 | 15.2 | 15.2 | 15.1 | 15.1 | 15.1 | 14.9 | 14.8 | 14.6 | 14.4 | 14.3 | 14.3 | 14.2 | 14.1 | 14.1 | 13.6 | 13.1
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.3 | 15.2 | 15.2 | 15.2 | 15.1 | 15.1 | 15 | 14.9 | 14.7 | 14.5 | 14.2 | 13.9 | 13.6 | 13.3 | 12.3 | 11 | 9.9 | 0 | 0
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.3 | 15.2 | 15.2 | 15.1 | 15.1 | 15.1 | 15 | 14.7 | 14.4 | 14.1 | 13.7 | 13.5 | 12.2 | 9.6 | 8.6 | 7.6 | 6.6 | 0 | 0
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.3 | 15.2 | 15.2 | 15.2 | 15.2 | 15.1 | 15.1 | 15 | 14.9 | 14.7 | 14.4 | 14.3 | 14.1 | 13.9 | 13.9 | 13.7 | 13.6 | 8.5 | 4.4
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 24.7 | 24.7 | 24.6 | 24.4 | 24.3 | 24.1 | 23.9 | 23.6 | 23.1 | 22.4 | 21.6 | 20.9 | 20.3 | 19.9 | 19.5 | 19.2 | 18.8 | 16 | 13.7
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 24.7 | 24.4 | 24 | 23.4 | 22.7 | 21.8 | 21 | 20.1 | 18.8 | 17.7 | 16.5 | 15.3 | 14.1 | 12.8 | 11.8 | 10.7 | 9.6 | 3.8 | 0
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 24.7 | 24.3 | 23.7 | 22.8 | 22 | 20.8 | 19.7 | 18.3 | 16.9 | 15.6 | 14.2 | 13 | 12 | 10.8 | 10 | 9 | 8 | 2.4 | 0
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 24.7 | 24.6 | 24.3 | 23.8 | 23.4 | 22.8 | 22.1 | 21.4 | 20.5 | 19.5 | 18.3 | 17.3 | 16.5 | 15.7 | 15 | 14.3 | 13.5 | 8.6 | 5
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.9 | 5.8 | 5.8 | 5.8 | 5.7 | 5.6 | 5.4 | 4.8 | 4 | 3.1 | 2.4 | 2 | 1.7 | 1.5 | 2.1 | 1.8 | 0 | 0
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.9 | 5.8 | 5.7 | 5.6 | 5.4 | 6.1 | 5.8 | 4.9 | 3.7 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.8 | 5.7 | 5.6 | 5.5 | 5.4 | 6 | 5 | 3.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.9 | 5.8 | 5.8 | 5.7 | 5.6 | 6.3 | 6.1 | 5.4 | 4.6 | 3.4 | 2.5 | 1.7 | 1.1 | 0.7 | 0 | 0 | 0 | 0
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.9 | 17.8 | 17.7 | 17.6 | 17.4 | 17.3 | 17.1 | 16.9 | 16.6 | 16.2 | 15.7 | 15.3 | 14.9 | 14.7 | 14.5 | 14.4 | 14.3 | 13.5 | 12.4
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.9 | 17.7 | 17.4 | 17.2 | 16.9 | 16.5 | 15.9 | 15.4 | 14.7 | 13.9 | 13.1 | 12.3 | 11.6 | 11 | 10.5 | 10 | 9.6 | 6.8 | 4.9
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.9 | 17.6 | 17.2 | 16.8 | 16.5 | 15.8 | 15.2 | 14.4 | 13.4 | 12.7 | 11.9 | 11.3 | 10.7 | 10.3 | 9.9 | 9.5 | 9 | 6.5 | 4.9
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.9 | 17.8 | 17.6 | 17.4 | 17.1 | 16.7 | 16.2 | 15.7 | 15.2 | 14.6 | 13.9 | 13.5 | 13 | 12.8 | 12.6 | 12.4 | 12.1 | 10.5 | 8.8
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.2 | 15.2 | 15.1 | 15.1 | 15.1 | 15 | 15.2 | 15.1 | 14.6 | 13.8 | 13.2 | 12.8 | 12.5 | 12.3 | 12.1 | 11.9 | 11.7 | 10.2 | 8.6
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.2 | 15.1 | 15 | 14.8 | 14.5 | 14.2 | 13.9 | 13.6 | 12.9 | 12.1 | 11.2 | 10.3 | 9.5 | 7.4 | 6.8 | 6.1 | 5.5 | 1.5 | 0
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.2 | 15.1 | 14.9 | 14.7 | 14.3 | 14 | 13.7 | 12.9 | 11.7 | 10.8 | 9.7 | 9 | 7.9 | 5.9 | 5.4 | 4.8 | 4.2 | 2.1 | 0
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.2 | 15.2 | 15 | 14.8 | 14.6 | 14.3 | 14.1 | 13.8 | 13.2 | 12.6 | 11.8 | 11.3 | 10.8 | 9.8 | 9.4 | 9.1 | 8.7 | 5.8 | 3.1
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.5 | 17.5 | 17.4 | 17.3 | 17.3 | 17.2 | 17.2 | 17.1 | 17.1 | 17 | 16.9 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.7 | 16.5
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.5 | 17.4 | 17.3 | 17.2 | 17.1 | 17 | 16.9 | 16.7 | 16.6 | 16.6 | 16.5 | 16.4 | 16.3 | 16.2 | 16.2 | 16.1 | 16.1 | 14.9 | 14.5
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.5 | 17.4 | 17.2 | 17 | 16.9 | 16.7 | 16.6 | 16.4 | 16.3 | 16.2 | 16.1 | 16.1 | 16 | 16 | 15.9 | 15.9 | 15.9 | 14.6 | 14.1
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.5 | 17.5 | 17.4 | 17.3 | 17.2 | 17.1 | 17 | 16.9 | 16.8 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.6 | 16.6 | 16.3 | 16
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.8 | 17.7 | 17.7 | 17.6 | 17.6 | 17.6 | 17.5 | 15 | 14.9 | 14.8 | 14.7 | 14.7 | 14.6 | 14.6 | 14.6 | 14.6 | 14.6 | 14.2 | 13.7
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.8 | 17.6 | 17.5 | 17.5 | 14.8 | 14.7 | 14.8 | 14.7 | 14.5 | 14.3 | 14.1 | 13.9 | 13.7 | 13.4 | 13.2 | 11.2 | 11 | 7.2 | 3.1
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.8 | 17.6 | 17.5 | 14.8 | 14.7 | 14.5 | 14.4 | 14.2 | 13.8 | 13.5 | 13.2 | 13 | 12.8 | 12.6 | 12.4 | 10.2 | 9.4 | 4.8 | 1.3
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.8 | 17.7 | 17.6 | 17.6 | 17.6 | 14.8 | 14.9 | 14.8 | 14.6 | 14.5 | 14.3 | 14.3 | 14.2 | 14.2 | 14.1 | 13.3 | 13.1 | 12.2 | 10
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.5 | 8.5 | 8.5 | 8.5 | 8.4 | 8.4 | 8.4 | 8.4 | 8.3 | 7.5 | 7.2 | 7 | 6.8 | 6.7 | 6.6 | 6.5 | 6.3 | 5.4 | 4.3
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.5 | 8.5 | 8.4 | 8.4 | 7.8 | 7.8 | 7.7 | 7.6 | 7.2 | 6.8 | 6.2 | 5.6 | 5.1 | 4.5 | 4.1 | 3.7 | 3.2 | 0.5 | 0
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.5 | 8.4 | 8.4 | 7.8 | 7.7 | 7.6 | 7.6 | 7.3 | 6.6 | 6.1 | 5.5 | 5 | 4.5 | 4.1 | 3.7 | 3.4 | 2.9 | 0.7 | 0
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.5 | 8.5 | 8.5 | 8.4 | 8.4 | 7.8 | 8.3 | 7.7 | 7.5 | 7.2 | 6.8 | 6.5 | 6.2 | 5.9 | 5.7 | 5.5 | 5.2 | 3.5 | 1.8
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 32.1 | 31.7 | 31.5 | 31.3 | 31.1 | 30.8 | 30.4 | 30.1 | 29.7 | 29.3 | 29 | 28.8 | 28.7 | 28.6 | 28.4 | 28.4 | 28.3 | 24.6 | 23.9
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 32.1 | 31.4 | 31 | 30.6 | 30.1 | 29.4 | 28.5 | 28.2 | 24.7 | 24.3 | 23.3 | 22.8 | 22.2 | 21.7 | 21.2 | 20.8 | 20.4 | 18 | 15.6
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 32.1 | 31.2 | 30.6 | 30 | 29.3 | 28.8 | 24.9 | 24.5 | 23.7 | 22.4 | 21.5 | 21 | 20.5 | 20.1 | 19.7 | 19.3 | 18.8 | 16 | 13.6
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 32.1 | 31.6 | 31.3 | 31 | 30.6 | 30 | 29.3 | 28.8 | 28.4 | 24.8 | 24.5 | 24.3 | 24 | 23.7 | 23.5 | 23.1 | 22.7 | 20.9 | 19.2
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.3 | 4.2 | 4.1 | 4 | 4 | 3.9 | 4.2 | 4.1 | 3.9 | 3.5 | 3.1 | 2.7 | 2.5 | 2.5 | 2.4 | 2.3 | 2.2 | 1.4 | 0
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.3 | 4.1 | 3.8 | 3.7 | 3.5 | 3.4 | 3.6 | 3.1 | 2.5 | 2 | 1.5 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.3 | 3.9 | 3.6 | 3.3 | 3.1 | 2.8 | 2.6 | 1.9 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.3 | 4.2 | 4 | 3.9 | 3.8 | 3.7 | 3.7 | 3.3 | 2.9 | 2.6 | 2.2 | 1.9 | 1.7 | 1.5 | 1.4 | 1.3 | 1.1 | 0 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.4 | 14.3 | 13.9 | 13.6 | 13.3 | 13 | 12.5 | 12.3 | 11.4 | 10.2 | 8.7 | 7.7 | 7.2 | 6.9 | 6.4 | 6.9 | 6.4 | 2.8 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.4 | 13.9 | 13.1 | 12.3 | 11.2 | 9.8 | 9.6 | 9.1 | 7.6 | 5.6 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.4 | 13.8 | 12.8 | 11.5 | 10.5 | 9.9 | 9.6 | 7.8 | 4.8 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.4 | 14 | 13.3 | 12.6 | 11.6 | 10.3 | 9.9 | 9.6 | 8.4 | 7.2 | 5.3 | 4 | 2.9 | 2 | 1.4 | 0.7 | 0 | 0 | 0
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.9 | 16.6 | 16.5 | 16.4 | 16.3 | 16.2 | 16.2 | 16.1 | 16 | 15.9 | 15.9 | 15.7 | 15.6 | 15.4 | 15.2 | 15.1 | 15.1 | 14.9 | 13.1
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.9 | 16.4 | 16.2 | 16.1 | 16 | 15.9 | 15.7 | 15.6 | 15.4 | 15 | 14.9 | 13.1 | 12.9 | 12.7 | 12.5 | 12.3 | 12.2 | 11 | 9.8
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.9 | 16.3 | 16 | 15.8 | 15.6 | 15.5 | 15.2 | 15 | 13.2 | 13 | 12.6 | 12.4 | 12.1 | 11.9 | 11.8 | 11.5 | 11.3 | 9.9 | 8.6
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.9 | 16.6 | 16.4 | 16.3 | 16.2 | 16.1 | 16 | 15.9 | 15.7 | 15.3 | 15 | 15 | 14.9 | 13.1 | 13.1 | 13.1 | 13.1 | 12.5 | 11.7
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.1 | 19 | 19 | 18.9 | 18.7 | 18.2 | 17.8 | 17.3 | 16.7 | 15.7 | 15.5 | 15.3 | 15.1 | 14.9 | 14.8 | 14.6 | 14.5 | 13.8 | 13.4
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.1 | 18.8 | 18.4 | 17.6 | 16.6 | 14.9 | 13.3 | 11.6 | 10 | 8.3 | 7.8 | 7.3 | 6.9 | 6.4 | 5.9 | 5.5 | 5 | 3.8 | 2.8
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.1 | 18.8 | 18.2 | 17.2 | 15.7 | 14.4 | 12.8 | 10.9 | 9.1 | 7.3 | 6.8 | 6.3 | 5.9 | 5.5 | 5 | 4.6 | 4.2 | 3 | 1.9
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.1 | 18.9 | 18.6 | 17.8 | 16.7 | 15.1 | 13.5 | 11.9 | 10.2 | 8.6 | 8.1 | 7.8 | 7.5 | 7.2 | 6.9 | 6.5 | 6.2 | 5.2 | 4.4
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 33.2 | 32.6 | 32.4 | 32.3 | 32.1 | 31.9 | 31.3 | 31 | 30.5 | 30.1 | 30 | 24.7 | 24.6 | 24.4 | 24.3 | 24.2 | 24.1 | 22.5 | 20.4
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 33.2 | 32.3 | 31.8 | 31.4 | 30.9 | 30.5 | 29.8 | 24.8 | 24.4 | 23.8 | 22.9 | 21.9 | 20.9 | 19.8 | 18.9 | 18 | 17 | 11.8 | 7
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 33.2 | 32.1 | 31.5 | 30.8 | 30.4 | 30.3 | 24.8 | 24 | 22.9 | 21.7 | 20.4 | 19.5 | 18.5 | 17.6 | 16.9 | 16 | 15.1 | 10 | 6.6
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 33.2 | 32.5 | 32.2 | 31.8 | 31.4 | 31 | 30.2 | 29.9 | 24.8 | 24.6 | 23.9 | 23.4 | 22.8 | 22.4 | 22 | 21.6 | 21.1 | 17.5 | 13.6
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 49.5 | 48.1 | 47.7 | 47.3 | 46.7 | 46.2 | 48.5 | 47.5 | 45.8 | 43.6 | 41.4 | 39.9 | 39 | 38.3 | 37.6 | 37.1 | 36.5 | 31.3 | 25.2
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 49.5 | 47.5 | 46.3 | 43.9 | 38.4 | 33.3 | 39 | 37.4 | 34.8 | 32 | 29.1 | 26.1 | 23.2 | 19 | 16.8 | 14.4 | 12 | 0 | 0
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 49.5 | 47.1 | 44.9 | 38.3 | 30.8 | 24.4 | 36.4 | 33.3 | 29.5 | 26.2 | 22.5 | 20.1 | 17.2 | 13.6 | 11.7 | 9.6 | 6.5 | 0 | 0
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 49.5 | 47.8 | 46.9 | 45 | 42.3 | 37.7 | 40.8 | 39.5 | 37.3 | 35.1 | 32.3 | 30.5 | 28.9 | 27 | 26 | 24.8 | 23.4 | 13.7 | 2.8
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 41.3 | 40.7 | 40.4 | 40.1 | 39.9 | 39.6 | 69.1 | 68.8 | 68.5 | 68 | 67.3 | 64.7 | 63.4 | 61.7 | 60.2 | 59.6 | 59.5 | 58.1 | 55.6
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 41.3 | 40.2 | 39.6 | 39.1 | 37.7 | 32.7 | 67.3 | 65.2 | 62.1 | 55 | 52.3 | 49.9 | 47.2 | 41.9 | 37.1 | 29.4 | 23.4 | 0 | 0
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 41.3 | 40 | 39 | 37.6 | 30.3 | 23.9 | 64 | 60 | 54 | 47.6 | 43.4 | 39 | 33 | 24.8 | 19.9 | 12.5 | 6.4 | 0 | 0
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 41.3 | 40.5 | 40 | 39.5 | 39.1 | 37 | 67.7 | 66.1 | 63.5 | 57.1 | 51.6 | 50 | 48.3 | 46.8 | 45.7 | 45.2 | 44.5 | 16 | 2.7
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.2 | 16.5 | 16.5 | 16.5 | 15.5 | 15.5 | 15.4 | 15.3 | 15.2 | 15.1 | 14.9 | 14.8 | 14.8 | 14.7 | 14.7 | 14.6 | 14.6 | 14.2 | 13.9
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.2 | 15.6 | 15.5 | 14.6 | 12.9 | 12.1 | 11.1 | 11 | 10.8 | 10.6 | 10.4 | 10.2 | 10.1 | 9.9 | 9.8 | 9.6 | 9.5 | 8.7 | 8.2
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.2 | 15.6 | 15.5 | 14.5 | 12.9 | 12 | 11 | 10.8 | 10.5 | 10.3 | 10 | 9.9 | 9.7 | 9.6 | 9.4 | 9.3 | 9.4 | 8.6 | 8.1
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.2 | 16.5 | 15.6 | 14.7 | 13 | 12.2 | 11.2 | 11.1 | 11 | 10.8 | 10.6 | 10.5 | 10.4 | 10.3 | 10.2 | 10.1 | 10 | 9.4 | 8.7
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 14.4 | 14.3 | 13.9 | 13.6 | 13.3 | 13 | 12.5 | 12.3 | 11.4 | 10.2 | 8.7 | 7.7 | 7.2 | 6.9 | 6.4 | 6.9 | 6.4 | 2.7 | 0
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 14.4 | 13.9 | 13.1 | 12.3 | 11.2 | 9.8 | 9.6 | 9.1 | 7.5 | 5.6 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 14.4 | 13.8 | 12.8 | 11.5 | 10.5 | 9.9 | 9.6 | 7.7 | 4.8 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 14.4 | 14 | 13.3 | 12.6 | 11.6 | 10.3 | 9.9 | 9.6 | 8.4 | 7.2 | 5.3 | 4 | 2.9 | 2 | 1.4 | 0.7 | 0 | 0 | 0
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.5 | 16.5 | 16.5 | 16.4 | 16.3 | 16.3 | 16.2 | 15.9 | 15.9 | 15.9 | 15.8 | 15.6 | 15.5 | 15.4 | 15.3 | 15.3 | 15.3 | 15 | 14.5
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.5 | 16.4 | 16.2 | 15.9 | 15.8 | 15.8 | 15.8 | 15.5 | 15.1 | 14.6 | 14.5 | 14.3 | 14.1 | 13.9 | 13.7 | 12.4 | 11.7 | 7.2 | 3.1
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.5 | 16.3 | 15.9 | 15.8 | 15.7 | 15.6 | 15.2 | 14.8 | 14.5 | 14.2 | 14 | 13.9 | 13.7 | 13.6 | 12.9 | 10.2 | 9.4 | 4.8 | 1.3
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.5 | 16.4 | 16.3 | 16.3 | 15.9 | 15.9 | 15.8 | 15.6 | 15.4 | 15 | 14.8 | 14.7 | 14.7 | 14.6 | 14.5 | 14.5 | 14.4 | 13.4 | 10
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.5 | 14.4 | 14.4 | 14.4 | 14.4 | 14.3 | 14.1 | 14.1 | 13.9 | 13.8 | 13.7 | 11.7 | 11 | 10.2 | 9.5 | 9.2 | 9.1 | 8.4 | 7.5
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.5 | 14.3 | 14.3 | 14.2 | 14.1 | 14 | 13.7 | 11.9 | 11.1 | 8.8 | 7 | 6.1 | 5.3 | 4.5 | 3.8 | 3.4 | 3.1 | 1.2 | 0
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.5 | 14.3 | 14.2 | 14 | 13.8 | 13.8 | 11.7 | 10.3 | 8.4 | 6.4 | 5.3 | 4.6 | 3.9 | 3.2 | 2.8 | 2.4 | 2.1 | 0 | 0
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.5 | 14.4 | 14.4 | 14.3 | 14.2 | 14.1 | 13.8 | 12 | 11.5 | 9.4 | 7.5 | 6.8 | 6.2 | 5.6 | 5.1 | 4.9 | 4.7 | 3.3 | 1.7
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 44.7 | 44.5 | 43.8 | 43.3 | 42.8 | 42.5 | 68.1 | 67.3 | 66 | 64.1 | 61.6 | 59.9 | 58.8 | 57.9 | 56.9 | 54.6 | 53.9 | 48.3 | 42.3
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 44.7 | 43.8 | 42.4 | 41.4 | 37.2 | 35.8 | 60.7 | 58.8 | 56.1 | 52.7 | 48.4 | 44.7 | 41.3 | 37.9 | 35.3 | 29.4 | 26.7 | 6.6 | 0
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 44.7 | 43.5 | 41.7 | 40 | 35.8 | 34.2 | 58.5 | 55.1 | 50.7 | 46.4 | 42.2 | 39.2 | 35.5 | 31.2 | 29.1 | 24.1 | 21.7 | 4.5 | 0
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 44.7 | 44.1 | 43 | 42.1 | 38.3 | 36.9 | 61.8 | 60.2 | 58 | 55.7 | 52 | 49.9 | 48 | 46.4 | 45.2 | 42.1 | 40.6 | 27.5 | 17.6

## Fault Level Contribution
[5 empty] | Break contribution (kA) | [17 empty] | Make contribution (kA)
Associated GSP | Substation | Supply Level | Voltage Level (kV) | Scenario | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.0875 | 1.1932 | 1.3253 | 1.4742 | 1.5898 | 1.6818 | 1.7811 | 1.9464 | 2.0825 | 2.2329 | 2.3805 | 2.5571 | 2.7614 | 2.9703 | 3.1672 | 3.3424 | 3.7981 | 4.0198 | 2.5243 | 2.7461 | 3.0212 | 3.3304 | 3.57 | 3.7592 | 3.9629 | 4.3018 | 4.5836 | 4.8978 | 5.2021 | 5.5664 | 5.9863 | 6.4158 | 6.8199 | 7.1772 | 8.1292 | 8.6128
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.1585 | 1.3492 | 1.5958 | 1.8742 | 2.1205 | 2.3497 | 2.6184 | 2.9696 | 3.3056 | 3.6036 | 3.7775 | 3.8489 | 3.9041 | 3.9567 | 4.0107 | 4.117 | 4.4303 | 4.6969 | 2.6795 | 3.0836 | 3.6021 | 4.1863 | 4.6986 | 5.1741 | 5.7238 | 6.4455 | 7.1414 | 7.7646 | 8.1408 | 8.3025 | 8.4296 | 8.5492 | 8.6715 | 8.9261 | 9.6561 | 10.2706
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.134 | 1.2815 | 1.4687 | 1.683 | 1.8676 | 2.0321 | 2.2414 | 2.5374 | 2.7842 | 3.0211 | 3.3746 | 3.7065 | 3.9385 | 4.1583 | 4.3003 | 4.3656 | 4.6853 | 4.9552 | 2.636 | 2.9572 | 3.3602 | 3.8203 | 4.2186 | 4.5677 | 5.0137 | 5.6398 | 6.1607 | 6.6572 | 7.4387 | 8.1693 | 8.6523 | 9.1092 | 9.4101 | 9.5578 | 10.2872 | 10.9027
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.1126 | 1.2456 | 1.4202 | 1.6204 | 1.7718 | 1.9089 | 2.0731 | 2.323 | 2.5803 | 2.8626 | 3.0961 | 3.3214 | 3.5406 | 3.7466 | 3.8683 | 3.9699 | 4.25 | 4.4917 | 2.5807 | 2.8652 | 3.2362 | 3.6612 | 3.9799 | 4.2683 | 4.6076 | 5.1238 | 5.6623 | 6.2542 | 6.7342 | 7.1964 | 7.6457 | 8.0676 | 8.3211 | 8.5627 | 9.2094 | 9.7588
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.33924 | 0.41155 | 0.49583 | 0.58825 | 0.69686 | 0.8221 | 0.96181 | 1.1909 | 1.3841 | 1.5759 | 1.7706 | 1.9702 | 2.1913 | 2.4227 | 2.655 | 2.897 | 3.5268 | 3.8251 | 0.75567 | 0.90629 | 1.0807 | 1.2717 | 1.4962 | 1.7552 | 2.0435 | 2.515 | 2.9182 | 3.3159 | 3.7169 | 4.1256 | 4.5755 | 5.047 | 5.5208 | 6.0153 | 7.3315 | 7.9806
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.42604 | 0.60514 | 0.82775 | 1.0742 | 1.3545 | 1.6431 | 2.0001 | 2.4525 | 2.8511 | 3.176 | 3.3329 | 3.4158 | 3.5007 | 3.5772 | 3.6544 | 3.7343 | 4.1169 | 4.4768 | 0.94394 | 1.3223 | 1.7879 | 2.2975 | 2.876 | 3.4687 | 4.1995 | 5.128 | 5.9479 | 6.6203 | 6.957 | 7.1457 | 7.3404 | 7.5112 | 7.6843 | 7.8661 | 8.7424 | 9.5711
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.39382 | 0.52314 | 0.66397 | 0.81867 | 0.97738 | 1.1592 | 1.385 | 1.717 | 2.0066 | 2.3256 | 2.6547 | 2.9628 | 3.282 | 3.5883 | 3.7879 | 3.8866 | 4.344 | 4.7041 | 0.88674 | 1.1741 | 1.4757 | 1.8061 | 2.1429 | 2.526 | 3.004 | 3.7006 | 4.3088 | 4.9794 | 5.666 | 6.303 | 6.9693 | 7.6083 | 8.0328 | 8.2552 | 9.296 | 10.1189
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.36668 | 0.46427 | 0.60264 | 0.73575 | 0.88714 | 1.061 | 1.2726 | 1.5834 | 1.8429 | 2.1292 | 2.433 | 2.7379 | 3.0368 | 3.326 | 3.4997 | 3.5758 | 3.9179 | 4.2352 | 0.8158 | 1.0229 | 1.3203 | 1.5978 | 1.9128 | 2.2733 | 2.7098 | 3.3491 | 3.8837 | 4.4752 | 5.0996 | 5.7264 | 6.3404 | 6.9355 | 7.2986 | 7.4668 | 8.2384 | 8.9598
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.42358 | 0.4783 | 0.52912 | 0.58874 | 0.65677 | 0.76769 | 0.87489 | 1.0679 | 1.2429 | 1.4374 | 1.6223 | 1.7979 | 1.9808 | 2.1643 | 2.3456 | 2.5313 | 3.2526 | 3.8097 | 0.95819 | 1.0742 | 1.1798 | 1.3032 | 1.4437 | 1.6712 | 1.8906 | 2.2979 | 2.6756 | 3.1006 | 3.4965 | 3.8655 | 4.2438 | 4.6238 | 4.9988 | 5.3829 | 6.9197 | 8.1297
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.47628 | 0.60035 | 0.73664 | 0.89204 | 1.0675 | 1.3192 | 1.603 | 2.0008 | 2.3994 | 2.7735 | 3.0667 | 3.2854 | 3.4912 | 3.6596 | 3.8349 | 4.0105 | 4.9376 | 5.524 | 1.0729 | 1.3384 | 1.6207 | 1.9416 | 2.3031 | 2.8199 | 3.3988 | 4.2329 | 5.0787 | 5.8787 | 6.5192 | 7.0042 | 7.4638 | 7.8314 | 8.2122 | 8.5968 | 10.6334 | 12.0044
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.45766 | 0.54803 | 0.63384 | 0.73082 | 0.83963 | 1.0233 | 1.2782 | 1.6489 | 1.9691 | 2.3365 | 2.694 | 3.0427 | 3.3752 | 3.6645 | 3.8945 | 4.0589 | 4.9 | 5.3023 | 1.0397 | 1.2409 | 1.4242 | 1.6305 | 1.8608 | 2.2437 | 2.7998 | 3.6125 | 4.3086 | 5.1109 | 5.8784 | 6.6252 | 7.3354 | 7.9434 | 8.4323 | 8.7905 | 10.6391 | 11.535
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.44323 | 0.52141 | 0.59894 | 0.69006 | 0.79469 | 0.96039 | 1.1332 | 1.4147 | 1.6822 | 2.0098 | 2.3197 | 2.6145 | 2.8924 | 3.1331 | 3.3179 | 3.4461 | 4.0858 | 4.6744 | 1.0014 | 1.1714 | 1.3327 | 1.5218 | 1.7386 | 2.0807 | 2.4346 | 3.0261 | 3.5942 | 4.3004 | 4.9573 | 5.5788 | 6.161 | 6.66 | 7.0473 | 7.3247 | 8.7491 | 10.0928
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 6.6 | Counterfactual | 0.030293 | 0.042033 | 0.055382 | 0.070375 | 0.087783 | 0.10722 | 0.12906 | 0.16412 | 0.19195 | 0.2218 | 0.2522 | 0.28481 | 0.32155 | 0.35741 | 0.393 | 0.43072 | 0.53853 | 0.60142 | 0.06741 | 0.092044 | 0.11974 | 0.15078 | 0.18669 | 0.22672 | 0.27156 | 0.34305 | 0.39996 | 0.46092 | 0.52282 | 0.58914 | 0.66367 | 0.7364 | 0.80862 | 0.88522 | 1.1074 | 1.2387
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 6.6 | Electric Engagement | 0.042908 | 0.069851 | 0.10267 | 0.14024 | 0.18195 | 0.22733 | 0.2827 | 0.351 | 0.41362 | 0.46506 | 0.49321 | 0.51124 | 0.52747 | 0.5432 | 0.56017 | 0.57495 | 0.64413 | 0.69629 | 0.094423 | 0.1512 | 0.2192 | 0.29692 | 0.38291 | 0.47628 | 0.5896 | 0.72898 | 0.85695 | 0.96244 | 1.0214 | 1.06 | 1.0951 | 1.1292 | 1.1656 | 1.1979 | 1.3512 | 1.4677
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 6.6 | Holistic Transition | 0.038254 | 0.057368 | 0.079631 | 0.10503 | 0.13055 | 0.16206 | 0.1985 | 0.25106 | 0.29657 | 0.34622 | 0.39905 | 0.45114 | 0.50187 | 0.5499 | 0.58608 | 0.60658 | 0.69162 | 0.76322 | 0.08606 | 0.12812 | 0.17574 | 0.22994 | 0.28404 | 0.35021 | 0.4264 | 0.53508 | 0.6295 | 0.73227 | 0.84146 | 0.94925 | 1.0543 | 1.1539 | 1.2297 | 1.2742 | 1.4615 | 1.6198
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | 0.034536 | 0.049757 | 0.06888 | 0.092568 | 0.11788 | 0.14695 | 0.182 | 0.23265 | 0.27715 | 0.32623 | 0.37787 | 0.42779 | 0.47917 | 0.52418 | 0.55521 | 0.56942 | 0.62872 | 0.68797 | 0.076525 | 0.1088 | 0.14862 | 0.19784 | 0.25019 | 0.31018 | 0.3821 | 0.48541 | 0.57634 | 0.67629 | 0.78166 | 0.88371 | 0.98872 | 1.081 | 1.145 | 1.1756 | 1.3047 | 1.4322
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Counterfactual | 0.28261 | 0.37559 | 0.49485 | 0.66213 | 0.85423 | 1.0584 | 1.2802 | 1.596 | 1.8273 | 2.0716 | 2.3007 | 2.5454 | 2.8211 | 3.0968 | 3.3807 | 3.6882 | 4.5047 | 4.8812 | 0.62546 | 0.81989 | 1.0673 | 1.4141 | 1.8123 | 2.2351 | 2.6938 | 3.3408 | 3.8157 | 4.3171 | 4.782 | 5.2772 | 5.8336 | 6.3894 | 6.9638 | 7.59 | 9.2819 | 10.0896
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Electric Engagement | 0.39498 | 0.61892 | 0.91068 | 1.2836 | 1.7136 | 2.1648 | 2.6806 | 3.251 | 3.7516 | 4.157 | 4.3365 | 4.4436 | 4.5488 | 4.6486 | 4.7467 | 4.8387 | 5.2571 | 5.697 | 0.868 | 1.3363 | 1.941 | 2.7164 | 3.6112 | 4.548 | 5.6113 | 6.7736 | 7.7928 | 8.6207 | 8.9967 | 9.2349 | 9.4713 | 9.6955 | 9.9154 | 10.1232 | 11.0795 | 12.074
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Holistic Transition | 0.35265 | 0.5038 | 0.69741 | 0.94674 | 1.2133 | 1.481 | 1.7968 | 2.1983 | 2.5762 | 2.9899 | 3.4302 | 3.8922 | 4.3479 | 4.7772 | 5.0523 | 5.1823 | 5.7538 | 6.2443 | 0.79259 | 1.1216 | 1.5363 | 2.0698 | 2.6386 | 3.2055 | 3.8704 | 4.7 | 5.4865 | 6.3466 | 7.2591 | 8.2159 | 9.1601 | 10.05 | 10.6306 | 10.9209 | 12.2115 | 13.3307
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Hydrogen Evolution | 0.31642 | 0.44028 | 0.60809 | 0.83798 | 1.102 | 1.3763 | 1.6826 | 2.0614 | 2.378 | 2.7207 | 3.131 | 3.5425 | 3.9461 | 4.3224 | 4.5484 | 4.6443 | 5.045 | 5.4139 | 0.69885 | 0.96016 | 1.3112 | 1.7949 | 2.3509 | 2.9261 | 3.5628 | 4.3354 | 4.9788 | 5.6745 | 6.5152 | 7.3586 | 8.186 | 8.9579 | 9.4284 | 9.6386 | 10.5321 | 11.3582
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Counterfactual | 0.14295 | 0.17674 | 0.21511 | 0.26035 | 0.31274 | 0.37201 | 0.43764 | 0.5405 | 0.62236 | 0.70999 | 0.80057 | 0.89667 | 1.0054 | 1.1108 | 1.2145 | 1.3264 | 1.6656 | 1.8774 | 0.32951 | 0.40124 | 0.48128 | 0.57534 | 0.68385 | 0.80637 | 0.94173 | 1.1521 | 1.3202 | 1.4999 | 1.6853 | 1.8814 | 2.1026 | 2.3168 | 2.5277 | 2.7554 | 3.4573 | 3.9007
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Electric Engagement | 0.17818 | 0.25732 | 0.35512 | 0.46701 | 0.59209 | 0.72808 | 0.89363 | 1.0954 | 1.2843 | 1.4405 | 1.5298 | 1.5923 | 1.6462 | 1.6996 | 1.7574 | 1.8065 | 2.0546 | 2.2395 | 0.40528 | 0.57364 | 0.77696 | 1.0092 | 1.268 | 1.5488 | 1.8888 | 2.3019 | 2.6893 | 3.0111 | 3.1991 | 3.3331 | 3.4505 | 3.5667 | 3.6914 | 3.7988 | 4.3491 | 4.7618
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Holistic Transition | 0.16527 | 0.22429 | 0.29234 | 0.36936 | 0.44727 | 0.54508 | 0.65704 | 0.81451 | 0.9514 | 1.1034 | 1.2635 | 1.4265 | 1.5875 | 1.7401 | 1.8579 | 1.927 | 2.2325 | 2.4766 | 0.38224 | 0.51377 | 0.66037 | 0.82558 | 0.99164 | 1.1979 | 1.4331 | 1.7599 | 2.045 | 2.361 | 2.6931 | 3.0314 | 3.3661 | 3.6836 | 3.9312 | 4.0816 | 4.7534 | 5.2943
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Hydrogen Evolution | 0.15459 | 0.19914 | 0.25691 | 0.32883 | 0.40579 | 0.49369 | 0.59935 | 0.75219 | 0.88568 | 1.0339 | 1.1907 | 1.3397 | 1.497 | 1.6301 | 1.7322 | 1.7788 | 1.9989 | 2.1986 | 0.35453 | 0.44998 | 0.57093 | 0.72074 | 0.88034 | 1.0622 | 1.2799 | 1.5927 | 1.8662 | 2.1686 | 2.4897 | 2.7954 | 3.1177 | 3.3914 | 3.6032 | 3.7039 | 4.182 | 4.6133
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | 0.4094 | 0.57364 | 0.80253 | 1.0757 | 1.3357 | 1.5701 | 1.8136 | 2.1731 | 2.4861 | 2.9164 | 3.3993 | 3.8976 | 4.3966 | 5.0038 | 5.5064 | 5.9508 | 7.2715 | 8.0201 | 0.89711 | 1.2422 | 1.7189 | 2.2932 | 2.8339 | 3.3199 | 3.8242 | 4.5705 | 5.228 | 6.139 | 7.1587 | 8.2058 | 9.2479 | 10.5683 | 11.6338 | 12.5582 | 15.3527 | 16.9732
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | 0.51495 | 0.82065 | 1.3545 | 1.8815 | 2.3736 | 2.9493 | 3.6192 | 4.5465 | 5.4576 | 6.28 | 6.7606 | 7.0864 | 7.3365 | 7.5599 | 7.7863 | 8.0194 | 9.1691 | 10.0615 | 1.1261 | 1.7749 | 2.9454 | 4.0768 | 5.1112 | 6.3237 | 7.728 | 9.6872 | 11.6232 | 13.4162 | 14.4622 | 15.1854 | 15.7439 | 16.2383 | 16.7379 | 17.2534 | 19.8059 | 21.8286
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | 0.47727 | 0.71716 | 1.0432 | 1.4692 | 2.3464 | 2.8855 | 3.5839 | 4.3159 | 4.9773 | 5.5649 | 6.1078 | 6.65 | 7.182 | 7.6761 | 8.0513 | 8.2956 | 9.4837 | 10.3232 | 1.059 | 1.5821 | 2.2835 | 3.2192 | 5.2149 | 6.3766 | 7.8919 | 9.4664 | 10.8888 | 12.1468 | 13.2961 | 14.4429 | 15.5674 | 16.607 | 17.4088 | 17.949 | 20.588 | 22.4658
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | 0.44414 | 0.65923 | 1.0203 | 1.4226 | 1.8647 | 2.3151 | 2.8347 | 3.5786 | 4.2618 | 5.1246 | 5.7017 | 6.2067 | 6.6903 | 7.1357 | 7.4523 | 7.658 | 8.6416 | 9.5027 | 0.97352 | 1.4345 | 2.2202 | 3.0965 | 4.0422 | 5.0038 | 6.1099 | 7.6934 | 9.1531 | 11.0848 | 12.3023 | 13.3603 | 14.3701 | 15.2986 | 15.9691 | 16.4201 | 18.6036 | 20.5311
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | 0.1099 | 0.13519 | 0.17481 | 0.20468 | 0.23618 | 0.2694 | 0.30621 | 0.36986 | 0.42441 | 0.48877 | 0.5524 | 0.60941 | 0.66708 | 0.72965 | 0.78742 | 0.85157 | 1.0471 | 1.1617 | 0.23832 | 0.29168 | 0.37314 | 0.43481 | 0.49976 | 0.5681 | 0.64369 | 0.77363 | 0.88615 | 1.0188 | 1.1497 | 1.2657 | 1.383 | 1.5099 | 1.6274 | 1.7578 | 2.16 | 2.3993
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | 0.12687 | 0.1774 | 0.24844 | 0.30863 | 0.37471 | 0.45625 | 0.56569 | 0.68138 | 0.77684 | 0.85744 | 0.93524 | 0.99048 | 1.0427 | 1.0938 | 1.1493 | 1.1973 | 1.4289 | 1.6475 | 0.27478 | 0.38282 | 0.53025 | 0.655 | 0.79162 | 0.96125 | 1.189 | 1.4269 | 1.6225 | 1.788 | 1.948 | 2.0632 | 2.1724 | 2.2794 | 2.3951 | 2.4958 | 2.983 | 3.4427
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | 0.12044 | 0.16158 | 0.20851 | 0.25161 | 0.3291 | 0.38133 | 0.43769 | 0.52125 | 0.59594 | 0.68078 | 0.78899 | 0.89954 | 1.0033 | 1.1078 | 1.1913 | 1.2487 | 1.5128 | 1.7368 | 0.26318 | 0.35444 | 0.45507 | 0.547 | 0.71425 | 0.82381 | 0.94215 | 1.1152 | 1.2705 | 1.4464 | 1.6689 | 1.8962 | 2.1101 | 2.325 | 2.4979 | 2.6189 | 3.1765 | 3.6521
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | 0.11599 | 0.14919 | 0.20116 | 0.23988 | 0.29982 | 0.36747 | 0.4299 | 0.51149 | 0.58786 | 0.66283 | 0.76418 | 0.85583 | 0.94555 | 1.0353 | 1.0985 | 1.1466 | 1.3425 | 1.5039 | 0.2513 | 0.32232 | 0.43035 | 0.51089 | 0.63706 | 0.77878 | 0.90751 | 1.0741 | 1.2301 | 1.383 | 1.5894 | 1.7763 | 1.9595 | 2.1425 | 2.2725 | 2.3722 | 2.7816 | 3.1211
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.68976 | 0.78687 | 0.91181 | 1.0658 | 1.2483 | 1.475 | 1.7286 | 2.098 | 2.4122 | 2.7389 | 3.0889 | 3.4307 | 3.784 | 4.0658 | 4.3487 | 4.6377 | 5.3845 | 5.7134 | 1.5971 | 1.7999 | 2.0589 | 2.3779 | 2.7575 | 3.2296 | 3.7562 | 4.5216 | 5.1782 | 5.8608 | 6.5993 | 7.3075 | 8.0351 | 8.6087 | 9.1848 | 9.7738 | 11.327 | 12.0409
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.7969 | 1.0238 | 1.307 | 1.653 | 2.0664 | 2.5456 | 3.1027 | 3.7679 | 4.3654 | 4.8744 | 5.2123 | 5.417 | 5.5911 | 5.6851 | 5.7741 | 5.859 | 6.2547 | 6.6658 | 1.8285 | 2.3042 | 2.8918 | 3.6118 | 4.4727 | 5.4754 | 6.6385 | 8.0213 | 9.2622 | 10.3259 | 11.069 | 11.5255 | 11.9163 | 12.1288 | 12.3307 | 12.5244 | 13.4355 | 14.3749
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.75697 | 0.9147 | 1.1048 | 1.3639 | 1.6339 | 1.976 | 2.374 | 2.8974 | 3.3544 | 3.8482 | 4.4045 | 4.9243 | 5.4125 | 5.802 | 6.0471 | 6.1604 | 6.6724 | 7.1166 | 1.7575 | 2.1007 | 2.5079 | 3.0631 | 3.6406 | 4.3773 | 5.2316 | 6.3415 | 7.3074 | 8.3507 | 9.5376 | 10.6306 | 11.655 | 12.4642 | 12.9834 | 13.2391 | 14.4059 | 15.4204
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.72223 | 0.85517 | 1.0217 | 1.256 | 1.5133 | 1.8218 | 2.1868 | 2.6798 | 3.1199 | 3.5702 | 4.0981 | 4.5839 | 5.0355 | 5.3862 | 5.5926 | 5.6789 | 6.046 | 6.4022 | 1.6677 | 1.949 | 2.2977 | 2.795 | 3.3376 | 3.9902 | 4.7626 | 5.796 | 6.7224 | 7.6627 | 8.7807 | 9.7932 | 10.7316 | 11.4514 | 11.882 | 12.0724 | 12.8998 | 13.7037
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | 0.64844 | 0.70616 | 0.77089 | 0.84541 | 0.92918 | 1.0244 | 1.1309 | 1.3005 | 1.4346 | 1.5769 | 1.7225 | 1.879 | 2.0541 | 2.2485 | 2.4291 | 2.609 | 3.1179 | 3.3891 | 1.347 | 1.4681 | 1.6026 | 1.7571 | 1.9301 | 2.1265 | 2.3459 | 2.6926 | 2.9684 | 3.261 | 3.5594 | 3.879 | 4.2352 | 4.6407 | 5.0117 | 5.3779 | 6.4324 | 7.0076
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | 0.71062 | 0.84402 | 1.008 | 1.1946 | 1.4039 | 1.6305 | 1.8994 | 2.2347 | 2.5407 | 2.8525 | 2.983 | 3.0645 | 3.1375 | 3.2076 | 3.2792 | 3.3434 | 3.6517 | 3.9291 | 1.4813 | 1.7621 | 2.1025 | 2.4891 | 2.9216 | 3.3888 | 3.9398 | 4.6257 | 5.2532 | 5.9213 | 6.1974 | 6.376 | 6.5378 | 6.6931 | 6.8509 | 6.9938 | 7.6894 | 8.315
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | 0.68797 | 0.78305 | 0.89315 | 1.0164 | 1.189 | 1.3355 | 1.5125 | 1.7653 | 1.9867 | 2.231 | 2.4886 | 2.7549 | 3.0176 | 3.2647 | 3.4355 | 3.5261 | 3.9227 | 4.2452 | 1.4409 | 1.6497 | 1.8861 | 2.1501 | 2.5354 | 2.8444 | 3.2169 | 3.7427 | 4.2046 | 4.7135 | 5.2484 | 5.8013 | 6.3468 | 6.8604 | 7.2206 | 7.4205 | 8.306 | 9.033
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | 0.66815 | 0.74403 | 0.8393 | 0.95042 | 1.0687 | 1.2037 | 1.3665 | 1.6077 | 1.8152 | 2.099 | 2.3455 | 2.5878 | 2.8311 | 3.051 | 3.1969 | 3.2633 | 3.5526 | 3.8125 | 1.3898 | 1.5505 | 1.7498 | 1.9817 | 2.2273 | 2.5068 | 2.8424 | 3.3369 | 3.7626 | 4.37 | 4.8755 | 5.3726 | 5.8716 | 6.3232 | 6.6263 | 6.7706 | 7.4077 | 7.9816
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.47234 | 0.51681 | 0.56579 | 0.64227 | 0.72445 | 0.84064 | 0.97588 | 1.165 | 1.3419 | 1.5293 | 1.7285 | 1.9198 | 2.1084 | 2.2835 | 2.4307 | 2.558 | 2.9462 | 3.2389 | 1.0061 | 1.1013 | 1.2068 | 1.3655 | 1.5363 | 1.7778 | 2.0591 | 2.4544 | 2.8288 | 3.2278 | 3.6495 | 4.0517 | 4.4453 | 4.8098 | 5.1146 | 5.3765 | 6.1881 | 6.8095
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.50149 | 0.59292 | 0.71241 | 0.84917 | 1.0186 | 1.2428 | 1.5005 | 1.8137 | 2.1158 | 2.3968 | 2.6422 | 2.8442 | 3.0228 | 3.1709 | 3.2896 | 3.3832 | 3.7528 | 3.9916 | 1.0702 | 1.2703 | 1.5325 | 1.8189 | 2.1735 | 2.6447 | 3.1847 | 3.8449 | 4.4867 | 5.0874 | 5.6199 | 6.0619 | 6.4547 | 6.7776 | 7.0352 | 7.2397 | 8.0479 | 8.6002
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.4919 | 0.56517 | 0.65841 | 0.76216 | 0.87607 | 1.055 | 1.28 | 1.5614 | 1.817 | 2.0909 | 2.3758 | 2.646 | 2.8966 | 3.1145 | 3.2689 | 3.3631 | 3.7192 | 3.9052 | 1.053 | 1.2184 | 1.4294 | 1.6517 | 1.8965 | 2.2783 | 2.7652 | 3.3731 | 3.9246 | 4.5165 | 5.128 | 5.7074 | 6.2435 | 6.7061 | 7.0354 | 7.2396 | 8.0185 | 8.4332
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.48387 | 0.55164 | 0.64094 | 0.74219 | 0.86649 | 1.048 | 1.2526 | 1.5159 | 1.7652 | 2.0386 | 2.3212 | 2.5896 | 2.8392 | 3.0562 | 3.2085 | 3.3021 | 3.6108 | 3.8471 | 1.0321 | 1.1832 | 1.3836 | 1.5982 | 1.861 | 2.2455 | 2.6778 | 3.2345 | 3.7651 | 4.3498 | 4.9507 | 5.5199 | 6.0471 | 6.503 | 6.8235 | 7.0227 | 7.6947 | 8.2296
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Counterfactual | 0.60117 | 0.64966 | 0.75928 | 0.82122 | 0.89021 | 0.97123 | 1.0624 | 1.214 | 1.3534 | 1.5078 | 1.6539 | 1.7931 | 1.9371 | 2.0813 | 2.2228 | 2.3672 | 2.8831 | 2.9322 | 1.4523 | 1.5548 | 1.7777 | 1.9061 | 2.0489 | 2.2161 | 2.4043 | 2.7246 | 3.0249 | 3.3609 | 3.674 | 3.9675 | 4.2674 | 4.568 | 4.8629 | 5.1635 | 6.2714 | 6.2773
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.64183 | 0.80379 | 0.91549 | 1.0514 | 1.2042 | 1.3825 | 1.5993 | 1.8902 | 2.1779 | 2.4405 | 2.6348 | 2.7814 | 2.9178 | 3.0301 | 3.1448 | 3.2562 | 3.8467 | 3.986 | 1.5409 | 1.8792 | 2.1118 | 2.395 | 2.7131 | 3.0833 | 3.5321 | 4.1464 | 4.7607 | 5.3264 | 5.7566 | 6.0875 | 6.396 | 6.6456 | 6.8994 | 7.1474 | 8.4735 | 8.7366
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.62796 | 0.76714 | 0.84746 | 0.94798 | 1.0605 | 1.2003 | 1.402 | 1.6757 | 1.9126 | 2.1769 | 2.4351 | 2.6799 | 2.9149 | 3.1203 | 3.2836 | 3.4004 | 3.9831 | 4.0481 | 1.5162 | 1.8114 | 1.9838 | 2.199 | 2.4399 | 2.7364 | 3.1787 | 3.7787 | 4.2952 | 4.8731 | 5.4312 | 5.9606 | 6.4679 | 6.9058 | 7.2588 | 7.5187 | 8.8244 | 8.8846
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.61577 | 0.74386 | 0.81328 | 0.90339 | 1.0045 | 1.1271 | 1.2727 | 1.4891 | 1.6937 | 1.9361 | 2.1661 | 2.3847 | 2.6009 | 2.7827 | 2.9194 | 3.0102 | 3.4806 | 3.6087 | 1.4849 | 1.7527 | 1.8986 | 2.0882 | 2.3011 | 2.5581 | 2.8621 | 3.3215 | 3.7595 | 4.2844 | 4.7756 | 5.2406 | 5.7012 | 6.0834 | 6.3749 | 6.5762 | 7.6383 | 7.8587
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | 0.3462 | 0.392 | 0.45113 | 0.51582 | 0.58569 | 0.66908 | 0.75475 | 0.84332 | 0.92144 | 1.0111 | 1.0895 | 1.1732 | 1.2639 | 1.3495 | 1.4395 | 1.5267 | 1.7752 | 1.9083 | 0.70846 | 0.80411 | 0.92666 | 1.0608 | 1.2058 | 1.3784 | 1.5556 | 1.7389 | 1.9024 | 2.0933 | 2.2572 | 2.4302 | 2.6159 | 2.7914 | 2.9753 | 3.1537 | 3.6768 | 3.9683
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | 0.37753 | 0.46133 | 0.5701 | 0.69433 | 0.8314 | 1.0017 | 1.1677 | 1.3379 | 1.4963 | 1.6353 | 1.7111 | 1.7645 | 1.8119 | 1.857 | 1.8979 | 1.9428 | 2.1608 | 2.3322 | 0.77669 | 0.95342 | 1.1829 | 1.4432 | 1.7305 | 2.0925 | 2.4375 | 2.7886 | 3.1183 | 3.4093 | 3.5742 | 3.6939 | 3.8018 | 3.9018 | 3.9931 | 4.0927 | 4.5794 | 4.975
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | 0.3663 | 0.43079 | 0.51375 | 0.61643 | 0.71643 | 0.83274 | 0.96846 | 1.1112 | 1.2299 | 1.3671 | 1.5055 | 1.6378 | 1.7671 | 1.8857 | 1.9685 | 2.0171 | 2.2466 | 2.402 | 0.7567 | 0.89675 | 1.0744 | 1.2984 | 1.5148 | 1.7628 | 2.055 | 2.3591 | 2.6118 | 2.9041 | 3.1958 | 3.4748 | 3.7472 | 3.9951 | 4.1713 | 4.2787 | 4.7914 | 5.1409
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | 0.3566 | 0.4135 | 0.49373 | 0.57941 | 0.67584 | 0.79551 | 0.91296 | 1.0361 | 1.1452 | 1.2629 | 1.3918 | 1.5171 | 1.6397 | 1.7517 | 1.8243 | 1.8585 | 2.0361 | 2.2015 | 0.73163 | 0.8525 | 1.0233 | 1.2047 | 1.4086 | 1.6674 | 1.9139 | 2.1688 | 2.3957 | 2.643 | 2.9111 | 3.1708 | 3.4244 | 3.6549 | 3.8064 | 3.8816 | 4.2771 | 4.6508
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | 0.51902 | 0.69272 | 0.88427 | 1.0891 | 1.3214 | 1.579 | 1.8762 | 2.286 | 2.635 | 3.0296 | 3.4792 | 3.9372 | 4.4333 | 4.9386 | 5.4355 | 5.9554 | 7.0149 | 7.5433 | 1.1315 | 1.4962 | 1.8948 | 2.3197 | 2.8014 | 3.3357 | 3.952 | 4.7935 | 5.5164 | 6.3339 | 7.2684 | 8.2166 | 9.2396 | 10.2865 | 11.3127 | 12.3856 | 14.5814 | 15.7086
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | 0.6741 | 1.031 | 1.4638 | 1.9557 | 2.5075 | 3.1168 | 3.8714 | 4.7249 | 5.4911 | 6.1732 | 6.5419 | 6.8025 | 7.0452 | 7.2837 | 7.5286 | 7.731 | 8.3604 | 8.9559 | 1.4709 | 2.2253 | 3.1311 | 4.1612 | 5.3136 | 6.585 | 8.1556 | 9.918 | 11.502 | 12.9345 | 13.7221 | 14.2955 | 14.8343 | 15.3628 | 15.9035 | 16.3537 | 17.7762 | 19.1177
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | 0.62152 | 0.89129 | 1.2223 | 1.5884 | 2.0605 | 2.5527 | 3.0701 | 3.7038 | 4.2692 | 4.8814 | 5.5295 | 6.1948 | 6.8522 | 7.4815 | 7.9275 | 8.1562 | 8.9758 | 9.6689 | 1.377 | 1.9665 | 2.6784 | 3.4709 | 4.4971 | 5.5513 | 6.652 | 7.9783 | 9.1658 | 10.4495 | 11.8038 | 13.1937 | 14.568 | 15.8844 | 16.8331 | 17.3388 | 19.175 | 20.7401
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | 0.57737 | 0.80099 | 1.0697 | 1.3915 | 1.7806 | 2.2575 | 2.7721 | 3.3797 | 3.9107 | 4.5152 | 5.1285 | 5.737 | 6.3439 | 6.9056 | 7.2971 | 7.4793 | 8.0442 | 8.5843 | 1.2628 | 1.7394 | 2.3079 | 2.9902 | 3.8155 | 4.8286 | 5.9128 | 7.1715 | 8.2739 | 9.5399 | 10.8097 | 12.0705 | 13.3279 | 14.4935 | 15.3179 | 15.7174 | 16.9687 | 18.1633
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.34836 | 0.42928 | 0.53344 | 0.64432 | 0.76719 | 0.90458 | 1.0604 | 1.3155 | 1.5231 | 1.7452 | 1.9689 | 2.1965 | 2.4494 | 2.7024 | 2.9574 | 3.2173 | 3.848 | 4.0984 | 0.75694 | 0.92554 | 1.1412 | 1.3704 | 1.6238 | 1.9068 | 2.2269 | 2.748 | 3.1747 | 3.6316 | 4.0903 | 4.5549 | 5.0693 | 5.583 | 6.1014 | 6.6302 | 7.939 | 8.4841
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.44719 | 0.64029 | 0.89093 | 1.1697 | 1.4814 | 1.8253 | 2.2438 | 2.7507 | 3.1965 | 3.5572 | 3.7173 | 3.7952 | 3.8713 | 3.9425 | 4.0124 | 4.0795 | 4.394 | 4.7224 | 0.97043 | 1.3735 | 1.8928 | 2.4692 | 3.1117 | 3.8214 | 4.6807 | 5.7171 | 6.6292 | 7.3706 | 7.7104 | 7.8876 | 8.0615 | 8.2239 | 8.3832 | 8.5366 | 9.2612 | 10.0104
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.40999 | 0.53825 | 0.70218 | 0.87907 | 1.0795 | 1.2982 | 1.5492 | 1.9109 | 2.2278 | 2.5739 | 2.9402 | 3.3009 | 3.6571 | 3.9911 | 4.1986 | 4.2895 | 4.702 | 5.07 | 0.90421 | 1.1827 | 1.5339 | 1.912 | 2.3388 | 2.802 | 3.3295 | 4.0812 | 4.7412 | 5.4618 | 6.2213 | 6.9698 | 7.709 | 8.4025 | 8.8419 | 9.0481 | 9.9912 | 10.8347
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.37729 | 0.48342 | 0.62582 | 0.77855 | 0.95273 | 1.1624 | 1.394 | 1.7307 | 2.0182 | 2.3248 | 2.6687 | 3.0119 | 3.3474 | 3.6615 | 3.8402 | 3.906 | 4.1987 | 4.4772 | 0.82003 | 1.0434 | 1.3412 | 1.6603 | 2.0235 | 2.4613 | 2.9392 | 3.6289 | 4.2185 | 4.8459 | 5.5504 | 6.2535 | 6.9408 | 7.5844 | 7.9564 | 8.1027 | 8.7619 | 9.3899
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.18937 | 0.21236 | 0.24 | 0.30111 | 0.35773 | 0.42844 | 0.50391 | 0.62193 | 0.72919 | 0.84292 | 0.95379 | 1.0645 | 1.1815 | 1.2995 | 1.3929 | 1.4842 | 1.7932 | 2.0116 | 0.40403 | 0.45215 | 0.50945 | 0.6401 | 0.75741 | 0.90326 | 1.059 | 1.3073 | 1.5369 | 1.7829 | 2.0193 | 2.2523 | 2.496 | 2.7419 | 2.935 | 3.1233 | 3.782 | 4.2602
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.2141 | 0.26764 | 0.33877 | 0.47718 | 0.59279 | 0.73115 | 0.88992 | 1.102 | 1.3135 | 1.5087 | 1.6585 | 1.7713 | 1.8786 | 1.9714 | 2.0399 | 2.1125 | 2.4868 | 2.7347 | 0.45743 | 0.56979 | 0.717 | 1.0201 | 1.2613 | 1.5485 | 1.8764 | 2.3228 | 2.7728 | 3.192 | 3.5214 | 3.7735 | 4.0145 | 4.2189 | 4.3693 | 4.5298 | 5.3581 | 5.94
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.20428 | 0.24015 | 0.28589 | 0.39473 | 0.47543 | 0.58977 | 0.73478 | 0.92871 | 1.0968 | 1.2846 | 1.4675 | 1.6446 | 1.8167 | 1.9709 | 2.0711 | 2.1404 | 2.4878 | 2.6599 | 0.43979 | 0.5186 | 0.61632 | 0.86181 | 1.0345 | 1.2771 | 1.5937 | 2.0181 | 2.3839 | 2.7944 | 3.1885 | 3.5695 | 3.9391 | 4.2659 | 4.4801 | 4.6323 | 5.4021 | 5.7894
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.19749 | 0.22762 | 0.26893 | 0.37459 | 0.45045 | 0.54673 | 0.65596 | 0.81939 | 0.9742 | 1.1527 | 1.3204 | 1.482 | 1.6388 | 1.7796 | 1.8639 | 1.9209 | 2.1963 | 2.4399 | 0.42153 | 0.48523 | 0.57111 | 0.80706 | 0.96672 | 1.1683 | 1.3962 | 1.742 | 2.0725 | 2.4579 | 2.8149 | 3.1577 | 3.4884 | 3.7834 | 3.9602 | 4.0841 | 4.699 | 5.2582
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.57415 | 0.71718 | 0.90978 | 1.1404 | 1.3731 | 1.5648 | 1.7508 | 2.1027 | 2.3574 | 2.6366 | 2.9186 | 3.2327 | 3.5822 | 3.933 | 4.3039 | 4.6528 | 5.4055 | 5.7193 | 1.268 | 1.568 | 1.9689 | 2.4476 | 2.9307 | 3.3277 | 3.7097 | 4.4388 | 4.9717 | 5.5587 | 6.1454 | 6.7954 | 7.5141 | 8.2352 | 9.0139 | 9.7484 | 11.326 | 12.0204
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.69567 | 0.98273 | 1.3686 | 1.8115 | 2.286 | 2.7837 | 3.2709 | 3.9031 | 4.5214 | 5.1391 | 5.551 | 5.7098 | 5.8397 | 5.9457 | 6.0529 | 6.1555 | 6.6531 | 7.025 | 1.5331 | 2.1402 | 2.9499 | 3.8768 | 4.8685 | 5.9087 | 6.9059 | 8.21 | 9.4979 | 10.8256 | 11.7498 | 12.1099 | 12.4087 | 12.6487 | 12.8901 | 13.1236 | 14.2646 | 15.154
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.65359 | 0.86785 | 1.1481 | 1.4845 | 1.8771 | 2.2936 | 2.683 | 3.1828 | 3.6636 | 4.2268 | 4.6841 | 5.1255 | 5.5543 | 5.9406 | 6.1908 | 6.305 | 6.8285 | 7.1091 | 1.4584 | 1.9271 | 2.5299 | 3.2522 | 4.0963 | 4.9912 | 5.8265 | 6.8891 | 7.9345 | 9.1722 | 10.1321 | 11.058 | 11.9563 | 12.759 | 13.2889 | 13.5463 | 14.743 | 15.3995
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.61636 | 0.80109 | 1.0634 | 1.376 | 1.7092 | 2.0137 | 2.3192 | 2.7878 | 3.2219 | 3.7383 | 4.2565 | 4.7049 | 5.103 | 5.4605 | 5.6724 | 5.7526 | 6.1201 | 6.4508 | 1.3622 | 1.7564 | 2.3135 | 2.9755 | 3.6818 | 4.3242 | 4.9563 | 5.9303 | 6.8395 | 7.9387 | 9.0484 | 9.9902 | 10.8089 | 11.5405 | 11.9804 | 12.1583 | 12.9985 | 13.7691
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.24696 | 0.28476 | 0.34101 | 0.39372 | 0.4267 | 0.46691 | 0.55136 | 0.65319 | 0.74357 | 0.83805 | 0.93841 | 1.0284 | 1.1014 | 1.1761 | 1.2502 | 1.3294 | 1.557 | 1.6889 | 0.58141 | 0.66069 | 0.77783 | 0.88737 | 0.95546 | 1.0382 | 1.2139 | 1.424 | 1.6118 | 1.8082 | 2.0167 | 2.2028 | 2.3509 | 2.5025 | 2.6529 | 2.8142 | 3.2843 | 3.5606
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.2732 | 0.34275 | 0.45115 | 0.55209 | 0.6512 | 0.79752 | 0.94852 | 1.1172 | 1.2683 | 1.4002 | 1.4836 | 1.5188 | 1.5506 | 1.582 | 1.6463 | 1.6746 | 1.8286 | 1.9461 | 0.63855 | 0.78579 | 1.0146 | 1.226 | 1.4324 | 1.741 | 2.0567 | 2.4061 | 2.7197 | 2.9946 | 3.1725 | 3.2486 | 3.3179 | 3.3868 | 3.5355 | 3.5979 | 3.939 | 4.201
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.26377 | 0.31745 | 0.40653 | 0.50359 | 0.57806 | 0.69266 | 0.79935 | 0.92632 | 1.0442 | 1.2248 | 1.3534 | 1.4585 | 1.5633 | 1.6657 | 1.7436 | 1.7854 | 1.9723 | 2.1248 | 0.62164 | 0.73895 | 0.93058 | 1.1393 | 1.299 | 1.5448 | 1.7716 | 2.0374 | 2.2848 | 2.6865 | 2.9556 | 3.1729 | 3.3898 | 3.6026 | 3.7657 | 3.857 | 4.2683 | 4.6057
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.2569 | 0.30376 | 0.38783 | 0.48337 | 0.55656 | 0.66624 | 0.77363 | 0.90081 | 1.0156 | 1.1368 | 1.2621 | 1.3599 | 1.4616 | 1.5546 | 1.6492 | 1.6803 | 1.8213 | 1.9464 | 0.60339 | 0.70322 | 0.88182 | 1.0846 | 1.2388 | 1.4719 | 1.6979 | 1.9615 | 2.1996 | 2.4507 | 2.7099 | 2.9093 | 3.1171 | 3.3081 | 3.5162 | 3.583 | 3.8889 | 4.1597
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | 0.53858 | 0.70592 | 0.95196 | 1.1981 | 1.4524 | 1.7383 | 2.0606 | 2.5847 | 3.0546 | 3.5949 | 4.2002 | 4.8115 | 5.4827 | 6.1064 | 6.6358 | 7.1634 | 8.6098 | 9.3173 | 1.1407 | 1.491 | 1.9975 | 2.5064 | 3.0308 | 3.6193 | 4.281 | 5.3517 | 6.3193 | 7.4353 | 8.6891 | 9.9511 | 11.3322 | 12.6099 | 13.686 | 14.7585 | 17.7429 | 19.2406
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | 0.72186 | 1.1054 | 1.6421 | 2.2142 | 2.8249 | 3.5737 | 4.5182 | 5.6353 | 6.6323 | 7.4843 | 8.0683 | 8.4954 | 8.9145 | 9.249 | 9.5591 | 9.8487 | 11.2452 | 12.5386 | 1.5366 | 2.3419 | 3.4509 | 4.6366 | 5.8969 | 7.4497 | 9.4064 | 11.7083 | 13.763 | 15.5274 | 16.7552 | 17.6698 | 18.5691 | 19.282 | 19.9401 | 20.5566 | 23.5423 | 26.3056
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | 0.65437 | 0.92332 | 1.2838 | 1.6701 | 2.2206 | 2.8061 | 3.4109 | 4.2222 | 4.9467 | 5.7337 | 6.6637 | 7.6079 | 8.5424 | 9.3581 | 9.9459 | 10.2988 | 11.8963 | 13.2252 | 1.4164 | 2.0039 | 2.771 | 3.5968 | 4.7752 | 6.0235 | 7.2998 | 8.9899 | 10.5041 | 12.1458 | 14.0729 | 16.0295 | 17.9669 | 19.6488 | 20.873 | 21.6274 | 25.059 | 27.9354
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | 0.59504 | 0.81511 | 1.1662 | 1.5246 | 1.9534 | 2.5169 | 3.1146 | 3.9101 | 4.6134 | 5.3658 | 6.2161 | 7.0659 | 7.9144 | 8.6295 | 9.1024 | 9.3605 | 10.523 | 11.4924 | 1.2633 | 1.7289 | 2.4566 | 3.2052 | 4.1036 | 5.2895 | 6.5358 | 8.1777 | 9.6322 | 11.1825 | 12.9322 | 14.6816 | 16.4284 | 17.891 | 18.8663 | 19.412 | 21.8814 | 23.9538
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.40584 | 0.469 | 0.54973 | 0.65136 | 0.76844 | 0.90458 | 1.0476 | 1.2534 | 1.4332 | 1.6574 | 1.8472 | 2.0407 | 2.2484 | 2.4551 | 2.6577 | 2.8626 | 3.5243 | 3.9768 | 0.90252 | 1.0358 | 1.2046 | 1.4163 | 1.6595 | 1.9415 | 2.2376 | 2.6632 | 3.0399 | 3.524 | 3.9199 | 4.3208 | 4.7487 | 5.1745 | 5.5917 | 6.0133 | 7.4015 | 8.3683
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.47808 | 0.63036 | 0.84051 | 1.0533 | 1.3014 | 1.601 | 1.925 | 2.3164 | 2.683 | 3.0015 | 3.2112 | 3.3602 | 3.4974 | 3.6238 | 3.7525 | 3.8733 | 4.4638 | 4.9587 | 1.0637 | 1.3928 | 1.8455 | 2.2892 | 2.8075 | 3.4401 | 4.1129 | 4.926 | 5.6908 | 6.3595 | 6.8104 | 7.1374 | 7.4408 | 7.7184 | 8.0001 | 8.2665 | 9.5753 | 10.6892
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.45725 | 0.59321 | 0.72024 | 0.89888 | 1.0859 | 1.314 | 1.5692 | 1.8975 | 2.1888 | 2.5002 | 2.8153 | 3.1201 | 3.4152 | 3.6904 | 3.902 | 4.0422 | 4.7035 | 5.2328 | 1.0266 | 1.3363 | 1.609 | 1.9986 | 2.3996 | 2.8871 | 3.434 | 4.1318 | 4.7507 | 5.4119 | 6.0764 | 6.7196 | 7.3421 | 7.921 | 8.3723 | 8.6803 | 10.1441 | 11.3212
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.43921 | 0.54001 | 0.68679 | 0.82994 | 1.0007 | 1.2206 | 1.4436 | 1.7405 | 2.0097 | 2.3045 | 2.5999 | 2.8855 | 3.164 | 3.4169 | 3.6005 | 3.7113 | 4.2252 | 4.7069 | 0.98 | 1.202 | 1.5248 | 1.8261 | 2.1866 | 2.6569 | 3.1246 | 3.744 | 4.308 | 4.9264 | 5.5422 | 6.137 | 6.7162 | 7.242 | 7.6288 | 7.8705 | 9.0051 | 10.0748
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | 1.2868 | 1.3662 | 1.4996 | 1.617 | 1.7427 | 1.9201 | 2.115 | 2.3766 | 2.6013 | 2.8396 | 3.0838 | 3.3801 | 3.7065 | 4.0334 | 4.3446 | 4.6177 | 5.5217 | 5.8553 | 2.6035 | 2.7712 | 3.0458 | 3.2888 | 3.549 | 3.9168 | 4.3207 | 4.8596 | 5.3251 | 5.8183 | 6.3239 | 6.9392 | 7.6166 | 8.2949 | 8.9398 | 9.5033 | 11.3896 | 12.09
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | 1.3481 | 1.5107 | 1.7504 | 1.9878 | 2.253 | 2.5821 | 2.9571 | 3.4129 | 3.8695 | 4.2999 | 4.6789 | 4.9588 | 5.2115 | 5.4567 | 5.7057 | 5.9422 | 6.9991 | 7.6578 | 2.7357 | 3.0822 | 3.5795 | 4.0744 | 4.6261 | 5.3163 | 6.0968 | 7.0426 | 7.9956 | 8.9011 | 9.7048 | 10.3004 | 10.8383 | 11.3609 | 11.8907 | 12.3953 | 14.6526 | 16.0408
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | 1.3253 | 1.4521 | 1.6188 | 1.7934 | 1.9755 | 2.2702 | 2.5973 | 3.0041 | 3.3882 | 3.7521 | 4.187 | 4.6236 | 5.0562 | 5.4796 | 5.8281 | 6.0936 | 7.2474 | 7.8971 | 2.6948 | 2.9759 | 3.3313 | 3.705 | 4.0946 | 4.7269 | 5.4257 | 6.2857 | 7.0995 | 7.866 | 8.7723 | 9.6828 | 10.5851 | 11.4684 | 12.2016 | 12.7686 | 15.2374 | 16.6248
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | 1.3066 | 1.4089 | 1.5888 | 1.752 | 1.9176 | 2.1631 | 2.4487 | 2.8301 | 3.2019 | 3.6624 | 4.0633 | 4.4577 | 4.8472 | 5.2204 | 5.5158 | 5.7453 | 6.6953 | 7.1631 | 2.6461 | 2.8655 | 3.2391 | 3.5813 | 3.9286 | 4.4464 | 5.0472 | 5.8432 | 6.6235 | 7.5951 | 8.4265 | 9.2443 | 10.0522 | 10.8273 | 11.4464 | 11.9337 | 13.9574 | 14.9458
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.28865 | 0.37782 | 0.51358 | 0.63982 | 0.78085 | 0.94108 | 1.1216 | 1.4077 | 1.6325 | 1.8728 | 2.1166 | 2.3801 | 2.6743 | 2.9665 | 3.2613 | 3.5621 | 4.3458 | 4.7039 | 0.64261 | 0.82838 | 1.1073 | 1.3677 | 1.6579 | 1.9871 | 2.3572 | 2.94 | 3.4 | 3.8911 | 4.3885 | 4.9256 | 5.5231 | 6.1162 | 6.7147 | 7.3256 | 8.9425 | 9.7033
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.39343 | 0.60214 | 0.8975 | 1.2045 | 1.5474 | 1.9176 | 2.3611 | 2.9148 | 3.419 | 3.8356 | 4.0862 | 4.2492 | 4.4098 | 4.5668 | 4.7282 | 4.8852 | 5.6634 | 6.3659 | 0.86878 | 1.3049 | 1.9142 | 2.5484 | 3.2547 | 4.0164 | 4.923 | 6.0522 | 7.0828 | 7.9375 | 8.4601 | 8.8082 | 9.1515 | 9.4865 | 9.8298 | 10.1639 | 11.8244 | 13.3246
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.35386 | 0.49507 | 0.69279 | 0.88984 | 1.0934 | 1.3374 | 1.6267 | 2.0326 | 2.3925 | 2.7872 | 3.2532 | 3.7168 | 4.1754 | 4.6141 | 4.9264 | 5.1094 | 5.9746 | 6.6862 | 0.79817 | 1.1055 | 1.5253 | 1.9458 | 2.3776 | 2.8911 | 3.4971 | 4.3377 | 5.0845 | 5.9025 | 6.8622 | 7.8177 | 8.7632 | 9.6677 | 10.3185 | 10.7108 | 12.568 | 14.1058
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.31983 | 0.43511 | 0.62659 | 0.80614 | 0.99733 | 1.2195 | 1.4916 | 1.8821 | 2.2274 | 2.5967 | 3.0214 | 3.4434 | 3.8627 | 4.2552 | 4.5137 | 4.6492 | 5.2883 | 5.8167 | 0.71051 | 0.9531 | 1.3491 | 1.7227 | 2.1187 | 2.5774 | 3.1367 | 3.9352 | 4.6418 | 5.3954 | 6.2621 | 7.1234 | 7.9791 | 8.7804 | 9.3134 | 9.6 | 10.9562 | 12.0855
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Counterfactual | 0.095998 | 0.1115 | 0.13023 | 0.15123 | 0.17557 | 0.20645 | 0.2381 | 0.29003 | 0.33392 | 0.37704 | 0.42126 | 0.46716 | 0.51838 | 0.57148 | 0.62459 | 0.67994 | 0.82783 | 0.90253 | 0.2113 | 0.24354 | 0.2822 | 0.32545 | 0.37574 | 0.43951 | 0.50499 | 0.61174 | 0.70343 | 0.79203 | 0.88252 | 0.97601 | 1.0799 | 1.1877 | 1.2957 | 1.4083 | 1.7147 | 1.8738
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Electric Engagement | 0.1148 | 0.15685 | 0.21053 | 0.26447 | 0.32506 | 0.39317 | 0.47379 | 0.57558 | 0.6642 | 0.73559 | 0.76981 | 0.78765 | 0.80544 | 0.8236 | 0.84421 | 0.86038 | 0.93386 | 1.0062 | 0.25193 | 0.34162 | 0.45482 | 0.56595 | 0.69041 | 0.82996 | 0.99483 | 1.2029 | 1.3843 | 1.531 | 1.6036 | 1.6434 | 1.6835 | 1.7241 | 1.7695 | 1.8061 | 1.974 | 2.1385
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Holistic Transition | 0.10779 | 0.14007 | 0.16983 | 0.20222 | 0.23866 | 0.28231 | 0.33193 | 0.40468 | 0.46785 | 0.53724 | 0.60907 | 0.67935 | 0.74829 | 0.81774 | 0.86135 | 0.88278 | 0.98006 | 1.0567 | 0.23948 | 0.31239 | 0.37588 | 0.44481 | 0.52191 | 0.61341 | 0.71766 | 0.869 | 1.0006 | 1.1452 | 1.2941 | 1.44 | 1.5831 | 1.7272 | 1.8194 | 1.8672 | 2.0862 | 2.2605
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Hydrogen Evolution | 0.1017 | 0.12398 | 0.16087 | 0.19105 | 0.22521 | 0.26719 | 0.31514 | 0.38647 | 0.44641 | 0.51172 | 0.58144 | 0.65159 | 0.71999 | 0.78594 | 0.82917 | 0.84718 | 0.92063 | 0.98278 | 0.22369 | 0.27129 | 0.35201 | 0.41465 | 0.48535 | 0.57177 | 0.67024 | 0.81617 | 0.93889 | 1.0727 | 1.2151 | 1.3585 | 1.4984 | 1.6335 | 1.723 | 1.7621 | 1.9253 | 2.0651
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 3.1067 | 3.1617 | 3.2253 | 3.328 | 3.4646 | 3.6251 | 3.81 | 4.0641 | 4.2907 | 4.5332 | 4.7315 | 4.9021 | 5.0901 | 5.2801 | 5.464 | 5.6392 | 6.1279 | 6.3812 | 7.6596 | 7.7745 | 7.9062 | 8.1188 | 8.4024 | 8.7358 | 9.1203 | 9.6477 | 10.1238 | 10.6502 | 11.0654 | 11.4179 | 11.8044 | 12.1942 | 12.5705 | 12.928 | 13.9477 | 14.4947
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 3.168 | 3.2946 | 3.4526 | 3.6743 | 3.9655 | 4.3878 | 4.7626 | 5.2047 | 5.6251 | 5.9515 | 6.1587 | 6.252 | 6.3322 | 6.4083 | 6.4837 | 6.5571 | 6.9153 | 7.2522 | 7.792 | 8.0571 | 8.3845 | 8.8463 | 9.4577 | 10.387 | 11.1751 | 12.0999 | 12.9853 | 13.6702 | 14.1171 | 14.3233 | 14.5026 | 14.6705 | 14.8366 | 14.9982 | 15.795 | 16.5494
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 3.145 | 3.2322 | 3.3389 | 3.5213 | 3.7907 | 4.0363 | 4.3347 | 4.7208 | 5.0695 | 5.368 | 5.6748 | 5.9367 | 6.1949 | 6.4354 | 6.5996 | 6.6921 | 6.9854 | 7.3465 | 7.7509 | 7.9411 | 8.1694 | 8.5668 | 9.1677 | 9.698 | 10.3433 | 11.1679 | 11.9127 | 12.5446 | 13.1893 | 13.7349 | 14.2732 | 14.7731 | 15.12 | 15.3234 | 15.94 | 16.7531
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 3.1257 | 3.1972 | 3.2936 | 3.4398 | 3.6421 | 3.9721 | 4.2399 | 4.589 | 4.9176 | 5.2309 | 5.5238 | 5.7654 | 6.0038 | 6.2245 | 6.3618 | 6.4321 | 6.7487 | 7.04 | 7.7009 | 7.8516 | 8.0522 | 8.3605 | 8.7897 | 9.53 | 10.1003 | 10.8361 | 11.5336 | 12.1931 | 12.8034 | 13.3007 | 13.7908 | 14.2438 | 14.5295 | 14.6809 | 15.3767 | 16.0228
Berkswell 132kV | WARWICK 11kV S STN | Bulk Supply Point | 11 | Counterfactual | 1.4015 | 1.6024 | 1.9013 | 2.1716 | 2.4703 | 2.8033 | 3.1708 | 3.766 | 4.2368 | 4.8305 | 5.3743 | 5.9232 | 6.5219 | 7.1414 | 7.7531 | 8.3942 | 10.0728 | 10.9044 | 3.1117 | 3.5317 | 4.1759 | 4.7349 | 5.3511 | 6.0369 | 6.7919 | 8.0077 | 8.9782 | 10.2355 | 11.3524 | 12.4737 | 13.6905 | 14.9511 | 16.1962 | 17.5035 | 20.9859 | 22.7611
Berkswell 132kV | WARWICK 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | 1.6246 | 2.0851 | 2.7274 | 3.3796 | 4.1174 | 5.1305 | 6.076 | 7.2425 | 8.3191 | 9.1976 | 9.6157 | 9.8366 | 10.0368 | 10.2511 | 10.4674 | 10.6544 | 11.5713 | 12.4128 | 3.5946 | 4.561 | 5.9185 | 7.2678 | 8.7917 | 10.9706 | 12.9086 | 15.2954 | 17.5075 | 19.3228 | 20.2114 | 20.7024 | 21.1476 | 21.6217 | 22.0985 | 22.5134 | 24.5722 | 26.4673
Berkswell 132kV | WARWICK 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | 1.5428 | 1.8585 | 2.2388 | 2.7709 | 3.2413 | 3.8335 | 4.4631 | 5.3496 | 6.1066 | 6.9264 | 7.7406 | 8.5375 | 9.3379 | 10.1184 | 10.6421 | 10.9089 | 12.0711 | 13.0717 | 3.4492 | 4.1401 | 4.9552 | 6.1257 | 7.1275 | 8.404 | 9.7323 | 11.5814 | 13.163 | 14.8737 | 16.5503 | 18.1963 | 19.8531 | 21.4727 | 22.5772 | 23.1669 | 25.764 | 28.0165
Berkswell 132kV | WARWICK 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | 1.4724 | 1.7339 | 2.1346 | 2.5315 | 2.9786 | 3.6752 | 4.2271 | 5.0357 | 5.7548 | 6.5415 | 7.3713 | 8.185 | 8.9912 | 9.7539 | 10.2282 | 10.4385 | 11.3526 | 12.1867 | 3.2667 | 3.8194 | 4.6817 | 5.5115 | 6.4446 | 7.976 | 9.1121 | 10.7668 | 12.2446 | 13.8611 | 15.5622 | 17.2299 | 18.8809 | 20.4456 | 21.4318 | 21.8902 | 23.9139 | 25.7644
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.25397 | 0.28915 | 0.33249 | 0.38651 | 0.44891 | 0.53187 | 0.62153 | 0.76256 | 0.8793 | 1.0017 | 1.1308 | 1.2647 | 1.4094 | 1.5527 | 1.6914 | 1.8312 | 2.2717 | 2.547 | 0.60291 | 0.67656 | 0.76625 | 0.87773 | 1.0063 | 1.1764 | 1.36 | 1.65 | 1.8925 | 2.1482 | 2.4167 | 2.6935 | 2.9906 | 3.284 | 3.5673 | 3.8526 | 4.7671 | 5.3489
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.29542 | 0.38046 | 0.4917 | 0.62831 | 0.78319 | 0.97662 | 1.212 | 1.5055 | 1.792 | 2.0413 | 2.2111 | 2.3302 | 2.4364 | 2.5283 | 2.6226 | 2.7117 | 3.1501 | 3.3806 | 0.69244 | 0.8708 | 1.1004 | 1.3824 | 1.7017 | 2.0985 | 2.5825 | 3.1881 | 3.7841 | 4.3025 | 4.662 | 4.9178 | 5.1477 | 5.345 | 5.5466 | 5.7385 | 6.684 | 7.2111
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.28006 | 0.33691 | 0.40687 | 0.49416 | 0.59416 | 0.74438 | 0.92489 | 1.1667 | 1.3808 | 1.615 | 1.8525 | 2.0767 | 2.2883 | 2.4777 | 2.6199 | 2.7093 | 3.1269 | 3.3322 | 0.66511 | 0.7898 | 0.93912 | 1.1245 | 1.3363 | 1.6539 | 2.0387 | 2.5505 | 3.0015 | 3.4943 | 3.9908 | 4.4592 | 4.901 | 5.2946 | 5.5931 | 5.7857 | 6.6918 | 7.1496
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.26681 | 0.31341 | 0.37527 | 0.45742 | 0.55143 | 0.67864 | 0.8309 | 1.0462 | 1.2493 | 1.471 | 1.6892 | 1.9011 | 2.1007 | 2.2776 | 2.4018 | 2.4726 | 2.7723 | 3.0055 | 0.63083 | 0.7293 | 0.8577 | 1.0283 | 1.2234 | 1.4857 | 1.8008 | 2.2464 | 2.6705 | 3.1326 | 3.5831 | 4.0196 | 4.4301 | 4.7929 | 5.05 | 5.2011 | 5.8524 | 6.3713
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.24056 | 0.26916 | 0.30112 | 0.33679 | 0.37791 | 0.45225 | 0.52918 | 0.7062 | 0.88974 | 1.1061 | 1.292 | 1.444 | 1.5878 | 1.7333 | 1.8757 | 2.0205 | 2.6557 | 3.1788 | 0.56642 | 0.62687 | 0.69322 | 0.76709 | 0.85194 | 1.0033 | 1.1599 | 1.5504 | 1.9669 | 2.4659 | 2.8844 | 3.2175 | 3.5243 | 3.8355 | 4.1396 | 4.4486 | 5.8694 | 7.0695
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.27335 | 0.34294 | 0.42887 | 0.68619 | 0.79606 | 0.96853 | 1.1734 | 1.5241 | 1.9103 | 2.2894 | 2.6213 | 2.8878 | 3.1513 | 3.3446 | 3.5429 | 3.7494 | 4.8731 | 5.6348 | 0.63721 | 0.78479 | 0.96283 | 1.5634 | 1.7896 | 2.1412 | 2.5577 | 3.3201 | 4.1743 | 5.0208 | 5.7778 | 6.3926 | 7.0027 | 7.4374 | 7.8811 | 8.3456 | 10.8714 | 12.7122
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.26108 | 0.31044 | 0.3652 | 0.42639 | 0.495 | 0.6265 | 0.89786 | 1.3141 | 1.6574 | 2.065 | 2.4218 | 2.7562 | 3.0739 | 3.3197 | 3.5303 | 3.6992 | 4.6319 | 4.981 | 0.61525 | 0.72506 | 0.84261 | 0.97318 | 1.1188 | 1.3905 | 2.0074 | 2.9655 | 3.7467 | 4.6803 | 5.4796 | 6.2294 | 6.9387 | 7.4725 | 7.9349 | 8.3142 | 10.4141 | 11.2081
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.25055 | 0.28854 | 0.3351 | 0.39138 | 0.45474 | 0.56395 | 0.68462 | 0.93096 | 1.1816 | 1.5229 | 1.8134 | 2.0807 | 2.3283 | 2.5245 | 2.6846 | 2.8095 | 3.5716 | 4.3138 | 0.58817 | 0.66939 | 0.76656 | 0.88337 | 1.0146 | 1.2378 | 1.4839 | 2.0241 | 2.5809 | 3.3559 | 4.0021 | 4.5917 | 5.1314 | 5.5502 | 5.8962 | 6.1763 | 7.9291 | 9.685
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.18325 | 0.2103 | 0.2424 | 0.28196 | 0.3271 | 0.39383 | 0.464 | 0.58258 | 0.69055 | 0.80774 | 0.92038 | 1.0266 | 1.1365 | 1.2477 | 1.3565 | 1.4656 | 1.8318 | 2.0762 | 0.43851 | 0.49558 | 0.56227 | 0.64428 | 0.73768 | 0.87454 | 1.0184 | 1.2683 | 1.5006 | 1.7559 | 1.9969 | 2.2206 | 2.4486 | 2.6795 | 2.9051 | 3.1313 | 3.9172 | 4.4588
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.21445 | 0.28006 | 0.36399 | 0.46213 | 0.57402 | 0.72475 | 0.89964 | 1.1366 | 1.3749 | 1.5936 | 1.7585 | 1.879 | 1.9967 | 2.0948 | 2.1944 | 2.2973 | 2.8267 | 3.1329 | 0.50593 | 0.64459 | 0.81867 | 1.022 | 1.2536 | 1.5634 | 1.9213 | 2.4184 | 2.9245 | 3.3933 | 3.7554 | 4.0252 | 4.2896 | 4.5049 | 4.7227 | 4.9487 | 6.1098 | 6.8316
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.20263 | 0.25276 | 0.30426 | 0.36675 | 0.43838 | 0.54831 | 0.70525 | 0.92746 | 1.1201 | 1.3356 | 1.5457 | 1.746 | 1.9389 | 2.1074 | 2.2363 | 2.3273 | 2.795 | 2.9955 | 0.48485 | 0.59555 | 0.70603 | 0.83962 | 0.99233 | 1.2225 | 1.5652 | 2.0528 | 2.4723 | 2.9441 | 3.3966 | 3.8276 | 4.241 | 4.5967 | 4.8724 | 5.0723 | 6.1031 | 6.5557
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.19281 | 0.23244 | 0.27803 | 0.334 | 0.39798 | 0.49167 | 0.5957 | 0.7585 | 0.91388 | 1.0986 | 1.2738 | 1.443 | 1.6032 | 1.746 | 1.8488 | 1.9192 | 2.2669 | 2.5686 | 0.45929 | 0.54382 | 0.6391 | 0.75621 | 0.88991 | 1.0837 | 1.2982 | 1.6416 | 1.9731 | 2.3733 | 2.7466 | 3.1048 | 3.442 | 3.7392 | 3.956 | 4.1098 | 4.8867 | 5.5811
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.31394 | 0.32086 | 0.32869 | 0.33704 | 0.34654 | 0.3625 | 0.37924 | 0.4105 | 0.43612 | 0.46368 | 0.49075 | 0.51612 | 0.54283 | 0.5697 | 0.59609 | 0.62286 | 0.71159 | 0.77011 | 0.63326 | 0.64777 | 0.66395 | 0.68122 | 0.7008 | 0.73332 | 0.76739 | 0.8325 | 0.88714 | 0.94659 | 1.004 | 1.0569 | 1.1119 | 1.1672 | 1.2215 | 1.2765 | 1.4654 | 1.5939
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.32266 | 0.33916 | 0.35962 | 0.38261 | 0.40856 | 0.44941 | 0.49472 | 0.55497 | 0.61562 | 0.67082 | 0.71136 | 0.73998 | 0.76835 | 0.79299 | 0.81878 | 0.84552 | 0.99353 | 1.0658 | 0.65212 | 0.68679 | 0.72909 | 0.77653 | 0.82994 | 0.91324 | 1.0055 | 1.1309 | 1.2584 | 1.3752 | 1.4631 | 1.5262 | 1.5889 | 1.642 | 1.6973 | 1.7549 | 2.0727 | 2.2409
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.31942 | 0.33071 | 0.34339 | 0.35736 | 0.37289 | 0.40342 | 0.44136 | 0.49451 | 0.54168 | 0.59483 | 0.64712 | 0.69627 | 0.74418 | 0.78687 | 0.81966 | 0.84196 | 0.9686 | 1.0257 | 0.64631 | 0.67111 | 0.69831 | 0.72818 | 0.76116 | 0.82435 | 0.90625 | 1.0215 | 1.1231 | 1.238 | 1.3493 | 1.4538 | 1.5554 | 1.6447 | 1.7141 | 1.7623 | 2.0364 | 2.1623
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.31667 | 0.32562 | 0.33622 | 0.34839 | 0.36224 | 0.38795 | 0.41329 | 0.45306 | 0.49062 | 0.53521 | 0.57798 | 0.61927 | 0.65947 | 0.69515 | 0.72083 | 0.73674 | 0.82694 | 0.90388 | 0.6392 | 0.65814 | 0.68026 | 0.70553 | 0.73424 | 0.7868 | 0.83859 | 0.92177 | 1.0011 | 1.0965 | 1.1866 | 1.2731 | 1.3569 | 1.4305 | 1.484 | 1.5183 | 1.716 | 1.8894
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.50917 | 0.52627 | 0.54728 | 0.56977 | 0.58008 | 1.754 | 1.7766 | 1.8297 | 1.8859 | 1.9522 | 2.0084 | 2.0527 | 2.0939 | 2.136 | 2.1773 | 2.2188 | 2.4068 | 2.5671 | 1.2563 | 1.2927 | 1.3364 | 1.3831 | 1.4043 | 4.3287 | 4.3746 | 4.4926 | 4.621 | 4.7751 | 4.9025 | 5.0007 | 5.0893 | 5.1802 | 5.2691 | 5.3584 | 5.7835 | 6.1543
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.52702 | 0.55932 | 0.61662 | 0.68127 | 0.73142 | 0.80136 | 0.87514 | 1.0022 | 1.145 | 1.2786 | 1.3977 | 1.4997 | 1.6109 | 1.6917 | 1.7587 | 1.8409 | 2.2639 | 2.5483 | 1.298 | 1.3683 | 1.4968 | 1.6418 | 1.7547 | 1.9063 | 2.0636 | 2.349 | 2.6744 | 2.9791 | 3.2543 | 3.4932 | 3.7549 | 3.9403 | 4.0905 | 4.278 | 5.2369 | 5.9288
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.52367 | 0.55029 | 0.59621 | 0.64416 | 0.67936 | 0.72725 | 0.81377 | 0.94694 | 1.0569 | 1.1853 | 1.3 | 1.4053 | 1.5054 | 1.583 | 1.6512 | 1.7102 | 2.0361 | 2.1583 | 1.292 | 1.3515 | 1.4562 | 1.5648 | 1.6462 | 1.7492 | 1.9479 | 2.2577 | 2.5106 | 2.8072 | 3.0675 | 3.3068 | 3.5333 | 3.7039 | 3.8556 | 3.9889 | 4.7265 | 5.0091
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.52086 | 0.54521 | 0.57205 | 0.60163 | 0.61664 | 0.64684 | 0.67884 | 0.74928 | 0.82336 | 0.92572 | 1.0119 | 1.0916 | 1.1642 | 1.2225 | 1.2702 | 1.3117 | 1.5593 | 1.7994 | 1.2847 | 1.3386 | 1.3957 | 1.4585 | 1.4896 | 1.5512 | 1.6162 | 1.7722 | 1.9387 | 2.1741 | 2.368 | 2.5456 | 2.7054 | 2.8305 | 2.9345 | 3.0277 | 3.5981 | 4.1676
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.18685 | 0.21388 | 0.24406 | 0.27736 | 0.31552 | 0.36354 | 0.41639 | 0.5211 | 0.61812 | 0.72915 | 0.83152 | 0.92621 | 1.025 | 1.1232 | 1.219 | 1.316 | 1.6557 | 1.8846 | 0.44069 | 0.49793 | 0.56058 | 0.62954 | 0.70829 | 0.80682 | 0.91503 | 1.1377 | 1.349 | 1.5938 | 1.8151 | 2.015 | 2.22 | 2.4239 | 2.6226 | 2.8238 | 3.5567 | 4.0693
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.21689 | 0.2825 | 0.36031 | 0.44996 | 0.55073 | 0.67279 | 0.82307 | 1.0359 | 1.2507 | 1.4451 | 1.5809 | 1.6796 | 1.7691 | 1.8324 | 1.8976 | 1.9597 | 2.3119 | 2.6025 | 0.50536 | 0.64467 | 0.80599 | 0.99109 | 1.1986 | 1.449 | 1.756 | 2.2041 | 2.6622 | 3.081 | 3.3841 | 3.6094 | 3.8167 | 3.9606 | 4.1078 | 4.2496 | 5.0543 | 5.7493
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.20539 | 0.25232 | 0.30209 | 0.35851 | 0.42108 | 0.50966 | 0.64773 | 0.85286 | 1.0251 | 1.2244 | 1.4072 | 1.5844 | 1.7522 | 1.8902 | 1.9934 | 2.0552 | 2.3896 | 2.5746 | 0.48476 | 0.5893 | 0.69629 | 0.8167 | 0.94955 | 1.1352 | 1.4387 | 1.8919 | 2.2695 | 2.7082 | 3.1029 | 3.4853 | 3.8476 | 4.1405 | 4.3635 | 4.5037 | 5.265 | 5.6878
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.196 | 0.23212 | 0.27519 | 0.32785 | 0.38708 | 0.46495 | 0.55742 | 0.71317 | 0.85916 | 1.0417 | 1.2091 | 1.3657 | 1.5138 | 1.6336 | 1.7178 | 1.7605 | 2.0349 | 2.3128 | 0.46053 | 0.53784 | 0.62775 | 0.73701 | 0.85962 | 1.02 | 1.2096 | 1.5391 | 1.8506 | 2.2462 | 2.6029 | 2.9352 | 3.2472 | 3.4968 | 3.6749 | 3.7705 | 4.4003 | 5.0502
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.68982 | 0.75377 | 0.82689 | 0.91602 | 1.013 | 1.1216 | 1.2406 | 1.4249 | 1.5768 | 1.7366 | 1.901 | 2.0745 | 2.2631 | 2.4507 | 2.6339 | 2.8186 | 3.391 | 3.7386 | 1.6828 | 1.8206 | 1.9753 | 2.1628 | 2.3662 | 2.593 | 2.8405 | 3.2224 | 3.5405 | 3.876 | 4.2188 | 4.5787 | 4.9671 | 5.3536 | 5.7308 | 6.1108 | 7.3131 | 8.0623
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.75549 | 0.89248 | 1.063 | 1.2715 | 1.5003 | 1.7544 | 2.0527 | 2.4254 | 2.7849 | 3.0981 | 3.2989 | 3.4377 | 3.5599 | 3.6608 | 3.758 | 3.8483 | 4.2772 | 4.5838 | 1.8278 | 2.1218 | 2.4814 | 2.9196 | 3.3992 | 3.9281 | 4.5445 | 5.3163 | 6.0661 | 6.7213 | 7.1513 | 7.4554 | 7.7278 | 7.9519 | 8.1654 | 8.3674 | 9.3325 | 10.0502
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.73407 | 0.83385 | 0.94881 | 1.0911 | 1.2467 | 1.4322 | 1.6528 | 1.9534 | 2.2213 | 2.5144 | 2.8105 | 3.0947 | 3.3617 | 3.5998 | 3.7728 | 3.8715 | 4.3185 | 4.6139 | 1.7895 | 2.013 | 2.2639 | 2.5719 | 2.9076 | 3.302 | 3.7722 | 4.4077 | 4.9736 | 5.5916 | 6.2127 | 6.8088 | 7.3693 | 7.8681 | 8.2362 | 8.4553 | 9.4597 | 10.1396
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.71733 | 0.79875 | 0.89259 | 1.0179 | 1.155 | 1.3167 | 1.5069 | 1.7768 | 2.0247 | 2.3028 | 2.5799 | 2.8469 | 3.098 | 3.317 | 3.4649 | 3.5378 | 3.8394 | 4.0902 | 1.7456 | 1.9224 | 2.1196 | 2.3826 | 2.6696 | 3.0056 | 3.3987 | 3.9555 | 4.4694 | 5.0469 | 5.619 | 6.1694 | 6.6865 | 7.1371 | 7.4452 | 7.6036 | 8.2733 | 8.8385
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.68368 | 0.70539 | 0.73157 | 0.7638 | 0.80074 | 0.84577 | 0.8955 | 0.97667 | 1.0479 | 1.1259 | 1.2026 | 1.2761 | 1.3552 | 1.4348 | 1.5128 | 1.5904 | 1.8052 | 1.9158 | 1.6908 | 1.7363 | 1.7905 | 1.8572 | 1.9334 | 2.026 | 2.1281 | 2.2959 | 2.4452 | 2.6096 | 2.7698 | 2.9216 | 3.0838 | 3.2468 | 3.4066 | 3.5653 | 4.0161 | 4.2574
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.70966 | 0.76282 | 0.83315 | 0.91254 | 1.0031 | 1.1115 | 1.2431 | 1.4034 | 1.5421 | 1.6565 | 1.7212 | 1.7632 | 1.8065 | 1.8441 | 1.8817 | 1.9183 | 2.0949 | 2.2185 | 1.7469 | 1.8587 | 2.0045 | 2.1687 | 2.3559 | 2.5797 | 2.8509 | 3.1822 | 3.467 | 3.7022 | 3.8385 | 3.9313 | 4.029 | 4.1125 | 4.1959 | 4.2775 | 4.6724 | 4.9617
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.70002 | 0.74024 | 0.78842 | 0.84341 | 0.90049 | 0.97218 | 1.0547 | 1.1697 | 1.2694 | 1.3859 | 1.5075 | 1.6257 | 1.74 | 1.8441 | 1.915 | 1.9545 | 2.1341 | 2.2377 | 1.7297 | 1.818 | 1.9212 | 2.0388 | 2.1602 | 2.3115 | 2.4849 | 2.7249 | 2.9326 | 3.1794 | 3.4358 | 3.6847 | 3.925 | 4.1423 | 4.2929 | 4.3806 | 4.7833 | 5.0201
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.69188 | 0.72424 | 0.76765 | 0.81478 | 0.86994 | 0.93668 | 1.0118 | 1.1223 | 1.2161 | 1.3173 | 1.4219 | 1.5248 | 1.6238 | 1.7164 | 1.7774 | 1.8464 | 1.9805 | 2.0975 | 1.7086 | 1.7773 | 1.8682 | 1.9667 | 2.0821 | 2.221 | 2.3762 | 2.6054 | 2.7986 | 3.0074 | 3.2218 | 3.4326 | 3.635 | 3.8241 | 3.9515 | 4.1139 | 4.4142 | 4.6816
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.8452 | 0.88357 | 0.93155 | 0.97672 | 1.0243 | 1.1041 | 1.1868 | 1.3399 | 1.4844 | 1.6456 | 1.7955 | 1.933 | 2.0749 | 2.0293 | 2.1674 | 2.3047 | 2.8216 | 3.2052 | 2.0162 | 2.0976 | 2.1974 | 2.2911 | 2.3893 | 2.5522 | 2.7208 | 3.0469 | 3.3621 | 3.7191 | 4.0438 | 4.3351 | 4.6308 | 4.4575 | 4.745 | 5.0306 | 6.1453 | 6.9943
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.88276 | 0.9694 | 1.0814 | 1.1969 | 1.3219 | 1.5078 | 1.7299 | 2.0461 | 2.377 | 2.6912 | 2.9447 | 3.1372 | 3.3211 | 3.2804 | 3.4341 | 3.5899 | 4.4452 | 4.9159 | 2.0973 | 2.2822 | 2.516 | 2.7551 | 3.013 | 3.3926 | 3.8448 | 4.5115 | 5.2182 | 5.8946 | 6.4521 | 6.881 | 7.2927 | 7.1439 | 7.4773 | 7.8169 | 9.6804 | 10.7927
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.86881 | 0.93343 | 1.0108 | 1.0857 | 1.1676 | 1.3179 | 1.5372 | 1.8488 | 2.1159 | 2.4247 | 2.7134 | 2.9836 | 3.2426 | 3.2725 | 3.453 | 3.5868 | 4.3158 | 4.6159 | 2.0724 | 2.2166 | 2.3833 | 2.5435 | 2.718 | 3.0305 | 3.5117 | 4.2015 | 4.7869 | 5.4671 | 6.0906 | 6.6749 | 7.2335 | 7.2244 | 7.61 | 7.9024 | 9.497 | 10.166
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.85707 | 0.90741 | 0.97528 | 1.0444 | 1.1172 | 1.2358 | 1.3705 | 1.5947 | 1.8121 | 2.0848 | 2.3286 | 2.5575 | 2.7769 | 2.7711 | 2.9138 | 3.01 | 3.5598 | 4.0497 | 2.0421 | 2.1504 | 2.2934 | 2.4374 | 2.5882 | 2.8312 | 3.1065 | 3.5825 | 4.0483 | 4.6425 | 5.1644 | 5.6515 | 6.1142 | 6.0235 | 6.3235 | 6.5326 | 7.7546 | 8.8767
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.30405 | 0.32435 | 0.3467 | 0.37634 | 0.4104 | 0.4635 | 0.51755 | 0.62472 | 0.73084 | 0.85211 | 0.96108 | 1.0593 | 1.1603 | 1.2619 | 1.3584 | 1.4503 | 1.8271 | 2.1332 | 0.68232 | 0.72557 | 0.77214 | 0.83368 | 0.90426 | 1.0126 | 1.1229 | 1.3551 | 1.5913 | 1.8657 | 2.1063 | 2.3177 | 2.531 | 2.7458 | 2.9495 | 3.1431 | 3.9699 | 4.6561
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.3251 | 0.37376 | 0.43303 | 0.50488 | 0.58637 | 0.70351 | 0.84224 | 1.0567 | 1.2915 | 1.5238 | 1.7061 | 1.8401 | 1.9668 | 2.0761 | 2.1968 | 2.3208 | 2.9978 | 3.3976 | 0.72777 | 0.83191 | 0.95515 | 1.1045 | 1.2737 | 1.5131 | 1.7959 | 2.2555 | 2.7662 | 3.2758 | 3.6774 | 3.976 | 4.2596 | 4.499 | 4.7636 | 5.0369 | 6.5278 | 7.4808
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.31731 | 0.35279 | 0.39198 | 0.44153 | 0.502 | 0.60251 | 0.76887 | 1.0046 | 1.1811 | 1.3803 | 1.5713 | 1.7613 | 1.944 | 2.0943 | 2.2256 | 2.3303 | 2.9014 | 3.1271 | 0.71395 | 0.79372 | 0.87825 | 0.98462 | 1.1143 | 1.3237 | 1.6952 | 2.228 | 2.617 | 3.0582 | 3.4742 | 3.8929 | 4.2942 | 4.6162 | 4.9 | 5.1306 | 6.3913 | 6.896
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.31076 | 0.33791 | 0.3704 | 0.41558 | 0.46721 | 0.54352 | 0.63007 | 0.78757 | 0.94859 | 1.1566 | 1.3135 | 1.4578 | 1.597 | 1.7087 | 1.802 | 1.8694 | 2.3161 | 2.7252 | 0.69688 | 0.75544 | 0.82346 | 0.91799 | 1.026 | 1.1825 | 1.36 | 1.7003 | 2.0519 | 2.5147 | 2.8529 | 3.1618 | 3.4566 | 3.688 | 3.883 | 4.0282 | 5.0327 | 5.9804
Bicker Fen 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.5268 | 2.0637 | 2.1311 | 2.203 | 2.9139 | 3.035 | 3.1616 | 3.3796 | 3.5852 | 3.8158 | 4.03 | 4.2235 | 4.4215 | 4.62 | 4.8139 | 5.0105 | 5.7432 | 6.2742 | 3.7618 | 5.0819 | 5.2221 | 5.3713 | 7.1136 | 7.3619 | 7.6213 | 8.0855 | 8.5345 | 9.0452 | 9.5093 | 9.9195 | 10.3316 | 10.7452 | 11.1487 | 11.5577 | 13.1416 | 14.3248
Bicker Fen 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.0628 | 2.1933 | 2.3937 | 2.7601 | 3.0072 | 3.3298 | 3.6959 | 4.195 | 4.7142 | 5.1826 | 5.5437 | 5.8312 | 6.1246 | 6.3478 | 6.5471 | 6.7708 | 7.979 | 8.7452 | 5.0825 | 5.3599 | 5.7949 | 6.6344 | 7.166 | 7.8479 | 8.6127 | 9.6845 | 10.814 | 11.8358 | 12.6416 | 13.2958 | 13.9714 | 14.4733 | 14.911 | 15.411 | 18.0973 | 19.9216
Bicker Fen 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.0414 | 2.1374 | 2.28 | 2.4329 | 2.6007 | 2.8361 | 3.1614 | 3.6129 | 3.9989 | 4.4387 | 4.8548 | 5.2513 | 5.6315 | 5.9515 | 6.2064 | 6.3889 | 7.4026 | 7.884 | 5.0441 | 5.2575 | 5.5773 | 5.9171 | 6.2887 | 6.7896 | 7.5062 | 8.509 | 9.3581 | 10.3289 | 11.2318 | 12.0925 | 12.9159 | 13.5971 | 14.1472 | 14.5521 | 16.8029 | 17.8945
Bicker Fen 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.0234 | 2.0997 | 2.1914 | 2.2993 | 2.4196 | 2.6009 | 2.8027 | 3.116 | 3.4172 | 3.7947 | 4.1393 | 4.4647 | 4.7744 | 5.033 | 5.2267 | 5.3506 | 6.0969 | 6.7933 | 4.9978 | 5.1613 | 5.354 | 5.5795 | 5.8307 | 6.205 | 6.6205 | 7.2857 | 7.9314 | 8.7545 | 9.4928 | 10.1861 | 10.8402 | 11.3795 | 11.7883 | 12.0602 | 13.7331 | 15.3354
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.38562 | 0.4726 | 0.56825 | 0.73246 | 0.92835 | 1.152 | 1.4667 | 1.8438 | 2.1601 | 2.4987 | 2.8379 | 3.2537 | 3.7067 | 4.3504 | 4.9386 | 5.3507 | 6.7539 | 7.7549 | 0.88332 | 1.0647 | 1.2623 | 1.6025 | 2.0087 | 2.4704 | 3.1237 | 3.9079 | 4.5735 | 5.2903 | 6.0023 | 6.8729 | 7.8161 | 9.1689 | 10.4024 | 11.2573 | 14.2346 | 16.403
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.48949 | 0.70269 | 0.96341 | 1.3131 | 1.7491 | 2.2388 | 2.8086 | 3.5566 | 4.2503 | 4.9093 | 5.4566 | 5.93 | 6.3872 | 6.8451 | 7.133 | 7.4209 | 8.8941 | 10.0164 | 1.108 | 1.5552 | 2.0953 | 2.8236 | 3.7358 | 4.7554 | 5.9353 | 7.4989 | 8.9558 | 10.3533 | 11.5458 | 12.5936 | 13.6069 | 14.614 | 15.2449 | 15.8779 | 19.116 | 21.6536
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.45119 | 0.60755 | 0.7756 | 1.0415 | 1.3901 | 1.8373 | 2.3914 | 3.1143 | 3.7484 | 4.4265 | 5.1108 | 5.7773 | 6.4198 | 6.9797 | 7.3781 | 7.6454 | 8.9966 | 9.9782 | 1.0396 | 1.3805 | 1.7404 | 2.3104 | 3.0596 | 4.0157 | 5.2138 | 6.7715 | 8.1348 | 9.5939 | 11.0547 | 12.4762 | 13.8437 | 15.0264 | 15.878 | 16.4667 | 19.4484 | 21.6322
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.41844 | 0.54148 | 0.68894 | 0.93024 | 1.2228 | 1.5539 | 1.9546 | 2.5083 | 3.0366 | 3.7106 | 4.3925 | 5.0556 | 5.6977 | 6.2975 | 6.6496 | 6.8798 | 8.0395 | 9.1407 | 0.95532 | 1.2156 | 1.5239 | 2.0331 | 2.6529 | 3.3501 | 4.1925 | 5.3582 | 6.4782 | 7.9201 | 9.3694 | 10.776 | 12.1341 | 13.4009 | 14.148 | 14.6535 | 17.2194 | 19.6774
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.9103 | 1.9598 | 2.0195 | 2.0822 | 2.1448 | 2.2225 | 2.3067 | 2.4712 | 2.6228 | 2.795 | 2.9545 | 3.1032 | 3.2577 | 3.4125 | 3.5641 | 3.7164 | 4.2401 | 4.5873 | 4.5764 | 4.6803 | 4.8042 | 4.9338 | 5.0627 | 5.2215 | 5.3935 | 5.742 | 6.0714 | 6.4498 | 6.7937 | 7.107 | 7.4272 | 7.7483 | 8.0624 | 8.3779 | 9.5068 | 10.2847
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.956 | 2.6974 | 2.8379 | 2.9869 | 3.1454 | 3.3401 | 3.5753 | 3.911 | 4.2479 | 4.5524 | 4.7658 | 4.9198 | 5.0648 | 5.1703 | 5.2744 | 5.3798 | 5.9662 | 6.4133 | 4.6752 | 6.4859 | 6.78 | 7.0901 | 7.4182 | 7.8187 | 8.3001 | 9.0079 | 9.7284 | 10.3857 | 10.8622 | 11.2151 | 11.5511 | 11.7904 | 12.0249 | 12.2646 | 13.5949 | 14.6661
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.9381 | 2.6482 | 2.7429 | 2.8385 | 2.9345 | 3.0703 | 3.2828 | 3.5978 | 3.8636 | 4.1689 | 4.4527 | 4.7253 | 4.9843 | 5.1995 | 5.3564 | 5.4523 | 5.9804 | 6.2477 | 4.6432 | 6.3944 | 6.5991 | 6.8043 | 7.009 | 7.2936 | 7.761 | 8.4575 | 9.0404 | 9.7131 | 10.3268 | 10.9162 | 11.4754 | 11.932 | 12.2712 | 12.4882 | 13.6862 | 14.2989
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.9247 | 1.9934 | 2.7068 | 2.7942 | 2.8827 | 3.003 | 3.144 | 3.3824 | 3.6065 | 3.8834 | 4.1406 | 4.3841 | 4.6116 | 4.8027 | 4.9336 | 5.0058 | 5.4381 | 5.8572 | 4.6079 | 4.7544 | 6.5042 | 6.6863 | 6.8694 | 7.1166 | 7.4052 | 7.9092 | 8.3872 | 8.9881 | 9.5365 | 10.0527 | 10.5316 | 10.929 | 11.2059 | 11.3665 | 12.3549 | 13.3374
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.13134 | 0.15265 | 0.17767 | 0.19973 | 0.22508 | 0.27823 | 0.3349 | 0.43338 | 0.52252 | 0.61778 | 0.71159 | 0.7975 | 0.88683 | 0.97706 | 1.0655 | 1.155 | 1.4919 | 1.7566 | 0.29587 | 0.34098 | 0.39301 | 0.43863 | 0.49092 | 0.59879 | 0.71379 | 0.91992 | 1.1103 | 1.3167 | 1.5158 | 1.6952 | 1.8792 | 2.0652 | 2.2473 | 2.4315 | 3.1437 | 3.7118
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.15043 | 0.19699 | 0.25622 | 0.31846 | 0.39481 | 0.52217 | 0.6684 | 0.86754 | 1.0684 | 1.2592 | 1.4215 | 1.5483 | 1.672 | 1.7812 | 1.8938 | 2.0095 | 2.6359 | 2.897 | 0.33708 | 0.4362 | 0.55942 | 0.68769 | 0.84436 | 1.1031 | 1.3994 | 1.8142 | 2.2372 | 2.6415 | 2.9899 | 3.2643 | 3.5327 | 3.7642 | 4.0021 | 4.2475 | 5.5743 | 6.1778
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.14325 | 0.17759 | 0.21764 | 0.25465 | 0.2957 | 0.3907 | 0.52217 | 0.70545 | 0.86592 | 1.0479 | 1.2267 | 1.3896 | 1.5484 | 1.6882 | 1.8086 | 1.9058 | 2.4237 | 2.6047 | 0.32428 | 0.40057 | 0.48655 | 0.56554 | 0.65272 | 0.84779 | 1.131 | 1.5293 | 1.8748 | 2.2688 | 2.6495 | 2.9969 | 3.3341 | 3.6258 | 3.8785 | 4.0849 | 5.1874 | 5.5815
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.1371 | 0.16486 | 0.20007 | 0.23368 | 0.278 | 0.36191 | 0.45213 | 0.59113 | 0.72357 | 0.88296 | 1.0341 | 1.1788 | 1.3206 | 1.4468 | 1.5502 | 1.6305 | 2.0205 | 2.3123 | 0.30841 | 0.36798 | 0.44197 | 0.51176 | 0.60317 | 0.77378 | 0.95705 | 1.2473 | 1.5264 | 1.8679 | 2.1864 | 2.4899 | 2.7849 | 3.0446 | 3.2585 | 3.4274 | 4.266 | 4.9174
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Counterfactual | 0.46009 | 0.57301 | 0.71295 | 0.86126 | 1.0093 | 1.1638 | 1.3314 | 1.6488 | 1.9148 | 2.2126 | 2.5037 | 2.7876 | 3.092 | 3.4206 | 3.7216 | 4.0166 | 4.9058 | 5.4247 | 1.0604 | 1.2977 | 1.5883 | 1.8953 | 2.2008 | 2.518 | 2.861 | 3.5242 | 4.0904 | 4.7299 | 5.3471 | 5.9392 | 6.5665 | 7.2548 | 7.8771 | 8.4825 | 10.3739 | 11.525
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.56264 | 0.81095 | 1.1255 | 1.4572 | 1.803 | 2.1724 | 2.6362 | 3.2557 | 3.8541 | 4.427 | 4.7449 | 4.9447 | 5.1296 | 5.2725 | 5.4179 | 5.5565 | 6.3259 | 6.9678 | 1.2822 | 1.8079 | 2.4643 | 3.1533 | 3.8677 | 4.6256 | 5.5784 | 6.8702 | 8.1327 | 9.3741 | 10.0777 | 10.5353 | 10.9633 | 11.2873 | 11.6154 | 11.9313 | 13.6904 | 15.212
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.52466 | 0.70738 | 0.92791 | 1.1515 | 1.368 | 1.6347 | 2.0042 | 2.5383 | 3.0584 | 3.5589 | 4.0432 | 4.5139 | 4.9684 | 5.3663 | 5.6434 | 5.792 | 6.5662 | 7.0426 | 1.2143 | 1.6157 | 2.0895 | 2.568 | 3.0287 | 3.5942 | 4.3984 | 5.5578 | 6.705 | 7.7889 | 8.8209 | 9.8234 | 10.79 | 11.6257 | 12.2188 | 12.5543 | 14.3166 | 15.4046
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.49354 | 0.64871 | 0.85062 | 1.061 | 1.266 | 1.494 | 1.7723 | 2.2148 | 2.6209 | 3.155 | 3.6117 | 4.0428 | 4.4581 | 4.8191 | 5.0521 | 5.159 | 5.7705 | 6.3801 | 1.1337 | 1.4651 | 1.8904 | 2.3314 | 2.7582 | 3.2288 | 3.8036 | 4.7306 | 5.5898 | 6.7526 | 7.7141 | 8.6159 | 9.48 | 10.2249 | 10.7133 | 10.9509 | 12.3467 | 13.7594
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.80131 | 0.83365 | 0.8731 | 0.92191 | 0.97833 | 1.0584 | 1.1435 | 1.3018 | 1.4628 | 1.6456 | 1.8219 | 1.9703 | 2.1214 | 2.2691 | 2.409 | 2.5504 | 3.0671 | 3.4343 | 1.9746 | 2.0424 | 2.1242 | 2.2251 | 2.3416 | 2.5058 | 2.68 | 3.0161 | 3.3651 | 3.7658 | 4.1491 | 4.4664 | 4.7844 | 5.0942 | 5.3851 | 5.6791 | 6.7914 | 7.6038
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.83956 | 0.91922 | 1.045 | 1.1938 | 1.3578 | 1.6075 | 1.8869 | 2.2786 | 2.6458 | 2.9613 | 3.2037 | 3.3411 | 3.5201 | 3.6647 | 3.7967 | 3.9388 | 4.6502 | 5.1219 | 2.0571 | 2.2247 | 2.4939 | 2.8121 | 3.1605 | 3.6828 | 4.275 | 5.1198 | 5.9225 | 6.609 | 7.1481 | 7.4469 | 7.8554 | 8.18 | 8.4713 | 8.7903 | 10.3862 | 11.5113
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.82535 | 0.8855 | 0.97683 | 1.0875 | 1.2127 | 1.4033 | 1.6032 | 1.9124 | 2.1831 | 2.4848 | 2.7724 | 3.0479 | 3.3077 | 3.526 | 3.6985 | 3.8208 | 4.4977 | 4.777 | 2.0317 | 2.1638 | 2.3657 | 2.6078 | 2.8813 | 3.2961 | 3.7265 | 4.4109 | 5.006 | 5.6706 | 6.2946 | 6.8915 | 7.4534 | 7.9179 | 8.2899 | 8.5617 | 10.0926 | 10.729
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.81338 | 0.86196 | 0.92657 | 1.0044 | 1.0978 | 1.2357 | 1.4114 | 1.6642 | 1.9052 | 2.176 | 2.4205 | 2.6852 | 2.9014 | 3.0846 | 3.2208 | 3.3121 | 3.7734 | 4.1934 | 2.0007 | 2.104 | 2.2392 | 2.4013 | 2.5965 | 2.8832 | 3.2544 | 3.7966 | 4.3213 | 4.9123 | 5.4351 | 6.0097 | 6.4665 | 6.8492 | 7.1378 | 7.3386 | 8.3821 | 9.3584
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.48595 | 0.53571 | 0.59674 | 0.67013 | 0.75515 | 0.84357 | 0.94466 | 1.1063 | 1.2453 | 1.3986 | 1.5501 | 1.7023 | 1.8646 | 2.0253 | 2.1817 | 2.3387 | 2.7903 | 3.0211 | 1.1725 | 1.2771 | 1.4038 | 1.5557 | 1.7316 | 1.9137 | 2.1217 | 2.4548 | 2.7446 | 3.0671 | 3.3826 | 3.6964 | 4.0284 | 4.3567 | 4.6758 | 4.9958 | 5.9342 | 6.4289
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.54 | 0.65985 | 0.81786 | 0.99895 | 1.2038 | 1.437 | 1.7133 | 2.0487 | 2.3677 | 2.6375 | 2.7954 | 2.8964 | 2.9812 | 3.0492 | 3.1149 | 3.1749 | 3.4775 | 3.7104 | 1.289 | 1.5421 | 1.8728 | 2.2506 | 2.6773 | 3.1646 | 3.7357 | 4.429 | 5.0926 | 5.6545 | 5.9923 | 6.215 | 6.4051 | 6.5567 | 6.7017 | 6.8361 | 7.5166 | 8.0582
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.51969 | 0.60591 | 0.71795 | 0.84792 | 0.99148 | 1.1512 | 1.3427 | 1.6045 | 1.8348 | 2.0857 | 2.3387 | 2.5885 | 2.8235 | 3.0333 | 3.1764 | 3.2459 | 3.5715 | 3.7973 | 1.2526 | 1.4424 | 1.6845 | 1.9637 | 2.274 | 2.6136 | 3.0211 | 3.5738 | 4.0589 | 4.586 | 5.1135 | 5.6343 | 6.124 | 6.56 | 6.8621 | 7.0169 | 7.7476 | 8.2619
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.50271 | 0.57324 | 0.66932 | 0.78323 | 0.90984 | 1.0499 | 1.2254 | 1.4635 | 1.6811 | 1.9222 | 2.1631 | 2.3953 | 2.6139 | 2.8049 | 2.9261 | 2.9742 | 3.2098 | 3.4243 | 1.2089 | 1.3591 | 1.5611 | 1.7996 | 2.0646 | 2.3555 | 2.7229 | 3.2154 | 3.6674 | 4.1683 | 4.6649 | 5.1427 | 5.5914 | 5.9828 | 6.234 | 6.3388 | 6.8631 | 7.3465
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.40777 | 0.46513 | 0.53376 | 0.61739 | 0.71353 | 0.82652 | 0.95217 | 1.1444 | 1.3026 | 1.4686 | 1.6409 | 1.8199 | 2.0184 | 2.2164 | 2.4102 | 2.6039 | 3.1047 | 3.33 | 0.91634 | 1.0368 | 1.1791 | 1.3522 | 1.5507 | 1.7835 | 2.042 | 2.4342 | 2.7588 | 3.0991 | 3.452 | 3.8178 | 4.222 | 4.6247 | 5.0188 | 5.4123 | 6.443 | 6.9182
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.47493 | 0.61293 | 0.79057 | 0.99687 | 1.232 | 1.5014 | 1.8258 | 2.2093 | 2.5607 | 2.8522 | 3.0091 | 3.0963 | 3.1718 | 3.2431 | 3.3146 | 3.38 | 3.6754 | 3.8764 | 1.0615 | 1.3521 | 1.7204 | 2.1475 | 2.6339 | 3.1904 | 3.8578 | 4.6418 | 5.3622 | 5.9617 | 6.2917 | 6.4813 | 6.6466 | 6.8029 | 6.9591 | 7.103 | 7.7561 | 8.2123
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.44993 | 0.54609 | 0.66571 | 0.80021 | 0.95504 | 1.1408 | 1.3498 | 1.6331 | 1.8842 | 2.1511 | 2.4323 | 2.7076 | 2.9744 | 3.2241 | 3.3897 | 3.47 | 3.8142 | 4.0512 | 1.0171 | 1.2289 | 1.4857 | 1.7734 | 2.1036 | 2.497 | 2.9364 | 3.5243 | 4.0465 | 4.6001 | 5.1819 | 5.751 | 6.3027 | 6.8192 | 7.1672 | 7.344 | 8.1092 | 8.6501
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.42853 | 0.50592 | 0.61139 | 0.73245 | 0.87343 | 1.046 | 1.2413 | 1.5119 | 1.7522 | 2.0095 | 2.2776 | 2.5407 | 2.7955 | 3.03 | 3.1751 | 3.2375 | 3.4747 | 3.6556 | 0.96151 | 1.1258 | 1.3464 | 1.5993 | 1.8937 | 2.2536 | 2.6576 | 3.212 | 3.7057 | 4.2329 | 4.781 | 5.3184 | 5.8385 | 6.3178 | 6.6176 | 6.752 | 7.2701 | 7.6699
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.92975 | 1.0379 | 1.1585 | 1.2998 | 1.4632 | 1.6779 | 1.9099 | 2.2706 | 2.5724 | 2.8912 | 3.1129 | 3.4488 | 3.8117 | 4.1739 | 4.528 | 4.8852 | 5.9553 | 6.5791 | 2.2471 | 2.4747 | 2.7251 | 3.0179 | 3.3557 | 3.7971 | 4.2736 | 5.018 | 5.648 | 6.3173 | 6.7347 | 7.4281 | 8.1715 | 8.9135 | 9.6384 | 10.369 | 12.6051 | 13.9415
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.0425 | 1.2899 | 1.5915 | 1.9421 | 2.3421 | 2.8334 | 3.4097 | 4.1355 | 4.8367 | 5.4496 | 5.7507 | 6.0239 | 6.2775 | 6.5068 | 6.7419 | 7.0484 | 8.1791 | 8.9265 | 2.4903 | 3.013 | 3.6384 | 4.3644 | 5.1918 | 6.2034 | 7.3842 | 8.881 | 10.3378 | 11.6184 | 12.2248 | 12.8216 | 13.3785 | 13.875 | 14.3823 | 15.0735 | 17.5314 | 19.2145
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.0007 | 1.1819 | 1.3749 | 1.5995 | 1.8592 | 2.216 | 2.6538 | 3.2544 | 3.7838 | 4.3611 | 5.0048 | 5.5815 | 6.1398 | 6.6513 | 7.0271 | 7.2589 | 8.3552 | 9.0455 | 2.4158 | 2.8148 | 3.2286 | 3.7086 | 4.2617 | 5.0119 | 5.9452 | 7.2198 | 8.3407 | 9.5643 | 10.9383 | 12.1484 | 13.3178 | 14.3826 | 15.1748 | 15.6783 | 18.0743 | 19.5928
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.96533 | 1.1127 | 1.2814 | 1.4881 | 1.7256 | 2.0383 | 2.3952 | 2.9102 | 3.3822 | 3.9104 | 4.3348 | 4.849 | 5.3477 | 5.7985 | 6.1107 | 6.3653 | 7.1401 | 7.8922 | 2.3242 | 2.6382 | 2.9905 | 3.422 | 3.9174 | 4.5654 | 5.302 | 6.3677 | 7.3507 | 8.4566 | 9.2934 | 10.358 | 11.3872 | 12.3145 | 12.964 | 13.5395 | 15.2368 | 16.8893
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.30832 | 0.33657 | 0.37957 | 0.42355 | 0.46204 | 0.50952 | 0.55842 | 0.63417 | 0.69538 | 0.75968 | 0.82577 | 0.89794 | 0.97731 | 1.056 | 1.1329 | 1.2096 | 1.4438 | 1.5737 | 0.71196 | 0.77175 | 0.86146 | 0.95279 | 1.0324 | 1.1303 | 1.2312 | 1.3869 | 1.5138 | 1.6473 | 1.7838 | 1.9321 | 2.0944 | 2.2551 | 2.412 | 2.5685 | 3.0531 | 3.3277
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.3322 | 0.3924 | 0.47897 | 0.57322 | 0.66574 | 0.77297 | 0.89502 | 1.0453 | 1.1879 | 1.3101 | 1.383 | 1.4331 | 1.4714 | 1.5039 | 1.5364 | 1.5677 | 1.7001 | 1.8103 | 0.76345 | 0.89138 | 1.0727 | 1.269 | 1.4605 | 1.6817 | 1.9322 | 2.2404 | 2.5347 | 2.7879 | 2.9425 | 3.0508 | 3.1353 | 3.2071 | 3.2784 | 3.3475 | 3.6451 | 3.8972
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.32294 | 0.36736 | 0.43002 | 0.49563 | 0.5564 | 0.63418 | 0.72219 | 0.84274 | 0.94883 | 1.0639 | 1.1809 | 1.3053 | 1.4214 | 1.5272 | 1.6028 | 1.6401 | 1.8051 | 1.919 | 0.74688 | 0.8452 | 0.98003 | 1.1205 | 1.2499 | 1.4141 | 1.6004 | 1.8532 | 2.0756 | 2.3165 | 2.5599 | 2.818 | 3.0592 | 3.2788 | 3.4378 | 3.52 | 3.8876 | 4.1469
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.3162 | 0.35304 | 0.41077 | 0.47338 | 0.53025 | 0.60116 | 0.68039 | 0.79397 | 0.89542 | 1.0073 | 1.1206 | 1.234 | 1.3394 | 1.4331 | 1.4982 | 1.528 | 1.6482 | 1.7462 | 0.72895 | 0.8079 | 0.92987 | 1.0615 | 1.1801 | 1.3273 | 1.4912 | 1.7252 | 1.9348 | 2.166 | 2.3991 | 2.6321 | 2.8485 | 3.0406 | 3.1756 | 3.2398 | 3.5045 | 3.7239
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.8503 | 1.8747 | 1.9045 | 1.9408 | 1.9821 | 2.059 | 2.1353 | 2.2446 | 2.336 | 2.4267 | 2.5286 | 2.6331 | 2.7474 | 2.8618 | 2.9712 | 3.0789 | 3.4684 | 3.7401 | 4.5957 | 4.6465 | 4.7081 | 4.7832 | 4.8685 | 5.0247 | 5.1799 | 5.4017 | 5.5881 | 5.7735 | 5.9824 | 6.1967 | 6.4304 | 6.6638 | 6.8861 | 7.1045 | 7.8997 | 8.4585
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.88 | 1.9375 | 2.0838 | 2.2657 | 2.4546 | 2.706 | 2.9806 | 3.3203 | 3.6737 | 3.9806 | 4.2222 | 4.4262 | 4.6499 | 4.8364 | 4.9764 | 5.1538 | 6.0337 | 6.3754 | 4.6596 | 4.7797 | 5.1127 | 5.5239 | 5.9477 | 6.4928 | 7.0802 | 7.8108 | 8.5772 | 9.2316 | 9.7477 | 10.1931 | 10.6923 | 11.1013 | 11.3914 | 11.7756 | 13.6519 | 14.4377
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.8686 | 1.9069 | 2.0158 | 2.1408 | 2.2801 | 2.4672 | 2.6462 | 2.868 | 3.0734 | 3.2961 | 3.5395 | 3.7668 | 3.9808 | 4.1784 | 4.342 | 4.4674 | 5.1364 | 5.4298 | 4.6393 | 4.7225 | 4.9772 | 5.264 | 5.5829 | 5.9873 | 6.3652 | 6.8311 | 7.2597 | 7.7202 | 8.2274 | 8.7007 | 9.1462 | 9.5573 | 9.8997 | 10.1657 | 11.5813 | 12.2321
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.8595 | 1.8911 | 1.9319 | 1.9919 | 2.0588 | 2.1741 | 2.3071 | 2.4819 | 2.6555 | 2.8449 | 3.0274 | 3.2097 | 3.3813 | 3.5362 | 3.6556 | 3.7389 | 4.1209 | 4.3906 | 4.6157 | 4.6821 | 4.7671 | 4.8919 | 5.0309 | 5.2659 | 5.539 | 5.8968 | 6.2549 | 6.6439 | 7.0159 | 7.387 | 7.7361 | 8.0513 | 8.2953 | 8.4682 | 9.2599 | 9.8264
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 5.7262 | 5.778 | 5.8382 | 5.9064 | 5.9888 | 6.0865 | 6.1936 | 6.3667 | 6.5169 | 6.6777 | 6.839 | 7.0015 | 7.1815 | 7.3602 | 7.5327 | 7.7075 | 8.2061 | 8.4783 | 14.2336 | 14.3423 | 14.467 | 14.6082 | 14.7785 | 14.9802 | 15.2009 | 15.5594 | 15.8754 | 16.2142 | 16.5509 | 16.8869 | 17.2561 | 17.6226 | 17.9762 | 18.3342 | 19.3787 | 19.9673
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 5.7834 | 5.9039 | 6.0544 | 6.2384 | 6.4449 | 6.6699 | 6.9392 | 7.2739 | 7.5879 | 7.8516 | 8.0054 | 8.0958 | 8.1785 | 7.4682 | 7.5514 | 4.4913 | 4.911 | 5.2072 | 14.357 | 14.6104 | 14.9221 | 15.3066 | 15.7359 | 16.1995 | 16.7523 | 17.4405 | 18.0897 | 18.6375 | 18.9663 | 19.1659 | 19.3499 | 17.5491 | 17.733 | 10.0619 | 11.0177 | 11.7036
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 5.762 | 5.8453 | 5.9609 | 6.0781 | 6.2072 | 6.3662 | 6.5509 | 6.8133 | 7.0411 | 7.2873 | 7.5296 | 7.8732 | 4.2098 | 4.4531 | 4.62 | 4.7109 | 7.911 | 8.1885 | 14.3187 | 14.5016 | 14.7517 | 15.0032 | 15.2779 | 15.614 | 16.0053 | 16.558 | 17.0372 | 17.5544 | 18.0556 | 18.8084 | 9.5458 | 10.0526 | 10.4065 | 10.6078 | 18.5015 | 19.1309
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 5.7445 | 5.8121 | 5.9018 | 6.0124 | 6.1384 | 6.2786 | 6.4432 | 6.6904 | 6.9044 | 7.1411 | 7.3801 | 7.6134 | 7.8431 | 7.2386 | 7.3785 | 8.629 | 8.9914 | 9.2789 | 14.2733 | 14.4165 | 14.6034 | 14.8374 | 15.1023 | 15.394 | 15.7341 | 16.247 | 16.6905 | 17.1824 | 17.6756 | 18.1562 | 18.6285 | 17.0229 | 17.3149 | 20.4193 | 21.2455 | 21.8998
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.17028 | 0.19187 | 0.21664 | 0.24322 | 0.27707 | 0.31917 | 0.36578 | 0.45879 | 0.55618 | 0.67463 | 0.82073 | 0.95154 | 1.0813 | 1.2126 | 1.3141 | 1.3885 | 1.5973 | 1.7186 | 0.38276 | 0.42798 | 0.4793 | 0.53427 | 0.60418 | 0.69082 | 0.78649 | 0.98152 | 1.1892 | 1.4436 | 1.7615 | 2.0459 | 2.329 | 2.6156 | 2.8322 | 2.9853 | 3.431 | 3.7028
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.19614 | 0.24978 | 0.32015 | 0.39749 | 0.48656 | 0.5942 | 0.77173 | 0.97897 | 1.202 | 1.3984 | 1.531 | 1.6339 | 1.7336 | 1.8319 | 1.8859 | 1.925 | 2.1541 | 2.3173 | 0.43857 | 0.55142 | 0.69783 | 0.85812 | 1.0426 | 1.2655 | 1.6412 | 2.0844 | 2.5769 | 3.0091 | 3.3084 | 3.5464 | 3.7782 | 4.0021 | 4.1228 | 4.2113 | 4.724 | 5.1116
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.18644 | 0.23231 | 0.2923 | 0.36407 | 0.42091 | 0.51552 | 0.65063 | 0.83967 | 1.0131 | 1.1824 | 1.3571 | 1.526 | 1.6901 | 1.8261 | 1.9102 | 1.9487 | 2.1698 | 2.2893 | 0.42129 | 0.52184 | 0.65099 | 0.80504 | 0.92635 | 1.1318 | 1.4339 | 1.8571 | 2.2466 | 2.6236 | 3.0064 | 3.3771 | 3.7371 | 4.025 | 4.2062 | 4.2933 | 4.7887 | 5.0619
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.17796 | 0.21402 | 0.2629 | 0.31228 | 0.37573 | 0.44979 | 0.54211 | 0.68021 | 0.84281 | 1.0299 | 1.2103 | 1.3689 | 1.5226 | 1.6676 | 1.7404 | 1.7675 | 1.9295 | 2.085 | 0.39946 | 0.47631 | 0.57949 | 0.68319 | 0.81702 | 0.97243 | 1.1681 | 1.4655 | 1.8295 | 2.2463 | 2.6394 | 2.9841 | 3.3172 | 3.6305 | 3.7849 | 3.8456 | 4.2126 | 4.5737
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Counterfactual | 2.6613 | 2.7782 | 2.9067 | 3.0491 | 3.2157 | 3.4146 | 3.642 | 4.0079 | 4.3143 | 4.6538 | 5.0057 | 5.3616 | 5.7549 | 6.1441 | 6.5241 | 6.9065 | 7.9199 | 8.4267 | 6.432 | 6.6761 | 6.9421 | 7.2362 | 7.5798 | 7.989 | 8.4562 | 9.2072 | 9.8415 | 10.5474 | 11.276 | 12.009 | 12.8145 | 13.6105 | 14.3871 | 15.1682 | 17.281 | 18.372
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.7911 | 3.0612 | 3.3805 | 3.7401 | 4.1559 | 4.636 | 5.2371 | 5.9845 | 6.6766 | 7.26 | 7.5911 | 7.772 | 7.9387 | 8.087 | 8.2461 | 8.3841 | 9.2883 | 9.8094 | 6.7117 | 7.2775 | 7.9372 | 8.679 | 9.5355 | 10.5244 | 11.7615 | 13.3001 | 14.7319 | 15.9457 | 16.6552 | 17.0515 | 17.4184 | 17.7423 | 18.0877 | 18.3871 | 20.3295 | 21.5038
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.7419 | 2.9268 | 3.128 | 3.3517 | 3.6254 | 3.9709 | 4.3744 | 4.9288 | 5.4135 | 5.9414 | 6.4743 | 7.0037 | 7.5302 | 8.0211 | 8.3617 | 8.5385 | 9.8248 | 10.4351 | 6.624 | 7.0271 | 7.4576 | 7.9351 | 8.5174 | 9.2497 | 10.1014 | 11.2586 | 12.2711 | 13.3714 | 14.4714 | 15.5672 | 16.6595 | 17.6768 | 18.3932 | 18.781 | 21.6509 | 23.0249
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.7007 | 2.8538 | 3.0286 | 3.2304 | 3.4733 | 3.7696 | 4.129 | 4.648 | 5.1184 | 5.6394 | 6.1704 | 6.6783 | 7.1787 | 7.6315 | 7.9214 | 8.0439 | 9.7797 | 10.333 | 6.5174 | 6.8406 | 7.2045 | 7.6243 | 8.1298 | 8.7455 | 9.4902 | 10.5616 | 11.5383 | 12.6217 | 13.7188 | 14.762 | 15.7884 | 16.7154 | 17.3164 | 17.5786 | 21.6853 | 22.92
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.7806 | 2.801 | 2.8238 | 2.8419 | 2.8625 | 2.892 | 2.9237 | 2.988 | 3.0496 | 3.1204 | 3.189 | 3.2497 | 3.3107 | 2.7402 | 2.7964 | 2.8536 | 3.057 | 3.2095 | 6.8746 | 6.9174 | 6.9642 | 7.0018 | 7.0444 | 7.1049 | 7.1697 | 7.3081 | 7.4442 | 7.6027 | 7.7542 | 7.8856 | 8.0148 | 6.5655 | 6.6831 | 6.8028 | 7.2484 | 7.5938
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.7972 | 2.8415 | 2.909 | 2.9656 | 3.028 | 3.1097 | 3.205 | 3.3305 | 3.459 | 3.5665 | 3.6444 | 3.7019 | 3.7968 | 3.2012 | 3.2403 | 1.9729 | 2.428 | 2.6504 | 6.9103 | 7.0052 | 7.1527 | 7.2734 | 7.4056 | 7.578 | 7.7775 | 8.0434 | 8.3201 | 8.5503 | 8.7218 | 8.8514 | 9.0575 | 7.5554 | 7.6393 | 4.4575 | 5.4835 | 6.019
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.7911 | 2.8282 | 2.8722 | 2.9105 | 2.9686 | 3.0232 | 3.0945 | 3.2024 | 3.2921 | 3.3924 | 3.4735 | 3.6193 | 3.743 | 1.9023 | 2.0482 | 2.0975 | 3.9024 | 4.0291 | 6.8994 | 6.9828 | 7.08 | 7.1647 | 7.2975 | 7.4132 | 7.5677 | 7.8041 | 7.9983 | 8.2158 | 8.3829 | 8.7139 | 8.9721 | 4.3398 | 4.6822 | 4.7934 | 9.2039 | 9.4946
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.7858 | 2.8136 | 2.8547 | 2.8818 | 2.9127 | 2.9664 | 3.0178 | 3.1091 | 3.1868 | 3.2788 | 3.3646 | 3.4459 | 3.5407 | 2.9732 | 3.0177 | 3.1325 | 3.4382 | 3.6376 | 6.8857 | 6.9457 | 7.0355 | 7.0921 | 7.1564 | 7.2713 | 7.3775 | 7.5736 | 7.7391 | 7.9375 | 8.119 | 8.2899 | 8.4861 | 7.0385 | 7.1302 | 7.4081 | 8.1131 | 8.5818
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.24914 | 0.27434 | 0.30416 | 0.33811 | 0.37705 | 0.42428 | 0.47633 | 0.55381 | 0.61792 | 0.68725 | 0.77406 | 0.85959 | 0.95192 | 1.0375 | 1.116 | 1.1981 | 1.4138 | 1.5268 | 0.55893 | 0.61191 | 0.67382 | 0.74414 | 0.8246 | 0.92179 | 1.0287 | 1.1877 | 1.3206 | 1.4649 | 1.6513 | 1.8335 | 2.0284 | 2.2065 | 2.3675 | 2.5363 | 2.9858 | 3.2288
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.27731 | 0.33547 | 0.40578 | 0.48959 | 0.58504 | 0.68852 | 0.85287 | 1.0393 | 1.2258 | 1.3563 | 1.4318 | 1.4671 | 1.5007 | 1.5313 | 1.5634 | 1.5935 | 1.7644 | 1.8745 | 0.61978 | 0.74246 | 0.88808 | 1.0618 | 1.2592 | 1.4716 | 1.8251 | 2.2201 | 2.622 | 2.8959 | 3.0589 | 3.1353 | 3.2083 | 3.2737 | 3.3422 | 3.406 | 3.7735 | 4.0239
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.2669 | 0.30709 | 0.35175 | 0.39979 | 0.45358 | 0.56885 | 0.68809 | 0.82974 | 0.94521 | 1.0582 | 1.1648 | 1.271 | 1.3789 | 1.48 | 1.5499 | 1.5868 | 1.7665 | 1.8872 | 0.60129 | 0.68998 | 0.78589 | 0.88871 | 1.0032 | 1.2634 | 1.529 | 1.8354 | 2.0827 | 2.3199 | 2.5376 | 2.7559 | 2.9789 | 3.1871 | 3.3331 | 3.4132 | 3.8034 | 4.0757
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.25776 | 0.28954 | 0.3282 | 0.37389 | 0.42336 | 0.48596 | 0.58665 | 0.72155 | 0.85995 | 0.97982 | 1.0939 | 1.1996 | 1.303 | 1.3961 | 1.4549 | 1.478 | 1.6348 | 1.7566 | 0.57769 | 0.64517 | 0.72583 | 0.82119 | 0.92388 | 1.0531 | 1.2721 | 1.5613 | 1.8658 | 2.1198 | 2.3569 | 2.5738 | 2.7845 | 2.9736 | 3.0942 | 3.1425 | 3.4923 | 3.764
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.82279 | 0.88509 | 4.1788 | 4.2683 | 4.3736 | 4.4985 | 4.641 | 4.8668 | 5.0528 | 5.2506 | 5.4507 | 5.6553 | 5.8823 | 6.1084 | 6.3303 | 6.5517 | 7.1382 | 7.422 | 1.7138 | 1.8441 | 10.046 | 10.2309 | 10.4485 | 10.7061 | 10.9996 | 11.4653 | 11.8535 | 12.267 | 12.6823 | 13.1039 | 13.5687 | 14.0313 | 14.4853 | 14.9378 | 16.1649 | 16.7826
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.89911 | 1.0495 | 4.4601 | 4.6992 | 4.9702 | 5.2602 | 5.6063 | 6.0424 | 6.4522 | 6.7963 | 6.9921 | 7.1075 | 7.2156 | 7.3105 | 7.4064 | 7.4973 | 7.8631 | 8.1479 | 1.8786 | 2.1935 | 10.6371 | 11.1351 | 11.6978 | 12.2961 | 13.0062 | 13.9044 | 14.7538 | 15.4721 | 15.8942 | 16.1529 | 16.397 | 16.6086 | 16.8215 | 17.0249 | 17.8298 | 18.4796
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.87052 | 0.97072 | 4.3311 | 4.4846 | 4.6439 | 4.8431 | 5.0875 | 5.4345 | 5.7359 | 6.0613 | 6.3937 | 6.6957 | 6.9985 | 7.2796 | 7.4681 | 7.5622 | 7.9733 | 8.41 | 1.8276 | 2.0465 | 10.3988 | 10.7277 | 11.0666 | 11.4877 | 12.0085 | 12.7428 | 13.3801 | 14.0685 | 14.7657 | 15.39 | 16.0183 | 16.6 | 16.9968 | 17.2038 | 18.1121 | 19.1347
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.84574 | 0.92748 | 4.2529 | 4.3876 | 4.5433 | 4.7283 | 4.943 | 5.2496 | 5.5216 | 5.8226 | 6.1315 | 6.4344 | 6.7297 | 6.999 | 7.1685 | 7.2465 | 9.205 | 9.5136 | 1.7638 | 1.9362 | 10.2052 | 10.4891 | 10.8156 | 11.2016 | 11.6465 | 12.2806 | 12.8457 | 13.4738 | 14.1137 | 14.7397 | 15.349 | 15.9029 | 16.2568 | 16.4278 | 21.2322 | 21.9327
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.33968 | 0.38437 | 0.43286 | 0.4858 | 0.55169 | 0.6385 | 0.71494 | 0.84704 | 0.96068 | 1.0924 | 1.224 | 1.3517 | 1.4847 | 1.6185 | 1.7511 | 1.885 | 2.2775 | 2.5024 | 0.74591 | 0.83944 | 0.93981 | 1.0492 | 1.1852 | 1.364 | 1.5202 | 1.7949 | 2.0355 | 2.3168 | 2.5941 | 2.8593 | 3.1327 | 3.4073 | 3.6795 | 3.9544 | 4.7849 | 5.2804
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.38475 | 0.48483 | 0.60278 | 0.73219 | 0.89009 | 1.0815 | 1.2878 | 1.5631 | 1.8309 | 2.069 | 2.2168 | 2.3117 | 2.4012 | 2.4753 | 2.5518 | 2.6809 | 3.1148 | 3.3855 | 0.8435 | 1.0539 | 1.2982 | 1.5652 | 1.8919 | 2.2868 | 2.7078 | 3.2781 | 3.839 | 4.3422 | 4.6645 | 4.8784 | 5.0812 | 5.2461 | 5.4152 | 5.6907 | 6.6469 | 7.2836
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.36814 | 0.43815 | 0.51418 | 0.59375 | 0.69534 | 0.83026 | 0.99459 | 1.2306 | 1.4288 | 1.6521 | 1.8741 | 2.0941 | 2.3062 | 2.4947 | 2.6262 | 2.7539 | 3.1752 | 3.3697 | 0.81387 | 0.96659 | 1.1292 | 1.2988 | 1.515 | 1.7995 | 2.1538 | 2.6624 | 3.0872 | 3.5676 | 4.0384 | 4.5043 | 4.9523 | 5.3461 | 5.6258 | 5.8977 | 6.8277 | 7.2721
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.35377 | 0.4139 | 0.4823 | 0.55505 | 0.64961 | 0.77255 | 0.89328 | 1.0824 | 1.2592 | 1.4654 | 1.6661 | 1.8599 | 2.0439 | 2.21 | 2.3184 | 2.4025 | 2.7027 | 2.9505 | 0.77689 | 0.90454 | 1.0475 | 1.199 | 1.3968 | 1.653 | 1.9008 | 2.2945 | 2.666 | 3.1041 | 3.5247 | 3.9285 | 4.3105 | 4.6526 | 4.8794 | 5.0587 | 5.7282 | 6.3017
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Counterfactual | 1.5755 | 1.6588 | 1.7577 | 1.8727 | 1.9921 | 2.1352 | 2.2852 | 2.5275 | 2.7717 | 2.9826 | 2.3436 | 2.5764 | 2.8309 | 3.0668 | 3.2794 | 3.4957 | 4.0918 | 4.4029 | 3.8816 | 4.0561 | 4.2616 | 4.5002 | 4.7496 | 5.0526 | 5.3716 | 5.8847 | 6.4185 | 6.8632 | 5.1804 | 5.6757 | 6.2115 | 6.703 | 7.1383 | 7.5808 | 8.834 | 9.5137
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Electric Engagement | 1.6529 | 1.8296 | 2.0517 | 2.3958 | 2.8158 | 3.1426 | 3.5247 | 4.0072 | 4.5411 | 4.9152 | 4.2307 | 4.3547 | 4.4687 | 4.5688 | 4.6704 | 4.7664 | 5.3136 | 5.6936 | 4.0489 | 4.422 | 4.8858 | 5.6431 | 6.5805 | 7.2751 | 8.076 | 9.0955 | 10.2611 | 11.0583 | 9.2826 | 9.5619 | 9.8217 | 10.0457 | 10.2715 | 10.4873 | 11.7427 | 12.6251
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Holistic Transition | 1.6252 | 1.7544 | 2.0042 | 2.2945 | 2.4998 | 2.73 | 3.0357 | 3.4732 | 3.8209 | 4.1463 | 3.5949 | 4.0615 | 4.3782 | 4.6647 | 4.8642 | 4.974 | 5.4836 | 5.8276 | 3.9996 | 4.2824 | 4.8514 | 5.5142 | 5.9616 | 6.4629 | 7.1401 | 8.104 | 8.8622 | 9.5551 | 8.046 | 9.0873 | 9.7538 | 10.3529 | 10.7774 | 11.0223 | 12.1699 | 12.9486
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Hydrogen Evolution | 1.5995 | 1.7057 | 1.8529 | 2.0957 | 2.4014 | 2.6627 | 2.8885 | 3.2344 | 3.6246 | 3.9825 | 3.4109 | 3.7082 | 4.0051 | 4.2656 | 4.4351 | 4.5137 | 4.9675 | 5.3204 | 3.9341 | 4.1598 | 4.4703 | 5.0157 | 5.7136 | 6.2883 | 6.7647 | 7.5001 | 8.3633 | 9.1347 | 7.5746 | 8.1914 | 8.8053 | 9.3419 | 9.6964 | 9.8697 | 10.9082 | 11.71
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.043915 | 0.049862 | 0.0552 | 0.061115 | 0.067959 | 0.078871 | 0.090712 | 0.12686 | 0.16746 | 0.21773 | 0.25814 | 0.28732 | 0.31328 | 0.33945 | 0.36487 | 0.39184 | 0.52212 | 0.63543 | 0.10641 | 0.11934 | 0.13052 | 0.14286 | 0.15708 | 0.17947 | 0.20378 | 0.2861 | 0.38096 | 0.49986 | 0.59359 | 0.65954 | 0.71647 | 0.77404 | 0.82986 | 0.88898 | 1.19 | 1.4582
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.048996 | 0.063398 | 0.077995 | 0.094329 | 0.11299 | 0.13892 | 0.17053 | 0.23598 | 0.31107 | 0.38533 | 0.4531 | 0.50967 | 0.56568 | 0.60254 | 0.64034 | 0.67978 | 0.89673 | 1.0845 | 0.11727 | 0.149 | 0.17964 | 0.21379 | 0.25268 | 0.30612 | 0.37113 | 0.51817 | 0.69004 | 0.86193 | 1.0221 | 1.1571 | 1.2913 | 1.3776 | 1.4656 | 1.558 | 2.066 | 2.5269
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.047044 | 0.059357 | 0.069193 | 0.080005 | 0.092024 | 0.11178 | 0.16769 | 0.25829 | 0.33042 | 0.41783 | 0.48847 | 0.55524 | 0.61871 | 0.6644 | 0.70447 | 0.73869 | 0.92337 | 0.99833 | 0.11377 | 0.1423 | 0.16389 | 0.18741 | 0.21337 | 0.25479 | 0.38602 | 0.60062 | 0.77002 | 0.97639 | 1.1399 | 1.2947 | 1.4413 | 1.5439 | 1.635 | 1.7146 | 2.1463 | 2.3217
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.04539 | 0.053594 | 0.061593 | 0.07104 | 0.081637 | 0.097745 | 0.1163 | 0.16441 | 0.21408 | 0.28611 | 0.34455 | 0.39658 | 0.44386 | 0.47869 | 0.50819 | 0.53287 | 0.69591 | 0.8706 | 0.10955 | 0.12772 | 0.1446 | 0.16441 | 0.18648 | 0.21965 | 0.25783 | 0.36686 | 0.48094 | 0.64962 | 0.78383 | 0.90256 | 1.009 | 1.0855 | 1.1513 | 1.2085 | 1.5958 | 2.0179
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.9664 | 2.0171 | 2.0859 | 2.1512 | 2.2143 | 2.2994 | 2.3957 | 2.5483 | 2.6637 | 2.798 | 2.9291 | 3.056 | 3.1912 | 3.326 | 3.4584 | 3.5923 | 4.0176 | 4.2778 | 4.8492 | 4.9558 | 5.0991 | 5.2345 | 5.3651 | 5.5405 | 5.7394 | 6.0593 | 6.3059 | 6.5956 | 6.8747 | 7.1404 | 7.4203 | 7.699 | 7.9721 | 8.2483 | 9.1539 | 9.7279
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.011 | 2.1154 | 2.2617 | 2.4081 | 2.5657 | 2.7654 | 2.9953 | 3.285 | 3.555 | 3.796 | 3.9625 | 4.077 | 4.1848 | 4.3056 | 4.3855 | 4.4575 | 4.8501 | 4.3864 | 4.9461 | 5.1671 | 5.4738 | 5.7783 | 6.1055 | 6.5187 | 6.9942 | 7.6003 | 8.1707 | 8.6828 | 9.0478 | 9.3056 | 9.5499 | 9.811 | 9.9845 | 10.1399 | 10.9996 | 9.7935
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.9951 | 2.0724 | 2.1827 | 2.2914 | 2.3976 | 2.5471 | 2.7338 | 2.98 | 3.1908 | 3.4087 | 3.6156 | 3.8297 | 4.0417 | 4.2621 | 4.3985 | 4.4789 | 5.0241 | 4.5151 | 4.9176 | 5.0872 | 5.3242 | 5.557 | 5.7837 | 6.1021 | 6.5089 | 7.0443 | 7.4996 | 7.965 | 8.3968 | 8.8452 | 9.2906 | 9.7463 | 10.0347 | 10.2106 | 11.4578 | 10.1346
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.9815 | 2.047 | 2.148 | 2.2491 | 2.3474 | 2.4756 | 2.6183 | 2.8183 | 2.9999 | 3.2123 | 3.4172 | 3.6159 | 3.8051 | 3.9884 | 4.0973 | 4.6427 | 4.9701 | 4.5353 | 4.8825 | 5.0225 | 5.2362 | 5.4492 | 5.6556 | 5.9235 | 6.2211 | 6.6419 | 7.0274 | 7.4826 | 7.9145 | 8.3316 | 8.7268 | 9.1056 | 9.332 | 10.6757 | 11.4146 | 10.2701
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Counterfactual | 0.15817 | 0.19792 | 0.2461 | 0.29217 | 0.34984 | 0.41609 | 0.47316 | 0.55771 | 0.63082 | 0.70013 | 0.79834 | 0.89374 | 0.99356 | 1.0822 | 1.154 | 1.2289 | 1.4235 | 1.5164 | 0.36779 | 0.4513 | 0.55162 | 0.64723 | 0.76705 | 0.90458 | 1.0224 | 1.1977 | 1.3512 | 1.4973 | 1.7146 | 1.9236 | 2.1399 | 2.3278 | 2.4743 | 2.6274 | 3.0363 | 3.2425
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.18712 | 0.26252 | 0.38502 | 0.48207 | 0.60161 | 0.7619 | 0.93982 | 1.1354 | 1.3329 | 1.4546 | 1.5181 | 1.5523 | 1.5855 | 1.6129 | 1.6436 | 1.6739 | 1.8251 | 1.9476 | 0.4307 | 0.59047 | 0.8591 | 1.0616 | 1.3121 | 1.6581 | 2.0439 | 2.4619 | 2.8916 | 3.1471 | 3.2849 | 3.363 | 3.4393 | 3.5013 | 3.5701 | 3.6383 | 3.9799 | 4.2671
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.17664 | 0.24375 | 0.31228 | 0.38723 | 0.55998 | 0.67179 | 0.79458 | 0.94063 | 1.061 | 1.1738 | 1.2888 | 1.4034 | 1.5159 | 1.618 | 1.686 | 1.7188 | 1.8762 | 1.9822 | 0.41202 | 0.56156 | 0.70908 | 0.87262 | 1.2744 | 1.518 | 1.7904 | 2.1075 | 2.3656 | 2.6052 | 2.8466 | 3.0869 | 3.3223 | 3.5347 | 3.679 | 3.7528 | 4.1093 | 4.3529
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.16775 | 0.21858 | 0.31072 | 0.37298 | 0.45357 | 0.62007 | 0.72091 | 0.8515 | 0.98099 | 1.0892 | 1.1923 | 1.2936 | 1.3914 | 1.481 | 1.5354 | 1.5578 | 1.6665 | 1.7768 | 0.389 | 0.49779 | 0.70421 | 0.83574 | 1.0069 | 1.388 | 1.6058 | 1.8851 | 2.1677 | 2.3973 | 2.6111 | 2.8204 | 3.0219 | 3.2055 | 3.3191 | 3.3688 | 3.6159 | 3.87
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.43661 | 0.49566 | 0.5641 | 0.63945 | 0.71612 | 0.81184 | 0.92128 | 1.1022 | 1.258 | 1.4248 | 1.5959 | 1.7651 | 1.9534 | 2.1385 | 2.3232 | 2.5047 | 3.0139 | 3.2847 | 0.9864 | 1.1103 | 1.253 | 1.4096 | 1.5682 | 1.7649 | 1.9893 | 2.3633 | 2.6896 | 3.0408 | 3.3976 | 3.7475 | 4.134 | 4.5138 | 4.8923 | 5.2643 | 6.3347 | 6.9256
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.49747 | 0.63474 | 0.79617 | 0.96667 | 1.1559 | 1.4003 | 1.6871 | 2.0536 | 2.4033 | 2.703 | 2.8894 | 3.0081 | 3.1259 | 3.2308 | 3.3344 | 3.4423 | 4.0566 | 4.4127 | 1.1179 | 1.4092 | 1.7445 | 2.0969 | 2.4865 | 2.9902 | 3.5784 | 4.3352 | 5.0626 | 5.6901 | 6.0917 | 6.3555 | 6.6172 | 6.8469 | 7.0735 | 7.309 | 8.637 | 9.4496
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.47462 | 0.57202 | 0.67693 | 0.78159 | 0.90849 | 1.0797 | 1.2896 | 1.5891 | 1.8506 | 2.1314 | 2.4251 | 2.7061 | 2.9856 | 3.2411 | 3.4224 | 3.5293 | 4.1383 | 4.4528 | 1.0771 | 1.2924 | 1.517 | 1.7409 | 2.0113 | 2.3722 | 2.8211 | 3.4583 | 4.0134 | 4.6109 | 5.228 | 5.8189 | 6.4055 | 6.9383 | 7.3218 | 7.5564 | 8.8793 | 9.5838
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.45499 | 0.53721 | 0.63308 | 0.72672 | 0.8374 | 0.97653 | 1.1498 | 1.4048 | 1.631 | 1.8873 | 2.1503 | 2.4079 | 2.6598 | 2.8895 | 3.0401 | 3.1194 | 3.5459 | 3.8708 | 1.0264 | 1.2034 | 1.404 | 1.5993 | 1.8294 | 2.1175 | 2.4756 | 3.0043 | 3.4762 | 4.0139 | 4.5604 | 5.0944 | 5.615 | 6.0877 | 6.402 | 6.5739 | 7.5035 | 8.2319
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.0568 | 2.0982 | 2.1467 | 2.2035 | 2.2778 | 2.3672 | 2.4683 | 2.6267 | 2.7665 | 2.9105 | 3.0569 | 3.1974 | 3.3414 | 3.4844 | 3.6244 | 3.7649 | 4.1351 | 4.3064 | 5.0682 | 5.1549 | 5.2554 | 5.3729 | 5.5271 | 5.7123 | 5.9216 | 6.25 | 6.5439 | 6.8461 | 7.1514 | 7.4416 | 7.7364 | 8.0291 | 8.3152 | 8.6023 | 9.3773 | 9.7517
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.1071 | 2.2056 | 2.3288 | 2.504 | 2.696 | 2.9153 | 3.1715 | 3.4831 | 3.7488 | 3.9706 | 4.0951 | 4.1628 | 4.2266 | 4.2829 | 4.3413 | 4.5611 | 4.8404 | 5.0427 | 5.1768 | 5.3835 | 5.6385 | 6.0093 | 6.4121 | 6.8694 | 7.3999 | 8.0461 | 8.5966 | 9.0591 | 9.3273 | 9.4782 | 9.621 | 9.7454 | 9.8739 | 10.4071 | 11.0254 | 11.4904
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.0883 | 2.155 | 2.265 | 2.3787 | 2.5098 | 2.6691 | 2.8525 | 3.0689 | 3.258 | 3.4619 | 4.0004 | 4.2035 | 4.4052 | 4.5917 | 4.7173 | 4.781 | 5.1439 | 5.3557 | 5.1432 | 5.2892 | 5.5304 | 5.7756 | 6.0566 | 6.3961 | 6.7874 | 7.2429 | 7.6408 | 8.0693 | 9.3286 | 9.7516 | 10.172 | 10.5595 | 10.8248 | 10.9661 | 11.7908 | 12.2715
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.0721 | 2.1259 | 2.1934 | 2.2986 | 2.4143 | 2.5454 | 2.6986 | 2.9135 | 3.106 | 3.3179 | 3.5244 | 3.7135 | 3.9002 | 4.0689 | 4.1741 | 4.9828 | 5.2115 | 5.4189 | 5.1014 | 5.215 | 5.3561 | 5.5823 | 5.8288 | 6.1045 | 6.4241 | 6.8713 | 7.2738 | 7.7178 | 8.1466 | 8.5363 | 8.9203 | 9.2663 | 9.4849 | 11.4928 | 12.0036 | 12.4713
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.4486 | 1.5122 | 1.5844 | 1.6627 | 1.751 | 1.8523 | 1.9722 | 2.1668 | 2.328 | 2.4974 | 2.6776 | 2.8923 | 3.1448 | 3.4973 | 3.7998 | 4.016 | 4.5461 | 4.7548 | 3.5672 | 3.6996 | 3.8491 | 4.0109 | 4.1929 | 4.4012 | 4.6478 | 5.0453 | 5.3766 | 5.7251 | 6.0952 | 6.5369 | 7.055 | 7.7875 | 8.4162 | 8.8607 | 9.9568 | 10.4055
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.5267 | 1.6775 | 1.9163 | 2.1865 | 2.48 | 2.7939 | 3.1665 | 3.6409 | 4.0802 | 4.4622 | 4.7183 | 4.9216 | 5.1468 | 5.3164 | 5.3886 | 5.4797 | 5.8674 | 6.2162 | 3.736 | 4.0506 | 4.5677 | 5.153 | 5.7834 | 6.4534 | 7.2379 | 8.2374 | 9.1703 | 9.9847 | 10.5509 | 11.0119 | 11.5294 | 11.9182 | 12.0801 | 12.2933 | 13.2023 | 14.0193
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.4979 | 1.5978 | 1.7596 | 1.9287 | 2.1171 | 2.3425 | 2.588 | 2.934 | 3.2627 | 3.6151 | 3.9724 | 4.3475 | 4.7128 | 5.0187 | 5.2122 | 5.3038 | 5.7035 | 6.0319 | 3.6847 | 3.9014 | 4.2646 | 4.6419 | 5.06 | 5.549 | 6.0712 | 6.7996 | 7.4991 | 8.2472 | 8.9976 | 9.784 | 10.5505 | 11.1883 | 11.5998 | 11.8071 | 12.7225 | 13.4835
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.4727 | 1.5561 | 1.6571 | 1.7686 | 1.8956 | 2.0483 | 2.243 | 2.5226 | 2.78 | 3.1042 | 3.4683 | 3.8249 | 4.1675 | 4.4522 | 4.6055 | 4.6628 | 4.9057 | 5.1167 | 3.6198 | 3.795 | 4.0055 | 4.2377 | 4.5016 | 4.8183 | 5.2216 | 5.7955 | 6.327 | 7.003 | 7.7654 | 8.5085 | 9.2199 | 9.8078 | 10.1262 | 10.2522 | 10.7929 | 11.2642
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.65642 | 0.69849 | 0.74769 | 0.80457 | 0.86951 | 0.9449 | 1.0301 | 1.1816 | 1.3362 | 1.5284 | 1.7414 | 1.918 | 2.0931 | 2.2668 | 2.4423 | 2.6248 | 3.0665 | 3.2875 | 1.6057 | 1.694 | 1.7959 | 1.9135 | 2.0474 | 2.2025 | 2.3773 | 2.6925 | 3.0195 | 3.4287 | 3.8796 | 4.2489 | 4.6114 | 4.9709 | 5.3362 | 5.7165 | 6.6517 | 7.1371
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.70336 | 0.805 | 0.9436 | 1.0839 | 1.2432 | 1.44 | 1.6981 | 2.0398 | 2.3569 | 2.6351 | 2.825 | 2.9356 | 3.0446 | 3.1388 | 3.2352 | 3.3302 | 3.8108 | 4.0672 | 1.7069 | 1.9211 | 2.2097 | 2.4999 | 2.8289 | 3.2371 | 3.7726 | 4.489 | 5.1576 | 5.7522 | 6.1718 | 6.4206 | 6.6673 | 6.8776 | 7.0918 | 7.3044 | 8.4209 | 9.0243
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.68587 | 0.77763 | 0.88336 | 0.98793 | 1.1036 | 1.2527 | 1.4468 | 1.7178 | 1.9641 | 2.2296 | 2.4804 | 2.9464 | 3.1693 | 3.3701 | 3.5211 | 3.6163 | 3.9718 | 4.1851 | 1.6757 | 1.877 | 2.1043 | 2.3282 | 2.5751 | 2.8919 | 3.3114 | 3.8955 | 4.4283 | 5.0044 | 5.5384 | 6.619 | 7.0929 | 7.5161 | 7.8398 | 8.0517 | 8.8543 | 9.3381
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.67079 | 0.74297 | 0.84183 | 0.92636 | 1.0249 | 1.1602 | 1.3286 | 1.5725 | 1.7972 | 2.0482 | 2.3017 | 2.5229 | 2.7403 | 2.9318 | 3.0683 | 3.1457 | 3.5456 | 3.7941 | 1.6369 | 1.791 | 1.9996 | 2.1759 | 2.3814 | 2.6648 | 3.0171 | 3.5297 | 4.0047 | 4.5398 | 5.0776 | 5.5424 | 5.9961 | 6.3945 | 6.6827 | 6.8536 | 7.7857 | 8.3551
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.27944 | 0.34237 | 0.42148 | 0.51157 | 0.6131 | 0.729 | 0.85904 | 1.0622 | 1.2455 | 1.6252 | 1.8081 | 1.9967 | 2.2027 | 2.4072 | 2.6143 | 2.829 | 3.3921 | 3.6679 | 0.63335 | 0.76515 | 0.92897 | 1.1155 | 1.3254 | 1.5644 | 1.8321 | 2.252 | 2.642 | 3.5185 | 3.8998 | 4.2887 | 4.7105 | 5.1287 | 5.5556 | 5.999 | 7.1831 | 7.7899
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.35398 | 0.50147 | 0.80203 | 1.0219 | 1.2716 | 1.5343 | 1.8508 | 2.4939 | 2.8756 | 3.2087 | 3.4028 | 3.5022 | 3.5997 | 3.6774 | 3.757 | 3.8365 | 4.2299 | 4.5823 | 0.79429 | 1.1036 | 1.7755 | 2.2309 | 2.7474 | 3.2881 | 3.9362 | 5.3649 | 6.158 | 6.861 | 7.2882 | 7.5148 | 7.7384 | 7.9146 | 8.094 | 8.2743 | 9.1752 | 9.9958
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.32623 | 0.42494 | 0.54189 | 0.82773 | 0.97961 | 1.156 | 1.383 | 1.9413 | 2.2317 | 2.5553 | 2.8635 | 3.1716 | 3.478 | 3.7546 | 3.9366 | 4.0304 | 4.474 | 4.78 | 0.7448 | 0.96075 | 1.2109 | 1.8782 | 2.2016 | 2.5742 | 3.0601 | 4.3348 | 4.9563 | 5.6524 | 6.2999 | 6.9475 | 7.591 | 8.1679 | 8.5551 | 8.7659 | 9.7742 | 10.4737
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.30251 | 0.38318 | 0.60285 | 0.7244 | 0.86006 | 1.0206 | 1.2098 | 1.7321 | 1.9835 | 2.273 | 2.5744 | 2.8647 | 3.1402 | 3.3865 | 3.5376 | 3.6057 | 3.9357 | 4.2491 | 0.68349 | 0.85393 | 1.3601 | 1.614 | 1.8967 | 2.2303 | 2.6209 | 3.8026 | 4.3261 | 4.9351 | 5.5672 | 6.1712 | 6.7402 | 7.2467 | 7.5625 | 7.7129 | 8.4615 | 9.18
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Counterfactual | 0.2837 | 0.31623 | 0.4386 | 0.47973 | 0.52667 | 0.57401 | 0.62927 | 0.71896 | 0.79473 | 0.87921 | 0.96588 | 1.12 | 1.3432 | 1.5675 | 1.7471 | 1.8421 | 2.0907 | 2.2121 | 0.61199 | 0.67994 | 0.92734 | 1.0125 | 1.1095 | 1.2069 | 1.3201 | 1.5055 | 1.6644 | 1.8425 | 2.023 | 2.3461 | 2.8144 | 3.2859 | 3.6638 | 3.86 | 4.3814 | 4.647
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Electric Engagement | 0.31572 | 0.47475 | 0.56082 | 0.65763 | 0.76747 | 0.88011 | 1.0227 | 1.2277 | 1.4471 | 1.6917 | 1.9129 | 2.0583 | 2.1961 | 2.2347 | 2.2747 | 2.367 | 2.5523 | 2.7019 | 0.68106 | 1.0066 | 1.1853 | 1.3859 | 1.613 | 1.8446 | 2.1365 | 2.5622 | 3.0239 | 3.5477 | 4.0332 | 4.3544 | 4.6608 | 4.7469 | 4.8355 | 5.0291 | 5.4488 | 5.7965
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Holistic Transition | 0.30397 | 0.46756 | 0.52471 | 0.59495 | 0.70977 | 0.85724 | 1.0346 | 1.2507 | 1.4136 | 1.5922 | 1.7627 | 1.9293 | 2.0729 | 2.1947 | 2.277 | 2.3724 | 2.5712 | 2.6984 | 0.66018 | 1.0014 | 1.124 | 1.2745 | 1.5214 | 1.8382 | 2.2219 | 2.687 | 3.0376 | 3.4233 | 3.7842 | 4.1374 | 4.4404 | 4.6939 | 4.8684 | 5.0689 | 5.5164 | 5.8041
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Hydrogen Evolution | 0.29362 | 0.4235 | 0.47398 | 0.53242 | 0.59995 | 0.66853 | 0.78141 | 0.97517 | 1.1831 | 1.4372 | 1.6391 | 1.8273 | 2.0073 | 2.1179 | 2.189 | 2.2429 | 2.3903 | 2.5248 | 0.63354 | 0.89829 | 1.0039 | 1.126 | 1.2665 | 1.4084 | 1.6443 | 2.0534 | 2.4955 | 3.0414 | 3.4707 | 3.8684 | 4.2471 | 4.4742 | 4.6222 | 4.736 | 5.0673 | 5.3739
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.22843 | 0.26719 | 0.31176 | 0.36546 | 0.42118 | 0.48314 | 0.55331 | 0.67158 | 0.76674 | 0.86863 | 0.97438 | 1.0866 | 1.2118 | 1.3358 | 1.457 | 1.5794 | 1.9091 | 2.0863 | 0.51902 | 0.60082 | 0.69343 | 0.80467 | 0.91965 | 1.0472 | 1.1912 | 1.4323 | 1.6273 | 1.8359 | 2.0522 | 2.281 | 2.5356 | 2.7874 | 3.0333 | 3.2816 | 3.959 | 4.3318
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.27232 | 0.36472 | 0.48005 | 0.61252 | 0.75617 | 0.91388 | 1.1058 | 1.3492 | 1.5697 | 1.7531 | 1.8476 | 1.8981 | 1.9386 | 1.9754 | 2.0123 | 2.0442 | 2.1898 | 2.3422 | 0.61379 | 0.80918 | 1.0483 | 1.3224 | 1.6184 | 1.9426 | 2.3354 | 2.8326 | 3.2835 | 3.6598 | 3.858 | 3.9677 | 4.0567 | 4.1382 | 4.2196 | 4.2908 | 4.6226 | 4.9678
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.25586 | 0.3206 | 0.39477 | 0.47834 | 0.56703 | 0.671 | 0.79217 | 0.96994 | 1.124 | 1.2909 | 1.4652 | 1.6405 | 1.8108 | 1.9704 | 2.0759 | 2.1243 | 2.3277 | 2.5147 | 0.58434 | 0.72781 | 0.88706 | 1.0658 | 1.2544 | 1.4735 | 1.7271 | 2.095 | 2.4144 | 2.7595 | 3.1187 | 3.4796 | 3.8309 | 4.1606 | 4.3819 | 4.4891 | 4.9472 | 5.3721
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.24221 | 0.29345 | 0.35943 | 0.43738 | 0.52057 | 0.61694 | 0.73282 | 0.90742 | 1.059 | 1.2249 | 1.3965 | 1.5629 | 1.7248 | 1.8706 | 1.9611 | 1.9955 | 2.1309 | 2.2698 | 0.54896 | 0.65817 | 0.79596 | 0.95846 | 1.131 | 1.3302 | 1.5684 | 1.9254 | 2.2356 | 2.5742 | 2.9237 | 3.2624 | 3.592 | 3.889 | 4.0755 | 4.1496 | 4.4476 | 4.7545
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.34936 | 0.37022 | 0.39248 | 0.41717 | 0.44504 | 0.48316 | 0.52432 | 0.61824 | 0.71129 | 0.82088 | 0.91579 | 0.99698 | 1.0765 | 1.1568 | 1.2364 | 1.3166 | 1.6284 | 1.8685 | 0.74819 | 0.79282 | 0.83922 | 0.89055 | 0.94827 | 1.0266 | 1.1111 | 1.3163 | 1.5257 | 1.7758 | 1.9876 | 2.1634 | 2.3317 | 2.5017 | 2.6702 | 2.8399 | 3.5327 | 4.0851
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.3714 | 0.42204 | 0.48008 | 0.54691 | 0.62209 | 0.7175 | 0.83086 | 1.0156 | 1.2088 | 1.3921 | 1.5367 | 1.6465 | 1.7518 | 1.8755 | 1.949 | 2.0237 | 2.5223 | 2.8716 | 0.79568 | 0.90423 | 1.0249 | 1.1634 | 1.3187 | 1.5145 | 1.7462 | 2.1441 | 2.5683 | 2.9749 | 3.3061 | 3.563 | 3.8114 | 4.0808 | 4.2496 | 4.4226 | 5.5478 | 6.3961
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.36297 | 0.40088 | 0.43846 | 0.481 | 0.52866 | 0.59513 | 0.72693 | 0.93047 | 1.0976 | 1.2941 | 1.4663 | 1.6344 | 1.7931 | 1.9697 | 2.0668 | 2.1344 | 2.5899 | 2.7555 | 0.78056 | 0.86591 | 0.94707 | 1.0383 | 1.1399 | 1.2792 | 1.5774 | 2.0417 | 2.4194 | 2.8659 | 3.2488 | 3.6215 | 3.9729 | 4.3463 | 4.5609 | 4.7163 | 5.7393 | 6.1257
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.35625 | 0.38437 | 0.41656 | 0.4541 | 0.49693 | 0.55531 | 0.62287 | 0.75585 | 0.88462 | 1.0532 | 1.2013 | 1.3401 | 1.4648 | 1.5915 | 1.665 | 1.7146 | 2.0589 | 2.3766 | 0.76314 | 0.82388 | 0.89132 | 0.9696 | 1.0587 | 1.1791 | 1.3178 | 1.6065 | 1.8896 | 2.2683 | 2.5938 | 2.8964 | 3.166 | 3.4315 | 3.5908 | 3.7037 | 4.4965 | 5.2579
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | 0.82843 | 1.0054 | 1.2194 | 1.4391 | 1.6923 | 1.9783 | 2.3113 | 2.8408 | 3.2708 | 3.7374 | 4.216 | 4.7657 | 5.4057 | 6.0489 | 6.6756 | 7.2591 | 8.5626 | 8.9616 | 1.8972 | 2.266 | 2.7083 | 3.1624 | 3.6841 | 4.2724 | 4.9559 | 6.0354 | 6.9173 | 7.875 | 8.8551 | 9.9811 | 11.2908 | 12.6059 | 13.8958 | 15.0951 | 17.7831 | 18.6509
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | 1.048 | 1.4702 | 1.9922 | 2.5772 | 3.2397 | 3.9694 | 4.8663 | 5.9699 | 7.0184 | 7.9714 | 8.5129 | 8.685 | 8.8076 | 8.9502 | 9.0903 | 9.2262 | 9.865 | 10.4391 | 2.3717 | 3.2532 | 4.3321 | 5.5391 | 6.9036 | 8.4036 | 10.2396 | 12.4925 | 14.6448 | 16.6357 | 17.8107 | 18.1962 | 18.4741 | 18.7951 | 19.1102 | 19.4157 | 20.8623 | 22.1664
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | 0.96664 | 1.2717 | 1.6016 | 1.9568 | 2.3819 | 2.9089 | 3.5669 | 4.4063 | 5.1041 | 5.8771 | 6.6285 | 7.4108 | 8.1966 | 8.9316 | 9.3843 | 9.5603 | 10.3459 | 10.9571 | 2.2269 | 2.8901 | 3.5951 | 4.3534 | 5.2585 | 6.3765 | 7.7679 | 9.5137 | 10.9778 | 12.6059 | 14.1506 | 15.7602 | 17.3795 | 18.8947 | 19.8442 | 20.2391 | 22.0199 | 23.4243
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | 0.89467 | 1.1257 | 1.4202 | 1.7262 | 2.0868 | 2.5112 | 3.0382 | 3.8622 | 4.5982 | 5.4121 | 6.1894 | 6.9162 | 7.616 | 8.2839 | 8.6601 | 8.7743 | 9.3023 | 9.7432 | 2.0415 | 2.5275 | 3.14 | 3.7778 | 4.5271 | 5.4066 | 6.4954 | 8.193 | 9.7155 | 11.4055 | 13.0126 | 14.5004 | 15.9231 | 17.284 | 18.0606 | 18.3124 | 19.487 | 20.4763
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.6471 | 1.7675 | 1.9093 | 2.0716 | 2.2585 | 2.0671 | 2.309 | 2.7305 | 3.1976 | 3.7584 | 4.2727 | 4.6251 | 5.0102 | 5.3969 | 5.7815 | 6.1828 | 7.2539 | 7.7895 | 3.8359 | 4.0872 | 4.3808 | 4.7164 | 5.1017 | 4.5266 | 5.0232 | 5.893 | 6.8734 | 8.0576 | 9.1364 | 9.861 | 10.6467 | 11.4352 | 12.2237 | 13.0483 | 15.2885 | 16.4531
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.7864 | 2.0724 | 2.4497 | 2.8543 | 3.3144 | 3.489 | 4.2592 | 5.2686 | 6.0925 | 6.7396 | 7.0916 | 7.279 | 7.4558 | 7.6115 | 7.7665 | 7.9214 | 8.7923 | 9.4153 | 4.1364 | 4.7355 | 5.5183 | 6.3543 | 7.3034 | 7.49 | 9.0888 | 11.1974 | 12.9161 | 14.274 | 15.0406 | 15.462 | 15.863 | 16.21 | 16.5545 | 16.9006 | 18.8782 | 20.322
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.7347 | 1.9575 | 2.2284 | 2.5475 | 2.8992 | 2.9017 | 3.4194 | 4.097 | 4.6629 | 5.2708 | 5.8478 | 6.5788 | 7.1485 | 7.6626 | 8.0127 | 8.1911 | 9.0536 | 9.6092 | 4.0444 | 4.5304 | 5.1114 | 5.7936 | 6.5448 | 6.3948 | 7.5035 | 8.9433 | 10.1485 | 11.4456 | 12.652 | 14.2457 | 15.4373 | 16.506 | 17.2463 | 17.6429 | 19.5771 | 20.8389
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.6894 | 1.8706 | 2.1192 | 2.3631 | 2.6636 | 2.6607 | 3.1493 | 3.8066 | 4.3347 | 4.8937 | 5.4535 | 5.9932 | 6.5175 | 6.9892 | 7.2832 | 7.4145 | 8.1302 | 8.6919 | 3.9277 | 4.3114 | 4.8337 | 5.3428 | 5.9717 | 5.8015 | 6.8244 | 8.1952 | 9.2965 | 10.4663 | 11.6315 | 12.7477 | 13.8256 | 14.7921 | 15.4028 | 15.6897 | 17.3108 | 18.5887
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.0246 | 2.0635 | 2.1086 | 2.1597 | 2.2172 | 2.2824 | 2.3548 | 2.4681 | 2.5678 | 2.6795 | 2.7869 | 2.8906 | 3.0043 | 3.1168 | 3.2259 | 3.3333 | 3.622 | 3.7636 | 5.0266 | 5.1077 | 5.2009 | 5.3064 | 5.4248 | 5.5592 | 5.7082 | 5.9407 | 6.1475 | 6.3799 | 6.6022 | 6.8152 | 7.0478 | 7.2774 | 7.5 | 7.7192 | 8.3196 | 8.6237
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.0615 | 2.1469 | 2.2598 | 2.3744 | 2.5043 | 2.6557 | 2.8395 | 3.0571 | 3.2486 | 3.4076 | 3.4937 | 3.5445 | 3.5909 | 3.6325 | 3.6762 | 3.6813 | 3.8585 | 4.015 | 5.1064 | 5.2856 | 5.5207 | 5.758 | 6.027 | 6.341 | 6.7211 | 7.1685 | 7.5629 | 7.8915 | 8.0743 | 8.1861 | 8.2889 | 8.3803 | 8.4756 | 8.4773 | 8.8711 | 9.2224
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.0478 | 2.1214 | 2.2073 | 2.292 | 2.3791 | 2.4834 | 2.6027 | 2.7653 | 2.9061 | 3.0554 | 3.2106 | 3.3632 | 3.5141 | 3.6103 | 3.7057 | 3.7538 | 4.0148 | 4.1911 | 5.0822 | 5.242 | 5.4261 | 5.607 | 5.7928 | 6.0138 | 6.2659 | 6.6058 | 6.9003 | 7.2117 | 7.5326 | 7.849 | 8.1623 | 8.3429 | 8.5436 | 8.6497 | 9.2414 | 9.6372
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.0356 | 2.0974 | 2.1821 | 2.2523 | 2.3367 | 2.4345 | 2.545 | 2.7 | 2.8352 | 2.9799 | 3.1323 | 3.2793 | 3.4265 | 3.557 | 3.6415 | 4.6147 | 4.7858 | 4.9367 | 5.0508 | 5.1819 | 5.3602 | 5.5072 | 5.6838 | 5.8883 | 6.1175 | 6.4377 | 6.7169 | 7.0154 | 7.3285 | 7.6307 | 7.9326 | 8.2 | 8.3752 | 10.7961 | 11.1745 | 11.5107
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.15266 | 0.19689 | 0.25157 | 0.30332 | 0.35327 | 0.40871 | 0.47072 | 0.5552 | 0.6236 | 0.70082 | 0.77551 | 0.84897 | 0.92686 | 1.007 | 1.0828 | 1.1622 | 1.3909 | 1.509 | 0.3473 | 0.43995 | 0.5538 | 0.6609 | 0.76433 | 0.87893 | 1.0067 | 1.1806 | 1.3231 | 1.4843 | 1.6393 | 1.7899 | 1.9486 | 2.1118 | 2.2662 | 2.4275 | 2.9045 | 3.1588
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.18358 | 0.26698 | 0.37011 | 0.46998 | 0.57945 | 0.70518 | 0.84708 | 1.0085 | 1.1583 | 1.2795 | 1.3485 | 1.3881 | 1.4254 | 1.4578 | 1.4925 | 1.5285 | 1.7168 | 1.8603 | 0.41487 | 0.59152 | 0.80805 | 1.0162 | 1.2439 | 1.5051 | 1.7982 | 2.1304 | 2.4399 | 2.6916 | 2.839 | 2.9267 | 3.0101 | 3.0814 | 3.1575 | 3.2362 | 3.6522 | 3.9769
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.17311 | 0.23813 | 0.31825 | 0.38814 | 0.46321 | 0.54586 | 0.64476 | 0.77018 | 0.87969 | 0.99755 | 1.123 | 1.245 | 1.367 | 1.476 | 1.5547 | 1.5994 | 1.8034 | 1.9371 | 0.39619 | 0.53777 | 0.70971 | 0.85944 | 1.0194 | 1.1946 | 1.4049 | 1.669 | 1.8995 | 2.148 | 2.4094 | 2.6638 | 2.9178 | 3.1438 | 3.3093 | 3.4071 | 3.8571 | 4.1553
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.16398 | 0.22163 | 0.2957 | 0.36051 | 0.43383 | 0.51903 | 0.60713 | 0.71991 | 0.81832 | 0.92915 | 1.0428 | 1.1529 | 1.2619 | 1.3582 | 1.4198 | 1.4535 | 1.6031 | 1.7364 | 0.37275 | 0.49582 | 0.65258 | 0.78898 | 0.9429 | 1.1216 | 1.3048 | 1.537 | 1.7402 | 1.97 | 2.204 | 2.4304 | 2.6542 | 2.8511 | 2.9783 | 3.0508 | 3.3796 | 3.6753
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.59986 | 0.75295 | 0.93929 | 1.1632 | 1.4135 | 1.7004 | 2.0858 | 2.6627 | 3.2213 | 3.6559 | 4.1359 | 4.6254 | 5.1501 | 5.6645 | 6.1481 | 6.6207 | 7.8045 | 8.3123 | 1.3465 | 1.6657 | 2.0514 | 2.5146 | 3.0327 | 3.6281 | 4.4315 | 5.6287 | 6.808 | 7.7077 | 8.7106 | 9.7283 | 10.8122 | 11.8691 | 12.8561 | 13.8196 | 16.2799 | 17.3788
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.77053 | 1.1457 | 1.6207 | 2.1779 | 2.8665 | 3.6272 | 4.5068 | 5.5349 | 6.5489 | 7.2893 | 7.6683 | 7.8809 | 8.0782 | 8.2367 | 8.3928 | 8.5416 | 9.2841 | 9.8795 | 1.7156 | 2.5033 | 3.4917 | 4.6647 | 6.1259 | 7.7378 | 9.5829 | 11.7215 | 13.8597 | 15.4013 | 16.214 | 16.6904 | 17.1355 | 17.4922 | 17.843 | 18.179 | 19.8525 | 21.2192
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.70689 | 0.969 | 1.3308 | 1.7691 | 2.2475 | 2.7997 | 3.4421 | 4.2723 | 4.9574 | 5.6419 | 6.3479 | 7.0116 | 7.6576 | 8.2585 | 8.6484 | 8.8323 | 9.7064 | 10.3512 | 1.6025 | 2.1734 | 2.9635 | 3.9218 | 4.9644 | 6.1665 | 7.5538 | 9.3226 | 10.7728 | 12.21 | 13.684 | 15.0668 | 16.4125 | 17.6618 | 18.4878 | 18.901 | 20.869 | 22.3393
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.65218 | 0.87695 | 1.1684 | 1.5639 | 2.0303 | 2.5584 | 3.1075 | 3.8351 | 4.5463 | 5.2211 | 5.899 | 6.5547 | 7.1919 | 7.7686 | 8.1133 | 8.2518 | 8.8781 | 9.4166 | 1.4606 | 1.9365 | 2.5485 | 3.396 | 4.4043 | 5.5475 | 6.7121 | 8.2336 | 9.7472 | 11.1564 | 12.5559 | 13.9068 | 15.2182 | 16.4029 | 17.1208 | 17.4264 | 18.8223 | 20.0342
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.5584 | 1.6487 | 1.7505 | 1.8644 | 1.9978 | 2.1505 | 2.3272 | 1.662 | 1.8892 | 2.1417 | 2.4299 | 2.7218 | 3.0403 | 3.3456 | 3.6329 | 3.9255 | 4.6667 | 5.0225 | 3.8309 | 4.0199 | 4.2306 | 4.4658 | 4.7406 | 5.0548 | 5.4178 | 3.626 | 4.0921 | 4.6111 | 5.214 | 5.8222 | 6.482 | 7.1095 | 7.6943 | 8.2899 | 9.8229 | 10.5781
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.6584 | 1.8738 | 2.127 | 2.4116 | 2.7398 | 3.1068 | 3.6205 | 3.2778 | 3.8453 | 4.2622 | 4.4773 | 4.5995 | 4.7096 | 4.8124 | 4.9166 | 5.0094 | 5.5021 | 5.8518 | 4.0465 | 4.4988 | 5.0221 | 5.609 | 6.2851 | 7.0414 | 8.1224 | 7.0139 | 8.208 | 9.07 | 9.5254 | 9.7941 | 10.0386 | 10.2666 | 10.4969 | 10.7039 | 11.835 | 12.6273
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.6205 | 1.7694 | 1.929 | 2.1046 | 2.311 | 2.6265 | 2.9838 | 2.4891 | 2.8636 | 3.2551 | 3.6638 | 4.0536 | 4.4353 | 4.7925 | 5.1935 | 5.3172 | 5.8399 | 6.2532 | 3.9789 | 4.3046 | 4.646 | 5.0205 | 5.4591 | 6.1517 | 6.927 | 5.5164 | 6.3026 | 7.1177 | 7.9661 | 8.7762 | 9.5693 | 10.3117 | 11.2198 | 11.494 | 12.6666 | 13.6029
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.5889 | 1.7121 | 1.8531 | 2.0153 | 2.2103 | 2.4407 | 2.7572 | 2.2457 | 2.6607 | 3.0571 | 3.456 | 3.8433 | 4.2255 | 4.5735 | 4.7942 | 4.8892 | 5.3486 | 5.6758 | 3.897 | 4.1576 | 4.4509 | 4.788 | 5.1933 | 5.6716 | 6.3429 | 4.8882 | 5.7725 | 6.5947 | 7.4127 | 8.2064 | 8.9894 | 9.7028 | 10.1612 | 10.3676 | 11.4045 | 12.1282
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.61836 | 0.74466 | 0.88939 | 1.0606 | 1.2373 | 1.4247 | 1.6276 | 1.9522 | 2.2131 | 2.495 | 2.911 | 3.3545 | 3.873 | 4.3839 | 4.7786 | 5.1327 | 5.9968 | 6.3562 | 1.4485 | 1.7127 | 2.0129 | 2.3673 | 2.7325 | 3.1186 | 3.5356 | 4.1971 | 4.7318 | 5.3093 | 6.2169 | 7.1901 | 8.3337 | 9.4563 | 10.2923 | 11.0182 | 12.7998 | 13.5643
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.74493 | 1.019 | 1.3636 | 1.7622 | 2.1946 | 2.6441 | 3.2685 | 4.0779 | 5.052 | 5.7364 | 6.1172 | 6.3468 | 6.5606 | 6.7634 | 6.8744 | 6.9732 | 7.4196 | 7.8003 | 1.7225 | 2.2987 | 3.0177 | 3.8486 | 4.7468 | 5.6769 | 6.998 | 8.724 | 10.8969 | 12.398 | 13.265 | 13.8108 | 14.3218 | 14.8033 | 15.0488 | 15.2703 | 16.2799 | 17.1445
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.69905 | 0.89213 | 1.1228 | 1.3882 | 1.6739 | 2.0709 | 2.5902 | 3.3095 | 3.9896 | 4.6286 | 5.2194 | 5.8058 | 6.3778 | 6.8235 | 7.1147 | 7.2476 | 7.8072 | 8.2253 | 1.6409 | 2.0625 | 2.5593 | 3.1293 | 3.741 | 4.6206 | 5.7903 | 7.3916 | 8.9203 | 10.3304 | 11.6049 | 12.8661 | 14.0934 | 15.0154 | 15.6282 | 15.9233 | 17.1819 | 18.123
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.6592 | 0.82268 | 1.0253 | 1.2655 | 1.5188 | 1.7902 | 2.1589 | 2.7314 | 3.4712 | 4.1485 | 4.746 | 5.3194 | 5.8653 | 6.3746 | 6.6252 | 6.7204 | 7.1111 | 7.4503 | 1.5379 | 1.8844 | 2.3094 | 2.8135 | 3.3434 | 3.9085 | 4.6948 | 5.9251 | 7.6039 | 9.1108 | 10.4019 | 11.6343 | 12.8006 | 13.8886 | 14.4073 | 14.6143 | 15.4753 | 16.2227
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Counterfactual | 2.1555 | 2.3115 | 2.5279 | 2.7812 | 3.0567 | 3.3493 | 3.6826 | 4.1904 | 4.6058 | 5.0438 | 5.4836 | 5.9188 | 6.4051 | 6.8963 | 7.3648 | 7.846 | 9.0382 | 9.5267 | 5.2204 | 5.5473 | 5.9994 | 6.5284 | 7.1001 | 7.7047 | 8.3925 | 9.4325 | 10.2887 | 11.1912 | 12.0949 | 12.9841 | 13.9748 | 14.975 | 15.9272 | 16.9057 | 19.3688 | 20.4136
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.3416 | 2.7305 | 3.241 | 3.8976 | 4.5427 | 5.2337 | 6.0497 | 7.041 | 7.9463 | 8.7038 | 9.084 | 9.2393 | 9.3837 | 9.5213 | 9.6804 | 9.8267 | 10.5205 | 11.0641 | 5.6253 | 6.4534 | 7.5278 | 8.9355 | 10.2802 | 11.7177 | 13.4031 | 15.4432 | 17.3118 | 18.8826 | 19.6929 | 20.041 | 20.3687 | 20.6786 | 21.0319 | 21.3611 | 22.943 | 24.1778
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.276 | 2.5498 | 2.9025 | 3.3021 | 3.7586 | 4.2849 | 4.8267 | 5.5345 | 6.1625 | 6.8345 | 7.5186 | 8.2873 | 8.9359 | 9.553 | 9.9559 | 10.1404 | 10.971 | 11.6229 | 5.5084 | 6.1162 | 6.8851 | 7.7494 | 8.7291 | 9.8539 | 10.9991 | 12.4733 | 13.7853 | 15.185 | 16.6032 | 18.2419 | 19.5816 | 20.8586 | 21.7069 | 22.1172 | 23.9953 | 25.4775
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.2189 | 2.4514 | 2.7588 | 3.1221 | 3.5153 | 3.9421 | 4.4426 | 5.1382 | 5.7588 | 6.4232 | 7.0666 | 7.6774 | 8.2801 | 8.8446 | 9.1938 | 9.3278 | 10.4219 | 10.9178 | 5.3614 | 5.8649 | 6.5189 | 7.2894 | 8.1163 | 9.0103 | 10.0514 | 11.4851 | 12.7682 | 14.1393 | 15.4561 | 16.7027 | 17.9325 | 19.0856 | 19.8101 | 20.1034 | 22.6781 | 23.7769
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.53704 | 0.5901 | 0.64821 | 0.71772 | 0.79478 | 0.8801 | 0.97844 | 1.1389 | 1.2806 | 1.4388 | 1.6334 | 1.826 | 2.0354 | 2.2078 | 2.3523 | 2.505 | 2.9204 | 3.1537 | 1.2936 | 1.4053 | 1.5262 | 1.6704 | 1.8299 | 2.0063 | 2.2091 | 2.539 | 2.8334 | 3.163 | 3.5831 | 3.9977 | 4.4458 | 4.8079 | 5.1015 | 5.4122 | 6.2721 | 6.7675
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.58754 | 0.70404 | 0.84663 | 1.008 | 1.1953 | 1.4066 | 1.7012 | 2.0704 | 2.486 | 2.7583 | 2.9151 | 3.013 | 3.0881 | 3.1377 | 3.193 | 3.2413 | 3.4718 | 3.6855 | 1.4028 | 1.6496 | 1.9469 | 2.282 | 2.67 | 3.1079 | 3.7309 | 4.5176 | 5.4364 | 6.0176 | 6.3605 | 6.578 | 6.7454 | 6.8554 | 6.9774 | 7.0857 | 7.6098 | 8.1004
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.5692 | 0.6589 | 0.75829 | 0.86448 | 0.98403 | 1.1743 | 1.4309 | 1.7582 | 2.0179 | 2.2655 | 2.4983 | 2.7266 | 2.9464 | 3.1355 | 3.2646 | 3.3308 | 3.6187 | 3.8463 | 1.3701 | 1.5677 | 1.7815 | 2.0093 | 2.2649 | 2.6832 | 3.2573 | 3.9817 | 4.5505 | 5.0811 | 5.5709 | 6.0473 | 6.5061 | 6.8977 | 7.1695 | 7.316 | 7.9633 | 8.4783
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.55371 | 0.62616 | 0.71701 | 0.81446 | 0.93239 | 1.0779 | 1.2715 | 1.5513 | 1.8845 | 2.1644 | 2.4091 | 2.6389 | 2.8536 | 3.0281 | 3.1474 | 3.2022 | 3.4247 | 3.628 | 1.33 | 1.4846 | 1.6758 | 1.88 | 2.1265 | 2.4307 | 2.8429 | 3.4425 | 4.1878 | 4.7936 | 5.307 | 5.7844 | 6.226 | 6.5821 | 6.8282 | 6.9459 | 7.4365 | 7.8909
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.31237 | 0.37576 | 0.45102 | 0.53034 | 0.61527 | 0.72007 | 0.83568 | 1.0456 | 1.2375 | 1.4418 | 1.6358 | 1.814 | 1.999 | 2.1817 | 2.3593 | 2.5403 | 3.125 | 3.528 | 0.72856 | 0.86297 | 1.0196 | 1.1842 | 1.36 | 1.5758 | 1.8136 | 2.2596 | 2.6767 | 3.1269 | 3.5477 | 3.9259 | 4.3119 | 4.6924 | 5.0611 | 5.4366 | 6.7034 | 7.6104
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.36831 | 0.51048 | 0.68698 | 0.86842 | 1.0723 | 1.316 | 1.6073 | 2.0139 | 2.4153 | 2.7586 | 2.9987 | 3.1672 | 3.3274 | 3.4458 | 3.5718 | 3.6971 | 4.3538 | 4.8878 | 0.84907 | 1.1526 | 1.525 | 1.9019 | 2.3247 | 2.8292 | 3.4297 | 4.29 | 5.1509 | 5.8938 | 6.4326 | 6.8211 | 7.1935 | 7.4623 | 7.7466 | 8.0316 | 9.5321 | 10.8112
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.34727 | 0.45845 | 0.57295 | 0.69484 | 0.84822 | 1.0198 | 1.2821 | 1.6656 | 1.982 | 2.3312 | 2.6557 | 2.9658 | 3.2646 | 3.5158 | 3.7083 | 3.831 | 4.4446 | 4.7763 | 0.81138 | 1.0596 | 1.3063 | 1.5686 | 1.9037 | 2.2655 | 2.8445 | 3.6944 | 4.3907 | 5.1634 | 5.8674 | 6.5399 | 7.1868 | 7.7204 | 8.1373 | 8.4145 | 9.813 | 10.5732
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.32977 | 0.41678 | 0.52902 | 0.64009 | 0.76565 | 0.93148 | 1.1115 | 1.4058 | 1.6762 | 1.9917 | 2.2843 | 2.5595 | 2.8213 | 3.0415 | 3.1988 | 3.2874 | 3.7731 | 4.2788 | 0.7663 | 0.95352 | 1.1936 | 1.4261 | 1.6887 | 2.0377 | 2.4104 | 3.0361 | 3.6166 | 4.3038 | 4.9295 | 5.5147 | 6.0668 | 6.5251 | 6.8586 | 7.0565 | 8.1755 | 9.3613
Chesterfield 132kV | PINXTON 11kV S STN | Bulk Supply Point | 11 | Counterfactual | 3.6282 | 3.6741 | 3.7161 | 3.7639 | 3.8502 | 3.9122 | 3.992 | 4.1178 | 4.2475 | 4.3497 | 4.4527 | 4.5607 | 4.6769 | 4.7945 | 4.9059 | 5.0229 | 5.3555 | 5.5442 | 9.0041 | 9.1004 | 9.1869 | 9.2852 | 9.4649 | 9.5953 | 9.7651 | 10.0325 | 10.3175 | 10.5316 | 10.7456 | 10.968 | 11.2058 | 11.4467 | 11.6747 | 11.9138 | 12.6088 | 13.0131
Chesterfield 132kV | PINXTON 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | 3.6654 | 3.7554 | 3.8674 | 4.0182 | 4.2091 | 4.4226 | 4.6201 | 4.8395 | 5.1093 | 5.2901 | 5.3968 | 5.4724 | 5.536 | 5.5979 | 5.6552 | 5.7106 | 6.0628 | 6.2452 | 9.0844 | 9.2736 | 9.5073 | 9.834 | 10.2572 | 10.7289 | 11.1437 | 11.5968 | 12.1825 | 12.561 | 12.7912 | 12.9578 | 13.1007 | 13.2368 | 13.3628 | 13.4857 | 14.2685 | 14.683
Chesterfield 132kV | PINXTON 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | 3.6517 | 3.7211 | 3.8261 | 3.9494 | 4.0885 | 4.2213 | 4.351 | 4.5362 | 4.76 | 4.9351 | 5.1131 | 5.3948 | 5.5644 | 5.7158 | 5.8322 | 5.8974 | 6.2703 | 6.4809 | 9.0598 | 9.2106 | 9.446 | 9.7282 | 10.0441 | 10.3315 | 10.6079 | 10.9997 | 11.4955 | 11.8658 | 12.2391 | 12.871 | 13.224 | 13.5387 | 13.783 | 13.9247 | 14.747 | 15.2153
Chesterfield 132kV | PINXTON 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | 3.6401 | 3.6989 | 3.7677 | 3.8628 | 4 | 4.1792 | 4.3113 | 4.4769 | 4.6287 | 4.794 | 4.9657 | 5.1311 | 5.2933 | 5.4365 | 5.54 | 5.5879 | 7.4942 | 7.6985 | 9.0299 | 9.1538 | 9.298 | 9.5074 | 9.818 | 10.2239 | 10.5053 | 10.8474 | 11.1624 | 11.5069 | 11.8623 | 12.2041 | 12.5385 | 12.8333 | 13.0485 | 13.1526 | 17.8373 | 18.291
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.43995 | 0.49145 | 0.54283 | 0.59643 | 0.65229 | 0.71817 | 0.79409 | 0.91566 | 1.0143 | 1.1213 | 1.2311 | 1.3453 | 1.4745 | 1.6012 | 1.7258 | 1.8524 | 2.1805 | 2.3263 | 1.0559 | 1.1645 | 1.271 | 1.3819 | 1.4971 | 1.6327 | 1.7886 | 2.0367 | 2.2394 | 2.4594 | 2.6844 | 2.9174 | 3.1805 | 3.4382 | 3.6914 | 3.9485 | 4.6252 | 4.9349
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.48522 | 0.59918 | 0.71588 | 0.84265 | 0.98999 | 1.1486 | 1.3455 | 1.5839 | 1.8009 | 1.9781 | 2.0778 | 2.125 | 2.1648 | 2.2107 | 2.2557 | 2.2959 | 2.4799 | 2.6491 | 1.1534 | 1.3955 | 1.6373 | 1.8994 | 2.2031 | 2.5298 | 2.9336 | 3.4202 | 3.8651 | 4.23 | 4.4403 | 4.5433 | 4.6308 | 4.7312 | 4.8296 | 4.9182 | 5.3282 | 5.7051
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.46818 | 0.55661 | 0.63243 | 0.71468 | 0.80859 | 0.91905 | 1.0439 | 1.2169 | 1.3645 | 1.5218 | 1.6924 | 1.8692 | 2.0496 | 2.2177 | 2.3289 | 2.3861 | 2.6171 | 2.8051 | 1.1228 | 1.3179 | 1.4804 | 1.6561 | 1.8563 | 2.0899 | 2.3523 | 2.7111 | 3.0176 | 3.3428 | 3.6939 | 4.0582 | 4.4305 | 4.7777 | 5.0109 | 5.1359 | 5.6495 | 6.071
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.45489 | 0.52632 | 0.59618 | 0.66978 | 0.75209 | 0.85378 | 0.97011 | 1.1418 | 1.291 | 1.4558 | 1.6212 | 1.7821 | 1.9415 | 2.0944 | 2.1915 | 2.232 | 2.5413 | 2.6901 | 1.0881 | 1.2408 | 1.386 | 1.5391 | 1.7101 | 1.9205 | 2.16 | 2.5114 | 2.8176 | 3.1552 | 3.492 | 3.8192 | 4.1435 | 4.4554 | 4.6553 | 4.7421 | 5.4607 | 5.7854
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.16771 | 0.18036 | 0.19498 | 0.21202 | 0.23027 | 0.26793 | 0.30585 | 0.38987 | 0.4769 | 0.57843 | 0.66663 | 0.73765 | 0.80483 | 0.8732 | 0.93999 | 1.009 | 1.3209 | 1.5925 | 0.39236 | 0.41911 | 0.44947 | 0.48476 | 0.5224 | 0.59887 | 0.67591 | 0.86058 | 1.0573 | 1.2908 | 1.4886 | 1.6439 | 1.7871 | 1.9332 | 2.0755 | 2.2227 | 2.9162 | 3.5316
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.18212 | 0.21289 | 0.25202 | 0.29727 | 0.3466 | 0.43173 | 0.53133 | 0.69937 | 0.88427 | 1.0678 | 1.2332 | 1.367 | 1.4996 | 1.6102 | 1.7245 | 1.8344 | 2.4259 | 2.7995 | 0.42348 | 0.4888 | 0.56992 | 0.66339 | 0.76488 | 0.93803 | 1.1403 | 1.5046 | 1.9122 | 2.3201 | 2.6938 | 2.999 | 3.3025 | 3.5459 | 3.7965 | 4.0405 | 5.3535 | 6.2491
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.17689 | 0.19886 | 0.22434 | 0.25323 | 0.2843 | 0.35017 | 0.47987 | 0.6764 | 0.84009 | 1.0348 | 1.2077 | 1.3675 | 1.519 | 1.6481 | 1.7632 | 1.8524 | 2.3396 | 2.5193 | 0.41422 | 0.46316 | 0.51787 | 0.57948 | 0.64544 | 0.78099 | 1.0746 | 1.5256 | 1.8965 | 2.3405 | 2.7263 | 3.0833 | 3.4206 | 3.6983 | 3.9476 | 4.1455 | 5.2293 | 5.6338
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.17211 | 0.18907 | 0.21055 | 0.23657 | 0.26481 | 0.31932 | 0.37795 | 0.49368 | 0.61275 | 0.77334 | 0.91117 | 1.0385 | 1.1561 | 1.2561 | 1.342 | 1.4095 | 1.7994 | 2.1726 | 0.40195 | 0.4382 | 0.48305 | 0.53712 | 0.59557 | 0.70676 | 0.82614 | 1.0792 | 1.343 | 1.7067 | 2.0122 | 2.2921 | 2.5477 | 2.7599 | 2.9439 | 3.0932 | 3.9798 | 4.8537
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.031492 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873 | 0.07873
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.87573 | 0.8888 | 0.90321 | 0.92005 | 0.93745 | 0.95769 | 0.98048 | 1.0182 | 1.0496 | 1.084 | 1.1182 | 1.1529 | 1.1914 | 1.2292 | 1.2663 | 1.3039 | 1.405 | 1.4576 | 2.1727 | 2.2004 | 2.2304 | 2.2654 | 2.3014 | 2.3431 | 2.3899 | 2.4675 | 2.5332 | 2.6051 | 2.6763 | 2.7477 | 2.8263 | 2.9033 | 2.9787 | 3.0553 | 3.2662 | 3.3804
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.88985 | 0.91968 | 0.99089 | 1.0735 | 1.1569 | 1.2441 | 1.3349 | 1.4524 | 1.5708 | 1.6612 | 1.717 | 1.7634 | 1.8216 | 1.8633 | 1.8807 | 1.9145 | 2.0639 | 2.1921 | 2.2032 | 2.2666 | 2.4293 | 2.6181 | 2.8069 | 3.0024 | 3.2016 | 3.4604 | 3.725 | 3.9254 | 4.0529 | 4.164 | 4.3056 | 4.4064 | 4.4457 | 4.5269 | 4.8829 | 5.1933
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.88448 | 0.90608 | 0.95847 | 1.0126 | 1.071 | 1.1227 | 1.1697 | 1.237 | 1.2946 | 1.3538 | 1.4177 | 1.482 | 1.5454 | 1.6042 | 1.6452 | 1.6678 | 1.7804 | 1.873 | 2.1936 | 2.2417 | 2.3646 | 2.4908 | 2.6266 | 2.7424 | 2.8443 | 2.9889 | 3.1128 | 3.2384 | 3.3742 | 3.5109 | 3.6459 | 3.7707 | 3.8599 | 3.9123 | 4.1747 | 4.3938
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.88013 | 0.89668 | 0.91698 | 0.94079 | 0.96595 | 0.99612 | 1.032 | 1.086 | 1.1334 | 1.1871 | 1.2415 | 1.2936 | 1.3445 | 1.3899 | 1.4181 | 1.4286 | 1.4832 | 1.541 | 2.1823 | 2.2177 | 2.2602 | 2.3101 | 2.3624 | 2.4249 | 2.4987 | 2.6101 | 2.7082 | 2.8199 | 2.9319 | 3.0392 | 3.1436 | 3.2364 | 3.2946 | 3.3175 | 3.4402 | 3.571
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.96342 | 1.0048 | 1.0504 | 1.103 | 1.1487 | 1.2102 | 1.2772 | 1.3962 | 1.5075 | 1.6231 | 1.7304 | 1.8305 | 1.9337 | 2.0369 | 2.1389 | 2.2439 | 2.6151 | 2.8793 | 2.2563 | 2.344 | 2.4392 | 2.5486 | 2.6434 | 2.7699 | 2.908 | 3.1613 | 3.4037 | 3.6589 | 3.8911 | 4.1028 | 4.3172 | 4.5318 | 4.7437 | 4.962 | 5.7625 | 6.3513
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.99604 | 1.0801 | 1.1792 | 1.2925 | 1.405 | 1.5484 | 1.7176 | 1.9549 | 2.1932 | 2.4014 | 2.5543 | 2.6659 | 2.7724 | 2.961 | 3.0504 | 3.1394 | 3.6728 | 4.0107 | 2.3268 | 2.5061 | 2.7133 | 2.9497 | 3.1829 | 3.4784 | 3.826 | 4.3272 | 4.8371 | 5.2863 | 5.6264 | 5.8802 | 6.1238 | 6.52 | 6.7183 | 6.9171 | 8.0962 | 8.898
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.98407 | 1.0494 | 1.1201 | 1.2002 | 1.2746 | 1.3787 | 1.5347 | 1.7619 | 1.9549 | 2.1648 | 2.3631 | 2.5657 | 2.7618 | 3.0355 | 3.166 | 3.2524 | 3.7547 | 3.9764 | 2.3051 | 2.4497 | 2.6018 | 2.7737 | 2.9325 | 3.1512 | 3.4946 | 3.9972 | 4.4211 | 4.8845 | 5.3139 | 5.75 | 6.1714 | 6.7374 | 7.0175 | 7.2091 | 8.3167 | 8.819
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.97479 | 1.0289 | 1.0923 | 1.1671 | 1.2363 | 1.3284 | 1.4314 | 1.5995 | 1.7576 | 1.9399 | 2.1094 | 2.2718 | 2.4267 | 2.6108 | 2.7092 | 2.7711 | 3.1299 | 3.4562 | 2.2811 | 2.3975 | 2.5314 | 2.6889 | 2.8335 | 3.0249 | 3.2379 | 3.5948 | 3.934 | 4.3315 | 4.6942 | 5.0395 | 5.3664 | 5.7455 | 5.9538 | 6.0903 | 6.8965 | 7.6533
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 11 | Counterfactual | 3.1088 | 3.1785 | 3.3317 | 3.4257 | 3.5347 | 3.6564 | 3.8527 | 4.0605 | 4.2427 | 4.4184 | 4.595 | 4.7702 | 4.9687 | 5.1605 | 5.3454 | 5.54 | 6.1035 | 6.4216 | 7.694 | 7.8407 | 8.1884 | 8.3833 | 8.6086 | 8.8598 | 9.2909 | 9.7203 | 10.1011 | 10.4693 | 10.836 | 11.196 | 11.6009 | 11.9922 | 12.3692 | 12.7657 | 13.9412 | 14.6216
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 11 | Electric Engagement | 3.1748 | 3.3961 | 3.5833 | 3.7971 | 4.042 | 4.3681 | 4.6944 | 5.0986 | 5.4835 | 5.7853 | 5.9675 | 6.0815 | 6.183 | 6.273 | 6.3723 | 6.4593 | 6.972 | 7.4598 | 7.8358 | 8.3315 | 8.7206 | 9.1648 | 9.6727 | 10.3732 | 11.0455 | 11.8807 | 12.6803 | 13.3095 | 13.7004 | 13.9508 | 14.1759 | 14.372 | 14.5868 | 14.7763 | 15.8964 | 17.0471
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 11 | Holistic Transition | 3.2204 | 3.333 | 3.4615 | 3.6019 | 3.8224 | 4.0235 | 4.2584 | 4.5843 | 4.862 | 5.1412 | 5.4293 | 5.7066 | 5.9861 | 6.2442 | 6.4362 | 6.5411 | 7.4531 | 7.788 | 7.9672 | 8.2157 | 8.4914 | 8.792 | 9.2848 | 9.7098 | 10.2111 | 10.9011 | 11.4889 | 12.0781 | 12.6791 | 13.2566 | 13.8395 | 14.3752 | 14.7789 | 15.0079 | 17.1153 | 17.8594
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 11 | Hydrogen Evolution | 3.1301 | 3.2896 | 3.4063 | 3.5406 | 3.6922 | 3.8728 | 4.1405 | 4.4428 | 4.7129 | 4.9969 | 5.2733 | 5.535 | 5.8023 | 6.0343 | 6.1963 | 6.2656 | 6.6643 | 7.1718 | 7.7399 | 8.1059 | 8.3499 | 8.6307 | 8.9474 | 9.3233 | 9.9034 | 10.5299 | 11.0922 | 11.6827 | 12.2523 | 12.791 | 13.3397 | 13.8148 | 14.1497 | 14.2988 | 15.1738 | 16.3468
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | 1.3174 | 1.6394 | 1.7944 | 1.9551 | 2.1303 | 2.3334 | 2.5696 | 2.9439 | 3.2539 | 3.5901 | 3.939 | 4.3784 | 4.9143 | 5.4485 | 5.9501 | 6.3857 | 7.3908 | 7.8389 | 2.7853 | 3.4412 | 3.762 | 4.0934 | 4.4545 | 4.8721 | 5.3567 | 6.1208 | 6.7582 | 7.4495 | 8.1635 | 9.068 | 10.1707 | 11.2705 | 12.314 | 13.2168 | 15.2858 | 16.2319
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | 1.6498 | 1.9503 | 2.3237 | 2.7333 | 3.1898 | 3.6929 | 4.3085 | 5.0773 | 5.7996 | 6.4966 | 7.0257 | 7.4244 | 7.5487 | 7.6893 | 7.8331 | 7.9626 | 8.554 | 9.0253 | 3.4717 | 4.1028 | 4.8756 | 5.7253 | 6.6675 | 7.7038 | 8.9637 | 10.5352 | 12.0179 | 13.4864 | 14.6398 | 15.5122 | 15.7844 | 16.0909 | 16.403 | 16.6862 | 17.9899 | 19.0378
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | 1.5975 | 1.8371 | 2.0963 | 2.3474 | 2.6802 | 3.0754 | 3.5243 | 4.131 | 4.7232 | 5.3724 | 5.9728 | 6.527 | 7.0569 | 7.5583 | 7.9022 | 8.0657 | 8.772 | 9.3024 | 3.3781 | 3.9018 | 4.4593 | 4.9963 | 5.7061 | 6.5438 | 7.491 | 8.7557 | 10.0154 | 11.4054 | 12.6489 | 13.7923 | 14.8845 | 15.9181 | 16.6362 | 16.9925 | 18.5487 | 19.7318
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | 1.5536 | 1.7262 | 1.9489 | 2.1865 | 2.4578 | 2.7669 | 3.1659 | 3.744 | 4.2936 | 4.9715 | 5.6914 | 6.3575 | 6.8676 | 7.3433 | 7.6433 | 7.7666 | 8.273 | 8.6887 | 3.2649 | 3.63 | 4.0935 | 4.5909 | 5.1557 | 5.7949 | 6.6199 | 7.8073 | 8.9428 | 10.3604 | 11.8764 | 13.2665 | 14.3036 | 15.2729 | 15.8904 | 16.1539 | 17.2547 | 18.1631
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.013809 | 0.015111 | 0.016108 | 0.017683 | 0.019661 | 0.024076 | 0.028348 | 0.037118 | 0.046115 | 0.056376 | 0.065823 | 0.073691 | 0.081364 | 0.088817 | 0.096076 | 0.10392 | 0.14372 | 0.18198 | 0.028028 | 0.03082 | 0.032909 | 0.036153 | 0.040205 | 0.049127 | 0.057767 | 0.076819 | 0.096858 | 0.12012 | 0.141 | 0.15799 | 0.17419 | 0.19001 | 0.20538 | 0.22194 | 0.30845 | 0.39183
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.014691 | 0.017242 | 0.020428 | 0.024086 | 0.028264 | 0.037208 | 0.047815 | 0.064427 | 0.083222 | 0.10214 | 0.121 | 0.13742 | 0.15366 | 0.1672 | 0.1815 | 0.19586 | 0.27321 | 0.31377 | 0.029886 | 0.035397 | 0.041958 | 0.049526 | 0.058134 | 0.076368 | 0.097992 | 0.13396 | 0.17517 | 0.21697 | 0.25881 | 0.29521 | 0.33138 | 0.3607 | 0.39146 | 0.42264 | 0.59083 | 0.68602
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.014292 | 0.016533 | 0.018948 | 0.02153 | 0.024459 | 0.032757 | 0.046351 | 0.066285 | 0.08297 | 0.10268 | 0.12068 | 0.1372 | 0.15335 | 0.16682 | 0.18072 | 0.19349 | 0.25893 | 0.28537 | 0.029119 | 0.034232 | 0.039407 | 0.044886 | 0.051059 | 0.068096 | 0.098496 | 0.14378 | 0.18128 | 0.22583 | 0.26573 | 0.30244 | 0.33806 | 0.367 | 0.3967 | 0.42419 | 0.56627 | 0.62372
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.014271 | 0.015993 | 0.018155 | 0.021241 | 0.024732 | 0.031791 | 0.039423 | 0.052287 | 0.065681 | 0.083291 | 0.098276 | 0.11179 | 0.12549 | 0.13622 | 0.14762 | 0.15746 | 0.20863 | 0.25379 | 0.028951 | 0.032678 | 0.03716 | 0.04349 | 0.050628 | 0.065031 | 0.08064 | 0.10838 | 0.13766 | 0.17688 | 0.20971 | 0.23919 | 0.26866 | 0.29144 | 0.31556 | 0.33682 | 0.44996 | 0.5524
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.0101 | 2.0411 | 2.0767 | 2.1186 | 2.1762 | 2.2488 | 2.336 | 2.4475 | 2.5438 | 2.6475 | 2.7511 | 2.8531 | 2.9643 | 3.075 | 3.1833 | 3.2934 | 3.6011 | 3.7715 | 5.0002 | 5.065 | 5.1388 | 5.2253 | 5.3445 | 5.4942 | 5.6743 | 5.905 | 6.1072 | 6.3264 | 6.5429 | 6.7537 | 6.9818 | 7.2087 | 7.4307 | 7.6562 | 8.3043 | 8.6758
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.0459 | 2.1184 | 2.2094 | 2.3344 | 2.4798 | 2.622 | 2.7942 | 3.0143 | 3.2255 | 3.4061 | 3.5189 | 3.5916 | 3.6616 | 3.7236 | 3.7882 | 3.8514 | 4.13 | 4.293 | 5.0773 | 5.2296 | 5.4181 | 5.6785 | 5.9817 | 6.2744 | 6.6273 | 7.0826 | 7.523 | 7.9023 | 8.1467 | 8.3087 | 8.4655 | 8.6019 | 8.7432 | 8.882 | 9.4798 | 9.8519
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.0323 | 2.0815 | 2.1588 | 2.247 | 2.3214 | 2.4226 | 2.5508 | 2.7329 | 2.8907 | 3.0634 | 3.2373 | 3.384 | 3.5338 | 3.672 | 3.7723 | 3.8296 | 4.1014 | 4.2713 | 5.0532 | 5.1611 | 5.3273 | 5.5165 | 5.6749 | 5.8878 | 6.1626 | 6.5516 | 6.8879 | 7.2566 | 7.6235 | 7.9276 | 8.2394 | 8.5257 | 8.7362 | 8.8606 | 9.4485 | 9.8274
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.0212 | 2.0612 | 2.1114 | 2.1846 | 2.2689 | 2.3775 | 2.4812 | 2.6354 | 2.7747 | 2.9337 | 3.0926 | 3.2454 | 3.397 | 3.532 | 3.6237 | 3.6702 | 4.8483 | 5.0516 | 5.0242 | 5.1087 | 5.2135 | 5.3669 | 5.5439 | 5.7714 | 5.9854 | 6.3055 | 6.5963 | 6.931 | 7.262 | 7.5795 | 7.8936 | 8.1719 | 8.3635 | 8.4649 | 11.3436 | 11.8017
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 5.0064 | 5.0926 | 5.1889 | 5.2988 | 5.4124 | 5.5349 | 5.6812 | 5.9059 | 6.0916 | 6.2854 | 6.4771 | 6.7021 | 6.9638 | 7.2262 | 7.465 | 7.6871 | 8.2061 | 8.425 | 12.4482 | 12.6279 | 12.8274 | 13.0549 | 13.2894 | 13.542 | 13.8431 | 14.3024 | 14.6845 | 15.0824 | 15.475 | 15.9372 | 16.4743 | 17.0128 | 17.5012 | 17.9527 | 19.0253 | 19.4925
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 5.087 | 5.2693 | 5.489 | 5.7383 | 6.007 | 6.2924 | 6.6513 | 7.0957 | 7.5233 | 7.8928 | 8.0985 | 8.1784 | 8.2411 | 8.3022 | 8.3731 | 8.4347 | 7.7801 | 8.0195 | 12.6226 | 13.0052 | 13.462 | 13.9796 | 14.5354 | 15.1249 | 15.8641 | 16.7765 | 17.6591 | 18.426 | 18.8654 | 19.0419 | 19.1812 | 19.3165 | 19.4726 | 19.6088 | 17.8935 | 18.4349
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 5.0574 | 5.1879 | 5.3365 | 5.5068 | 5.704 | 5.9475 | 6.2496 | 6.6101 | 6.8881 | 7.168 | 7.4591 | 7.7374 | 7.0511 | 7.3125 | 7.4902 | 7.5731 | 8.9159 | 9.2111 | 12.5699 | 12.8536 | 13.1725 | 13.5372 | 13.9589 | 14.4787 | 15.1214 | 15.8755 | 16.4541 | 17.0337 | 17.6341 | 18.2086 | 16.3765 | 16.9185 | 17.2929 | 17.4773 | 20.7387 | 21.405
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 5.0313 | 5.1427 | 5.2748 | 5.4287 | 5.5886 | 5.7677 | 6.0039 | 6.3545 | 6.6805 | 7.0113 | 7.2948 | 7.5707 | 7.8451 | 8.0973 | 8.2538 | 8.3096 | 9.0658 | 9.2994 | 12.5028 | 12.7384 | 13.0155 | 13.3386 | 13.6729 | 14.0461 | 14.5385 | 15.2653 | 15.9437 | 16.6294 | 17.208 | 17.7706 | 18.3302 | 18.8451 | 19.1692 | 19.2907 | 21.1067 | 21.6202
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Counterfactual | 3.5788 | 3.6514 | 3.7377 | 3.8432 | 3.9635 | 4.0551 | 4.1585 | 4.3099 | 4.4429 | 4.5771 | 4.7357 | 4.8741 | 5.0291 | 5.1777 | 5.3208 | 5.4558 | 5.791 | 5.9559 | 8.8078 | 8.9603 | 9.14 | 9.3591 | 9.6091 | 9.7989 | 10.0125 | 10.3239 | 10.5995 | 10.8773 | 11.2084 | 11.4946 | 11.8135 | 12.1181 | 12.4102 | 12.6844 | 13.3776 | 13.73
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 3.6337 | 3.7751 | 3.9379 | 4.1569 | 4.3992 | 4.6102 | 4.8963 | 5.1987 | 5.4496 | 5.6461 | 5.7688 | 5.8345 | 5.8883 | 5.9431 | 6.0014 | 6.0409 | 6.2824 | 6.452 | 8.9271 | 9.2272 | 9.5681 | 10.0284 | 10.538 | 10.9778 | 11.5787 | 12.2062 | 12.7263 | 13.1311 | 13.3938 | 13.5388 | 13.6586 | 13.7793 | 13.9076 | 13.9951 | 14.5248 | 14.9099
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 3.615 | 3.7252 | 3.8632 | 4.0326 | 4.2348 | 4.4101 | 4.5838 | 4.7848 | 4.9468 | 5.1199 | 5.3305 | 5.5248 | 5.7187 | 5.9047 | 6.0379 | 6.0898 | 6.3801 | 6.6233 | 8.8938 | 9.1349 | 9.4325 | 9.7967 | 10.2327 | 10.6124 | 10.9853 | 11.4058 | 11.7432 | 12.1016 | 12.5387 | 12.9414 | 13.3436 | 13.7298 | 14.0112 | 14.1265 | 14.7635 | 15.3202
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 3.5966 | 3.688 | 3.8023 | 3.9661 | 4.1492 | 4.3084 | 4.4848 | 4.7029 | 4.8737 | 5.0536 | 5.2603 | 5.4521 | 5.6391 | 5.8103 | 5.9228 | 5.9572 | 7.7533 | 7.9256 | 8.8472 | 9.0425 | 9.2846 | 9.6324 | 10.0224 | 10.3591 | 10.7322 | 11.1869 | 11.5433 | 11.9133 | 12.3398 | 12.7338 | 13.117 | 13.468 | 13.7022 | 13.7767 | 18.2079 | 18.5893
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Counterfactual | 4.7467 | 4.8472 | 4.9672 | 5.1037 | 5.2511 | 5.4194 | 5.5991 | 5.8735 | 6.0926 | 6.3303 | 6.5746 | 6.8395 | 7.1443 | 7.4489 | 7.7558 | 8.0582 | 8.7321 | 5.5123 | 11.4953 | 11.7052 | 11.9541 | 12.2366 | 12.541 | 12.8881 | 13.2575 | 13.8171 | 14.2669 | 14.7554 | 15.2561 | 15.7981 | 16.4204 | 17.0421 | 17.6758 | 18.3008 | 19.6932 | 11.5516
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Electric Engagement | 4.852 | 5.0815 | 5.3678 | 6.6951 | 7.0486 | 7.4367 | 7.8876 | 8.4379 | 8.9522 | 9.4209 | 9.7204 | 9.8489 | 9.9335 | 10.0245 | 9.4466 | 9.5349 | 9.9567 | 7.5937 | 11.7224 | 12.2047 | 12.8003 | 15.982 | 16.713 | 17.5142 | 18.4373 | 19.5636 | 20.622 | 21.6075 | 22.2669 | 22.554 | 22.7465 | 22.9502 | 21.4801 | 21.6778 | 22.6312 | 16.6623
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Holistic Transition | 4.8126 | 4.9881 | 5.1758 | 5.3851 | 5.6103 | 5.8759 | 6.1564 | 6.5447 | 6.9353 | 7.3721 | 7.7784 | 8.1529 | 8.5277 | 8.8801 | 8.4371 | 8.5379 | 9.0388 | 6.5479 | 11.6524 | 12.0353 | 12.4379 | 12.886 | 13.3661 | 13.9296 | 14.5188 | 15.3247 | 16.1528 | 17.0837 | 17.926 | 18.7001 | 19.4757 | 20.2045 | 19.0064 | 19.2308 | 20.3667 | 14.0709
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 4.7783 | 4.9134 | 5.0808 | 5.2725 | 5.4807 | 5.7203 | 5.9774 | 6.3575 | 6.7065 | 7.1147 | 7.5537 | 7.9293 | 8.2847 | 8.616 | 8.1447 | 8.215 | 8.5255 | 5.9989 | 11.564 | 11.85 | 12.201 | 12.6025 | 13.0368 | 13.536 | 14.0648 | 14.8429 | 15.5614 | 16.4099 | 17.3285 | 18.1021 | 18.8258 | 19.5017 | 18.2369 | 18.3905 | 19.0784 | 12.691
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.2776 | 1.3362 | 1.4003 | 1.4721 | 1.5572 | 1.6544 | 1.8273 | 2.0059 | 2.1514 | 2.3129 | 2.4983 | 2.688 | 2.8927 | 3.0877 | 3.2737 | 3.4613 | 3.9284 | 4.1464 | 3.1034 | 3.2254 | 3.3579 | 3.5061 | 3.6813 | 3.8812 | 4.2629 | 4.6269 | 4.9252 | 5.2565 | 5.6443 | 6.0392 | 6.4631 | 6.8639 | 7.2421 | 7.6237 | 8.5888 | 9.0511
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.3436 | 1.4781 | 1.6405 | 1.8225 | 2.0327 | 2.3262 | 2.6612 | 3.0475 | 3.4138 | 3.6845 | 3.8195 | 3.8967 | 3.9674 | 4.0326 | 4.1004 | 4.1592 | 4.4364 | 4.6511 | 3.2456 | 3.5271 | 3.8625 | 4.238 | 4.6708 | 5.3017 | 6.008 | 6.8118 | 7.5818 | 8.1406 | 8.4264 | 8.596 | 8.7524 | 8.8957 | 9.044 | 9.1732 | 9.7896 | 10.272
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.3187 | 1.41 | 1.5121 | 1.6244 | 1.8161 | 2.0245 | 2.2522 | 2.5395 | 2.7794 | 3.0274 | 3.2882 | 3.5319 | 3.7722 | 3.9976 | 4.1532 | 4.2311 | 4.5961 | 4.8734 | 3.2013 | 3.4002 | 3.6188 | 3.8584 | 4.2884 | 4.7473 | 5.2409 | 5.8474 | 6.3491 | 6.8635 | 7.4022 | 7.907 | 8.405 | 8.8725 | 9.2002 | 9.372 | 10.1909 | 10.8128
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.2976 | 1.3725 | 1.4618 | 1.5656 | 1.6898 | 1.8363 | 2.1026 | 2.3795 | 2.646 | 2.9044 | 3.1631 | 3.4093 | 3.6575 | 3.8799 | 4.0214 | 4.0763 | 4.8314 | 5.0522 | 3.1468 | 3.3044 | 3.4903 | 3.7059 | 3.964 | 4.2682 | 4.8569 | 5.4365 | 6.0042 | 6.5396 | 7.0693 | 7.574 | 8.082 | 8.5369 | 8.83 | 8.9491 | 10.762 | 11.2455
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.15331 | 0.20066 | 0.26344 | 0.32718 | 0.39795 | 0.48558 | 0.58562 | 0.72129 | 0.83366 | 0.9591 | 1.086 | 1.211 | 1.3462 | 1.4807 | 1.6136 | 1.7482 | 2.0987 | 2.2699 | 0.35112 | 0.45001 | 0.58024 | 0.71218 | 0.85851 | 1.0393 | 1.2456 | 1.5252 | 1.7593 | 2.0221 | 2.286 | 2.5438 | 2.8209 | 3.0963 | 3.3681 | 3.6437 | 4.38 | 4.7551
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.20066 | 0.30797 | 0.44436 | 0.58567 | 0.74927 | 0.94155 | 1.173 | 1.4434 | 1.6947 | 1.908 | 2.0313 | 2.1069 | 2.1796 | 2.2442 | 2.3097 | 2.3749 | 2.6963 | 2.9162 | 0.45347 | 0.67909 | 0.96331 | 1.2562 | 1.5953 | 1.9937 | 2.4712 | 3.0291 | 3.5503 | 3.9958 | 4.2619 | 4.4312 | 4.5946 | 4.738 | 4.8828 | 5.0271 | 5.7397 | 6.2479
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.1829 | 0.25964 | 0.35378 | 0.44698 | 0.55486 | 0.69132 | 0.86085 | 1.0751 | 1.2623 | 1.4678 | 1.6779 | 1.8766 | 2.0711 | 2.2491 | 2.3712 | 2.439 | 2.7649 | 2.97 | 0.42189 | 0.58898 | 0.79115 | 0.99061 | 1.2209 | 1.5103 | 1.873 | 2.3273 | 2.7237 | 3.1596 | 3.6013 | 4.0192 | 4.4278 | 4.7995 | 5.059 | 5.2097 | 5.9365 | 6.4012
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.16742 | 0.23319 | 0.31718 | 0.40176 | 0.50141 | 0.62427 | 0.76427 | 0.94427 | 1.1073 | 1.2914 | 1.4815 | 1.6666 | 1.8462 | 2.0106 | 2.1141 | 2.1637 | 2.3975 | 2.6071 | 0.38189 | 0.52146 | 0.69835 | 0.87583 | 1.0852 | 1.3425 | 1.6339 | 2.0063 | 2.3455 | 2.7309 | 3.1259 | 3.5094 | 3.8809 | 4.2196 | 4.4362 | 4.5455 | 5.0675 | 5.5415
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.41046 | 0.44198 | 0.48023 | 0.53965 | 0.59942 | 0.68538 | 0.77338 | 0.90916 | 1.0366 | 1.1396 | 1.2323 | 1.3166 | 1.4044 | 1.4926 | 1.5801 | 1.6679 | 1.9202 | 2.0761 | 0.99979 | 1.0663 | 1.1458 | 1.2692 | 1.3932 | 1.5719 | 1.7547 | 2.0427 | 2.3181 | 2.5443 | 2.7442 | 2.9219 | 3.1041 | 3.287 | 3.4686 | 3.6507 | 4.2012 | 4.5613
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.45077 | 0.523 | 0.61019 | 0.73083 | 0.85987 | 1.0224 | 1.1984 | 1.4313 | 1.6599 | 1.823 | 1.9282 | 1.9964 | 2.0622 | 2.1075 | 2.1554 | 2.2039 | 2.5221 | 2.7604 | 1.0902 | 1.2437 | 1.4255 | 1.6783 | 1.9484 | 2.2902 | 2.6568 | 3.1514 | 3.6427 | 3.9958 | 4.234 | 4.3951 | 4.5516 | 4.6575 | 4.7686 | 4.8817 | 5.6365 | 6.2135
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.43942 | 0.49294 | 0.55236 | 0.64384 | 0.73476 | 0.8595 | 1.0192 | 1.2379 | 1.4264 | 1.5922 | 1.7457 | 2.0126 | 2.1477 | 2.2599 | 2.34 | 2.3866 | 2.6247 | 2.7634 | 1.0701 | 1.1885 | 1.3165 | 1.5133 | 1.7087 | 1.9764 | 2.329 | 2.813 | 3.2279 | 3.5953 | 3.9284 | 4.5503 | 4.844 | 5.0833 | 5.2587 | 5.367 | 5.9237 | 6.2478
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.4294 | 0.47274 | 0.52535 | 0.61013 | 0.69489 | 0.81211 | 0.93117 | 1.1056 | 1.2696 | 1.4172 | 1.556 | 1.6868 | 1.8083 | 1.9127 | 1.9791 | 2.0116 | 2.2656 | 2.4812 | 1.0443 | 1.1371 | 1.2479 | 1.4277 | 1.6073 | 1.8566 | 2.1075 | 2.4807 | 2.8346 | 3.1565 | 3.4534 | 3.7314 | 3.988 | 4.2051 | 4.3468 | 4.4214 | 5.03 | 5.5439
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.16989 | 0.20847 | 0.2515 | 0.2993 | 0.35659 | 0.41943 | 0.49186 | 0.61075 | 0.70525 | 0.80788 | 0.91549 | 1.0202 | 1.1371 | 1.2567 | 1.3712 | 1.4898 | 1.7876 | 1.9129 | 0.3867 | 0.46703 | 0.55604 | 0.65468 | 0.77247 | 0.90153 | 1.05 | 1.2928 | 1.4875 | 1.6995 | 1.9205 | 2.134 | 2.3714 | 2.614 | 2.8461 | 3.087 | 3.7027 | 3.9712
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.21386 | 0.30312 | 0.41186 | 0.53513 | 0.67557 | 0.82922 | 1.0208 | 1.2524 | 1.4622 | 1.6332 | 1.7196 | 1.7616 | 1.7984 | 1.8328 | 1.8696 | 1.9048 | 2.0744 | 2.2124 | 0.48175 | 0.66828 | 0.89291 | 1.1472 | 1.4362 | 1.7516 | 2.1432 | 2.6161 | 3.046 | 3.3978 | 3.5805 | 3.6736 | 3.7561 | 3.833 | 3.9143 | 3.9926 | 4.3721 | 4.6875
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.19748 | 0.25678 | 0.32438 | 0.39964 | 0.48111 | 0.57746 | 0.69753 | 0.86414 | 1.0098 | 1.1645 | 1.3285 | 1.4903 | 1.6519 | 1.8022 | 1.8989 | 1.9426 | 2.1404 | 2.2717 | 0.45259 | 0.58161 | 0.7262 | 0.88633 | 1.059 | 1.2617 | 1.5139 | 1.8608 | 2.1638 | 2.4854 | 2.8237 | 3.1582 | 3.4926 | 3.803 | 4.0062 | 4.1032 | 4.5462 | 4.8474
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.18322 | 0.23256 | 0.29288 | 0.36228 | 0.4389 | 0.53293 | 0.64036 | 0.8024 | 0.94003 | 1.0942 | 1.2512 | 1.4078 | 1.5625 | 1.705 | 1.7912 | 1.8251 | 1.9687 | 2.0824 | 0.41576 | 0.51947 | 0.6449 | 0.78893 | 0.94775 | 1.1419 | 1.3624 | 1.6938 | 1.9759 | 2.2922 | 2.6125 | 2.9318 | 3.2468 | 3.5373 | 3.7151 | 3.7881 | 4.1046 | 4.3606
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.12793 | 0.16846 | 0.2136 | 0.26584 | 0.33286 | 0.41812 | 0.5084 | 0.61329 | 0.71948 | 0.7979 | 0.87821 | 0.95594 | 1.0402 | 1.1248 | 1.2073 | 1.2977 | 1.5308 | 1.6291 | 0.2949 | 0.37977 | 0.47349 | 0.58172 | 0.72336 | 0.90556 | 1.0992 | 1.3227 | 1.5577 | 1.7212 | 1.8877 | 2.0471 | 2.2185 | 2.3908 | 2.5584 | 2.7432 | 3.2301 | 3.446
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.16218 | 0.24251 | 0.33862 | 0.54178 | 0.7579 | 0.91695 | 1.086 | 1.2603 | 1.4161 | 1.542 | 1.6022 | 1.6311 | 1.6593 | 1.6836 | 1.7129 | 1.74 | 1.8654 | 1.9855 | 0.36943 | 0.53884 | 0.73924 | 1.201 | 1.6881 | 2.0248 | 2.3761 | 2.7345 | 3.0559 | 3.3172 | 3.4473 | 3.514 | 3.58 | 3.636 | 3.7029 | 3.7655 | 4.0579 | 4.3388
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.14986 | 0.20849 | 0.2749 | 0.49089 | 0.61414 | 0.72288 | 0.83927 | 0.96727 | 1.0799 | 1.2029 | 1.3306 | 1.4618 | 1.5903 | 1.7101 | 1.7872 | 1.8207 | 1.9713 | 2.0868 | 0.34744 | 0.47524 | 0.61786 | 1.1309 | 1.4075 | 1.6404 | 1.8898 | 2.1593 | 2.3966 | 2.6559 | 2.9229 | 3.1969 | 3.465 | 3.7143 | 3.8781 | 3.9544 | 4.3016 | 4.5678
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.13984 | 0.19153 | 0.25231 | 0.40724 | 0.5742 | 0.70457 | 0.81307 | 0.92817 | 1.0276 | 1.1389 | 1.2574 | 1.3753 | 1.49 | 1.5959 | 1.6607 | 1.6859 | 1.7982 | 1.9037 | 0.32128 | 0.43133 | 0.55938 | 0.91897 | 1.3041 | 1.5905 | 1.8183 | 2.055 | 2.2601 | 2.491 | 2.7352 | 2.978 | 3.2136 | 3.431 | 3.5665 | 3.6227 | 3.8792 | 4.1217
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.22177 | 0.25136 | 0.28608 | 0.32488 | 0.37211 | 0.43323 | 0.49821 | 0.61724 | 0.72946 | 0.85183 | 0.97798 | 1.0792 | 1.184 | 1.2894 | 1.3925 | 1.4991 | 1.8399 | 2.0537 | 0.52085 | 0.58296 | 0.65499 | 0.73531 | 0.83297 | 0.95876 | 1.0922 | 1.3449 | 1.5886 | 1.8576 | 2.1297 | 2.3433 | 2.5608 | 2.7796 | 2.9934 | 3.2148 | 3.9539 | 4.4404
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.25684 | 0.32812 | 0.41757 | 0.52395 | 0.64436 | 0.77743 | 0.94612 | 1.1815 | 1.4053 | 1.5914 | 1.7285 | 1.808 | 1.885 | 1.9404 | 1.9997 | 2.0631 | 2.4503 | 2.7625 | 0.5967 | 0.74676 | 0.93236 | 1.153 | 1.4025 | 1.6757 | 2.022 | 2.5185 | 2.9965 | 3.3941 | 3.6983 | 3.8812 | 4.0594 | 4.1836 | 4.3162 | 4.4585 | 5.3416 | 6.0881
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.24393 | 0.29819 | 0.35799 | 0.42389 | 0.49022 | 0.58469 | 0.73164 | 0.92681 | 1.0885 | 1.2711 | 1.4525 | 1.6272 | 1.807 | 1.9603 | 2.0708 | 2.14 | 2.4996 | 2.689 | 0.57373 | 0.69297 | 0.82142 | 0.9626 | 1.1038 | 1.3026 | 1.627 | 2.0549 | 2.4068 | 2.8057 | 3.1919 | 3.5665 | 3.9546 | 4.2794 | 4.5187 | 4.6756 | 5.4952 | 5.9304
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.23241 | 0.27571 | 0.3249 | 0.38441 | 0.44996 | 0.53104 | 0.62793 | 0.78975 | 0.93364 | 1.0991 | 1.2726 | 1.424 | 1.5692 | 1.6933 | 1.7753 | 1.8143 | 2.1594 | 2.4505 | 0.544 | 0.6361 | 0.73895 | 0.86352 | 1.0003 | 1.1682 | 1.3683 | 1.7119 | 2.0203 | 2.3776 | 2.7469 | 3.0661 | 3.3701 | 3.6258 | 3.798 | 3.8831 | 4.6888 | 5.3727
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.15293 | 0.195 | 0.24093 | 0.2932 | 0.35297 | 0.42162 | 0.49866 | 0.62465 | 0.74727 | 0.89655 | 1.064 | 1.233 | 1.353 | 1.4716 | 1.6055 | 1.7488 | 2.0764 | 2.2403 | 0.34879 | 0.43661 | 0.53174 | 0.63991 | 0.76328 | 0.90466 | 1.063 | 1.3229 | 1.5797 | 1.8942 | 2.246 | 2.5986 | 2.8433 | 3.0851 | 3.366 | 3.6686 | 4.3551 | 4.7125
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.19757 | 0.29117 | 0.40334 | 0.53311 | 0.68049 | 0.84888 | 1.0891 | 1.3733 | 1.6279 | 1.8762 | 2.0484 | 2.1286 | 2.1857 | 2.2314 | 2.2816 | 2.3303 | 2.5891 | 2.7888 | 0.44502 | 0.64133 | 0.87372 | 1.1424 | 1.4469 | 1.7948 | 2.2938 | 2.8845 | 3.4154 | 3.9495 | 4.3355 | 4.5152 | 4.6443 | 4.7468 | 4.858 | 4.9668 | 5.5485 | 6.0113
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.18103 | 0.24981 | 0.32524 | 0.403 | 0.487 | 0.63236 | 0.80589 | 1.0192 | 1.2378 | 1.4881 | 1.692 | 1.8849 | 2.0575 | 2.2168 | 2.3248 | 2.382 | 2.6605 | 2.8471 | 0.41556 | 0.56572 | 0.72753 | 0.89379 | 1.0723 | 1.3821 | 1.7547 | 2.2081 | 2.6837 | 3.2343 | 3.6635 | 4.0692 | 4.431 | 4.7626 | 4.9913 | 5.1186 | 5.7435 | 6.1652
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.16683 | 0.22231 | 0.28875 | 0.36113 | 0.44013 | 0.56812 | 0.72951 | 0.92204 | 1.0957 | 1.3026 | 1.5342 | 1.7345 | 1.8978 | 2.0414 | 2.1343 | 2.1699 | 2.3716 | 2.5631 | 0.37892 | 0.49608 | 0.6351 | 0.78596 | 0.94998 | 1.2192 | 1.5575 | 1.958 | 2.321 | 2.7605 | 3.2583 | 3.6808 | 4.0168 | 4.311 | 4.5039 | 4.5826 | 5.0344 | 5.4666
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.19594 | 0.24537 | 0.30029 | 0.36184 | 0.43208 | 0.51081 | 0.60462 | 0.75827 | 0.90892 | 1.0917 | 1.3081 | 1.4984 | 1.6844 | 1.8641 | 2.0425 | 2.1873 | 2.5538 | 2.7162 | 0.44664 | 0.54972 | 0.66343 | 0.79072 | 0.93562 | 1.0977 | 1.2902 | 1.6061 | 1.9201 | 2.3031 | 2.7608 | 3.1599 | 3.547 | 3.9187 | 4.2856 | 4.5802 | 5.3435 | 5.6961
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.25079 | 0.36496 | 0.50802 | 0.66292 | 0.83902 | 1.0544 | 1.372 | 1.7299 | 2.0605 | 2.3153 | 2.4646 | 2.5435 | 2.6174 | 2.6883 | 2.7644 | 2.8093 | 3.0467 | 3.2462 | 0.56504 | 0.80427 | 1.1011 | 1.4214 | 1.7848 | 2.2321 | 2.9033 | 3.654 | 4.3528 | 4.8866 | 5.2087 | 5.3851 | 5.5514 | 5.7096 | 5.8785 | 5.9798 | 6.5177 | 6.9768
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.2304 | 0.32135 | 0.42577 | 0.54672 | 0.68356 | 0.87157 | 1.0617 | 1.3191 | 1.5386 | 1.7722 | 2.0127 | 2.2319 | 2.4504 | 2.653 | 2.7873 | 2.8442 | 3.1158 | 3.3189 | 0.52874 | 0.72701 | 0.95127 | 1.2105 | 1.5032 | 1.915 | 2.3284 | 2.8775 | 3.3431 | 3.8359 | 4.3399 | 4.7985 | 5.2558 | 5.6787 | 5.9634 | 6.0909 | 6.7042 | 7.1644
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.21246 | 0.28596 | 0.37916 | 0.47109 | 0.58863 | 0.74668 | 0.92579 | 1.1772 | 1.4167 | 1.6534 | 1.8901 | 2.1032 | 2.3146 | 2.5094 | 2.6326 | 2.6703 | 2.8652 | 3.0466 | 0.48256 | 0.63817 | 0.83406 | 1.026 | 1.2717 | 1.605 | 1.986 | 2.5157 | 3.028 | 3.5252 | 4.0166 | 4.4566 | 4.8926 | 5.2943 | 5.5518 | 5.6348 | 6.0708 | 6.4789
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.90141 | 0.92532 | 0.95395 | 0.99102 | 1.0252 | 1.0771 | 1.1323 | 1.2377 | 1.3442 | 1.4629 | 1.5774 | 1.6789 | 1.7789 | 1.8797 | 1.9786 | 2.0794 | 2.488 | 2.8205 | 2.2275 | 2.2778 | 2.3375 | 2.4145 | 2.4852 | 2.5917 | 2.7049 | 2.9331 | 3.1693 | 3.437 | 3.6891 | 3.9079 | 4.1196 | 4.333 | 4.5422 | 4.7554 | 5.6532 | 6.3993
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.92325 | 0.98012 | 1.0643 | 1.1601 | 1.2662 | 1.4045 | 1.5356 | 1.7422 | 2.0568 | 2.3549 | 2.6159 | 2.8434 | 3.0771 | 3.1806 | 3.2807 | 3.392 | 3.9701 | 4.4154 | 2.2747 | 2.396 | 2.5778 | 2.7842 | 3.0121 | 3.3048 | 3.5772 | 4.0266 | 4.721 | 5.382 | 5.9691 | 6.4852 | 7.0177 | 7.2526 | 7.476 | 7.7277 | 9.0328 | 10.1044
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.91517 | 0.95807 | 1.0341 | 1.1026 | 1.1788 | 1.2592 | 1.4925 | 1.797 | 2.0654 | 2.3617 | 2.643 | 2.8176 | 2.9844 | 3.1201 | 3.2373 | 3.3288 | 3.8879 | 4.1141 | 2.2603 | 2.3551 | 2.5231 | 2.6741 | 2.8417 | 3.0115 | 3.532 | 4.2176 | 4.8173 | 5.4823 | 6.1052 | 6.4927 | 6.8614 | 7.1542 | 7.4106 | 7.6157 | 8.8931 | 9.4073
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.90854 | 0.94206 | 0.98199 | 1.0419 | 1.0933 | 1.1674 | 1.2489 | 1.3937 | 1.5441 | 1.7343 | 1.9046 | 2.065 | 2.2162 | 2.3451 | 2.4486 | 2.53 | 2.9781 | 3.448 | 2.243 | 2.3154 | 2.3993 | 2.5258 | 2.6337 | 2.7874 | 2.9557 | 3.2693 | 3.5993 | 4.0247 | 4.3985 | 4.748 | 5.0745 | 5.3487 | 5.5719 | 5.7531 | 6.7724 | 7.8705
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.11551 | 0.13849 | 0.16582 | 0.19642 | 0.23108 | 0.28299 | 0.34402 | 0.44966 | 0.54678 | 0.65863 | 0.77078 | 0.87443 | 0.98098 | 1.0806 | 1.1783 | 1.2765 | 1.6014 | 1.8222 | 0.25726 | 0.30525 | 0.36187 | 0.42521 | 0.4968 | 0.60297 | 0.72756 | 0.9488 | 1.1562 | 1.3977 | 1.636 | 1.8533 | 2.0737 | 2.2794 | 2.4808 | 2.6834 | 3.3749 | 3.8575
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.14267 | 0.19709 | 0.26707 | 0.34803 | 0.44568 | 0.58171 | 0.74055 | 0.95217 | 1.1734 | 1.3764 | 1.5148 | 1.6157 | 1.7124 | 1.7937 | 1.8759 | 1.9599 | 2.4001 | 2.6419 | 0.31585 | 0.43007 | 0.57526 | 0.74258 | 0.94361 | 1.2223 | 1.5475 | 1.9898 | 2.4587 | 2.8926 | 3.1945 | 3.4187 | 3.6344 | 3.8116 | 3.9902 | 4.174 | 5.1352 | 5.7043
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.1327 | 0.17208 | 0.21963 | 0.27482 | 0.33093 | 0.42537 | 0.57521 | 0.78173 | 0.94282 | 1.1236 | 1.3007 | 1.4672 | 1.6279 | 1.7683 | 1.8761 | 1.9509 | 2.3328 | 2.4951 | 0.29808 | 0.38419 | 0.48615 | 0.60425 | 0.72378 | 0.92018 | 1.2458 | 1.6961 | 2.0447 | 2.4381 | 2.8172 | 3.1738 | 3.5166 | 3.8114 | 4.0409 | 4.2039 | 5.0421 | 5.4053
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.12395 | 0.15586 | 0.1971 | 0.24201 | 0.30041 | 0.38982 | 0.48409 | 0.63134 | 0.77785 | 0.95012 | 1.116 | 1.2722 | 1.4159 | 1.5442 | 1.6379 | 1.7015 | 2.0039 | 2.2516 | 0.27554 | 0.34312 | 0.42957 | 0.52354 | 0.6451 | 0.82914 | 1.0225 | 1.3308 | 1.6416 | 2.012 | 2.3632 | 2.6922 | 2.9925 | 3.2578 | 3.4537 | 3.5907 | 4.2596 | 4.8261
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.27045 | 0.33431 | 0.40891 | 0.49838 | 0.60592 | 0.73283 | 0.87503 | 1.1039 | 1.302 | 1.5141 | 1.7246 | 1.9363 | 2.1657 | 2.3951 | 2.6201 | 2.8441 | 3.4547 | 3.7686 | 0.61304 | 0.74672 | 0.90111 | 1.0862 | 1.3084 | 1.5701 | 1.8629 | 2.3365 | 2.7519 | 3.1988 | 3.6386 | 4.077 | 4.5483 | 5.0194 | 5.4809 | 5.9404 | 7.2284 | 7.9206
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.34748 | 0.50133 | 0.68817 | 0.91513 | 1.1791 | 1.4748 | 1.8287 | 2.2829 | 2.7064 | 3.064 | 3.2694 | 3.3926 | 3.51 | 3.6105 | 3.7103 | 3.808 | 4.2981 | 4.7137 | 0.77929 | 1.1022 | 1.4887 | 1.9589 | 2.5056 | 3.1165 | 3.8447 | 4.7853 | 5.6684 | 6.4198 | 6.8671 | 7.1469 | 7.415 | 7.6417 | 7.8661 | 8.0869 | 9.1969 | 10.1611
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.31838 | 0.42167 | 0.54396 | 0.69125 | 0.86417 | 1.0693 | 1.3312 | 1.6991 | 2.0184 | 2.3619 | 2.707 | 3.0419 | 3.3686 | 3.6657 | 3.8664 | 3.9737 | 4.5025 | 4.8834 | 0.72732 | 0.95369 | 1.2155 | 1.5307 | 1.9 | 2.3351 | 2.8972 | 3.6826 | 4.3628 | 5.0955 | 5.8239 | 6.5307 | 7.2195 | 7.8421 | 8.2711 | 8.5127 | 9.7095 | 10.5766
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.29347 | 0.37734 | 0.48183 | 0.61077 | 0.76457 | 0.94657 | 1.1614 | 1.4805 | 1.7664 | 2.0825 | 2.4004 | 2.7098 | 3.0097 | 3.2837 | 3.4544 | 3.536 | 3.9396 | 4.3262 | 0.66314 | 0.8405 | 1.058 | 1.3279 | 1.6501 | 2.0301 | 2.4762 | 3.1407 | 3.7394 | 4.4051 | 5.0679 | 5.711 | 6.3328 | 6.8988 | 7.2575 | 7.4384 | 8.3496 | 9.2309
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.49873 | 0.54969 | 0.6066 | 0.67059 | 0.74829 | 0.85416 | 0.97386 | 1.1985 | 1.5339 | 1.9136 | 2.2439 | 2.4245 | 2.6217 | 2.8125 | 2.983 | 3.153 | 3.6358 | 3.9254 | 1.1884 | 1.2958 | 1.4141 | 1.5467 | 1.709 | 1.9322 | 2.1854 | 2.6587 | 3.3809 | 4.194 | 4.8986 | 5.28 | 5.6944 | 6.094 | 6.4449 | 6.7912 | 7.7822 | 8.386
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.5564 | 0.69003 | 0.87429 | 1.111 | 1.4126 | 1.8086 | 2.2839 | 2.8459 | 3.3997 | 3.6992 | 3.8868 | 3.9904 | 4.086 | 4.1753 | 4.2623 | 4.3326 | 4.8508 | 5.1818 | 1.3127 | 1.5951 | 1.9799 | 2.5002 | 3.1705 | 4.0337 | 5.0462 | 6.242 | 7.4334 | 8.0646 | 8.4683 | 8.6913 | 8.898 | 9.0893 | 9.27 | 9.4136 | 10.5358 | 11.2882
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.53533 | 0.68117 | 0.91476 | 1.1992 | 1.4689 | 1.7685 | 2.0728 | 2.4351 | 2.6807 | 2.9308 | 3.1967 | 3.478 | 3.7564 | 4.0039 | 4.1909 | 4.3009 | 4.8515 | 5.2019 | 1.2751 | 1.5941 | 2.1199 | 2.7589 | 3.3591 | 4.0122 | 4.6707 | 5.4443 | 5.9626 | 6.4829 | 7.0344 | 7.6268 | 8.2121 | 8.7253 | 9.117 | 9.355 | 10.555 | 11.3297
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.51724 | 0.63254 | 0.78577 | 0.97587 | 1.2445 | 1.5419 | 1.9337 | 2.3154 | 2.6533 | 2.9376 | 3.2018 | 3.4395 | 3.6851 | 3.9011 | 4.0444 | 4.0986 | 4.4294 | 4.7869 | 1.2284 | 1.475 | 1.7999 | 2.2243 | 2.8305 | 3.4779 | 4.3385 | 5.1509 | 5.8815 | 6.4843 | 7.0338 | 7.5227 | 8.0269 | 8.47 | 8.7615 | 8.8713 | 9.5733 | 10.3591
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.35499 | 0.4145 | 0.49142 | 0.57829 | 0.68064 | 0.79632 | 0.92575 | 1.1345 | 1.293 | 1.4593 | 1.6298 | 1.8167 | 2.0242 | 2.2305 | 2.4362 | 2.6481 | 3.2887 | 3.6451 | 0.79542 | 0.92058 | 1.0804 | 1.2606 | 1.4725 | 1.7117 | 1.9788 | 2.4067 | 2.7331 | 3.0756 | 3.4257 | 3.8079 | 4.2303 | 4.6501 | 5.069 | 5.5009 | 6.8261 | 7.5797
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.42413 | 0.56782 | 0.7572 | 0.99064 | 1.2612 | 1.5349 | 1.8505 | 2.2489 | 2.6085 | 2.9112 | 3.0748 | 3.1838 | 3.2759 | 3.3615 | 3.448 | 3.525 | 3.8812 | 4.2495 | 0.94428 | 1.2458 | 1.6381 | 2.1224 | 2.6828 | 3.2461 | 3.8918 | 4.7062 | 5.4436 | 6.067 | 6.4122 | 6.6494 | 6.8533 | 7.0422 | 7.2334 | 7.4054 | 8.2128 | 9.0416
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.39763 | 0.49667 | 0.63861 | 0.79879 | 0.94041 | 1.1124 | 1.3243 | 1.6296 | 1.8956 | 2.1883 | 2.4977 | 2.8454 | 3.1845 | 3.5017 | 3.7225 | 3.8359 | 4.3286 | 4.7327 | 0.89682 | 1.1134 | 1.4172 | 1.7595 | 2.0597 | 2.4213 | 2.8667 | 3.5015 | 4.0562 | 4.6662 | 5.3086 | 6.0278 | 6.7299 | 7.3866 | 7.8507 | 8.1001 | 9.199 | 10.1121
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.37709 | 0.45694 | 0.56923 | 0.70441 | 0.85402 | 1.027 | 1.2285 | 1.5173 | 1.7631 | 2.0282 | 2.3224 | 2.6147 | 2.9034 | 3.1668 | 3.3427 | 3.4352 | 3.7817 | 4.0725 | 0.84303 | 1.0121 | 1.2467 | 1.5297 | 1.8411 | 2.2 | 2.6163 | 3.208 | 3.7126 | 4.2556 | 4.859 | 5.4588 | 6.0509 | 6.5914 | 6.9566 | 7.1549 | 7.9169 | 8.5646
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.2498 | 0.33067 | 0.42137 | 0.52524 | 0.6492 | 0.78183 | 0.94009 | 1.176 | 1.4273 | 1.617 | 1.8667 | 2.1294 | 2.3925 | 2.6478 | 2.8578 | 3.0527 | 3.5528 | 3.8108 | 0.58404 | 0.755 | 0.94467 | 1.1611 | 1.4198 | 1.6997 | 2.0367 | 2.5352 | 3.094 | 3.4953 | 4.0421 | 4.6178 | 5.1848 | 5.7329 | 6.1698 | 6.5647 | 7.593 | 8.1368
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.323 | 0.52198 | 0.74223 | 1.044 | 1.4517 | 1.8043 | 2.2242 | 2.7206 | 3.2686 | 3.6769 | 3.9062 | 4.0149 | 4.1034 | 4.2068 | 4.2744 | 4.3302 | 4.6213 | 4.8971 | 0.74249 | 1.1717 | 1.632 | 2.2852 | 3.1882 | 3.9599 | 4.8726 | 5.9427 | 7.1572 | 8.055 | 8.5758 | 8.8264 | 9.0339 | 9.2734 | 9.4218 | 9.5462 | 10.2016 | 10.8204
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.2967 | 0.4521 | 0.69582 | 0.96549 | 1.1839 | 1.4738 | 1.8133 | 2.2449 | 2.6276 | 2.9942 | 3.2973 | 3.6019 | 3.9032 | 4.1571 | 4.3307 | 4.4154 | 4.8202 | 5.1656 | 0.69559 | 1.0433 | 1.5874 | 2.2007 | 2.6939 | 3.3547 | 4.1247 | 5.0852 | 5.9439 | 6.7539 | 7.3964 | 8.042 | 8.6807 | 9.2063 | 9.5711 | 9.758 | 10.6607 | 11.4368
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.27441 | 0.39548 | 0.51972 | 0.74065 | 1.0316 | 1.334 | 1.6326 | 2.0254 | 2.4571 | 2.8665 | 3.2226 | 3.5123 | 3.7952 | 4.0534 | 4.1891 | 4.2414 | 4.4704 | 4.7236 | 0.63786 | 0.90282 | 1.1637 | 1.6502 | 2.3077 | 2.9912 | 3.6529 | 4.5102 | 5.4841 | 6.3919 | 7.1616 | 7.7704 | 8.3629 | 8.9056 | 9.1836 | 9.2961 | 9.7981 | 10.3497
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.64776 | 0.68436 | 0.74674 | 0.82487 | 0.91032 | 1.0132 | 1.127 | 1.2454 | 1.3752 | 1.4971 | 1.6176 | 1.719 | 1.8097 | 1.8917 | 1.9695 | 2.0501 | 2.2775 | 2.3948 | 1.4024 | 1.479 | 1.6092 | 1.7717 | 1.95 | 2.1654 | 2.4055 | 2.6548 | 2.9378 | 3.1982 | 3.4549 | 3.6699 | 3.8558 | 4.0226 | 4.1808 | 4.3447 | 4.8167 | 5.0686
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.6783 | 0.76676 | 0.9162 | 1.0939 | 1.3082 | 1.5609 | 1.8041 | 2.0103 | 2.1838 | 2.3346 | 2.4203 | 2.4588 | 2.4924 | 2.5291 | 2.5674 | 2.6021 | 2.7891 | 2.9628 | 1.4683 | 1.6557 | 1.9723 | 2.352 | 2.8165 | 3.3648 | 3.8878 | 4.3241 | 4.692 | 5.0143 | 5.204 | 5.2885 | 5.3631 | 5.4437 | 5.5274 | 5.6039 | 6.0175 | 6.4043
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.6667 | 0.74594 | 0.88736 | 1.0727 | 1.2554 | 1.4475 | 1.608 | 1.7568 | 1.8866 | 2.0245 | 2.1484 | 2.2876 | 2.4237 | 2.5541 | 2.6426 | 2.6873 | 2.9168 | 3.0982 | 1.4476 | 1.62 | 1.9287 | 2.3342 | 2.7362 | 3.1599 | 3.5131 | 3.8343 | 4.1161 | 4.4144 | 4.6712 | 4.9591 | 5.2406 | 5.5103 | 5.6959 | 5.7939 | 6.3004 | 6.7042
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.6578 | 0.71364 | 0.82275 | 0.94956 | 1.1105 | 1.2948 | 1.4714 | 1.626 | 1.7693 | 1.9221 | 2.0733 | 2.2058 | 2.3268 | 2.4237 | 2.4836 | 2.5121 | 2.647 | 2.7895 | 1.4242 | 1.5432 | 1.7759 | 2.0497 | 2.4029 | 2.8095 | 3.1948 | 3.5265 | 3.8352 | 4.1637 | 4.4855 | 4.7595 | 5.009 | 5.2066 | 5.3302 | 5.3916 | 5.6888 | 6.0033
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Counterfactual | 0.30248 | 0.40324 | 0.50788 | 0.63051 | 0.75804 | 0.87865 | 1.0064 | 1.2057 | 1.3811 | 1.5804 | 1.7948 | 2.0032 | 2.2248 | 2.4432 | 2.6398 | 2.8205 | 3.3688 | 3.6916 | 0.69263 | 0.90568 | 1.1255 | 1.3822 | 1.6479 | 1.8978 | 2.162 | 2.5729 | 2.9385 | 3.3548 | 3.8042 | 4.2374 | 4.6958 | 5.1489 | 5.5523 | 5.9206 | 7.0589 | 7.7441
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.37238 | 0.59204 | 0.82839 | 1.0562 | 1.2911 | 1.5608 | 1.8985 | 2.29 | 2.7224 | 3.0929 | 3.2923 | 3.4123 | 3.5207 | 3.6069 | 3.6988 | 3.78 | 4.1925 | 4.5402 | 0.84481 | 1.3207 | 1.8204 | 2.2964 | 2.7843 | 3.3458 | 4.0487 | 4.8607 | 5.7714 | 6.5605 | 6.9871 | 7.2502 | 7.4899 | 7.6793 | 7.88 | 8.0595 | 8.9813 | 9.7657
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.34972 | 0.54207 | 0.73595 | 0.92245 | 1.0783 | 1.2669 | 1.5551 | 1.9301 | 2.2679 | 2.5597 | 2.8533 | 3.1526 | 3.4429 | 3.7196 | 3.9182 | 4.0267 | 4.5376 | 4.9291 | 0.80449 | 1.2324 | 1.6524 | 2.0532 | 2.386 | 2.7883 | 3.4081 | 4.2068 | 4.9355 | 5.5494 | 6.1632 | 6.7851 | 7.3884 | 7.9629 | 8.3808 | 8.6186 | 9.7499 | 10.6238
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.32683 | 0.48279 | 0.6455 | 0.82057 | 1.0159 | 1.2027 | 1.4042 | 1.6874 | 1.9934 | 2.3224 | 2.6198 | 2.9088 | 3.1917 | 3.4242 | 3.5773 | 3.6467 | 3.9772 | 4.307 | 0.74647 | 1.0886 | 1.436 | 1.8059 | 2.2189 | 2.6112 | 3.0315 | 3.6198 | 4.2673 | 4.9668 | 5.5841 | 6.1833 | 6.7683 | 7.2473 | 7.5641 | 7.7148 | 8.4428 | 9.1688
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.9183 | 1.9685 | 2.0355 | 2.1193 | 2.1439 | 2.1803 | 2.2189 | 2.2933 | 2.3631 | 2.4428 | 2.7448 | 3.1059 | 3.5766 | 4.0664 | 4.3253 | 4.5244 | 4.7772 | 4.9655 | 4.3719 | 4.4801 | 4.6237 | 4.8026 | 4.8536 | 4.9278 | 5.0066 | 5.1656 | 5.3185 | 5.4956 | 6.2267 | 7.1046 | 8.2537 | 9.4502 | 10.07 | 10.474 | 11.0234 | 11.4448
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.9979 | 2.164 | 2.3969 | 2.4955 | 2.5599 | 2.6468 | 2.8866 | 3.2658 | 4.1098 | 4.6604 | 5.0475 | 5.6569 | 6.0168 | 6.3634 | 6.4068 | 6.7008 | 6.3933 | 6.6448 | 4.5526 | 4.9185 | 5.4289 | 5.6507 | 5.7836 | 5.9614 | 6.5132 | 7.4032 | 9.4589 | 10.7883 | 11.7262 | 13.1074 | 13.9897 | 14.8382 | 14.9271 | 15.5117 | 14.6404 | 15.2368
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.9906 | 2.1447 | 2.2091 | 2.2866 | 2.3266 | 2.5506 | 2.9557 | 3.5628 | 4.2108 | 4.699 | 5.0889 | 5.7338 | 6.141 | 6.23 | 5.6642 | 5.9361 | 6.2658 | 6.4225 | 4.5397 | 4.8828 | 5.0324 | 5.2131 | 5.2981 | 5.8319 | 6.8156 | 8.2929 | 9.8762 | 11.0566 | 11.9873 | 13.4331 | 14.4086 | 14.5901 | 13.1457 | 13.7027 | 14.4377 | 14.7902
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.9446 | 2.0214 | 2.1284 | 2.2021 | 2.2387 | 2.292 | 2.4493 | 2.7738 | 3.5377 | 4.2226 | 4.6457 | 5.1862 | 5.598 | 5.995 | 6.0605 | 6.2368 | 6.4882 | 6.7348 | 4.4358 | 4.6085 | 4.8488 | 5.0195 | 5.0957 | 5.2052 | 5.5713 | 6.3442 | 8.2198 | 9.8946 | 10.913 | 12.1636 | 13.1542 | 14.1106 | 14.2497 | 14.6119 | 15.1823 | 15.7541
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Counterfactual | 0.51877 | 0.59183 | 0.70564 | 0.86091 | 1.0294 | 1.2189 | 1.4203 | 1.7326 | 2.0675 | 2.5 | 2.9628 | 3.308 | 3.6748 | 4.0187 | 4.3193 | 4.6159 | 5.1752 | 5.49 | 1.2121 | 1.3653 | 1.602 | 1.9241 | 2.2737 | 2.6664 | 3.0841 | 3.7334 | 4.4384 | 5.3545 | 6.3538 | 7.0977 | 7.8852 | 8.6156 | 9.2401 | 9.8518 | 11.0033 | 11.6661
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.58898 | 0.75183 | 1.0141 | 1.3104 | 1.6405 | 2.0748 | 2.6509 | 3.3835 | 4.0818 | 4.6092 | 4.8981 | 5.1137 | 5.3183 | 5.5082 | 5.6876 | 5.8535 | 6.2722 | 6.6214 | 1.3636 | 1.7068 | 2.2565 | 2.8764 | 3.5673 | 4.4831 | 5.7118 | 7.2856 | 8.8247 | 9.964 | 10.5896 | 11.0666 | 11.5213 | 11.9392 | 12.3292 | 12.6886 | 13.6241 | 14.4316
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.5624 | 0.69264 | 0.90394 | 1.1806 | 1.5135 | 1.901 | 2.352 | 2.9202 | 3.3993 | 3.8152 | 4.2109 | 4.6081 | 5.0067 | 5.383 | 5.6791 | 5.8917 | 6.3708 | 6.6984 | 1.3162 | 1.6016 | 2.0562 | 2.6502 | 3.3678 | 4.2154 | 5.2136 | 6.4679 | 7.5229 | 8.4105 | 9.2426 | 10.0817 | 10.9263 | 11.7223 | 12.3572 | 12.8252 | 13.8965 | 14.6364
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.54109 | 0.64967 | 0.85171 | 1.0765 | 1.3707 | 1.7203 | 2.1225 | 2.6519 | 3.2105 | 3.7261 | 4.1356 | 4.5364 | 4.9342 | 5.2974 | 5.5591 | 5.7234 | 6.0105 | 6.3339 | 1.2604 | 1.4917 | 1.9202 | 2.3955 | 3.0218 | 3.7676 | 4.6315 | 5.7732 | 7.0184 | 8.1445 | 9.0067 | 9.8504 | 10.687 | 11.449 | 12.0005 | 12.3538 | 12.9733 | 13.7013
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.30598 | 0.40453 | 0.52819 | 0.67138 | 0.82569 | 0.9831 | 1.1342 | 1.3782 | 1.6193 | 1.8866 | 2.1452 | 2.3571 | 2.5915 | 2.8232 | 3.0468 | 3.2775 | 3.8275 | 4.0742 | 0.67557 | 0.88303 | 1.1414 | 1.4396 | 1.7602 | 2.0865 | 2.3981 | 2.9008 | 3.4042 | 3.9638 | 4.505 | 4.9433 | 5.4263 | 5.9028 | 6.3611 | 6.8344 | 7.976 | 8.5105
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.39635 | 0.66079 | 0.99439 | 1.3137 | 1.6688 | 2.0821 | 2.5161 | 2.9768 | 3.3821 | 3.7184 | 3.8903 | 3.9713 | 4.0441 | 4.1168 | 4.1927 | 4.2631 | 4.6284 | 4.9526 | 0.87373 | 1.4422 | 2.1466 | 2.8157 | 3.5601 | 4.4294 | 5.3318 | 6.2807 | 7.1212 | 7.823 | 8.1955 | 8.3794 | 8.545 | 8.7082 | 8.8775 | 9.0359 | 9.8629 | 10.6065
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.36642 | 0.61584 | 0.88284 | 1.164 | 1.4581 | 1.7443 | 1.9604 | 2.2725 | 2.5592 | 2.8696 | 3.1778 | 3.5063 | 3.8264 | 4.1259 | 4.3215 | 4.4091 | 4.8581 | 5.2015 | 0.82029 | 1.3698 | 1.9453 | 2.5496 | 3.1826 | 3.7967 | 4.2524 | 4.9055 | 5.513 | 6.1699 | 6.8118 | 7.495 | 8.1582 | 8.7785 | 9.1906 | 9.3867 | 10.398 | 11.1774
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.33977 | 0.521 | 0.72237 | 0.92544 | 1.1635 | 1.4521 | 1.6967 | 2.0193 | 2.3102 | 2.6211 | 2.9407 | 3.2484 | 3.5448 | 3.8078 | 3.9676 | 4.0366 | 4.3039 | 4.5837 | 0.75187 | 1.1465 | 1.5742 | 2.0036 | 2.5086 | 3.1229 | 3.6335 | 4.3006 | 4.9099 | 5.5604 | 6.2256 | 6.8631 | 7.4728 | 8.0117 | 8.3439 | 8.4965 | 9.097 | 9.7268
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | 0.9472 | 1.0361 | 1.1407 | 1.2979 | 1.4672 | 1.6613 | 1.8786 | 2.185 | 2.4408 | 2.7079 | 2.9813 | 3.2931 | 3.5525 | 3.8107 | 4.0669 | 4.3232 | 5.0439 | 5.4111 | 1.9767 | 2.164 | 2.382 | 2.7087 | 3.0604 | 3.4641 | 3.9157 | 4.5476 | 5.0784 | 5.6327 | 6.1998 | 6.8465 | 7.3765 | 7.9033 | 8.4265 | 8.9494 | 10.4454 | 11.2298
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | 1.0386 | 1.2455 | 1.4859 | 1.8199 | 2.1961 | 2.6015 | 3.0619 | 3.6215 | 4.1437 | 4.5991 | 4.8759 | 5.0737 | 5.1753 | 5.164 | 5.263 | 5.355 | 5.7918 | 6.2095 | 2.1742 | 2.6123 | 3.1127 | 3.8116 | 4.5991 | 5.4478 | 6.4043 | 7.5624 | 8.6466 | 9.5978 | 10.1918 | 10.6275 | 10.8539 | 10.7987 | 11.0187 | 11.2248 | 12.2126 | 13.1532
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | 1.0053 | 1.1587 | 1.3241 | 1.5768 | 1.8374 | 2.155 | 2.4992 | 2.9386 | 3.3354 | 3.7637 | 4.2153 | 4.6852 | 4.9586 | 5.3215 | 5.5665 | 5.6939 | 6.261 | 6.876 | 2.1149 | 2.4525 | 2.8087 | 3.3519 | 3.9118 | 4.5932 | 5.3267 | 6.2499 | 7.0869 | 7.9884 | 8.9367 | 9.9226 | 10.4442 | 11.1992 | 11.7175 | 12.0005 | 13.2737 | 14.6886
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | 0.9763 | 1.1007 | 1.2422 | 1.4709 | 1.7102 | 1.9758 | 2.342 | 2.7696 | 3.1522 | 3.5546 | 3.9788 | 4.4033 | 4.7447 | 5.0589 | 5.2594 | 5.3507 | 5.7541 | 6.1464 | 2.0398 | 2.3055 | 2.6026 | 3.0865 | 3.5926 | 4.1544 | 4.9468 | 5.8381 | 6.638 | 7.4762 | 8.3589 | 9.243 | 9.9446 | 10.5914 | 11.0099 | 11.2104 | 12.1045 | 12.9707
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.40971 | 0.50585 | 0.61026 | 0.72842 | 0.86192 | 1.0136 | 1.1779 | 1.463 | 1.6989 | 1.9651 | 2.2494 | 2.5313 | 2.8336 | 3.1194 | 3.4097 | 3.7028 | 4.3388 | 4.5868 | 0.92221 | 1.1226 | 1.3392 | 1.584 | 1.8594 | 2.1703 | 2.5061 | 3.0932 | 3.5854 | 4.1437 | 4.7357 | 5.3183 | 5.9381 | 6.522 | 7.1237 | 7.7335 | 9.0665 | 9.6192
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.51273 | 0.73634 | 0.98365 | 1.2867 | 1.6215 | 1.9725 | 2.3934 | 2.9322 | 3.5046 | 4.0274 | 4.3018 | 4.4156 | 4.5201 | 4.6041 | 4.7039 | 4.8007 | 5.2738 | 5.7512 | 1.145 | 1.6186 | 2.1298 | 2.7572 | 3.4487 | 4.1705 | 5.0306 | 6.1398 | 7.3352 | 8.4513 | 9.0648 | 9.3271 | 9.5701 | 9.7616 | 9.9881 | 10.2098 | 11.3008 | 12.4115
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.47503 | 0.63411 | 0.81086 | 0.99884 | 1.1945 | 1.4225 | 1.7891 | 2.286 | 2.6992 | 3.1584 | 3.5627 | 3.928 | 4.2865 | 4.6187 | 4.8502 | 4.9668 | 5.5207 | 5.9764 | 1.0783 | 1.4285 | 1.8071 | 2.2087 | 2.6242 | 3.104 | 3.891 | 4.9501 | 5.8406 | 6.8378 | 7.6859 | 8.4527 | 9.204 | 9.894 | 10.3874 | 10.6511 | 11.9165 | 12.9519
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.44043 | 0.57559 | 0.71544 | 0.88078 | 1.0667 | 1.2748 | 1.5297 | 1.9176 | 2.2817 | 2.7045 | 3.1641 | 3.572 | 3.9348 | 4.253 | 4.4369 | 4.4947 | 4.7852 | 5.0586 | 0.98926 | 1.2793 | 1.5705 | 1.9153 | 2.3017 | 2.7319 | 3.2568 | 4.0585 | 4.8181 | 5.7115 | 6.6857 | 7.5394 | 8.2862 | 8.9367 | 9.3182 | 9.4483 | 10.118 | 10.757
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.4217 | 0.61208 | 0.85393 | 1.1265 | 1.4022 | 1.6962 | 1.9991 | 2.3488 | 2.6422 | 2.9594 | 3.2151 | 3.4742 | 3.7491 | 4.0177 | 4.2735 | 4.4379 | 4.8582 | 5.0627 | 0.93831 | 1.3397 | 1.8452 | 2.4127 | 2.9882 | 3.6028 | 4.237 | 4.9675 | 5.5845 | 6.2997 | 6.8569 | 7.4185 | 8.0105 | 8.5874 | 9.1349 | 9.4697 | 10.3437 | 10.7867
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.49117 | 0.81668 | 1.2182 | 1.6629 | 2.1353 | 2.6243 | 3.2567 | 3.9245 | 4.495 | 4.9067 | 5.1777 | 5.387 | 5.5854 | 5.7311 | 5.792 | 5.8451 | 6.132 | 6.4013 | 1.0909 | 1.7918 | 2.6471 | 3.5918 | 4.5991 | 5.6442 | 7.0307 | 8.4847 | 9.7345 | 10.6366 | 11.247 | 11.7319 | 12.1947 | 12.5408 | 12.6767 | 12.7974 | 13.45 | 14.0664
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.46847 | 0.75473 | 1.1157 | 1.5104 | 1.902 | 2.4395 | 2.9818 | 3.5416 | 3.9909 | 4.3801 | 4.7611 | 5.1508 | 5.5317 | 5.772 | 5.9189 | 5.9912 | 6.35 | 6.6332 | 1.0506 | 1.6769 | 2.4569 | 3.3074 | 4.1552 | 5.3621 | 6.576 | 7.8142 | 8.8102 | 9.6701 | 10.5011 | 11.3511 | 12.1827 | 12.684 | 12.9949 | 13.1564 | 13.9653 | 14.606
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.44826 | 0.71385 | 1.0411 | 1.4163 | 1.7896 | 2.1805 | 2.6851 | 3.2363 | 3.6923 | 4.076 | 4.4346 | 4.7889 | 5.1391 | 5.4675 | 5.6385 | 5.6844 | 5.8989 | 6.1332 | 0.9984 | 1.5743 | 2.2765 | 3.08 | 3.8831 | 4.7265 | 5.8479 | 7.0617 | 8.0753 | 8.9197 | 9.6978 | 10.4661 | 11.2249 | 11.9385 | 12.2999 | 12.4012 | 12.8835 | 13.4095
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.7278 | 2.8218 | 2.9349 | 3.0644 | 3.2051 | 2.4016 | 2.5889 | 2.2661 | 2.5155 | 3.0875 | 3.7509 | 4.4297 | 5.1689 | 5.8944 | 6.6928 | 7.5433 | 9.1146 | 9.3892 | 6.7001 | 6.8964 | 7.1313 | 7.3999 | 7.6903 | 5.6078 | 5.9918 | 5.0493 | 5.569 | 6.7552 | 8.1318 | 9.5346 | 11.0559 | 12.5469 | 14.2443 | 16.081 | 19.3795 | 19.8869
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.8421 | 3.0809 | 3.3566 | 3.6817 | 4.0526 | 3.4772 | 3.9555 | 3.9397 | 5.42 | 6.8089 | 7.8181 | 8.4645 | 9.0547 | 9.2264 | 9.1105 | 9.3078 | 9.9214 | 10.5431 | 6.947 | 7.4526 | 8.0222 | 8.694 | 9.4595 | 7.8447 | 8.8216 | 8.5096 | 11.6099 | 14.5779 | 16.8296 | 18.2872 | 19.6227 | 20.0288 | 19.7066 | 20.1693 | 21.556 | 23.0143
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.7994 | 2.9619 | 3.1471 | 3.3505 | 3.56 | 2.8447 | 3.8672 | 4.505 | 5.727 | 7.147 | 8.3752 | 8.87 | 9.3535 | 9.7977 | 9.8255 | 9.9622 | 10.8088 | 11.3174 | 6.871 | 7.23 | 7.6264 | 8.0608 | 8.5053 | 6.6161 | 8.8073 | 9.9255 | 12.5599 | 15.6681 | 18.2879 | 19.354 | 20.395 | 21.3484 | 21.3171 | 21.6241 | 23.5789 | 24.7342
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.7616 | 2.8989 | 3.0519 | 3.2263 | 3.4251 | 2.6941 | 2.9704 | 2.7571 | 3.6004 | 4.5547 | 5.6646 | 6.7338 | 7.6942 | 8.5303 | 8.7192 | 8.9536 | 9.7384 | 10.4359 | 6.7737 | 7.0693 | 7.3882 | 7.7516 | 8.1649 | 6.2355 | 6.8033 | 6.088 | 7.8457 | 9.8548 | 12.2306 | 14.5108 | 16.5306 | 18.2831 | 18.577 | 19.1183 | 20.8809 | 22.4879
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | 0.045453 | 0.063097 | 0.096872 | 0.12802 | 0.15189 | 0.17769 | 0.23298 | 0.28038 | 0.32471 | 0.36548 | 0.49332 | 0.62457 | 0.77457 | 0.92848 | 1.0302 | 1.0804 | 1.2555 | 1.3618 | 0.092848 | 0.1295 | 0.19821 | 0.26381 | 0.3127 | 0.36557 | 0.48858 | 0.58491 | 0.67508 | 0.7582 | 1.0413 | 1.3223 | 1.6436 | 1.9724 | 2.1877 | 2.2895 | 2.6477 | 2.8675
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | 0.058155 | 0.091589 | 0.14627 | 0.20968 | 0.2826 | 0.3647 | 0.44563 | 0.61599 | 0.82851 | 1.0281 | 1.2094 | 1.3026 | 1.3699 | 1.4408 | 1.5066 | 1.5746 | 1.8924 | 2.1862 | 0.11998 | 0.19 | 0.30183 | 0.43789 | 0.59799 | 0.7768 | 0.94327 | 1.3039 | 1.7725 | 2.2113 | 2.5973 | 2.7916 | 2.9297 | 3.0748 | 3.2099 | 3.3492 | 4.0019 | 4.6046
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | 0.0533 | 0.079132 | 0.11848 | 0.1815 | 0.2845 | 0.41024 | 0.56251 | 0.77301 | 0.92975 | 1.0042 | 1.1079 | 1.2194 | 1.3252 | 1.4325 | 1.5286 | 1.5999 | 1.9402 | 2.2126 | 0.11117 | 0.16713 | 0.24924 | 0.38908 | 0.61729 | 0.88882 | 1.2178 | 1.6709 | 2.0352 | 2.1942 | 2.4057 | 2.6328 | 2.8488 | 3.0676 | 3.2638 | 3.4106 | 4.1115 | 4.675
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | 0.050264 | 0.071968 | 0.12249 | 0.15304 | 0.22847 | 0.30362 | 0.39209 | 0.58472 | 0.77673 | 1.029 | 1.1172 | 1.2004 | 1.2879 | 1.371 | 1.4439 | 1.5019 | 1.7585 | 1.9636 | 0.10305 | 0.1485 | 0.25127 | 0.31443 | 0.4866 | 0.65185 | 0.8383 | 1.2506 | 1.662 | 2.2311 | 2.4099 | 2.5788 | 2.7566 | 2.9253 | 3.0736 | 3.1923 | 3.7183 | 4.1402
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.52826 | 0.58661 | 0.77053 | 0.84854 | 0.93085 | 1.0341 | 1.1533 | 1.3814 | 1.6148 | 1.8653 | 2.1223 | 2.3837 | 2.6528 | 2.9229 | 3.3049 | 3.7139 | 4.7168 | 5.1114 | 1.1623 | 1.2851 | 1.658 | 1.8194 | 1.9891 | 2.201 | 2.4453 | 2.921 | 3.4156 | 3.95 | 4.4936 | 5.0423 | 5.6026 | 6.1649 | 7.0047 | 7.9108 | 10.0458 | 10.9057
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.58838 | 0.83779 | 1.0162 | 1.206 | 1.4126 | 1.6554 | 1.9521 | 2.3792 | 2.8244 | 3.3992 | 3.9133 | 4.1511 | 4.3761 | 4.6319 | 4.8512 | 5.0704 | 6.1474 | 6.5939 | 1.292 | 1.806 | 2.1817 | 2.5749 | 3.0011 | 3.4997 | 4.1077 | 4.9995 | 5.9407 | 7.23 | 8.4207 | 8.9495 | 9.4518 | 10.0055 | 10.4886 | 10.9734 | 13.3597 | 14.3991
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.56605 | 0.77632 | 0.88411 | 1.0056 | 1.1389 | 1.3035 | 1.5397 | 1.9056 | 2.4421 | 3.1172 | 3.5198 | 3.9097 | 4.2838 | 4.6797 | 4.9693 | 5.1917 | 6.2658 | 6.6271 | 1.2522 | 1.6925 | 1.9237 | 2.1834 | 2.4695 | 2.8147 | 3.3248 | 4.1151 | 5.3333 | 6.8886 | 7.7509 | 8.5872 | 9.3884 | 10.2236 | 10.8485 | 11.3394 | 13.7202 | 14.5362
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.54686 | 0.73933 | 0.8359 | 0.94662 | 1.066 | 1.2171 | 1.3994 | 1.7131 | 2.0398 | 2.483 | 3.0734 | 3.5398 | 3.8917 | 4.2448 | 4.5089 | 4.7061 | 5.6374 | 6.0697 | 1.2026 | 1.5975 | 1.7993 | 2.0304 | 2.2785 | 2.5904 | 2.9661 | 3.6236 | 4.3169 | 5.2924 | 6.6262 | 7.6495 | 8.3916 | 9.1308 | 9.6949 | 10.1268 | 12.1928 | 13.1782
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.1354 | 0.41472 | 0.41892 | 0.42399 | 0.4294 | 0.44523 | 0.46034 | 0.49458 | 0.53108 | 0.5733 | 0.60958 | 0.63781 | 0.66336 | 0.68951 | 0.9103 | 1.1756 | 1.3078 | 1.4289 | 0.33326 | 0.90017 | 0.90889 | 0.91937 | 0.93051 | 0.96255 | 0.99315 | 1.0692 | 1.1525 | 1.2509 | 1.3331 | 1.3958 | 1.4509 | 1.5075 | 2.0506 | 2.7049 | 3.0014 | 3.2766
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.40659 | 0.47342 | 0.52991 | 0.54313 | 0.55798 | 0.59125 | 0.62888 | 0.69682 | 0.77404 | 1.1617 | 1.6155 | 1.6803 | 1.7458 | 1.797 | 1.8503 | 1.907 | 2.2109 | 2.3877 | 0.87982 | 1.0434 | 1.1796 | 1.2069 | 1.2375 | 1.3049 | 1.3811 | 1.5299 | 1.702 | 2.6506 | 3.7665 | 3.9138 | 4.063 | 4.1758 | 4.2927 | 4.4179 | 5.0868 | 5.5095
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.40496 | 0.46944 | 0.47695 | 0.48534 | 0.51295 | 0.5399 | 0.5967 | 0.68209 | 1.08 | 1.685 | 1.7604 | 1.8288 | 1.894 | 1.945 | 1.9938 | 2.0388 | 2.2864 | 2.3736 | 0.87685 | 1.0362 | 1.0523 | 1.0701 | 1.1355 | 1.1906 | 1.32 | 1.5178 | 2.497 | 3.9926 | 4.1626 | 4.3169 | 4.4631 | 4.574 | 4.6807 | 4.7797 | 5.3261 | 5.5203
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.40375 | 0.46639 | 0.473 | 0.48023 | 0.48852 | 0.5098 | 0.53131 | 0.57664 | 0.62481 | 0.83484 | 1.2935 | 1.5219 | 1.5698 | 1.6091 | 1.6444 | 1.6778 | 1.8656 | 2.0397 | 0.87369 | 1.0284 | 1.0422 | 1.0572 | 1.0743 | 1.1175 | 1.1611 | 1.2614 | 1.3696 | 1.8813 | 3.014 | 3.571 | 3.6762 | 3.7605 | 3.8367 | 3.9101 | 4.3352 | 4.7417
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.8402 | 0.96475 | 1.1055 | 1.2566 | 1.4345 | 1.6398 | 1.8713 | 2.2437 | 2.5648 | 2.9094 | 3.252 | 3.5973 | 3.9718 | 4.3464 | 4.7131 | 5.0788 | 6.0606 | 6.5529 | 1.9931 | 2.2544 | 2.5462 | 2.859 | 3.2267 | 3.6503 | 4.1274 | 4.8971 | 5.5694 | 6.294 | 7.0085 | 7.7229 | 8.4919 | 9.2606 | 10.0127 | 10.7624 | 12.8313 | 13.9161
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.96758 | 1.2519 | 1.5751 | 1.9478 | 2.3819 | 2.8562 | 3.4318 | 4.1668 | 4.85 | 5.4227 | 5.7443 | 5.936 | 6.1149 | 6.2681 | 6.4195 | 6.5999 | 7.3941 | 8.0444 | 2.268 | 2.8681 | 3.5386 | 4.3112 | 5.2107 | 6.192 | 7.3772 | 8.8987 | 10.3221 | 11.5241 | 12.2246 | 12.6605 | 13.0703 | 13.4176 | 13.7597 | 14.1775 | 16.0035 | 17.5121
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.92001 | 1.123 | 1.3361 | 1.5799 | 1.8661 | 2.1997 | 2.622 | 3.2133 | 3.7267 | 4.2787 | 4.9021 | 5.4337 | 6.0772 | 6.5485 | 6.866 | 7.0328 | 7.843 | 8.4612 | 2.1833 | 2.629 | 3.0868 | 3.6092 | 4.2209 | 4.9298 | 5.8354 | 7.0952 | 8.1879 | 9.3635 | 10.705 | 11.8268 | 13.2326 | 14.221 | 14.9003 | 15.2776 | 17.121 | 18.5288
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.87874 | 1.0472 | 1.2301 | 1.4426 | 1.6973 | 1.9939 | 2.3461 | 2.8657 | 3.33 | 3.8426 | 4.3593 | 4.8614 | 5.3473 | 5.7902 | 6.0642 | 6.2236 | 6.9108 | 7.523 | 2.0769 | 2.4355 | 2.8182 | 3.263 | 3.7966 | 4.4166 | 5.1482 | 6.2292 | 7.2004 | 8.2773 | 9.3527 | 10.3957 | 11.4026 | 12.3172 | 12.893 | 13.2576 | 14.8272 | 16.22
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.43758 | 0.53604 | 0.65447 | 0.77426 | 0.91216 | 1.0565 | 1.2211 | 1.5046 | 1.815 | 2.1774 | 2.57 | 2.9161 | 3.2691 | 3.6665 | 4.0495 | 4.423 | 5.4789 | 5.9539 | 0.95902 | 1.1644 | 1.4097 | 1.6575 | 1.9425 | 2.2409 | 2.5819 | 3.1679 | 3.8292 | 4.5925 | 5.4214 | 6.1472 | 6.8757 | 7.7143 | 8.5189 | 9.3 | 11.5147 | 12.5376
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.54172 | 0.77046 | 1.1253 | 1.416 | 1.7741 | 2.1889 | 2.7 | 3.3357 | 4.1461 | 4.8012 | 5.2411 | 5.5073 | 5.762 | 5.9134 | 6.0618 | 6.2089 | 6.7977 | 7.159 | 1.1845 | 1.6648 | 2.4307 | 3.0379 | 3.7917 | 4.6657 | 5.7396 | 7.0693 | 8.7958 | 10.2079 | 11.1839 | 11.7732 | 12.3393 | 12.6759 | 13.0063 | 13.3341 | 14.6564 | 15.4842
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.50424 | 0.69298 | 0.92265 | 1.1439 | 1.46 | 1.7636 | 2.2976 | 2.9401 | 3.5633 | 4.1998 | 4.7536 | 5.2037 | 5.6414 | 6.0615 | 6.3531 | 6.5181 | 7.0722 | 7.4537 | 1.1178 | 1.5324 | 2.0307 | 2.5149 | 3.2257 | 3.8888 | 5.0522 | 6.4338 | 7.7905 | 9.1785 | 10.3477 | 11.2886 | 12.2034 | 13.0816 | 13.7026 | 14.0702 | 15.3191 | 16.1901
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.46925 | 0.60849 | 0.80877 | 0.99598 | 1.2442 | 1.5376 | 1.8706 | 2.3191 | 2.8326 | 3.4009 | 3.9266 | 4.3883 | 4.8172 | 5.2214 | 5.4855 | 5.6448 | 6.3835 | 6.8342 | 1.0284 | 1.3234 | 1.7534 | 2.152 | 2.6859 | 3.3187 | 4.0298 | 4.9748 | 6.0738 | 7.315 | 8.4393 | 9.4052 | 10.2933 | 11.1302 | 11.6863 | 12.0352 | 13.6693 | 14.6776
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Counterfactual | 0.5876 | 0.64863 | 0.71811 | 0.7954 | 0.89347 | 1.0056 | 1.1316 | 1.3545 | 1.6933 | 2.0472 | 2.368 | 2.5505 | 2.7202 | 2.8881 | 3.0717 | 3.2611 | 3.6713 | 3.855 | 1.4096 | 1.5372 | 1.6818 | 1.8429 | 2.0476 | 2.2823 | 2.5478 | 3.0148 | 3.7483 | 4.5009 | 5.1855 | 5.5714 | 5.9172 | 6.2583 | 6.6389 | 7.0336 | 7.8789 | 8.2719
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.65373 | 0.80936 | 1.0162 | 1.2557 | 1.5528 | 1.9092 | 2.353 | 2.9076 | 3.4961 | 3.8292 | 4.0168 | 4.0615 | 4.0986 | 4.1466 | 4.1965 | 4.2405 | 4.4639 | 4.6942 | 1.5523 | 1.8821 | 2.3181 | 2.8284 | 3.4718 | 4.2448 | 5.199 | 6.3829 | 7.6495 | 8.3707 | 8.7967 | 8.8969 | 8.9815 | 9.0884 | 9.1995 | 9.2976 | 9.8039 | 10.3226
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.62904 | 0.77032 | 0.98423 | 1.2361 | 1.4867 | 1.7804 | 2.1006 | 2.4813 | 2.8304 | 3.1516 | 3.3832 | 3.6238 | 3.8568 | 4.0842 | 4.2302 | 4.2963 | 4.6118 | 4.9055 | 1.5083 | 1.8182 | 2.288 | 2.8462 | 3.403 | 4.0578 | 4.7648 | 5.5887 | 6.3572 | 7.0663 | 7.543 | 8.0381 | 8.5179 | 8.9872 | 9.2939 | 9.4405 | 10.1485 | 10.8174
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.60782 | 0.72077 | 0.86669 | 1.0301 | 1.2624 | 1.5727 | 1.9087 | 2.3094 | 2.6867 | 2.973 | 3.2775 | 3.509 | 3.7186 | 3.9124 | 4.0185 | 4.0557 | 4.2301 | 4.4247 | 1.4535 | 1.6965 | 2.0069 | 2.3617 | 2.8754 | 3.5647 | 4.3014 | 5.1641 | 5.9834 | 6.6013 | 7.259 | 7.7375 | 8.1633 | 8.5568 | 8.7747 | 8.856 | 9.2447 | 9.6767
Coventry 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.11852 | 0.13517 | 0.15508 | 0.17952 | 0.20621 | 0.24231 | 0.2814 | 0.3428 | 0.39291 | 0.48114 | 0.60284 | 0.72698 | 0.85848 | 0.98209 | 1.1045 | 1.2285 | 1.7145 | 1.957 | 0.26746 | 0.30227 | 0.34345 | 0.39385 | 0.44866 | 0.52238 | 0.60207 | 0.72698 | 0.82954 | 1.0136 | 1.269 | 1.5292 | 1.8041 | 2.062 | 2.3173 | 2.576 | 3.6023 | 4.1149
Coventry 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.1379 | 0.17801 | 0.23087 | 0.2907 | 0.35822 | 0.44204 | 0.54344 | 0.66871 | 0.86994 | 1.0553 | 1.1909 | 1.3044 | 1.4138 | 1.5214 | 1.6342 | 1.745 | 2.2999 | 2.476 | 0.30925 | 0.39319 | 0.50218 | 0.62536 | 0.76399 | 0.93522 | 1.1418 | 1.3974 | 1.8221 | 2.2152 | 2.5057 | 2.7517 | 2.9893 | 3.2225 | 3.4667 | 3.7071 | 4.9116 | 5.3013
Coventry 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.13049 | 0.15696 | 0.19039 | 0.22709 | 0.26784 | 0.32609 | 0.47946 | 0.65876 | 0.81317 | 0.97571 | 1.1424 | 1.3002 | 1.4561 | 1.6073 | 1.7427 | 1.8552 | 2.3407 | 2.458 | 0.29599 | 0.35398 | 0.42522 | 0.50319 | 0.58928 | 0.71043 | 1.0402 | 1.4228 | 1.7519 | 2.0978 | 2.4515 | 2.7868 | 3.118 | 3.4394 | 3.7296 | 3.974 | 5.0294 | 5.2876
Coventry 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.12434 | 0.14615 | 0.17643 | 0.21116 | 0.25101 | 0.3046 | 0.36686 | 0.45606 | 0.61163 | 0.77593 | 0.94247 | 1.1078 | 1.2636 | 1.412 | 1.5371 | 1.637 | 2.1073 | 2.2688 | 0.28008 | 0.32607 | 0.38886 | 0.46065 | 0.54286 | 0.65266 | 0.77986 | 0.96167 | 1.2915 | 1.6395 | 1.9913 | 2.3408 | 2.6692 | 2.9825 | 3.2493 | 3.4658 | 4.49 | 4.8412
Coventry 132kV | RUGBY 11kV S STN | Bulk Supply Point | 11 | Counterfactual | 5.4357 | 5.5135 | 5.5986 | 5.6934 | 5.8096 | 5.9483 | 6.0962 | 6.3267 | 6.5144 | 6.7267 | 6.9653 | 7.2159 | 5.8701 | 6.1266 | 6.36 | 5.9274 | 6.5299 | 6.8222 | 13.522 | 13.6841 | 13.8609 | 14.0575 | 14.2974 | 14.5825 | 14.886 | 15.3572 | 15.7437 | 16.1823 | 16.6754 | 17.1915 | 13.7092 | 14.2333 | 14.7084 | 13.5209 | 14.7692 | 15.3928
Coventry 132kV | RUGBY 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | 5.5147 | 5.6958 | 5.8928 | 6.146 | 6.4362 | 6.7334 | 7.0679 | 7.491 | 8.0393 | 8.5159 | 8.8091 | 9.0086 | 7.5787 | 7.6395 | 7.7162 | 7.1232 | 7.4533 | 7.7637 | 13.6927 | 14.079 | 14.4858 | 15.0109 | 15.6129 | 16.2261 | 16.9095 | 17.7738 | 18.9214 | 19.9252 | 20.5563 | 20.9952 | 17.3708 | 17.5053 | 17.675 | 16.1718 | 16.9055 | 17.6053
Coventry 132kV | RUGBY 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | 5.4856 | 5.6197 | 5.7743 | 5.9451 | 6.1193 | 6.3064 | 6.6947 | 7.1718 | 7.5781 | 7.9895 | 8.4035 | 8.6825 | 7.3531 | 7.6104 | 7.7988 | 7.2295 | 7.6515 | 8.0617 | 13.6409 | 13.938 | 14.2686 | 14.6334 | 15.0035 | 15.3958 | 16.2272 | 17.2389 | 18.0991 | 18.9683 | 19.8388 | 20.4129 | 16.9673 | 17.496 | 17.8911 | 16.4401 | 17.3743 | 18.3035
Coventry 132kV | RUGBY 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | 5.4596 | 5.5752 | 5.69 | 5.8343 | 5.9998 | 6.1901 | 6.4094 | 6.7235 | 7.0344 | 7.3765 | 7.7263 | 8.0567 | 6.7684 | 7.0452 | 7.2173 | 6.6286 | 6.9412 | 7.2122 | 13.574 | 13.8243 | 14.0629 | 14.3642 | 14.7092 | 15.1039 | 15.556 | 16.2003 | 16.8453 | 17.5546 | 18.2769 | 18.9572 | 15.5946 | 16.1606 | 16.5169 | 15.0208 | 15.7092 | 16.3112
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Counterfactual | 0.40245 | 0.40697 | 0.4113 | 0.41779 | 0.43646 | 0.45928 | 0.48454 | 0.51666 | 0.54583 | 0.58271 | 0.62609 | 0.67063 | 0.71706 | 0.76604 | 0.79959 | 0.83335 | 0.8862 | 0.91683 | 0.84045 | 0.84959 | 0.85829 | 0.87135 | 0.90985 | 0.95705 | 1.0094 | 1.0759 | 1.1367 | 1.2141 | 1.3055 | 1.3991 | 1.4965 | 1.5993 | 1.6691 | 1.7393 | 1.8466 | 1.909
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Electric Engagement | 0.40522 | 0.41415 | 0.42646 | 0.47911 | 0.54143 | 0.60877 | 0.68008 | 0.75757 | 0.8044 | 0.84649 | 0.87972 | 0.89366 | 0.90018 | 0.90566 | 0.91325 | 0.91979 | 0.95048 | 0.97046 | 0.846 | 0.86411 | 0.88882 | 1.0004 | 1.1336 | 1.2781 | 1.4306 | 1.5959 | 1.6944 | 1.7834 | 1.8547 | 1.8845 | 1.8982 | 1.9095 | 1.9254 | 1.9393 | 2.0049 | 2.0492
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Holistic Transition | 0.40262 | 0.40724 | 0.4465 | 0.49663 | 0.55021 | 0.60941 | 0.69225 | 0.7334 | 0.77145 | 0.79704 | 0.81746 | 0.83731 | 0.8564 | 0.87417 | 0.88812 | 0.89624 | 0.92978 | 0.95212 | 0.8408 | 0.85034 | 0.93445 | 1.0417 | 1.1572 | 1.2854 | 1.4654 | 1.5528 | 1.6337 | 1.6871 | 1.7288 | 1.7691 | 1.8079 | 1.8439 | 1.8725 | 1.8896 | 1.961 | 2.0092
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Hydrogen Evolution | 0.40384 | 0.40911 | 0.41721 | 0.4436 | 0.47264 | 0.50538 | 0.54034 | 0.58377 | 0.63706 | 0.69259 | 0.74866 | 0.80408 | 0.85955 | 0.89871 | 0.93215 | 0.94282 | 0.9651 | 0.9783 | 0.84323 | 0.8539 | 0.87019 | 0.92582 | 0.98732 | 1.0568 | 1.1307 | 1.2219 | 1.3355 | 1.4539 | 1.5731 | 1.691 | 1.8091 | 1.8916 | 1.9627 | 1.985 | 2.0315 | 2.0599
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.1368 | 1.1588 | 1.1816 | 1.209 | 1.2351 | 1.2663 | 1.3008 | 1.3671 | 1.4251 | 1.5089 | 1.6039 | 1.6992 | 1.796 | 1.4991 | 1.5965 | 1.696 | 2.0799 | 1.9476 | 2.8178 | 2.8638 | 2.9111 | 2.9679 | 3.0215 | 3.0856 | 3.1562 | 3.2945 | 3.4177 | 3.5968 | 3.798 | 3.998 | 4.2001 | 3.4161 | 3.619 | 3.8263 | 4.6408 | 4.1996
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.1575 | 1.2058 | 1.2614 | 1.7581 | 1.8291 | 1.9103 | 2.0159 | 2.1609 | 2.4562 | 2.7344 | 2.9785 | 3.2047 | 3.4179 | 3.0524 | 3.0841 | 3.1138 | 3.3124 | 3.0332 | 2.8627 | 2.9644 | 3.0812 | 4.2974 | 4.4456 | 4.6142 | 4.8332 | 5.1375 | 5.775 | 6.3777 | 6.9122 | 7.4097 | 7.8833 | 6.9586 | 7.0265 | 7.0897 | 7.5379 | 6.811
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.1505 | 1.1861 | 1.2229 | 1.2628 | 1.3075 | 1.3739 | 1.6219 | 1.8969 | 2.1577 | 2.4294 | 2.6979 | 2.7832 | 2.8686 | 2.5525 | 2.6228 | 2.6675 | 2.8726 | 2.5678 | 2.8502 | 2.9276 | 3.0077 | 3.0939 | 3.1902 | 3.3308 | 3.873 | 4.4726 | 5.0402 | 5.6316 | 6.2145 | 6.39 | 6.5673 | 5.7415 | 5.8911 | 5.9893 | 6.4483 | 5.6497
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.1435 | 1.1715 | 1.2058 | 1.2445 | 1.2839 | 1.3323 | 1.3986 | 1.4966 | 1.6288 | 1.7694 | 1.9073 | 2.0433 | 2.1735 | 1.8973 | 1.9956 | 2.0689 | 2.4169 | 2.3018 | 2.8323 | 2.8914 | 2.9631 | 3.0436 | 3.1249 | 3.2245 | 3.3611 | 3.5655 | 3.8473 | 4.1481 | 4.4406 | 4.7282 | 5.0029 | 4.2647 | 4.4738 | 4.6331 | 5.4009 | 5.0223
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.0791 | 1.1749 | 1.2921 | 1.428 | 1.5857 | 1.7691 | 1.9706 | 2.3029 | 2.588 | 2.8883 | 3.1781 | 3.4846 | 3.8319 | 4.1816 | 4.5261 | 4.852 | 5.6993 | 6.2257 | 2.5421 | 2.742 | 2.9847 | 3.2657 | 3.5916 | 3.9699 | 4.385 | 5.0778 | 5.6831 | 6.3237 | 6.9333 | 7.5707 | 8.2871 | 9.0086 | 9.7239 | 10.3999 | 12.1999 | 13.3685
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.189 | 1.4127 | 1.7202 | 2.0803 | 2.4964 | 2.9284 | 3.4241 | 4.0891 | 4.7292 | 5.3321 | 5.7294 | 5.9389 | 6.1576 | 6.3228 | 6.4739 | 6.625 | 7.3744 | 8.1144 | 2.7793 | 3.2485 | 3.897 | 4.6547 | 5.5308 | 6.4311 | 7.4532 | 8.8442 | 10.1985 | 11.4944 | 12.3824 | 12.8675 | 13.3741 | 13.7519 | 14.093 | 14.4418 | 16.1767 | 17.9204
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.1479 | 1.3023 | 1.4982 | 1.7225 | 1.9883 | 2.2865 | 2.6856 | 3.2534 | 3.7626 | 4.3361 | 4.8409 | 5.3202 | 5.806 | 6.2297 | 6.5248 | 6.6826 | 7.4584 | 8.0418 | 2.7062 | 3.044 | 3.4709 | 3.9585 | 4.5359 | 5.1707 | 6.0359 | 7.2639 | 8.3693 | 9.6206 | 10.6962 | 11.7177 | 12.7494 | 13.6406 | 14.2737 | 14.6323 | 16.4115 | 17.7464
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.1121 | 1.2318 | 1.3898 | 1.5817 | 1.8073 | 2.0559 | 2.3463 | 2.8031 | 3.227 | 3.7958 | 4.2855 | 4.7363 | 5.1704 | 5.5546 | 5.7962 | 5.9072 | 6.4754 | 7.1225 | 2.6138 | 2.8665 | 3.1981 | 3.6002 | 4.0753 | 4.5923 | 5.1912 | 6.1444 | 7.0372 | 8.2562 | 9.2939 | 10.2398 | 11.1413 | 11.9342 | 12.4413 | 12.6895 | 13.9942 | 15.4906
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.0674 | 1.4801 | 1.5981 | 1.7286 | 1.9067 | 2.1125 | 2.3385 | 2.671 | 2.9335 | 3.2284 | 3.561 | 3.8942 | 4.2487 | 4.5953 | 4.9353 | 5.2745 | 6.1664 | 6.5733 | 2.3377 | 3.3293 | 3.5735 | 3.8432 | 4.2115 | 4.6368 | 5.103 | 5.7832 | 6.3227 | 6.9301 | 7.617 | 8.303 | 9.0293 | 9.7379 | 10.4325 | 11.1254 | 12.9794 | 13.8506
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.4983 | 1.7313 | 2.0115 | 2.4541 | 2.9648 | 3.4619 | 4.0399 | 4.7285 | 5.4624 | 6.092 | 6.4565 | 6.7076 | 6.9465 | 7.0053 | 7.0894 | 7.1683 | 7.5222 | 7.9032 | 3.3758 | 3.8644 | 4.4437 | 5.3693 | 6.4391 | 7.4765 | 8.6752 | 10.0957 | 11.628 | 12.9497 | 13.7328 | 14.2872 | 14.8166 | 14.9495 | 15.138 | 15.3158 | 16.1213 | 16.9857
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.456 | 1.6134 | 1.8963 | 2.2265 | 2.5414 | 2.8932 | 3.5069 | 4.1277 | 4.6513 | 5.1988 | 5.7674 | 6.1388 | 6.5008 | 6.8381 | 7.075 | 7.1822 | 7.6671 | 8.1247 | 3.3008 | 3.6447 | 4.2532 | 4.9616 | 5.6361 | 6.3877 | 7.7072 | 9.0184 | 10.1245 | 11.2781 | 12.4726 | 13.2371 | 13.9822 | 14.6763 | 15.1759 | 15.4161 | 16.5139 | 17.5566
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.4168 | 1.5441 | 1.7091 | 1.9393 | 2.1986 | 2.4831 | 2.8088 | 3.2486 | 3.6796 | 4.1335 | 4.598 | 5.0419 | 5.4666 | 5.8638 | 6.1089 | 6.2216 | 6.6988 | 7.03 | 3.2003 | 3.469 | 3.8134 | 4.2973 | 4.8423 | 5.4385 | 6.1159 | 7.0198 | 7.9147 | 8.8541 | 9.8115 | 10.7246 | 11.5969 | 12.4132 | 12.9247 | 13.1713 | 14.2284 | 14.9666
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.55698 | 0.63691 | 0.74568 | 0.85727 | 0.98102 | 1.1225 | 1.2748 | 1.5264 | 1.7352 | 1.9588 | 2.1796 | 2.4147 | 2.6761 | 2.9372 | 3.1963 | 3.4561 | 4.2146 | 4.6174 | 1.2238 | 1.3911 | 1.6163 | 1.8473 | 2.103 | 2.3947 | 2.7084 | 3.2239 | 3.6553 | 4.1178 | 4.5732 | 5.0553 | 5.5893 | 6.122 | 6.6508 | 7.1808 | 8.7546 | 9.6134
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.64538 | 0.83161 | 1.0838 | 1.3554 | 1.6586 | 2.0034 | 2.4231 | 2.9274 | 3.3757 | 3.7581 | 3.9877 | 4.1389 | 4.2738 | 4.4038 | 4.533 | 4.6578 | 5.2455 | 5.8306 | 1.4146 | 1.8045 | 2.3265 | 2.8884 | 3.514 | 4.2258 | 5.0901 | 6.1247 | 7.0469 | 7.837 | 8.3216 | 8.6491 | 8.9441 | 9.2269 | 9.5075 | 9.7792 | 11.0694 | 12.3503
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.61167 | 0.74066 | 0.91229 | 1.0923 | 1.3025 | 1.5585 | 1.8303 | 2.2025 | 2.5305 | 2.8882 | 3.2937 | 3.7291 | 4.1586 | 4.5636 | 4.8463 | 5.005 | 5.7307 | 6.3114 | 1.3544 | 1.6353 | 2.0013 | 2.3854 | 2.8329 | 3.3769 | 3.9509 | 4.7276 | 5.4129 | 6.1601 | 7.0012 | 7.9027 | 8.7925 | 9.6308 | 10.2236 | 10.5685 | 12.1559 | 13.4403
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.58433 | 0.69058 | 0.85024 | 1.0087 | 1.1898 | 1.4091 | 1.6644 | 2.0196 | 2.3293 | 2.6594 | 3.0261 | 3.3912 | 3.7529 | 4.0888 | 4.3098 | 4.433 | 4.9601 | 5.4103 | 1.2829 | 1.5074 | 1.8396 | 2.1705 | 2.5478 | 3.0047 | 3.5346 | 4.2654 | 4.9047 | 5.5846 | 6.3373 | 7.0871 | 7.8293 | 8.5187 | 8.9777 | 9.2411 | 10.3843 | 11.3716
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.25121 | 0.2751 | 0.30238 | 0.33338 | 0.36871 | 0.42048 | 0.47579 | 0.58166 | 0.68052 | 0.79903 | 0.90268 | 0.99661 | 1.0925 | 1.1891 | 1.2833 | 1.3802 | 1.7393 | 2.0124 | 0.55785 | 0.60799 | 0.66454 | 0.72861 | 0.80141 | 0.90719 | 1.0201 | 1.2457 | 1.4616 | 1.7259 | 1.9504 | 2.1495 | 2.3491 | 2.5505 | 2.7466 | 2.9481 | 3.7258 | 4.3333
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.2787 | 0.33569 | 0.41504 | 0.49601 | 0.58751 | 0.71015 | 0.85602 | 1.0696 | 1.2863 | 1.4867 | 1.6421 | 1.7574 | 1.8692 | 1.9592 | 2.0508 | 2.1976 | 2.7003 | 3.0404 | 0.61705 | 0.73691 | 0.90403 | 1.0709 | 1.2591 | 1.5098 | 1.807 | 2.2587 | 2.7234 | 3.1579 | 3.5038 | 3.7651 | 4.02 | 4.2196 | 4.4217 | 4.7364 | 5.8563 | 6.6627
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.26861 | 0.31091 | 0.35687 | 0.411 | 0.46798 | 0.55527 | 0.69626 | 0.90613 | 1.0824 | 1.2854 | 1.4777 | 1.6618 | 1.8381 | 1.9874 | 2.1059 | 2.244 | 2.692 | 2.9004 | 0.59905 | 0.69287 | 0.79105 | 0.90756 | 1.0282 | 1.2096 | 1.5211 | 1.988 | 2.3767 | 2.8271 | 3.2458 | 3.6461 | 4.028 | 4.345 | 4.5999 | 4.8941 | 5.8927 | 6.3614
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.25987 | 0.29144 | 0.33887 | 0.38499 | 0.43821 | 0.51456 | 0.60065 | 0.74924 | 0.89103 | 1.0682 | 1.2315 | 1.3861 | 1.5325 | 1.6586 | 1.7518 | 1.8416 | 2.1872 | 2.5215 | 0.57655 | 0.64344 | 0.7451 | 0.84084 | 0.95105 | 1.1077 | 1.2837 | 1.5992 | 1.9041 | 2.2923 | 2.6431 | 2.9731 | 3.2831 | 3.5465 | 3.7436 | 3.9361 | 4.719 | 5.4943
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.4901 | 1.5149 | 1.5438 | 1.5766 | 1.6141 | 1.6619 | 1.7143 | 1.812 | 1.8994 | 2.0009 | 2.1031 | 2.1915 | 2.2838 | 2.3763 | 2.4664 | 2.5591 | 2.2092 | 2.424 | 3.412 | 3.464 | 3.5239 | 3.5918 | 3.6691 | 3.767 | 3.8741 | 4.0803 | 4.2687 | 4.4898 | 4.7087 | 4.8943 | 5.0849 | 5.2763 | 5.4625 | 5.654 | 4.6688 | 5.145
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.5185 | 1.5775 | 1.653 | 1.7375 | 1.8337 | 1.9496 | 2.0881 | 2.2837 | 2.4811 | 2.6576 | 2.7752 | 2.8567 | 2.9864 | 3.0479 | 3.11 | 3.2257 | 2.895 | 3.158 | 3.4731 | 3.5968 | 3.7526 | 3.9267 | 4.1243 | 4.3617 | 4.6444 | 5.0543 | 5.4742 | 5.8536 | 6.1147 | 6.3006 | 6.5832 | 6.7211 | 6.8596 | 7.1071 | 6.2028 | 6.8255
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.5078 | 1.5475 | 1.5953 | 1.6477 | 1.7067 | 1.7852 | 1.912 | 2.0977 | 2.2461 | 2.4146 | 2.5771 | 2.7367 | 2.9433 | 3.0768 | 3.1758 | 3.2918 | 2.9523 | 3.1238 | 3.454 | 3.541 | 3.6429 | 3.7543 | 3.8791 | 4.0431 | 4.3208 | 4.7288 | 5.0527 | 5.4225 | 5.7728 | 6.1163 | 6.5521 | 6.8337 | 7.0461 | 7.2926 | 6.365 | 6.755
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.499 | 1.5319 | 1.5746 | 1.6234 | 1.6792 | 1.7507 | 1.8334 | 1.9708 | 2.1043 | 2.2652 | 2.4097 | 2.5479 | 2.7062 | 2.8213 | 2.9009 | 2.9745 | 2.5622 | 2.8076 | 3.4311 | 3.5007 | 3.5895 | 3.6906 | 3.8062 | 3.9534 | 4.123 | 4.412 | 4.6961 | 5.0443 | 5.3513 | 5.6432 | 5.9725 | 6.2115 | 6.3791 | 6.5362 | 5.4507 | 6.0222
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.99027 | 1.013 | 1.0394 | 1.0689 | 1.1023 | 1.1672 | 1.2329 | 1.3596 | 1.4825 | 1.6205 | 1.7464 | 1.8557 | 1.9637 | 1.4595 | 1.5671 | 1.6773 | 2.1335 | 2.5063 | 2.4117 | 2.4592 | 2.5139 | 2.575 | 2.6438 | 2.7758 | 2.9094 | 3.1821 | 3.4536 | 3.764 | 4.0401 | 4.2746 | 4.5015 | 3.1975 | 3.4232 | 3.6547 | 4.651 | 5.4835
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.017 | 1.0707 | 1.1407 | 1.2191 | 1.3074 | 0.84032 | 1.01 | 1.2688 | 1.5407 | 1.8034 | 2.0291 | 2.2056 | 2.3828 | 2.5294 | 2.6792 | 2.8625 | 3.7783 | 4.2672 | 2.4695 | 2.5819 | 2.7266 | 2.888 | 3.0698 | 1.8337 | 2.1782 | 2.7298 | 3.3183 | 3.8918 | 4.3937 | 4.791 | 5.1906 | 5.5112 | 5.8374 | 6.246 | 8.2376 | 9.3937
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.0071 | 1.0433 | 1.0877 | 1.1362 | 1.1906 | 0.68537 | 0.86872 | 1.1391 | 1.368 | 1.6339 | 1.9316 | 2.1704 | 2.4013 | 2.5966 | 2.759 | 2.8908 | 3.6655 | 3.9445 | 2.4518 | 2.5309 | 2.6256 | 2.7288 | 2.844 | 1.533 | 1.9408 | 2.5492 | 3.0584 | 3.6542 | 4.322 | 4.8453 | 5.3486 | 5.764 | 6.1127 | 6.4005 | 8.0889 | 8.7101
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.99893 | 1.0289 | 1.0674 | 1.111 | 1.1608 | 0.63735 | 0.73328 | 0.9047 | 1.0746 | 1.2922 | 1.4876 | 1.6743 | 1.8511 | 2.0052 | 2.1279 | 2.2518 | 2.8253 | 3.3235 | 2.4305 | 2.4938 | 2.5739 | 2.6647 | 2.7677 | 1.4178 | 1.6134 | 1.9815 | 2.3514 | 2.836 | 3.2618 | 3.6651 | 4.0432 | 4.3667 | 4.6269 | 4.905 | 6.182 | 7.3311
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Counterfactual | 2.3037 | 2.4144 | 2.5601 | 2.7289 | 2.9511 | 3.2132 | 3.5015 | 3.9003 | 4.1794 | 4.4718 | 4.7529 | 5.0252 | 5.3358 | 5.7783 | 6.1196 | 4.5122 | 5.3152 | 5.7197 | 5.6475 | 5.8894 | 6.2075 | 6.5783 | 7.0653 | 7.6405 | 8.2748 | 9.1393 | 9.7195 | 10.328 | 10.9105 | 11.4704 | 12.107 | 13.0733 | 13.7924 | 9.6443 | 11.313 | 12.1801
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.4367 | 2.7301 | 3.1317 | 3.6069 | 4.2122 | 3.0325 | 3.8143 | 4.7279 | 5.3252 | 6.2221 | 6.5023 | 6.6539 | 6.78 | 6.9005 | 7.0246 | 7.1373 | 7.6744 | 8.2051 | 5.9461 | 6.5977 | 7.4879 | 8.5498 | 9.9038 | 6.7736 | 8.5115 | 10.5222 | 11.7648 | 13.8128 | 14.4101 | 14.7425 | 15.0215 | 15.2878 | 15.5606 | 15.8107 | 17.0139 | 18.1982
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.3991 | 2.6304 | 2.9414 | 3.3198 | 3.8449 | 2.5762 | 3.2443 | 4.0262 | 4.8999 | 5.3305 | 5.7543 | 6.2118 | 6.6695 | 7.0973 | 7.3858 | 7.5374 | 8.2191 | 8.7841 | 5.8788 | 6.4122 | 7.1272 | 8.0015 | 9.2091 | 5.9124 | 7.4384 | 9.1952 | 11.2089 | 12.1121 | 12.9914 | 13.9392 | 14.8885 | 15.776 | 16.3836 | 16.7176 | 18.2336 | 19.5005
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.368 | 2.5723 | 2.8648 | 3.2188 | 3.6965 | 2.3802 | 3.0028 | 3.7414 | 4.1539 | 5.0375 | 5.4291 | 5.8152 | 6.1984 | 6.5528 | 6.7796 | 6.8866 | 7.3705 | 7.8109 | 5.7979 | 6.2645 | 6.9312 | 7.7452 | 8.8407 | 5.4332 | 6.8509 | 8.5033 | 9.3646 | 11.3886 | 12.1935 | 12.987 | 13.7738 | 14.5018 | 14.9743 | 15.2074 | 16.2744 | 17.2509
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.4632 | 1.5695 | 1.7064 | 1.8449 | 2.0016 | 2.1817 | 2.3788 | 2.7046 | 3.0169 | 3.4005 | 3.9012 | 4.2829 | 4.6904 | 5.0585 | 5.4 | 5.7292 | 6.5603 | 6.8961 | 3.5701 | 3.792 | 4.0765 | 4.3642 | 4.6894 | 5.0629 | 5.471 | 6.1427 | 6.8017 | 7.6065 | 8.6687 | 9.4737 | 10.3265 | 11.0945 | 11.7986 | 12.4699 | 14.1954 | 14.9233
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.5862 | 1.8447 | 2.1761 | 2.5351 | 2.9571 | 3.4407 | 4.0292 | 4.7654 | 5.5487 | 6.2067 | 6.587 | 6.7986 | 6.9927 | 6.2293 | 6.3344 | 6.4343 | 6.9455 | 7.4223 | 3.8362 | 4.3794 | 5.0703 | 5.8203 | 6.7065 | 7.722 | 8.9535 | 10.4902 | 12.1558 | 13.5568 | 14.3897 | 14.8683 | 15.3097 | 13.3756 | 13.6113 | 13.8368 | 14.9937 | 16.0823
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.5411 | 1.7244 | 1.9756 | 2.2438 | 2.5366 | 2.8993 | 3.3669 | 3.9748 | 4.5223 | 5.1128 | 5.6676 | 6.2047 | 5.8477 | 6.2857 | 6.5654 | 6.6903 | 7.3312 | 8.7548 | 3.756 | 4.1557 | 4.7003 | 5.2836 | 5.9189 | 6.7078 | 7.7249 | 9.0292 | 10.2101 | 11.4761 | 12.6452 | 13.7738 | 12.6712 | 13.5786 | 14.1692 | 14.4496 | 15.8955 | 19.3407
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.5011 | 1.6562 | 1.865 | 2.0783 | 2.3446 | 2.6697 | 3.0457 | 3.5643 | 4.0954 | 4.6734 | 5.2008 | 5.7003 | 6.1854 | 6.5982 | 6.823 | 6.918 | 7.3328 | 7.7271 | 3.6527 | 3.9825 | 4.4236 | 4.8768 | 5.4471 | 6.1444 | 6.9447 | 8.0368 | 9.1793 | 10.4172 | 11.5278 | 12.5713 | 13.5834 | 14.4408 | 14.9081 | 15.1182 | 16.0481 | 16.9366
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.40823 | 0.40884 | 0.40946 | 0.74752 | 0.74829 | 0.74905 | 0.74993 | 0.75141 | 0.75296 | 0.75475 | 0.75647 | 0.75799 | 0.75961 | 0.76113 | 0.76246 | 0.76409 | 0.77297 | 0.78176 | 0.98545 | 0.98686 | 0.98831 | 1.8333 | 1.835 | 1.8366 | 1.8384 | 1.8415 | 1.8449 | 1.8489 | 1.8525 | 1.8557 | 1.859 | 1.8621 | 1.8649 | 1.8682 | 1.8869 | 1.9054
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.40846 | 0.41188 | 0.75016 | 0.75121 | 0.75256 | 0.75407 | 0.75618 | 0.75913 | 0.76243 | 0.76552 | 0.76866 | 0.77149 | 0.77399 | 0.77622 | 0.77875 | 0.78081 | 0.79132 | 0.88214 | 0.98591 | 0.9942 | 1.8395 | 1.8417 | 1.8445 | 1.8476 | 1.852 | 1.8583 | 1.8654 | 1.8721 | 1.8789 | 1.885 | 1.8905 | 1.8953 | 1.9006 | 1.9051 | 1.9284 | 2.1542
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.40841 | 0.74911 | 0.74995 | 0.75095 | 0.75208 | 0.75383 | 0.75603 | 0.7595 | 0.76224 | 0.76553 | 0.76844 | 0.77123 | 0.77391 | 0.77615 | 0.77913 | 0.78165 | 0.96129 | 0.96795 | 0.9858 | 1.8374 | 1.8392 | 1.8414 | 1.8438 | 1.8474 | 1.8522 | 1.8598 | 1.8659 | 1.8731 | 1.8794 | 1.8854 | 1.8913 | 1.8961 | 1.9023 | 1.9076 | 2.3532 | 2.3674
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.40841 | 0.4114 | 0.74944 | 0.75072 | 0.75212 | 0.75375 | 0.75566 | 0.75865 | 0.76147 | 0.76537 | 0.76861 | 0.77114 | 0.77412 | 0.77588 | 0.77833 | 0.77981 | 0.78814 | 0.88068 | 0.9858 | 0.99315 | 1.8379 | 1.8406 | 1.8434 | 1.8467 | 1.8506 | 1.8568 | 1.8628 | 1.8711 | 1.878 | 1.8833 | 1.8895 | 1.8932 | 1.8983 | 1.9014 | 1.9197 | 2.1485
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.55842 | 0.59357 | 0.63316 | 0.67843 | 0.73018 | 0.80062 | 0.87694 | 0.99831 | 1.0974 | 1.2016 | 1.3099 | 1.4209 | 1.5438 | 1.6664 | 1.7864 | 1.9077 | 2.2606 | 2.4609 | 1.29 | 1.3634 | 1.4453 | 1.5387 | 1.6452 | 1.7891 | 1.9449 | 2.1925 | 2.3964 | 2.6112 | 2.8333 | 3.0598 | 3.3093 | 3.5583 | 3.8017 | 4.0476 | 4.7727 | 5.1903
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.59834 | 0.6798 | 0.7922 | 0.9196 | 1.0616 | 1.2382 | 1.4465 | 1.7074 | 1.9545 | 2.1675 | 2.3048 | 2.395 | 2.4808 | 2.5568 | 2.6299 | 2.7572 | 3.1842 | 3.3449 | 1.3763 | 1.5468 | 1.7826 | 2.0494 | 2.3453 | 2.7103 | 3.1379 | 3.6752 | 4.1868 | 4.6282 | 4.9174 | 5.1117 | 5.2989 | 5.4624 | 5.6167 | 5.8824 | 6.7883 | 7.1561
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.58307 | 0.63711 | 0.70908 | 0.78719 | 0.8748 | 0.99455 | 1.1329 | 1.325 | 1.4952 | 1.6825 | 1.88 | 2.0688 | 2.2509 | 2.4187 | 2.5396 | 2.662 | 3.0516 | 3.2034 | 1.349 | 1.4671 | 1.6234 | 1.7922 | 1.9805 | 2.2316 | 2.5221 | 2.9231 | 3.2777 | 3.6674 | 4.0765 | 4.4672 | 4.8438 | 5.1896 | 5.4412 | 5.6958 | 6.5248 | 6.8634
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.5713 | 0.61668 | 0.67481 | 0.74159 | 0.81783 | 0.92207 | 1.0427 | 1.2168 | 1.3737 | 1.5498 | 1.7299 | 1.9041 | 2.0734 | 2.2261 | 2.3295 | 2.4088 | 2.6569 | 2.8174 | 1.3179 | 1.4135 | 1.5343 | 1.6726 | 1.8302 | 2.044 | 2.2906 | 2.6462 | 2.9678 | 3.3297 | 3.6977 | 4.0531 | 4.398 | 4.7083 | 4.9199 | 5.084 | 5.6087 | 5.9567
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.76697 | 0.89601 | 1.0361 | 1.2329 | 1.3733 | 1.4963 | 1.6369 | 1.8164 | 1.979 | 2.0855 | 2.1821 | 2.28 | 2.3902 | 2.5031 | 2.6815 | 2.8794 | 3.2209 | 3.4371 | 1.7342 | 2.0134 | 2.314 | 2.736 | 3.0372 | 3.2988 | 3.5986 | 3.9805 | 4.3304 | 4.5574 | 4.7601 | 4.9634 | 5.1904 | 5.4229 | 5.8217 | 6.2671 | 6.9882 | 7.4578
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.79907 | 0.96843 | 1.1586 | 1.4135 | 1.6209 | 1.8213 | 2.0559 | 2.3397 | 2.6128 | 2.799 | 3.1694 | 3.2473 | 3.3298 | 3.4066 | 3.4812 | 3.5581 | 4.0765 | 4.3451 | 1.8033 | 2.1681 | 2.5724 | 3.1145 | 3.5546 | 3.9758 | 4.4681 | 5.0662 | 5.6453 | 6.0386 | 6.9247 | 7.0983 | 7.2818 | 7.45 | 7.6133 | 7.7817 | 8.9314 | 9.5454
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.7869 | 0.93636 | 1.0965 | 1.3155 | 1.4831 | 1.6481 | 1.8503 | 2.1007 | 2.327 | 2.5076 | 2.9332 | 3.258 | 3.4306 | 3.5911 | 3.7107 | 3.7897 | 4.2345 | 4.4844 | 1.7815 | 2.109 | 2.4551 | 2.9269 | 3.2891 | 3.6426 | 4.0812 | 4.6223 | 5.1108 | 5.4983 | 6.4954 | 7.2407 | 7.6059 | 7.9427 | 8.1973 | 8.3707 | 9.3386 | 9.8955
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.77694 | 0.91565 | 1.069 | 1.2823 | 1.4423 | 1.5905 | 1.7665 | 1.9897 | 2.1973 | 2.3627 | 2.6946 | 2.9207 | 3.0752 | 3.2158 | 3.3118 | 3.3716 | 3.7673 | 4.0344 | 1.7558 | 2.0562 | 2.3849 | 2.8418 | 3.1846 | 3.4996 | 3.8738 | 4.3478 | 4.7909 | 5.1417 | 5.9076 | 6.4112 | 6.7327 | 7.024 | 7.2256 | 7.3553 | 8.2444 | 8.842
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.64866 | 0.67517 | 0.70477 | 0.74575 | 0.80354 | 0.87396 | 0.9408 | 1.0495 | 1.1533 | 1.2709 | 1.3855 | 1.4955 | 1.5724 | 1.6495 | 1.7249 | 1.8012 | 2.0347 | 2.168 | 1.3885 | 1.444 | 1.5055 | 1.5905 | 1.7157 | 1.8727 | 2.0204 | 2.2608 | 2.4958 | 2.764 | 3.0235 | 3.2694 | 3.429 | 3.5888 | 3.7451 | 3.9031 | 4.4094 | 4.7152
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.67558 | 0.73279 | 0.80443 | 0.91626 | 1.1201 | 1.2906 | 1.4784 | 1.7145 | 1.9474 | 2.1618 | 2.3125 | 2.3739 | 2.4322 | 2.4734 | 2.5146 | 2.5567 | 2.8 | 2.9908 | 1.4469 | 1.5672 | 1.7164 | 1.9589 | 2.4258 | 2.8086 | 3.2264 | 3.752 | 4.2759 | 4.764 | 5.1184 | 5.2625 | 5.4006 | 5.4962 | 5.5916 | 5.6899 | 6.2635 | 6.7271
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.6659 | 0.70598 | 0.79662 | 0.89676 | 1.0406 | 1.1762 | 1.3494 | 1.5735 | 1.7726 | 1.989 | 2.1246 | 2.3034 | 2.4296 | 2.5352 | 2.6081 | 2.6493 | 2.8556 | 2.9577 | 1.4297 | 1.5173 | 1.7256 | 1.9538 | 2.2884 | 2.6029 | 3.0066 | 3.5232 | 3.9829 | 4.4821 | 4.7763 | 5.1795 | 5.4523 | 5.6764 | 5.8348 | 5.9298 | 6.4109 | 6.6497
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.65774 | 0.69185 | 0.73724 | 0.81542 | 0.97682 | 1.1142 | 1.2537 | 1.4401 | 1.6178 | 1.8191 | 1.9982 | 2.1126 | 2.22 | 2.3119 | 2.3704 | 2.3998 | 2.5917 | 2.7652 | 1.4085 | 1.4808 | 1.5758 | 1.7484 | 2.1265 | 2.4459 | 2.7654 | 3.1877 | 3.5942 | 4.0557 | 4.4593 | 4.7021 | 4.9284 | 5.1196 | 5.2441 | 5.3113 | 5.7664 | 6.181
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.33552 | 0.4104 | 0.49871 | 0.60436 | 0.72223 | 0.86233 | 1.0206 | 1.2725 | 1.4801 | 1.6884 | 1.9001 | 2.1193 | 2.3616 | 2.604 | 2.8423 | 3.086 | 3.7454 | 4.0757 | 0.76055 | 0.91681 | 1.0995 | 1.3181 | 1.5614 | 1.8498 | 2.175 | 2.6923 | 3.1226 | 3.5549 | 3.9917 | 4.4408 | 4.9345 | 5.4278 | 5.9125 | 6.4088 | 7.7865 | 8.5066
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.42818 | 0.61075 | 0.83275 | 1.1023 | 1.4088 | 1.7523 | 2.1555 | 2.6431 | 3.0927 | 3.4682 | 3.6715 | 3.7796 | 3.8864 | 3.9814 | 4.0778 | 4.1829 | 4.7336 | 5.1728 | 0.96073 | 1.3422 | 1.8012 | 2.3595 | 2.9933 | 3.7017 | 4.5284 | 5.5275 | 6.4532 | 7.2311 | 7.6666 | 7.9096 | 8.1509 | 8.3634 | 8.5783 | 8.8124 | 10.0421 | 11.0466
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.39367 | 0.51518 | 0.67421 | 0.84647 | 1.0364 | 1.2595 | 1.5154 | 1.8889 | 2.2219 | 2.5866 | 2.9654 | 3.333 | 3.6939 | 4.0268 | 4.247 | 4.3698 | 4.9784 | 5.4271 | 0.89943 | 1.1638 | 1.5044 | 1.8729 | 2.2778 | 2.7485 | 3.2897 | 4.0747 | 4.7743 | 5.5409 | 6.3313 | 7.0996 | 7.853 | 8.5454 | 9.0121 | 9.2864 | 10.6494 | 11.6646
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.36296 | 0.46319 | 0.58878 | 0.73745 | 0.90573 | 1.1084 | 1.3457 | 1.6873 | 1.9735 | 2.2963 | 2.6294 | 2.951 | 3.2655 | 3.5556 | 3.7234 | 3.7952 | 4.2145 | 4.6179 | 0.82037 | 1.0312 | 1.2929 | 1.6039 | 1.9552 | 2.3766 | 2.8664 | 3.5705 | 4.1603 | 4.8283 | 5.5127 | 6.1722 | 6.8158 | 7.4079 | 7.7553 | 7.9135 | 8.8485 | 9.7553
Drakelow 132kV | Burton 11kV | Bulk Supply Point | 11 | Counterfactual | 1.5941 | 1.7976 | 2.0362 | 2.3072 | 2.6199 | 2.9989 | 3.4766 | 4.2043 | 4.9128 | 5.5348 | 6.1765 | 6.8387 | 7.5136 | 8.1811 | 8.8356 | 9.4936 | 11.2249 | 12.0601 | 3.793 | 4.2181 | 4.7124 | 5.2733 | 5.921 | 6.7099 | 7.7091 | 9.2256 | 10.7494 | 12.057 | 13.4043 | 14.789 | 16.1705 | 17.5357 | 18.8735 | 20.2169 | 23.8203 | 25.6164
Drakelow 132kV | Burton 11kV | Bulk Supply Point | 11 | Electric Engagement | 1.8231 | 2.2872 | 2.8699 | 3.602 | 4.4966 | 5.487 | 6.6678 | 8.225 | 9.6011 | 10.6837 | 11.2926 | 11.6052 | 11.9208 | 12.1893 | 12.4572 | 12.7069 | 13.899 | 14.932 | 4.2882 | 5.2609 | 6.4738 | 8.0232 | 9.9365 | 12.0527 | 14.5424 | 17.8222 | 20.7272 | 23.0218 | 24.3567 | 25.0543 | 25.7586 | 26.3594 | 26.9541 | 27.5137 | 30.1968 | 32.5349
Drakelow 132kV | Burton 11kV | Bulk Supply Point | 11 | Holistic Transition | 1.7394 | 2.057 | 2.4959 | 3.0233 | 3.6112 | 4.2966 | 5.1253 | 6.3537 | 7.3832 | 8.4053 | 9.359 | 10.2964 | 11.2387 | 12.0997 | 12.6931 | 13.0012 | 14.4119 | 15.5789 | 4.1393 | 4.8322 | 5.7979 | 6.9663 | 8.262 | 9.7606 | 11.5594 | 14.1927 | 16.4042 | 18.5888 | 20.5788 | 22.5352 | 24.4999 | 26.295 | 27.5536 | 28.2399 | 31.402 | 34.0266
Drakelow 132kV | Burton 11kV | Bulk Supply Point | 11 | Hydrogen Evolution | 1.6648 | 1.9283 | 2.2536 | 2.6925 | 3.2519 | 3.9401 | 4.7225 | 5.9018 | 6.8983 | 7.8708 | 8.8526 | 9.7281 | 10.6062 | 11.3972 | 11.9028 | 12.1271 | 13.1671 | 14.1172 | 3.9473 | 4.5041 | 5.1847 | 6.1269 | 7.3458 | 8.8515 | 10.5294 | 13.0342 | 15.1566 | 17.2155 | 19.2762 | 21.081 | 22.8883 | 24.5168 | 25.5737 | 26.0671 | 28.3719 | 30.4796
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Counterfactual | 3.8708 | 4.0161 | 4.1867 | 4.3847 | 4.6104 | 4.8672 | 5.1452 | 5.5498 | 5.899 | 6.24 | 6.579 | 6.9212 | 7.289 | 7.6552 | 8.0151 | 8.3302 | 9.2339 | 9.2274 | 9.4008 | 9.7059 | 10.0606 | 10.4713 | 10.9399 | 11.4727 | 12.0493 | 12.893 | 13.6308 | 14.3541 | 15.0668 | 15.779 | 16.5383 | 17.294 | 18.0363 | 18.6822 | 20.5938 | 20.4298
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Electric Engagement | 3.9861 | 4.2827 | 4.6345 | 5.0848 | 5.5928 | 6.129 | 6.6877 | 7.3769 | 8.0305 | 8.5988 | 8.9569 | 9.2001 | 9.4388 | 9.6484 | 9.8456 | 9.9926 | 10.7166 | 10.7946 | 9.6503 | 10.2789 | 11.015 | 11.9583 | 13.0239 | 14.1461 | 15.3019 | 16.7353 | 18.1054 | 19.3074 | 20.0923 | 20.6427 | 21.1855 | 21.6561 | 22.0981 | 22.4318 | 24.0643 | 24.1403
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Holistic Transition | 3.9438 | 4.1688 | 4.4684 | 4.8024 | 5.1472 | 5.5144 | 5.9247 | 6.505 | 7.0178 | 7.5825 | 8.1495 | 8.7857 | 9.3096 | 9.7936 | 10.1283 | 10.286 | 11.2555 | 11.3502 | 9.5745 | 10.0674 | 10.7119 | 11.4289 | 12.1692 | 12.953 | 13.8376 | 15.0838 | 16.1834 | 17.3965 | 18.6016 | 19.9807 | 21.0831 | 22.0973 | 22.8105 | 23.1615 | 25.3855 | 25.4822
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 3.9063 | 4.0916 | 4.3264 | 4.6161 | 4.9328 | 5.2881 | 5.6799 | 6.2216 | 6.6726 | 7.181 | 7.6873 | 8.1773 | 8.6541 | 9.0873 | 9.377 | 9.4871 | 11.2481 | 11.3596 | 9.4785 | 9.8746 | 10.3716 | 10.9843 | 11.655 | 12.4067 | 13.2294 | 14.3678 | 15.3175 | 16.395 | 17.4574 | 18.4829 | 19.4775 | 20.3777 | 20.9906 | 21.2365 | 25.4965 | 25.6432
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.4957 | 2.586 | 2.6875 | 4.7744 | 4.9714 | 5.2034 | 5.4679 | 5.856 | 6.2122 | 6.5223 | 6.8239 | 7.131 | 7.4532 | 7.7745 | 8.0895 | 8.4103 | 9.3129 | 9.8228 | 6.1267 | 6.3156 | 6.5257 | 11.6916 | 12.1001 | 12.5813 | 13.1301 | 13.9441 | 14.703 | 15.3688 | 16.0079 | 16.6495 | 17.3147 | 17.9781 | 18.628 | 19.2903 | 21.2194 | 22.3638
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.6026 | 3.2087 | 3.7798 | 4.2126 | 4.7161 | 5.2338 | 5.8475 | 6.515 | 7.0858 | 7.5907 | 7.8927 | 8.0819 | 8.2662 | 8.409 | 8.5532 | 8.7014 | 9.3374 | 9.9561 | 6.3577 | 7.7873 | 9.1047 | 10.012 | 11.0705 | 12.1569 | 13.4385 | 14.8355 | 16.0358 | 17.1103 | 17.7823 | 18.2225 | 18.6542 | 18.9833 | 19.3146 | 19.6566 | 21.1011 | 22.5415
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.9555 | 3.4147 | 3.6983 | 4.0335 | 4.3722 | 4.7729 | 5.1794 | 5.6935 | 6.1306 | 6.6404 | 7.1387 | 7.5857 | 8.0324 | 8.4308 | 8.7003 | 8.8479 | 9.5458 | 10.3995 | 7.2685 | 8.3718 | 8.9824 | 9.7027 | 10.4306 | 11.2905 | 12.1753 | 13.2908 | 14.2351 | 15.3412 | 16.4063 | 17.3437 | 18.2845 | 19.1162 | 19.6911 | 20.0235 | 21.6005 | 23.6098
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.5288 | 3.04 | 3.4966 | 3.7606 | 4.0539 | 4.3852 | 4.7458 | 5.2694 | 5.6631 | 6.1439 | 6.6136 | 7.0582 | 7.4863 | 7.8664 | 8.1081 | 8.2181 | 9.853 | 10.5161 | 6.1991 | 7.4314 | 8.5144 | 9.0726 | 9.6935 | 10.395 | 11.152 | 12.2591 | 13.0909 | 14.1198 | 15.1112 | 16.0458 | 16.9412 | 17.7308 | 18.2431 | 18.4922 | 22.453 | 23.9929
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.4184 | 2.4553 | 2.4966 | 2.5437 | 2.607 | 2.6901 | 2.7762 | 2.9123 | 3.0252 | 3.1509 | 3.2728 | 3.3923 | 3.523 | 3.6533 | 3.781 | 3.911 | 2.7455 | 3.0009 | 6.0021 | 6.0801 | 6.1657 | 6.2635 | 6.3948 | 6.5663 | 6.7439 | 7.0289 | 7.2696 | 7.54 | 7.7985 | 8.0476 | 8.3175 | 8.5864 | 8.8497 | 9.1178 | 6.0538 | 6.6198
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.4618 | 2.5504 | 2.6553 | 2.795 | 2.9594 | 3.1253 | 3.3227 | 3.5859 | 3.8407 | 4.0652 | 4.2107 | 4.3076 | 4.4004 | 4.4792 | 4.5602 | 4.6398 | 3.5691 | 3.8968 | 6.0959 | 6.2832 | 6.5009 | 6.7921 | 7.1349 | 7.4767 | 7.8813 | 8.4293 | 8.9652 | 9.4419 | 9.7619 | 9.982 | 10.1925 | 10.3672 | 10.5462 | 10.722 | 7.9224 | 8.6826
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.4459 | 2.5081 | 2.5925 | 2.6888 | 2.7765 | 2.8953 | 3.0548 | 3.2855 | 3.4843 | 3.7085 | 3.9193 | 4.13 | 4.4714 | 4.6602 | 4.7969 | 4.8839 | 3.7471 | 4.0339 | 6.0678 | 6.2053 | 6.3871 | 6.5941 | 6.7815 | 7.0322 | 7.3784 | 7.8784 | 8.3074 | 8.7929 | 9.2385 | 9.6852 | 10.4588 | 10.8553 | 11.1474 | 11.3409 | 8.3786 | 9.0244
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.4317 | 2.4803 | 2.5376 | 2.618 | 2.711 | 2.8209 | 2.9441 | 3.1263 | 3.2916 | 3.4885 | 3.6806 | 3.8638 | 4.0459 | 4.2066 | 4.3138 | 4.3728 | 3.2044 | 3.5379 | 6.0312 | 6.1346 | 6.2547 | 6.4236 | 6.6193 | 6.8487 | 7.104 | 7.486 | 7.8349 | 8.2553 | 8.6598 | 9.0441 | 9.4244 | 9.7576 | 9.9834 | 10.1142 | 7.1083 | 7.8691
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.10768 | 0.15214 | 0.20079 | 0.26861 | 0.33664 | 0.43238 | 0.49258 | 0.5856 | 0.69327 | 0.80578 | 0.91494 | 1.0109 | 1.1129 | 1.2139 | 1.3152 | 1.4142 | 1.7016 | 1.8731 | 0.24203 | 0.33587 | 0.4372 | 0.57795 | 0.7196 | 0.91988 | 1.045 | 1.2363 | 1.462 | 1.6955 | 1.9217 | 2.1184 | 2.3267 | 2.533 | 2.7397 | 2.9418 | 3.5361 | 3.8959
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.13751 | 0.22421 | 0.32629 | 0.48083 | 0.635 | 0.80222 | 0.93739 | 1.1738 | 1.3826 | 1.5235 | 1.6043 | 1.6595 | 1.7053 | 1.7513 | 1.7978 | 1.8356 | 2.0125 | 2.1626 | 0.3061 | 0.49119 | 0.70469 | 1.0376 | 1.3658 | 1.7183 | 1.9954 | 2.4884 | 2.9246 | 3.2161 | 3.3874 | 3.5069 | 3.6074 | 3.7078 | 3.8091 | 3.8927 | 4.2878 | 4.6241
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.12629 | 0.19448 | 0.28858 | 0.39652 | 0.49891 | 0.62688 | 0.71317 | 0.90464 | 1.0719 | 1.2035 | 1.3427 | 1.4742 | 1.6053 | 1.7288 | 1.8206 | 1.8727 | 2.0978 | 2.2871 | 0.28596 | 0.43696 | 0.64653 | 0.88069 | 1.1005 | 1.3753 | 1.5561 | 1.9606 | 2.3146 | 2.5894 | 2.8791 | 3.1531 | 3.4264 | 3.6841 | 3.8781 | 3.9927 | 4.4923 | 4.9148
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.11774 | 0.17436 | 0.24226 | 0.36023 | 0.4729 | 0.60082 | 0.68601 | 0.8794 | 1.0456 | 1.1807 | 1.3166 | 1.4518 | 1.5851 | 1.7033 | 1.788 | 1.8337 | 2.0047 | 2.1628 | 0.26367 | 0.38509 | 0.5282 | 0.78536 | 1.0285 | 1.3016 | 1.4767 | 1.8816 | 2.2305 | 2.5084 | 2.7875 | 3.0652 | 3.339 | 3.5821 | 3.7582 | 3.8559 | 4.229 | 4.5726
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.14094 | 0.15984 | 0.1785 | 0.20274 | 0.24273 | 0.29429 | 0.33793 | 0.42143 | 0.49406 | 0.5815 | 0.66463 | 0.74573 | 0.83627 | 0.91716 | 0.99578 | 1.0757 | 1.3672 | 1.5833 | 0.32525 | 0.36491 | 0.40363 | 0.45382 | 0.53679 | 0.64385 | 0.73305 | 0.90771 | 1.0629 | 1.251 | 1.4274 | 1.5965 | 1.7829 | 1.9489 | 2.1102 | 2.2744 | 2.8907 | 3.3571
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.15956 | 0.20225 | 0.25147 | 0.33614 | 0.4443 | 0.53824 | 0.64713 | 0.80078 | 0.96035 | 1.0997 | 1.1903 | 1.2571 | 1.3159 | 1.3617 | 1.4034 | 1.4466 | 1.6588 | 1.8595 | 0.36545 | 0.45541 | 0.55733 | 0.73392 | 0.95876 | 1.1508 | 1.3725 | 1.6928 | 2.0311 | 2.3298 | 2.5295 | 2.68 | 2.8147 | 2.9171 | 3.0114 | 3.1095 | 3.5994 | 4.0725
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.15259 | 0.18298 | 0.23308 | 0.29105 | 0.33013 | 0.3886 | 0.49629 | 0.65088 | 0.77219 | 0.90349 | 1.0285 | 1.1567 | 1.2761 | 1.3801 | 1.4569 | 1.5062 | 1.7364 | 1.8706 | 0.35299 | 0.41974 | 0.52757 | 0.65192 | 0.73492 | 0.85678 | 1.0905 | 1.4275 | 1.6901 | 1.9765 | 2.2444 | 2.5186 | 2.7738 | 2.9928 | 3.1573 | 3.2674 | 3.7899 | 4.0958
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.14677 | 0.17138 | 0.19978 | 0.25415 | 0.32864 | 0.39381 | 0.47139 | 0.59575 | 0.71173 | 0.85113 | 0.98251 | 1.112 | 1.2254 | 1.3248 | 1.3997 | 1.4491 | 1.6757 | 1.854 | 0.33791 | 0.39004 | 0.44923 | 0.56407 | 0.72043 | 0.85372 | 1.0116 | 1.2705 | 1.5148 | 1.8121 | 2.0885 | 2.3595 | 2.5951 | 2.7997 | 2.9551 | 3.0606 | 3.5659 | 3.9824
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Counterfactual | 3.5655 | 3.6412 | 3.7356 | 3.848 | 4.2997 | 4.6195 | 4.9797 | 5.5221 | 5.8522 | 6.7571 | 7.0989 | 7.406 | 7.7136 | 7.8851 | 8.0524 | 8.2215 | 8.652 | 8.8486 | 8.7423 | 8.9013 | 9.098 | 9.3312 | 10.4084 | 11.0907 | 11.8538 | 12.9988 | 13.7177 | 15.9129 | 16.6999 | 17.3991 | 18.0901 | 18.4412 | 18.7835 | 19.1289 | 20.0166 | 20.4333
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 3.6275 | 3.7873 | 3.9973 | 4.2728 | 4.7033 | 5.6558 | 6.5661 | 7.7104 | 8.5401 | 9.1777 | 9.5882 | 9.9116 | 10.2283 | 10.3101 | 10.3915 | 10.4701 | 10.7449 | 10.9295 | 8.8769 | 9.2155 | 9.6569 | 10.2469 | 11.2137 | 13.4133 | 15.4802 | 18.0575 | 19.9509 | 21.4317 | 22.4024 | 23.1852 | 23.9551 | 24.1383 | 24.3188 | 24.4955 | 25.0904 | 25.518
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 3.6053 | 3.7262 | 3.9291 | 4.167 | 4.7835 | 5.5609 | 6.3973 | 7.4727 | 8.2107 | 8.7787 | 9.2675 | 9.7179 | 9.9548 | 10.1726 | 10.3196 | 10.3876 | 10.8855 | 11.0884 | 8.8372 | 9.1017 | 9.5558 | 10.0875 | 11.5595 | 13.3607 | 15.2952 | 17.7486 | 19.4607 | 20.7824 | 21.8985 | 22.9181 | 23.4061 | 23.8525 | 24.1583 | 24.3055 | 25.4545 | 25.9208
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 3.5862 | 3.6834 | 3.8112 | 3.9908 | 4.2288 | 4.891 | 5.7296 | 6.7831 | 7.5154 | 8.1382 | 8.6359 | 9.093 | 9.5436 | 9.9668 | 10.0994 | 10.1584 | 11.8999 | 12.1486 | 8.788 | 8.9954 | 9.2652 | 9.6543 | 10.1831 | 11.703 | 13.6368 | 16.0284 | 17.7199 | 19.1714 | 20.3079 | 21.3482 | 22.373 | 23.3389 | 23.6146 | 23.7441 | 28.0316 | 28.6047
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.77195 | 0.8635 | 0.975 | 1.0944 | 1.2542 | 1.4463 | 1.6545 | 1.9491 | 2.2042 | 2.4894 | 2.7862 | 3.0974 | 3.3676 | 3.6368 | 3.9008 | 4.1654 | 4.9663 | 5.3937 | 1.81 | 2.0026 | 2.2344 | 2.4821 | 2.8138 | 3.2123 | 3.6439 | 4.2561 | 4.7923 | 5.3945 | 6.0182 | 6.6683 | 7.2254 | 7.7801 | 8.3239 | 8.8685 | 10.5543 | 11.4796
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.8539 | 1.0456 | 1.2838 | 1.5504 | 1.8857 | 2.2733 | 2.717 | 3.2625 | 3.8239 | 4.3317 | 4.6879 | 4.9655 | 5.1615 | 5.3027 | 5.4458 | 5.6099 | 6.4394 | 6.9511 | 1.9878 | 2.3944 | 2.8923 | 3.4477 | 4.1492 | 4.9595 | 5.8807 | 7.0165 | 8.1963 | 9.2711 | 10.0434 | 10.6571 | 11.093 | 11.4041 | 11.7184 | 12.0746 | 13.9168 | 15.0853
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.82437 | 0.96689 | 1.1323 | 1.3134 | 1.5532 | 1.8586 | 2.2561 | 2.7549 | 3.205 | 3.6961 | 4.1933 | 4.8053 | 5.1803 | 5.5244 | 5.772 | 5.9466 | 6.7252 | 7.232 | 1.9352 | 2.2492 | 2.6051 | 2.9938 | 3.5088 | 4.1613 | 5.0181 | 6.0862 | 7.0495 | 8.1007 | 9.1565 | 10.5139 | 11.3032 | 12.0239 | 12.5508 | 12.9312 | 14.6447 | 15.781
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.79859 | 0.91709 | 1.0683 | 1.2347 | 1.4547 | 1.7225 | 2.0291 | 2.4387 | 2.8302 | 3.2704 | 3.7144 | 4.1541 | 4.515 | 4.8429 | 5.0697 | 5.2108 | 5.9243 | 6.427 | 1.8689 | 2.1223 | 2.4423 | 2.7923 | 3.2581 | 3.8242 | 4.469 | 5.3285 | 6.155 | 7.0874 | 8.0215 | 8.9464 | 9.6969 | 10.3774 | 10.8549 | 11.161 | 12.7552 | 13.8796
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Counterfactual | 0.65959 | 0.73775 | 0.81679 | 0.9008 | 1.0335 | 1.1975 | 1.373 | 1.6118 | 1.8046 | 2.0017 | 2.2064 | 2.4017 | 2.6045 | 2.8062 | 2.9952 | 3.1903 | 3.7523 | 4.0683 | 1.5804 | 1.7447 | 1.9087 | 2.0826 | 2.3578 | 2.6977 | 3.0614 | 3.555 | 3.9571 | 4.3694 | 4.7953 | 5.198 | 5.6127 | 6.0245 | 6.4094 | 6.807 | 7.9826 | 8.6672
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Electric Engagement | 0.7327 | 0.90136 | 1.0884 | 1.3805 | 1.7214 | 2.0318 | 2.4024 | 2.8376 | 3.2258 | 3.5538 | 3.7268 | 3.8282 | 3.9287 | 4.0196 | 4.1124 | 4.2097 | 4.808 | 5.198 | 1.7389 | 2.095 | 2.4834 | 3.096 | 3.8127 | 4.4582 | 5.2257 | 6.1256 | 6.9304 | 7.6146 | 7.9853 | 8.2114 | 8.4365 | 8.6376 | 8.8422 | 9.0578 | 10.4068 | 11.2978
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Holistic Transition | 0.70594 | 0.82875 | 1.0326 | 1.2573 | 1.4427 | 1.6733 | 1.9514 | 2.2835 | 2.5568 | 2.8512 | 3.1566 | 3.6181 | 3.9155 | 4.1893 | 4.3773 | 4.4921 | 5.0546 | 5.4501 | 1.6911 | 1.96 | 2.3992 | 2.8821 | 3.279 | 3.7703 | 4.3657 | 5.068 | 5.6445 | 6.2652 | 6.9042 | 7.9345 | 8.5565 | 9.1269 | 9.5254 | 9.7797 | 11.0312 | 11.9227
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Hydrogen Evolution | 0.68323 | 0.78682 | 0.89688 | 1.0739 | 1.2729 | 1.4928 | 1.7268 | 2.0343 | 2.3037 | 2.6017 | 2.8875 | 3.156 | 3.4167 | 3.6488 | 3.789 | 3.8584 | 4.3241 | 4.6926 | 1.6324 | 1.8529 | 2.0835 | 2.4577 | 2.8793 | 3.343 | 3.8322 | 4.4713 | 5.0328 | 5.6558 | 6.2471 | 6.8002 | 7.3356 | 7.8101 | 8.1004 | 8.2521 | 9.3072 | 10.1324
East Claydon 132kV | Banbury 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 6.7298 | 6.9346 | 7.1664 | 7.4451 | 7.7341 | 8.1932 | 8.589 | 9.2887 | 9.8192 | 10.6332 | 11.3771 | 12.1039 | 12.8759 | 13.5847 | 14.2038 | 14.8284 | 17.5347 | 18.4586 | 16.3898 | 16.8204 | 17.3027 | 17.8824 | 18.4822 | 19.4886 | 20.3113 | 21.7748 | 22.8825 | 24.6842 | 26.3011 | 27.8602 | 29.5 | 30.9829 | 32.2487 | 33.5249 | 39.0359 | 40.9954
East Claydon 132kV | Banbury 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 6.929 | 7.4367 | 8.1558 | 8.853 | 9.6047 | 10.5533 | 11.9483 | 13.6178 | 15.0017 | 16.2187 | 17.2062 | 18.0567 | 18.6312 | 17.846 | 18.069 | 18.2766 | 19.2413 | 20.0648 | 16.8229 | 17.8904 | 19.447 | 20.9035 | 22.4655 | 24.482 | 27.5332 | 31.1507 | 34.1222 | 36.7676 | 38.8885 | 40.6744 | 41.9053 | 39.827 | 40.323 | 40.787 | 42.9919 | 44.8842
East Claydon 132kV | Banbury 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 6.8697 | 7.3313 | 7.694 | 8.1353 | 8.6824 | 9.6733 | 10.8032 | 12.1183 | 13.0582 | 14.0584 | 14.9283 | 15.8633 | 15.5502 | 16.3444 | 17.0937 | 17.7555 | 19.564 | 20.4383 | 16.7212 | 17.7758 | 18.5542 | 19.5027 | 20.7041 | 22.9702 | 25.5398 | 28.4406 | 30.4634 | 32.6124 | 34.4108 | 36.3807 | 35.2398 | 36.8928 | 38.4543 | 39.8404 | 43.7532 | 45.7504
East Claydon 132kV | Banbury 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 6.8066 | 7.0747 | 7.3934 | 7.7842 | 8.3291 | 8.8376 | 9.7954 | 11.0943 | 12.1366 | 13.2888 | 14.3127 | 15.2795 | 16.1362 | 16.9159 | 19.5018 | 20.1188 | 21.6836 | 22.4798 | 16.5559 | 17.1241 | 17.7906 | 18.6096 | 19.8006 | 20.8656 | 23.002 | 25.8558 | 28.1302 | 30.6491 | 32.8276 | 34.8724 | 36.6529 | 38.2704 | 44.4275 | 45.702 | 49.0639 | 50.869
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Counterfactual | 3.0493 | 3.1579 | 3.2973 | 3.4438 | 3.6057 | 3.7868 | 3.9779 | 4.2822 | 4.5228 | 4.7808 | 5.0528 | 5.3321 | 5.6459 | 5.9572 | 6.2608 | 6.5695 | 7.3444 | 7.664 | 7.2788 | 7.5055 | 7.7935 | 8.096 | 8.43 | 8.8029 | 9.1946 | 9.8135 | 10.3053 | 10.8323 | 11.3874 | 11.955 | 12.5909 | 13.2213 | 13.8356 | 14.4598 | 16.0527 | 16.7292
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Electric Engagement | 3.168 | 3.4166 | 3.7372 | 4.0829 | 4.4751 | 4.8887 | 5.3852 | 5.9928 | 6.5433 | 6.9851 | 7.2105 | 7.3245 | 7.4268 | 7.5243 | 7.6271 | 7.7117 | 8.2013 | 8.613 | 7.5351 | 8.0564 | 8.7201 | 9.435 | 10.2446 | 11.0956 | 12.1108 | 13.3489 | 14.4725 | 15.3766 | 15.8476 | 16.0936 | 16.3169 | 16.5285 | 16.7502 | 16.9345 | 18.0093 | 18.9168
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Holistic Transition | 3.124 | 3.2957 | 3.5061 | 3.7273 | 3.9752 | 4.2501 | 4.5618 | 4.9937 | 5.3659 | 5.7766 | 6.2315 | 6.668 | 7.0938 | 7.4939 | 7.7582 | 7.877 | 8.2065 | 8.6735 | 7.4568 | 7.8315 | 8.2809 | 8.7535 | 9.2808 | 9.8604 | 10.5119 | 11.4029 | 12.172 | 13.0202 | 13.9549 | 14.8527 | 15.7282 | 16.5514 | 17.1018 | 17.3607 | 18.0114 | 19.0485
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 3.0858 | 3.2286 | 3.4249 | 3.6292 | 3.8631 | 4.1177 | 4.4149 | 4.8412 | 5.2098 | 5.61 | 6.0386 | 6.4579 | 6.8717 | 7.2452 | 7.4707 | 7.5464 | 8.6433 | 8.9856 | 7.3581 | 7.6597 | 8.0681 | 8.4944 | 8.9813 | 9.5081 | 10.1185 | 10.9879 | 11.7402 | 12.5548 | 13.426 | 14.2785 | 15.1186 | 15.8773 | 16.3392 | 16.5004 | 19.1098 | 19.8538
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Counterfactual | 1.5514 | 1.5833 | 1.6195 | 1.6537 | 1.6925 | 1.7403 | 1.7932 | 1.8852 | 1.9627 | 2.0477 | 2.1315 | 2.2151 | 2.3057 | 2.3964 | 2.4852 | 2.5758 | 2.846 | 3.0044 | 3.4901 | 3.5567 | 3.6318 | 3.7025 | 3.7824 | 3.8803 | 3.9886 | 4.1793 | 4.3426 | 4.5229 | 4.6983 | 4.8712 | 5.0568 | 5.2424 | 5.4238 | 5.6091 | 6.1781 | 6.5243
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Electric Engagement | 1.5839 | 1.6533 | 1.7396 | 1.829 | 1.9306 | 2.0526 | 2.1958 | 2.3842 | 2.5619 | 2.7147 | 2.8079 | 2.8634 | 2.9151 | 2.9586 | 3.0021 | 3.1254 | 3.4419 | 3.6276 | 3.5604 | 3.7061 | 3.8853 | 4.0695 | 4.2786 | 4.5287 | 4.821 | 5.2106 | 5.5809 | 5.902 | 6.1041 | 6.2291 | 6.3467 | 6.4435 | 6.5401 | 6.8366 | 7.5682 | 8.0011
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Holistic Transition | 1.5721 | 1.6203 | 1.6797 | 1.7343 | 1.7958 | 1.8741 | 1.9792 | 2.1319 | 2.2617 | 2.4062 | 2.7112 | 2.8582 | 3.0005 | 3.2949 | 3.382 | 3.4287 | 3.6673 | 3.8139 | 3.5394 | 3.6446 | 3.7714 | 3.8877 | 4.018 | 4.1821 | 4.4076 | 4.7344 | 5.0111 | 5.3199 | 6.0249 | 6.3345 | 6.6337 | 7.3162 | 7.5008 | 7.6046 | 8.1396 | 8.4725
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Hydrogen Evolution | 1.562 | 1.6035 | 1.6574 | 1.7072 | 1.7644 | 1.8356 | 1.919 | 2.0481 | 2.1643 | 2.2978 | 2.4311 | 2.5601 | 2.6841 | 2.7958 | 2.866 | 2.979 | 3.2363 | 3.4044 | 3.5132 | 3.6012 | 3.7137 | 3.8174 | 3.9359 | 4.083 | 4.2541 | 4.5216 | 4.7642 | 5.0456 | 5.3228 | 5.5904 | 5.8465 | 6.0758 | 6.222 | 6.4939 | 7.0942 | 7.4802
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.35859 | 0.41903 | 0.48798 | 0.57281 | 0.64842 | 0.72057 | 0.72977 | 0.87101 | 0.99378 | 1.1302 | 1.2641 | 1.393 | 1.5322 | 1.6694 | 1.8029 | 1.9409 | 2.3565 | 2.6075 | 0.84709 | 0.97479 | 1.1187 | 1.295 | 1.4517 | 1.5999 | 1.5869 | 1.8818 | 2.143 | 2.4352 | 2.7179 | 2.9858 | 3.2716 | 3.5534 | 3.8275 | 4.1106 | 4.9911 | 5.5397
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.40331 | 0.52736 | 0.67385 | 0.84466 | 1.0127 | 1.1866 | 1.3253 | 1.6044 | 1.8744 | 2.1077 | 2.2606 | 2.3636 | 2.4579 | 2.5341 | 2.6146 | 2.6897 | 3.0777 | 3.3427 | 0.94364 | 1.2096 | 1.5162 | 1.8729 | 2.2216 | 2.5783 | 2.8297 | 3.4105 | 3.9778 | 4.4727 | 4.8083 | 5.0401 | 5.2548 | 5.4246 | 5.6026 | 5.7707 | 6.6464 | 7.2764
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.38687 | 0.48399 | 0.59116 | 0.71362 | 0.82625 | 0.94701 | 1.042 | 1.2839 | 1.4862 | 1.7135 | 1.9375 | 2.1523 | 2.3606 | 2.5439 | 2.6816 | 2.763 | 3.147 | 3.3472 | 0.91428 | 1.1304 | 1.3606 | 1.6234 | 1.864 | 2.1173 | 2.2989 | 2.822 | 3.2578 | 3.7488 | 4.2256 | 4.6829 | 5.1255 | 5.5103 | 5.8032 | 5.9838 | 6.8458 | 7.299
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.37346 | 0.45467 | 0.55404 | 0.6722 | 0.78136 | 0.89036 | 0.94791 | 1.1511 | 1.3348 | 1.5536 | 1.7649 | 1.9624 | 2.1586 | 2.3241 | 2.442 | 2.4998 | 2.7917 | 3.0605 | 0.8794 | 1.0552 | 1.2651 | 1.5138 | 1.742 | 1.9665 | 2.0527 | 2.4758 | 2.8615 | 3.3261 | 3.769 | 4.1814 | 4.5889 | 4.9304 | 5.1763 | 5.303 | 5.961 | 6.5773
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.41995 | 0.5111 | 0.63293 | 0.77511 | 0.90435 | 1.0303 | 1.2309 | 1.4815 | 1.7125 | 1.9638 | 2.2157 | 2.4582 | 2.7172 | 2.9759 | 3.2242 | 3.4667 | 4.1946 | 4.6252 | 0.9368 | 1.1287 | 1.3822 | 1.6772 | 1.9449 | 2.2047 | 2.6213 | 3.1512 | 3.6533 | 4.2015 | 4.7415 | 5.2508 | 5.7879 | 6.3243 | 6.8388 | 7.3402 | 8.9075 | 9.8778
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.49854 | 0.68844 | 0.94818 | 1.2457 | 1.5768 | 1.9073 | 2.2832 | 2.7784 | 3.2705 | 3.7161 | 4.0177 | 4.213 | 4.3941 | 4.5335 | 4.6759 | 4.8161 | 5.5393 | 6.1241 | 1.1065 | 1.5089 | 2.0528 | 2.6773 | 3.3752 | 4.064 | 4.8396 | 5.8809 | 6.9297 | 7.8909 | 8.565 | 9.0157 | 9.4374 | 9.7551 | 10.0777 | 10.3978 | 12.0573 | 13.4546
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.4694 | 0.60959 | 0.80475 | 1.0417 | 1.2601 | 1.4901 | 1.806 | 2.2827 | 2.6854 | 3.1019 | 3.511 | 3.9019 | 4.2814 | 4.6093 | 4.8478 | 4.9905 | 5.6934 | 6.0805 | 1.0546 | 1.3631 | 1.7857 | 2.2994 | 2.7701 | 3.2597 | 3.9552 | 5.0047 | 5.8869 | 6.8009 | 7.6831 | 8.5261 | 9.3424 | 10.0371 | 10.5519 | 10.875 | 12.4805 | 13.368
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.4443 | 0.56147 | 0.73339 | 0.95223 | 1.1696 | 1.3862 | 1.6101 | 1.9709 | 2.3163 | 2.7438 | 3.1213 | 3.4753 | 3.8187 | 4.1136 | 4.3133 | 4.4167 | 4.9826 | 5.5316 | 0.9899 | 1.2403 | 1.6039 | 2.0692 | 2.5334 | 2.9909 | 3.4564 | 4.2202 | 4.9596 | 5.8868 | 6.6895 | 7.4385 | 8.16 | 8.7736 | 9.196 | 9.4282 | 10.729 | 12.0139
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.92119 | 0.9785 | 1.0513 | 1.1435 | 1.2428 | 1.3448 | 1.4647 | 1.6069 | 1.6589 | 1.7149 | 1.7729 | 1.8714 | 1.9935 | 2.1174 | 2.2207 | 2.2892 | 2.4469 | 2.5013 | 1.9132 | 2.0333 | 2.1851 | 2.3769 | 2.5839 | 2.797 | 3.0476 | 3.3442 | 3.4512 | 3.5664 | 3.6855 | 3.89 | 4.1441 | 4.4017 | 4.6157 | 4.7543 | 5.0811 | 5.2004
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.94865 | 1.0629 | 1.1975 | 1.3513 | 1.5302 | 1.697 | 1.8863 | 2.0897 | 2.2556 | 2.4262 | 2.5414 | 2.5782 | 2.5938 | 2.6075 | 2.624 | 2.6363 | 2.7144 | 2.7887 | 1.9725 | 2.2161 | 2.5012 | 2.8265 | 3.2066 | 3.5606 | 3.9595 | 4.3856 | 4.7315 | 5.0915 | 5.3419 | 5.4241 | 5.4605 | 5.4922 | 5.5294 | 5.558 | 5.7376 | 5.909
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.93846 | 1.0345 | 1.1446 | 1.2811 | 1.4548 | 1.6378 | 1.8597 | 2.0558 | 2.1388 | 2.2338 | 2.33 | 2.4258 | 2.5214 | 2.6072 | 2.6578 | 2.6776 | 2.7735 | 2.8524 | 1.9544 | 2.1629 | 2.4004 | 2.6942 | 3.0702 | 3.4676 | 3.9489 | 4.3688 | 4.5415 | 4.7391 | 4.9383 | 5.1364 | 5.3337 | 5.5109 | 5.6172 | 5.6618 | 5.8816 | 6.0631
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.92933 | 1.0198 | 1.1247 | 1.2527 | 1.3916 | 1.5178 | 1.6784 | 1.8759 | 2.0202 | 2.1724 | 2.269 | 2.3573 | 2.4426 | 2.5211 | 2.5659 | 2.5754 | 2.6391 | 2.6982 | 1.9309 | 2.1253 | 2.3497 | 2.6232 | 2.9217 | 3.1928 | 3.5369 | 3.9572 | 4.2625 | 4.585 | 4.783 | 4.9633 | 5.1372 | 5.2969 | 5.3891 | 5.4107 | 5.5549 | 5.6893
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.3205 | 2.407 | 2.4641 | 2.5269 | 2.5978 | 2.6771 | 2.767 | 2.9131 | 3.0291 | 3.1535 | 3.2842 | 3.4408 | 3.6244 | 3.8108 | 3.9817 | 4.1294 | 4.5053 | 4.6587 | 5.6446 | 5.8243 | 5.9426 | 6.0723 | 6.2186 | 6.3815 | 6.566 | 6.8636 | 7.1015 | 7.3566 | 7.624 | 7.9453 | 8.3219 | 8.7037 | 9.053 | 9.3521 | 10.1275 | 10.4552
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.3783 | 2.5365 | 2.6804 | 2.8409 | 3.0224 | 3.2181 | 3.456 | 3.7593 | 4.0487 | 4.3039 | 4.4538 | 4.5165 | 4.5603 | 4.6033 | 4.643 | 4.6795 | 4.8849 | 3.2157 | 5.7692 | 6.1014 | 6.3992 | 6.7304 | 7.1043 | 7.5064 | 7.9929 | 8.6126 | 9.2078 | 9.7369 | 10.0565 | 10.1933 | 10.2905 | 10.3848 | 10.4722 | 10.5526 | 11.0097 | 6.7853
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.357 | 2.4779 | 2.5691 | 2.6748 | 2.8344 | 3.011 | 3.1804 | 3.3934 | 3.5723 | 3.7698 | 3.9807 | 4.1852 | 4.3879 | 4.5743 | 4.6959 | 2.8788 | 3.1412 | 3.353 | 5.7314 | 5.9925 | 6.1878 | 6.414 | 6.7557 | 7.1327 | 7.4899 | 7.9309 | 8.3014 | 8.7103 | 9.1441 | 9.5654 | 9.9829 | 10.3668 | 10.6208 | 6.0624 | 6.648 | 7.1238
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.3382 | 2.444 | 2.5242 | 2.6136 | 2.7151 | 2.8312 | 2.9865 | 3.2244 | 3.4413 | 3.6756 | 3.8848 | 4.087 | 4.2808 | 4.4604 | 4.5624 | 4.5996 | 4.7903 | 4.9569 | 5.683 | 5.9061 | 6.0731 | 6.2591 | 6.4699 | 6.7101 | 7.0314 | 7.5228 | 7.9723 | 8.4569 | 8.8832 | 9.2944 | 9.6884 | 10.0531 | 10.2622 | 10.3414 | 10.7624 | 11.1282
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.09489 | 0.10571 | 0.11707 | 0.12675 | 0.13789 | 0.15317 | 0.16718 | 0.19225 | 0.21293 | 0.23212 | 0.25534 | 0.27922 | 0.30291 | 0.32921 | 0.3548 | 0.37809 | 0.45351 | 0.4963 | 0.19447 | 0.21693 | 0.24024 | 0.26025 | 0.28314 | 0.31433 | 0.34306 | 0.39397 | 0.43615 | 0.47541 | 0.52271 | 0.57106 | 0.61902 | 0.67214 | 0.72387 | 0.77094 | 0.92532 | 1.014
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.10298 | 0.12374 | 0.14505 | 0.16896 | 0.19601 | 0.22851 | 0.26449 | 0.3085 | 0.34802 | 0.38083 | 0.40208 | 0.41297 | 0.42214 | 0.43364 | 0.44242 | 0.4493 | 0.48945 | 0.5241 | 0.21176 | 0.25516 | 0.29919 | 0.34851 | 0.4041 | 0.47062 | 0.5442 | 0.63383 | 0.71449 | 0.78175 | 0.82586 | 0.84903 | 0.86882 | 0.89311 | 0.91193 | 0.92694 | 1.0154 | 1.0919
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.099955 | 0.11567 | 0.12978 | 0.14793 | 0.16517 | 0.18863 | 0.21211 | 0.24794 | 0.27947 | 0.3108 | 0.34631 | 0.382 | 0.41664 | 0.44924 | 0.47034 | 0.48375 | 0.53458 | 0.58003 | 0.20624 | 0.2402 | 0.27027 | 0.30843 | 0.34487 | 0.39373 | 0.44274 | 0.5164 | 0.58139 | 0.64613 | 0.71904 | 0.7923 | 0.86344 | 0.93037 | 0.97428 | 1.0027 | 1.1136 | 1.2124
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.097955 | 0.11132 | 0.12683 | 0.14149 | 0.1583 | 0.18053 | 0.20357 | 0.23997 | 0.27138 | 0.30255 | 0.33781 | 0.37257 | 0.40649 | 0.43387 | 0.45541 | 0.46655 | 0.50573 | 0.54804 | 0.20098 | 0.2289 | 0.26088 | 0.2912 | 0.32589 | 0.37145 | 0.4187 | 0.49276 | 0.55664 | 0.62005 | 0.69162 | 0.76224 | 0.83103 | 0.88664 | 0.93053 | 0.95364 | 1.0376 | 1.1273
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.54314 | 0.65897 | 0.6595 | 0.66054 | 0.66176 | 1.0386 | 1.0402 | 1.043 | 1.0454 | 1.048 | 1.0507 | 1.0535 | 1.0567 | 1.0597 | 1.0626 | 1.0657 | 1.0788 | 1.091 | 1.357 | 1.5887 | 1.5898 | 1.5919 | 1.5944 | 2.3481 | 2.3514 | 2.357 | 2.362 | 2.3675 | 2.3729 | 2.3787 | 2.3851 | 2.3912 | 2.397 | 2.4033 | 2.43 | 2.4548
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.65897 | 0.66016 | 0.66225 | 0.66457 | 0.6673 | 1.0458 | 1.0497 | 1.0547 | 1.0592 | 1.0633 | 1.067 | 1.0703 | 1.0729 | 1.0753 | 1.0779 | 1.08 | 0.63455 | 0.63991 | 1.5887 | 1.5913 | 1.5955 | 1.6002 | 1.6058 | 2.3628 | 2.3709 | 2.3809 | 2.3903 | 2.3987 | 2.4063 | 2.4132 | 2.4187 | 2.4238 | 2.4292 | 2.4335 | 1.3171 | 1.3289
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.65891 | 0.65971 | 0.66094 | 0.66252 | 0.66433 | 1.0421 | 1.045 | 1.0493 | 1.0528 | 1.0567 | 1.0606 | 1.0643 | 1.0678 | 1.0711 | 1.0746 | 1.0775 | 0.63422 | 0.63857 | 1.5886 | 1.5905 | 1.5931 | 1.5963 | 1.6001 | 2.3558 | 2.3618 | 2.3708 | 2.3782 | 2.3863 | 2.3941 | 2.4019 | 2.409 | 2.4159 | 2.423 | 2.429 | 1.3168 | 1.3261
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.65879 | 0.65932 | 0.66077 | 0.66291 | 0.66529 | 1.0434 | 1.0469 | 1.052 | 1.0565 | 1.0616 | 1.0666 | 1.0711 | 1.0758 | 1.0797 | 1.0836 | 1.0864 | 0.64182 | 0.64654 | 1.5883 | 1.5895 | 1.5924 | 1.5967 | 1.6015 | 2.3578 | 2.3647 | 2.3752 | 2.3844 | 2.3949 | 2.4049 | 2.4142 | 2.4238 | 2.4316 | 2.4396 | 2.4451 | 1.3301 | 1.3404
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.591 | 1.6423 | 1.7015 | 1.7627 | 1.8348 | 1.9157 | 2.008 | 2.1624 | 2.2903 | 2.4287 | 2.5737 | 2.729 | 2.9038 | 3.0791 | 3.2499 | 3.404 | 3.7783 | 3.9327 | 3.6884 | 3.7936 | 3.9145 | 4.0393 | 4.1862 | 4.3507 | 4.5382 | 4.8529 | 5.1159 | 5.4013 | 5.6983 | 6.0137 | 6.3672 | 6.7213 | 7.0661 | 7.3774 | 8.1454 | 8.4848
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.6537 | 1.778 | 1.9317 | 2.0999 | 2.2932 | 2.5023 | 2.7596 | 3.0873 | 3.3961 | 3.6584 | 3.8053 | 3.8754 | 3.9399 | 3.9965 | 4.0567 | 4.0951 | 4.3249 | 4.5342 | 3.8241 | 4.0839 | 4.4017 | 4.7489 | 5.1469 | 5.5765 | 6.1024 | 6.7743 | 7.4087 | 7.9511 | 8.263 | 8.4167 | 8.5582 | 8.6805 | 8.8099 | 8.894 | 9.4059 | 9.8802
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.6307 | 1.7146 | 1.8093 | 1.9167 | 2.0439 | 2.2156 | 2.3957 | 2.6306 | 2.8322 | 3.0576 | 3.2932 | 3.531 | 3.7622 | 3.9831 | 4.1277 | 4.1815 | 3.6804 | 3.8969 | 3.7833 | 3.9657 | 4.1687 | 4.3979 | 4.669 | 5.0344 | 5.4145 | 5.9038 | 6.3231 | 6.7918 | 7.2762 | 7.7658 | 8.2424 | 8.6965 | 8.9976 | 9.1167 | 7.7891 | 8.2806
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.6099 | 1.6792 | 1.7649 | 1.8587 | 1.9624 | 2.0873 | 2.2446 | 2.4823 | 2.6972 | 2.9316 | 3.1587 | 3.3828 | 3.6032 | 3.8045 | 3.9271 | 3.9611 | 4.2043 | 4.3931 | 3.7296 | 3.8755 | 4.054 | 4.2494 | 4.4648 | 4.7231 | 5.0477 | 5.5384 | 5.982 | 6.4663 | 6.9308 | 7.388 | 7.8367 | 8.2452 | 8.4961 | 8.5683 | 9.1191 | 9.5462
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.15748 | 0.17295 | 0.19098 | 0.21127 | 0.23376 | 0.26557 | 0.29976 | 0.36342 | 0.42373 | 0.49264 | 0.5568 | 0.60973 | 0.66367 | 0.71726 | 0.76954 | 0.82336 | 1.0213 | 1.1648 | 0.34913 | 0.38181 | 0.4193 | 0.46147 | 0.50803 | 0.57337 | 0.6436 | 0.78006 | 0.91259 | 1.066 | 1.2058 | 1.3186 | 1.4312 | 1.5433 | 1.6525 | 1.7649 | 2.1966 | 2.5197
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.1736 | 0.20986 | 0.25389 | 0.3036 | 0.35936 | 0.43129 | 0.51742 | 0.64223 | 0.77117 | 0.89049 | 0.97825 | 1.0409 | 1.1048 | 1.1535 | 1.204 | 1.255 | 1.5398 | 1.7343 | 0.3839 | 0.46087 | 0.55259 | 0.65583 | 0.77141 | 0.91951 | 1.0961 | 1.3615 | 1.6395 | 1.8995 | 2.0964 | 2.2395 | 2.3865 | 2.4953 | 2.6077 | 2.7218 | 3.3595 | 3.8236
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.16758 | 0.19422 | 0.22387 | 0.25703 | 0.29381 | 0.34794 | 0.43358 | 0.5594 | 0.66524 | 0.78706 | 0.89666 | 1.001 | 1.1018 | 1.1857 | 1.2519 | 1.2976 | 1.5483 | 1.665 | 0.3731 | 0.43209 | 0.49592 | 0.56706 | 0.64566 | 0.75918 | 0.94933 | 1.2307 | 1.4653 | 1.7363 | 1.9757 | 2.2034 | 2.4228 | 2.6016 | 2.7446 | 2.8467 | 3.4085 | 3.6717
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.16247 | 0.18363 | 0.2093 | 0.2402 | 0.27443 | 0.32098 | 0.37343 | 0.46218 | 0.54751 | 0.65527 | 0.74953 | 0.83477 | 0.91891 | 0.98742 | 1.039 | 1.0706 | 1.2684 | 1.461 | 0.35996 | 0.40521 | 0.45919 | 0.52393 | 0.5955 | 0.69197 | 0.80024 | 0.99025 | 1.1749 | 1.412 | 1.6155 | 1.7978 | 1.9766 | 2.1202 | 2.2299 | 2.3001 | 2.7505 | 3.1986
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.55265 | 0.61857 | 0.6876 | 0.76526 | 0.85491 | 0.95658 | 1.0754 | 1.2662 | 1.4194 | 1.5902 | 1.7719 | 1.9606 | 2.1755 | 2.3904 | 2.5933 | 2.7953 | 3.3455 | 3.612 | 1.2058 | 1.3421 | 1.4835 | 1.6423 | 1.8253 | 2.0326 | 2.2744 | 2.6621 | 2.9755 | 3.3273 | 3.6998 | 4.0855 | 4.5228 | 4.9598 | 5.3721 | 5.7815 | 6.9188 | 7.4843
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.62694 | 0.78381 | 0.97286 | 1.1841 | 1.4233 | 1.684 | 2.0071 | 2.4081 | 2.7853 | 3.0957 | 3.2632 | 3.3435 | 3.416 | 3.4793 | 3.55 | 3.6091 | 3.9497 | 4.2075 | 1.3661 | 1.6961 | 2.0876 | 2.5239 | 3.017 | 3.5529 | 4.2141 | 5.0346 | 5.809 | 6.4502 | 6.8061 | 6.9829 | 7.1441 | 7.2844 | 7.4392 | 7.5704 | 8.3335 | 8.9214
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.59924 | 0.72277 | 0.84382 | 0.9755 | 1.1262 | 1.3097 | 1.5193 | 1.8128 | 2.067 | 2.347 | 2.642 | 2.9267 | 3.2065 | 3.4666 | 3.6438 | 3.7238 | 4.1223 | 4.4242 | 1.3166 | 1.5878 | 1.8475 | 2.1292 | 2.4498 | 2.8366 | 3.2779 | 3.8888 | 4.4183 | 5.0012 | 5.612 | 6.2021 | 6.7815 | 7.3193 | 7.6907 | 7.8671 | 8.7561 | 9.434
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.5757 | 0.66392 | 0.77003 | 0.89319 | 1.0332 | 1.1969 | 1.3954 | 1.688 | 1.9491 | 2.2364 | 2.5253 | 2.7972 | 3.0733 | 3.3152 | 3.4666 | 3.518 | 3.8014 | 4.053 | 1.2558 | 1.4426 | 1.6639 | 1.9199 | 2.2102 | 2.5481 | 2.9567 | 3.5567 | 4.0936 | 4.6844 | 5.2749 | 5.8303 | 6.3932 | 6.8863 | 7.198 | 7.3094 | 7.9325 | 8.4877
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.25438 | 0.27732 | 0.30082 | 0.32657 | 0.35573 | 0.38863 | 0.42587 | 0.48889 | 0.53716 | 0.58922 | 0.64356 | 0.70075 | 0.76848 | 0.8329 | 0.89502 | 0.956 | 1.1131 | 1.182 | 0.56973 | 0.61747 | 0.66616 | 0.71939 | 0.77952 | 0.84717 | 0.92355 | 1.0519 | 1.151 | 1.258 | 1.3693 | 1.486 | 1.6238 | 1.7547 | 1.8808 | 2.0044 | 2.3287 | 2.4758
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.27841 | 0.32907 | 0.38848 | 0.45474 | 0.52961 | 0.61097 | 0.70969 | 0.83243 | 0.94531 | 1.0379 | 1.0841 | 1.1073 | 1.1248 | 1.1402 | 1.1562 | 1.1693 | 1.252 | 1.3223 | 0.62166 | 0.72768 | 0.85066 | 0.98751 | 1.1417 | 1.3089 | 1.5108 | 1.7614 | 1.9928 | 2.1835 | 2.2817 | 2.3327 | 2.3722 | 2.4068 | 2.4426 | 2.4724 | 2.6597 | 2.8207
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.26955 | 0.30952 | 0.34731 | 0.38821 | 0.43415 | 0.48679 | 0.54935 | 0.64037 | 0.71584 | 0.79967 | 0.89001 | 0.97498 | 1.0574 | 1.137 | 1.186 | 1.2054 | 1.3067 | 1.3868 | 0.6059 | 0.69282 | 0.77383 | 0.86125 | 0.95893 | 1.0699 | 1.2014 | 1.3901 | 1.547 | 1.7211 | 1.9077 | 2.0834 | 2.2538 | 2.4179 | 2.5207 | 2.5642 | 2.7925 | 2.9744
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.2617 | 0.29083 | 0.32398 | 0.36074 | 0.40278 | 0.45117 | 0.51309 | 0.60055 | 0.67654 | 0.7601 | 0.84743 | 0.92953 | 1.0099 | 1.0821 | 1.1271 | 1.1394 | 1.2106 | 1.273 | 0.58565 | 0.64692 | 0.71601 | 0.79255 | 0.87982 | 0.97993 | 1.1073 | 1.2865 | 1.4425 | 1.6141 | 1.7923 | 1.9598 | 2.1236 | 2.2703 | 2.3628 | 2.3896 | 2.5474 | 2.6866
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.79174 | 0.87593 | 0.97238 | 1.0767 | 1.1944 | 1.3258 | 1.4788 | 1.733 | 1.9348 | 2.1512 | 2.3786 | 2.6187 | 2.8909 | 3.1634 | 3.4262 | 3.685 | 4.3086 | 4.5512 | 1.6882 | 1.8632 | 2.0626 | 2.2779 | 2.5203 | 2.7902 | 3.1035 | 3.6209 | 4.0339 | 4.4771 | 4.9417 | 5.431 | 5.984 | 6.5374 | 7.0702 | 7.5938 | 8.8786 | 9.3976
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.89143 | 1.0877 | 1.329 | 1.6013 | 1.9153 | 2.2535 | 2.6662 | 3.1814 | 3.6491 | 4.031 | 4.2132 | 4.2887 | 4.3505 | 4.4054 | 4.4592 | 4.5078 | 4.7804 | 5.0283 | 1.9034 | 2.3128 | 2.8115 | 3.373 | 4.0182 | 4.7122 | 5.5552 | 6.6054 | 7.5623 | 8.3473 | 8.7331 | 8.9014 | 9.0419 | 9.1663 | 9.288 | 9.3987 | 10.0238 | 10.5945
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.85404 | 0.99803 | 1.1483 | 1.3116 | 1.5002 | 1.7204 | 1.9788 | 2.3427 | 2.6533 | 2.9959 | 3.3547 | 3.6989 | 4.0311 | 4.3389 | 4.5295 | 4.5962 | 4.9423 | 5.2264 | 1.8368 | 2.1493 | 2.4708 | 2.8191 | 3.2198 | 3.6839 | 4.2255 | 4.9787 | 5.6221 | 6.3319 | 7.0722 | 7.7823 | 8.4677 | 9.1023 | 9.5016 | 9.6524 | 10.4412 | 11.0925
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.82131 | 0.92975 | 1.0618 | 1.2081 | 1.3806 | 1.5815 | 1.8289 | 2.1942 | 2.512 | 2.8575 | 3.2092 | 3.5544 | 3.8882 | 4.1927 | 4.3643 | 4.4154 | 4.6668 | 4.8839 | 1.7526 | 1.9803 | 2.2553 | 2.5598 | 2.9174 | 3.3321 | 3.8409 | 4.5879 | 5.2395 | 5.9473 | 6.6637 | 7.3664 | 8.0452 | 8.6639 | 9.016 | 9.1269 | 9.6856 | 10.1727
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.0503 | 1.212 | 1.4152 | 1.6482 | 1.9073 | 2.2039 | 2.5473 | 3.0481 | 3.2288 | 3.4242 | 3.6296 | 3.8429 | 4.0865 | 4.3264 | 4.592 | 4.8614 | 5.4403 | 5.7023 | 2.33 | 2.6654 | 3.0855 | 3.5674 | 4.1037 | 4.7177 | 5.4267 | 6.453 | 6.8257 | 7.2296 | 7.6518 | 8.0884 | 8.5845 | 9.0732 | 9.6295 | 10.1961 | 11.3961 | 11.9589
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.134 | 1.4887 | 1.9476 | 2.4543 | 3.0383 | 3.6655 | 4.4135 | 5.3128 | 5.7274 | 6.1236 | 6.3689 | 6.4521 | 6.5229 | 6.5834 | 6.6439 | 6.6983 | 7.0638 | 7.3286 | 2.5108 | 3.2507 | 4.2061 | 5.2533 | 6.4599 | 7.7556 | 9.2928 | 11.1348 | 11.9878 | 12.8306 | 13.3779 | 13.5644 | 13.7259 | 13.8624 | 13.9984 | 14.1221 | 14.9732 | 15.5872
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.1031 | 1.3587 | 1.6547 | 1.9926 | 2.3944 | 2.8448 | 3.3529 | 4.002 | 4.3435 | 4.7477 | 5.0688 | 5.5058 | 5.8025 | 6.0773 | 6.2512 | 6.3253 | 6.6896 | 6.9663 | 2.456 | 3.0069 | 3.6366 | 4.3539 | 5.2085 | 6.162 | 7.2326 | 8.5828 | 9.32 | 10.2031 | 10.87 | 11.8321 | 12.4484 | 13.0172 | 13.3834 | 13.5494 | 14.3772 | 15.0094
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.0755 | 1.29 | 1.5618 | 1.8744 | 2.2304 | 2.6333 | 3.1178 | 3.771 | 4.0612 | 4.4041 | 4.794 | 5.1293 | 5.4264 | 5.6957 | 5.854 | 5.909 | 6.2469 | 6.4881 | 2.3848 | 2.8362 | 3.4042 | 4.0577 | 4.8012 | 5.642 | 6.6481 | 7.9938 | 8.5919 | 9.311 | 10.1423 | 10.8426 | 11.4493 | 11.9979 | 12.3239 | 12.4434 | 13.2142 | 13.7589
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.6466 | 1.7628 | 1.908 | 2.0608 | 2.2143 | 2.5636 | 2.721 | 2.994 | 3.2232 | 3.4737 | 3.7262 | 3.9734 | 4.2421 | 4.511 | 4.7719 | 5.0396 | 5.0729 | 5.3929 | 3.9021 | 4.1451 | 4.4467 | 4.7633 | 5.0805 | 5.7874 | 6.1091 | 6.6737 | 7.1549 | 7.6843 | 8.212 | 8.7223 | 9.2721 | 9.8221 | 10.3554 | 10.9023 | 10.7146 | 11.4303
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.7465 | 2.0013 | 2.3102 | 2.6324 | 2.9458 | 3.4924 | 3.9094 | 4.4581 | 4.9688 | 5.3999 | 5.644 | 5.7796 | 5.9169 | 6.0307 | 6.1453 | 6.2589 | 6.2193 | 6.6892 | 4.118 | 4.656 | 5.3013 | 5.9717 | 6.618 | 7.7295 | 8.5805 | 9.713 | 10.7754 | 11.6796 | 12.2117 | 12.5223 | 12.8371 | 13.0927 | 13.3491 | 13.6043 | 13.3453 | 14.4453
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.7093 | 1.8994 | 2.1183 | 2.3421 | 2.5286 | 2.9548 | 3.2552 | 3.6913 | 4.0582 | 4.472 | 4.8974 | 5.3037 | 5.6966 | 6.0496 | 6.283 | 6.4018 | 6.3548 | 6.7291 | 4.0518 | 4.4662 | 4.9365 | 5.4158 | 5.8127 | 6.6883 | 7.3317 | 8.263 | 9.0443 | 9.9278 | 10.8249 | 11.6816 | 12.5085 | 13.2448 | 13.741 | 14.0072 | 13.7374 | 14.5912
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.6764 | 1.843 | 2.0449 | 2.2478 | 2.4189 | 2.8203 | 3.0585 | 3.4276 | 3.7555 | 4.13 | 4.5147 | 4.89 | 5.2499 | 5.5768 | 5.7728 | 5.85 | 5.6379 | 6.0624 | 3.967 | 4.3222 | 4.7482 | 5.1754 | 5.5313 | 6.3475 | 6.8362 | 7.601 | 8.2847 | 9.0725 | 9.8733 | 10.6516 | 11.395 | 12.0661 | 12.4746 | 12.6463 | 12.0069 | 12.9831
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.27333 | 0.31658 | 0.36173 | 0.47235 | 0.57185 | 0.69926 | 0.77672 | 0.88326 | 0.97175 | 1.0631 | 1.1624 | 1.2801 | 1.4178 | 1.5561 | 1.6836 | 1.7896 | 2.08 | 2.2209 | 0.58067 | 0.6707 | 0.76377 | 0.99333 | 1.1998 | 1.4643 | 1.623 | 1.8395 | 2.0199 | 2.2062 | 2.4083 | 2.6492 | 2.9309 | 3.2137 | 3.4737 | 3.6881 | 4.2839 | 4.5788
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.31188 | 0.39973 | 0.5015 | 0.70089 | 0.90011 | 1.1043 | 1.2712 | 1.4829 | 1.6859 | 1.8647 | 1.9717 | 2.0198 | 2.0524 | 2.0832 | 2.1141 | 2.1425 | 2.2795 | 2.4011 | 0.66356 | 0.84815 | 1.0585 | 1.4786 | 1.8973 | 2.3264 | 2.6676 | 3.1 | 3.5171 | 3.8877 | 4.115 | 4.219 | 4.2905 | 4.3579 | 4.4255 | 4.4877 | 4.7947 | 5.067
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.29731 | 0.36317 | 0.4295 | 0.60558 | 0.78873 | 0.98327 | 1.1074 | 1.2637 | 1.3933 | 1.5384 | 1.6909 | 1.8372 | 1.9801 | 2.117 | 2.2075 | 2.2484 | 2.4393 | 2.5963 | 0.63742 | 0.78082 | 0.92246 | 1.3002 | 1.6946 | 2.1125 | 2.3733 | 2.6958 | 2.9633 | 3.2626 | 3.5762 | 3.8773 | 4.1714 | 4.4531 | 4.6417 | 4.7309 | 5.1532 | 5.5033
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.2856 | 0.34017 | 0.40213 | 0.56612 | 0.70963 | 0.861 | 0.98056 | 1.1568 | 1.3176 | 1.4881 | 1.6404 | 1.7866 | 1.9307 | 2.0616 | 2.1442 | 2.1748 | 2.3125 | 2.439 | 0.60713 | 0.72188 | 0.85036 | 1.1989 | 1.5035 | 1.8236 | 2.0704 | 2.4329 | 2.7653 | 3.1171 | 3.4269 | 3.7238 | 4.0163 | 4.2822 | 4.4511 | 4.5159 | 4.8132 | 5.0858
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.88964 | 0.9027 | 0.91461 | 0.929 | 0.9482 | 0.96634 | 0.98681 | 1.0204 | 1.0466 | 1.0777 | 1.1072 | 1.1615 | 1.2295 | 1.2955 | 1.3536 | 1.3872 | 1.4771 | 1.5228 | 2.1652 | 2.1924 | 2.217 | 2.2466 | 2.2859 | 2.323 | 2.3648 | 2.433 | 2.4864 | 2.5496 | 2.6096 | 2.7222 | 2.8636 | 3.0009 | 3.1212 | 3.1889 | 3.3728 | 3.4675
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.90072 | 0.92806 | 0.95981 | 0.99519 | 1.0352 | 1.081 | 1.1325 | 1.2056 | 1.2889 | 1.375 | 1.4437 | 1.4688 | 1.4817 | 1.4933 | 1.5047 | 1.5141 | 0.92516 | 0.96997 | 2.1891 | 2.2464 | 2.3119 | 2.3847 | 2.4669 | 2.5606 | 2.6659 | 2.8161 | 2.9897 | 3.1716 | 3.3195 | 3.3737 | 3.4012 | 3.4261 | 3.4505 | 3.4707 | 1.9867 | 2.0845
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.89654 | 0.91588 | 0.93572 | 0.96121 | 1.0321 | 1.1071 | 1.1628 | 1.212 | 1.2506 | 1.292 | 1.3386 | 1.3812 | 0.79241 | 0.83128 | 0.85808 | 0.87269 | 0.79871 | 0.84428 | 2.1816 | 2.2237 | 2.266 | 2.3204 | 2.4734 | 2.6357 | 2.7539 | 2.8557 | 2.9355 | 3.0207 | 3.1163 | 3.204 | 1.7138 | 1.7938 | 1.8496 | 1.8809 | 1.6783 | 1.7797
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.89303 | 0.9093 | 0.92782 | 0.94855 | 0.97512 | 1.0026 | 1.0505 | 1.133 | 1.2146 | 1.2973 | 1.3485 | 1.3963 | 1.4397 | 1.4824 | 1.5072 | 1.521 | 1.7466 | 1.7779 | 2.1726 | 2.2067 | 2.2451 | 2.288 | 2.3426 | 2.3992 | 2.4996 | 2.6726 | 2.8446 | 3.0194 | 3.1235 | 3.2204 | 3.3085 | 3.3949 | 3.4456 | 3.4741 | 4.022 | 4.0902
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.67431 | 0.74041 | 0.8175 | 0.89692 | 0.99001 | 1.0913 | 1.2092 | 1.3971 | 1.5506 | 1.7132 | 1.8856 | 2.0572 | 2.2516 | 2.4424 | 2.632 | 2.8206 | 3.2926 | 3.4705 | 1.442 | 1.5797 | 1.7391 | 1.9034 | 2.0952 | 2.3036 | 2.5454 | 2.9295 | 3.2456 | 3.5811 | 3.9355 | 4.2859 | 4.681 | 5.0685 | 5.4532 | 5.8359 | 6.8151 | 7.2031
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.75119 | 0.90393 | 1.091 | 1.2967 | 1.5327 | 1.7888 | 2.0984 | 2.4861 | 2.8395 | 3.1262 | 3.27 | 3.3336 | 3.3988 | 3.4572 | 3.5163 | 3.5762 | 3.9124 | 4.2 | 1.608 | 1.9272 | 2.314 | 2.7389 | 3.2248 | 3.7509 | 4.3841 | 5.1767 | 5.9015 | 6.4923 | 6.7976 | 6.9384 | 7.0848 | 7.2149 | 7.3459 | 7.4782 | 8.2242 | 8.8699
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.72257 | 0.82568 | 0.94749 | 1.0728 | 1.2164 | 1.3826 | 1.5827 | 1.8621 | 2.1042 | 2.3688 | 2.6609 | 2.9423 | 3.2166 | 3.4706 | 3.632 | 3.7053 | 4.081 | 4.3688 | 1.5572 | 1.7813 | 2.0416 | 2.3094 | 2.6144 | 2.9649 | 3.3865 | 3.9692 | 4.4741 | 5.0242 | 5.6292 | 6.212 | 6.7797 | 7.3042 | 7.6429 | 7.8048 | 8.6414 | 9.287
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.69721 | 0.78217 | 0.89124 | 1.0033 | 1.1335 | 1.2826 | 1.4612 | 1.7261 | 1.9531 | 2.2029 | 2.4723 | 2.731 | 2.9835 | 3.216 | 3.3501 | 3.394 | 3.6516 | 3.8881 | 1.4918 | 1.6706 | 1.8974 | 2.1309 | 2.4014 | 2.7101 | 3.0774 | 3.62 | 4.0862 | 4.5996 | 5.1508 | 5.6784 | 6.193 | 6.6666 | 6.943 | 7.0387 | 7.6065 | 8.1308
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.57368 | 0.62119 | 0.81685 | 0.88335 | 0.94773 | 1.0268 | 1.1082 | 1.2491 | 1.4114 | 1.6919 | 1.8985 | 2.0512 | 2.203 | 2.3538 | 2.5024 | 2.6552 | 3.1839 | 3.4958 | 1.3726 | 1.4846 | 1.9661 | 2.1231 | 2.2728 | 2.4492 | 2.631 | 2.9423 | 3.2996 | 3.9412 | 4.3897 | 4.7178 | 5.0404 | 5.3612 | 5.6773 | 6.0021 | 7.1499 | 7.841
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.62424 | 0.93417 | 1.1872 | 1.3771 | 1.5624 | 1.9127 | 2.3007 | 2.652 | 2.8889 | 3.114 | 3.3301 | 3.528 | 3.7228 | 3.8943 | 4.0698 | 4.2471 | 4.9994 | 5.3684 | 1.4928 | 2.2502 | 2.8491 | 3.2993 | 3.7344 | 4.5432 | 5.4246 | 6.2091 | 6.7178 | 7.2027 | 7.6779 | 8.1192 | 8.5549 | 8.9311 | 9.3146 | 9.704 | 11.3575 | 12.2302
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.75615 | 0.9575 | 1.1837 | 1.4707 | 1.6999 | 1.9625 | 2.2828 | 2.5763 | 2.7848 | 3.0311 | 3.2637 | 3.4877 | 3.7056 | 3.8971 | 4.0736 | 4.2273 | 4.8695 | 5.112 | 1.8272 | 2.3104 | 2.8458 | 3.5232 | 4.065 | 4.671 | 5.4199 | 6.0889 | 6.5494 | 7.0992 | 7.6103 | 8.1024 | 8.5794 | 8.9919 | 9.3742 | 9.7108 | 11.1234 | 11.6628
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.61275 | 0.92296 | 1.1806 | 1.3692 | 1.5701 | 1.8798 | 2.1718 | 2.4361 | 2.6082 | 2.8096 | 3.0849 | 3.2799 | 3.4722 | 3.6396 | 3.7929 | 3.9232 | 4.4455 | 4.8256 | 1.468 | 2.226 | 2.8382 | 3.2874 | 3.759 | 4.4838 | 5.1615 | 5.7586 | 6.1293 | 6.5679 | 7.1902 | 7.6137 | 8.0281 | 8.3861 | 8.7155 | 9.0008 | 10.1647 | 11.0353
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.19944 | 0.63346 | 0.66559 | 0.70304 | 0.74571 | 0.8034 | 0.86578 | 1.0061 | 1.1459 | 1.3121 | 1.4621 | 1.5869 | 1.7079 | 1.829 | 1.9474 | 2.071 | 2.5488 | 2.9122 | 0.45204 | 1.3237 | 1.3906 | 1.4682 | 1.5564 | 1.6746 | 1.8024 | 2.1094 | 2.4246 | 2.8045 | 3.1391 | 3.4101 | 3.6663 | 3.9232 | 4.1743 | 4.4361 | 5.5011 | 6.3387
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.22988 | 0.70343 | 0.78644 | 0.8796 | 0.98405 | 1.1161 | 1.2743 | 1.5365 | 1.8153 | 2.0756 | 2.2881 | 2.4568 | 2.6222 | 2.7398 | 2.8602 | 2.9835 | 3.6454 | 4.1833 | 0.51783 | 1.474 | 1.6464 | 1.8394 | 2.0551 | 2.326 | 2.6493 | 3.2175 | 3.8326 | 4.4151 | 4.9059 | 5.3019 | 5.6925 | 5.9631 | 6.2384 | 6.522 | 8.0472 | 9.3512
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.21818 | 0.67227 | 0.72594 | 0.78429 | 0.849 | 0.94346 | 1.1345 | 1.432 | 1.6707 | 1.9525 | 2.2064 | 2.4514 | 2.6873 | 2.874 | 3.0253 | 3.1368 | 3.7228 | 3.985 | 0.49694 | 1.417 | 1.5325 | 1.6578 | 1.7959 | 1.9934 | 2.4284 | 3.1115 | 3.6554 | 4.3015 | 4.8703 | 5.4185 | 5.9442 | 6.35 | 6.6841 | 6.9386 | 8.2845 | 8.8883
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.20936 | 0.65262 | 0.6999 | 0.75574 | 0.81872 | 0.90276 | 0.99814 | 1.1907 | 1.3764 | 1.6247 | 1.8473 | 2.0519 | 2.2459 | 2.4009 | 2.5217 | 2.6049 | 3.1119 | 3.6212 | 0.47351 | 1.3657 | 1.4645 | 1.5808 | 1.7116 | 1.8847 | 2.0804 | 2.5003 | 2.9108 | 3.4715 | 3.9639 | 4.4133 | 4.834 | 5.1643 | 5.4256 | 5.6141 | 6.7934 | 8.0052
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Counterfactual | 0.42898 | 0.49651 | 0.62015 | 0.80579 | 1.0019 | 1.2137 | 1.4382 | 1.7296 | 1.9342 | 2.152 | 2.2885 | 2.4248 | 2.5741 | 2.7236 | 2.8725 | 3.0174 | 3.3993 | 3.5683 | 0.91202 | 1.0532 | 1.3108 | 1.6967 | 2.1054 | 2.547 | 3.0159 | 3.6253 | 4.0568 | 4.5182 | 4.8026 | 5.0835 | 5.3889 | 5.6945 | 5.9984 | 6.2943 | 7.0977 | 7.4739
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Electric Engagement | 0.48474 | 0.61912 | 0.83873 | 1.1451 | 1.4811 | 1.8506 | 2.2636 | 2.7429 | 3.1274 | 3.4697 | 3.6031 | 3.6773 | 3.7473 | 3.8055 | 3.8675 | 3.9284 | 4.2697 | 4.5244 | 1.0325 | 1.3153 | 1.7779 | 2.4253 | 3.1376 | 3.9218 | 4.7931 | 5.8051 | 6.6157 | 7.3424 | 7.6321 | 7.8004 | 7.9605 | 8.0912 | 8.229 | 8.365 | 9.1261 | 9.7169
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Holistic Transition | 0.46391 | 0.5678 | 0.73719 | 0.98375 | 1.2544 | 1.5562 | 1.896 | 2.3075 | 2.6109 | 2.9362 | 3.1705 | 3.3934 | 3.6135 | 3.8099 | 3.9373 | 4.0003 | 4.341 | 4.5528 | 0.99544 | 1.2213 | 1.5863 | 2.1168 | 2.7009 | 3.3526 | 4.0899 | 4.9782 | 5.6293 | 6.3286 | 6.8205 | 7.2887 | 7.7497 | 8.1582 | 8.4281 | 8.5688 | 9.3318 | 9.812
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Hydrogen Evolution | 0.44558 | 0.53088 | 0.68913 | 0.92906 | 1.1875 | 1.4756 | 1.7881 | 2.1696 | 2.4555 | 2.7633 | 2.975 | 3.1802 | 3.3793 | 3.559 | 3.6657 | 3.7067 | 3.9551 | 4.1817 | 0.94823 | 1.1294 | 1.4663 | 1.9779 | 2.532 | 3.1511 | 3.8188 | 4.6314 | 5.2383 | 5.8942 | 6.3335 | 6.7576 | 7.1679 | 7.5361 | 7.7577 | 7.8486 | 8.4051 | 8.9221
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.63731 | 0.67979 | 0.72735 | 0.77666 | 0.8328 | 0.91812 | 1.009 | 1.1761 | 1.3287 | 1.4991 | 1.6598 | 1.8078 | 1.9605 | 2.1142 | 2.2645 | 2.4173 | 2.9418 | 3.3058 | 1.5457 | 1.6344 | 1.7329 | 1.8348 | 1.9504 | 2.1246 | 2.3102 | 2.6637 | 2.994 | 3.3679 | 3.7131 | 4.025 | 4.3415 | 4.6604 | 4.9719 | 5.2884 | 6.4162 | 7.2223
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.68262 | 0.77725 | 0.89666 | 1.0269 | 1.1739 | 1.3746 | 1.6132 | 1.9529 | 2.2943 | 2.6101 | 2.8515 | 3.027 | 3.1973 | 3.3344 | 3.4746 | 3.6683 | 4.416 | 4.8433 | 1.6435 | 1.8418 | 2.0891 | 2.3576 | 2.6599 | 3.0698 | 3.5559 | 4.2696 | 4.9967 | 5.6751 | 6.207 | 6.6013 | 6.9856 | 7.2869 | 7.5934 | 8.0348 | 9.6814 | 10.6997
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.66544 | 0.73014 | 0.8057 | 0.88495 | 0.97376 | 1.1153 | 1.3335 | 1.6532 | 1.9263 | 2.2393 | 2.6407 | 2.9218 | 3.1908 | 3.419 | 3.5961 | 3.7195 | 4.3573 | 4.5966 | 1.6128 | 1.7539 | 1.9152 | 2.0838 | 2.2717 | 2.5653 | 3.0436 | 3.7485 | 4.3452 | 5.0329 | 5.9338 | 6.5404 | 7.1189 | 7.6003 | 7.9786 | 8.2498 | 9.659 | 10.1974
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.65163 | 0.70616 | 0.77313 | 0.84543 | 0.92813 | 1.0518 | 1.1921 | 1.4249 | 1.6469 | 1.9206 | 2.1769 | 2.4201 | 2.6497 | 2.848 | 2.9915 | 3.1357 | 3.6165 | 4.0455 | 1.5768 | 1.6919 | 1.8315 | 1.9815 | 2.1527 | 2.4064 | 2.6932 | 3.1842 | 3.658 | 4.2524 | 4.7987 | 5.3138 | 5.7965 | 6.2083 | 6.51 | 6.841 | 7.9218 | 8.9157
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.47831 | 0.5484 | 0.63027 | 0.72833 | 0.84214 | 0.97929 | 1.133 | 1.3499 | 1.5378 | 1.7433 | 2.0025 | 2.2547 | 2.5184 | 2.7594 | 2.9643 | 3.173 | 3.831 | 4.2624 | 1.121 | 1.2709 | 1.4462 | 1.6563 | 1.9008 | 2.1947 | 2.5244 | 2.9762 | 3.3756 | 3.815 | 4.3846 | 4.9319 | 5.4973 | 6.0054 | 6.4253 | 6.853 | 8.243 | 9.1821
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.55484 | 0.72916 | 1.0361 | 1.3093 | 1.625 | 2.0347 | 2.5297 | 3.0148 | 3.5064 | 3.8621 | 4.0858 | 4.2311 | 4.3656 | 4.4716 | 4.5724 | 4.6761 | 5.2124 | 5.6668 | 1.2906 | 1.6704 | 2.3615 | 2.9577 | 3.6479 | 4.5564 | 5.6523 | 6.6884 | 7.7587 | 8.5171 | 9.0087 | 9.3392 | 9.6497 | 9.8897 | 10.1158 | 10.3518 | 11.5779 | 12.6524
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.52915 | 0.68061 | 0.85009 | 1.0591 | 1.4327 | 1.7348 | 2.1346 | 2.5328 | 2.8459 | 3.1805 | 3.5123 | 3.8325 | 4.1398 | 4.4091 | 4.5982 | 4.7064 | 5.2407 | 5.5687 | 1.2443 | 1.5945 | 1.9782 | 2.4558 | 3.3381 | 4.0251 | 4.9436 | 5.8197 | 6.4987 | 7.2214 | 7.9272 | 8.6085 | 9.261 | 9.8263 | 10.2301 | 10.4725 | 11.6855 | 12.4337
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.51231 | 0.62628 | 0.85557 | 1.0397 | 1.2575 | 1.6477 | 1.9763 | 2.3189 | 2.6548 | 2.9937 | 3.3093 | 3.6113 | 3.8982 | 4.1519 | 4.3183 | 4.407 | 4.8372 | 5.2552 | 1.1987 | 1.4526 | 1.9824 | 2.393 | 2.8802 | 3.784 | 4.519 | 5.2471 | 5.9756 | 6.7006 | 7.3604 | 7.9896 | 8.5846 | 9.1066 | 9.4538 | 9.6475 | 10.622 | 11.5886
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.579 | 1.6834 | 1.8308 | 1.9908 | 2.1272 | 2.2671 | 2.42 | 2.6633 | 2.8597 | 3.0703 | 3.2922 | 3.5319 | 3.8087 | 4.0804 | 4.3387 | 4.5848 | 5.2541 | 5.5925 | 3.6827 | 3.9018 | 4.2081 | 4.5395 | 4.8214 | 5.1086 | 5.4219 | 5.9178 | 6.3206 | 6.7528 | 7.2068 | 7.6964 | 8.2602 | 8.8133 | 9.3383 | 9.8366 | 11.2146 | 11.926
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.6676 | 1.8954 | 2.2063 | 2.5359 | 2.8633 | 3.2005 | 3.6073 | 4.1138 | 4.5923 | 4.989 | 5.2222 | 5.3485 | 5.4616 | 5.5628 | 5.6583 | 5.7487 | 5.7322 | 6.0865 | 3.8739 | 4.356 | 5.0115 | 5.7042 | 6.388 | 7.087 | 7.9241 | 8.9658 | 9.9554 | 10.7788 | 11.2746 | 11.5511 | 11.8031 | 12.026 | 12.2316 | 12.43 | 12.2532 | 13.0526
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.635 | 1.8122 | 2.0409 | 2.2722 | 2.5095 | 2.7657 | 3.0319 | 3.3906 | 3.6975 | 4.0354 | 4.3995 | 4.7488 | 5.0864 | 5.4054 | 5.6258 | 5.7389 | 5.7741 | 6.1607 | 3.8159 | 4.2044 | 4.6997 | 5.1991 | 5.7104 | 6.2543 | 6.8141 | 7.5587 | 8.1962 | 8.8968 | 9.6486 | 10.3705 | 11.0688 | 11.7279 | 12.1889 | 12.4351 | 12.366 | 13.2318
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.6066 | 1.7515 | 1.9541 | 2.1621 | 2.3525 | 2.5576 | 2.8087 | 3.1824 | 3.5108 | 3.8752 | 4.2279 | 4.5685 | 4.9047 | 5.2057 | 5.3987 | 5.4737 | 5.3482 | 5.6583 | 3.7425 | 4.0518 | 4.4783 | 4.9147 | 5.3112 | 5.7339 | 6.2509 | 7.0173 | 7.6924 | 8.4406 | 9.1598 | 9.8537 | 10.5375 | 11.1496 | 11.5452 | 11.7042 | 11.2661 | 11.9424
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.63327 | 0.76848 | 1.0122 | 1.3226 | 1.6383 | 2.0018 | 2.3399 | 2.6487 | 2.921 | 3.1666 | 3.3493 | 3.5404 | 3.7569 | 3.9734 | 4.1824 | 4.3853 | 4.8745 | 5.0571 | 1.353 | 1.6366 | 2.1446 | 2.7901 | 3.4478 | 4.207 | 4.913 | 5.5503 | 6.1161 | 6.6252 | 6.9979 | 7.387 | 7.8267 | 8.266 | 8.6896 | 9.0999 | 10.1075 | 10.4982
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.71469 | 0.98953 | 1.4339 | 1.9482 | 2.5123 | 3.0689 | 3.6339 | 4.1539 | 4.6367 | 4.975 | 5.1225 | 5.1855 | 5.2394 | 5.2928 | 5.3467 | 5.3966 | 5.6744 | 5.9105 | 1.5287 | 2.1132 | 3.0558 | 4.1452 | 5.3448 | 6.5287 | 7.7194 | 8.7958 | 9.7983 | 10.4976 | 10.8085 | 10.9474 | 11.068 | 11.1863 | 11.3052 | 11.4156 | 12.0346 | 12.5637
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.68422 | 0.9057 | 1.2786 | 1.7361 | 2.2081 | 2.6696 | 3.1084 | 3.5064 | 3.8573 | 4.1572 | 4.4521 | 4.7329 | 5.0037 | 5.2577 | 5.4175 | 5.4837 | 5.8159 | 6.0851 | 1.4745 | 1.957 | 2.7608 | 3.7457 | 4.7661 | 5.7644 | 6.7076 | 7.5429 | 8.2821 | 8.9056 | 9.5126 | 10.0913 | 10.6493 | 11.1727 | 11.5068 | 11.6535 | 12.3957 | 13.0029
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.65748 | 0.85919 | 1.2163 | 1.6616 | 2.1094 | 2.5439 | 2.9716 | 3.3636 | 3.7178 | 4.0141 | 4.2989 | 4.5728 | 4.8409 | 5.0861 | 5.2249 | 5.2668 | 5.492 | 5.6905 | 1.4057 | 1.8385 | 2.602 | 3.5539 | 4.5155 | 5.4493 | 6.3615 | 7.1783 | 7.9187 | 8.528 | 9.1075 | 9.6647 | 10.2093 | 10.7074 | 10.9923 | 11.0829 | 11.5762 | 12.0124
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.38976 | 0.41326 | 0.43935 | 0.46903 | 0.50446 | 0.553 | 0.61241 | 0.72592 | 0.85038 | 0.95473 | 1.0485 | 1.1341 | 1.2211 | 1.3085 | 1.3938 | 1.4805 | 1.7712 | 1.9707 | 0.93503 | 0.98446 | 1.0387 | 1.1002 | 1.174 | 1.2766 | 1.4046 | 1.6551 | 1.9402 | 2.1737 | 2.3792 | 2.5617 | 2.7436 | 2.9265 | 3.1049 | 3.2862 | 3.9121 | 4.3577
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.4158 | 0.47051 | 0.53859 | 0.64319 | 0.79537 | 0.96953 | 1.1122 | 1.2998 | 1.4897 | 1.6631 | 1.789 | 1.8629 | 1.9308 | 1.9764 | 2.0239 | 2.0651 | 2.3653 | 2.678 | 0.99127 | 1.1064 | 1.2474 | 1.4755 | 1.8178 | 2.2067 | 2.507 | 2.9062 | 3.3174 | 3.6973 | 3.984 | 4.1542 | 4.3126 | 4.415 | 4.5218 | 4.6134 | 5.3058 | 6.058
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.4057 | 0.44301 | 0.51204 | 0.61013 | 0.71648 | 0.80479 | 0.91255 | 1.0792 | 1.2146 | 1.3695 | 1.5026 | 1.6617 | 1.8237 | 1.9575 | 2.0556 | 2.1173 | 2.4405 | 2.6118 | 0.97314 | 1.0551 | 1.2122 | 1.4401 | 1.6858 | 1.8786 | 2.1155 | 2.4845 | 2.7815 | 3.1228 | 3.4051 | 3.7495 | 4.1026 | 4.3883 | 4.6021 | 4.7434 | 5.49 | 5.8856
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.3983 | 0.42918 | 0.46789 | 0.5374 | 0.64688 | 0.79204 | 0.88383 | 1.0182 | 1.1442 | 1.3048 | 1.4514 | 1.5789 | 1.6996 | 1.7991 | 1.8663 | 1.8963 | 2.1113 | 2.3782 | 0.95347 | 1.0189 | 1.0997 | 1.255 | 1.5073 | 1.8426 | 2.0395 | 2.3271 | 2.6002 | 2.9552 | 3.2728 | 3.5432 | 3.7972 | 4.0028 | 4.1436 | 4.2077 | 4.7004 | 5.3325
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.24812 | 0.30822 | 0.37574 | 0.4542 | 0.52171 | 0.60234 | 0.67997 | 0.83961 | 0.9943 | 1.1739 | 1.3424 | 1.4865 | 1.6289 | 1.7713 | 1.9113 | 2.0568 | 2.5998 | 2.9955 | 0.56159 | 0.68864 | 0.82953 | 0.99266 | 1.1328 | 1.2983 | 1.4571 | 1.8028 | 2.1473 | 2.5531 | 2.9245 | 3.2343 | 3.534 | 3.834 | 4.1284 | 4.4347 | 5.6315 | 6.5347
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.28887 | 0.40212 | 0.53756 | 0.69244 | 0.84183 | 1.0213 | 1.2229 | 1.5359 | 1.862 | 2.1664 | 2.4105 | 2.6015 | 2.7906 | 2.9345 | 3.0818 | 3.234 | 4.0452 | 4.6191 | 0.65026 | 0.8922 | 1.1764 | 1.5009 | 1.812 | 2.1812 | 2.5927 | 3.2632 | 3.9734 | 4.6444 | 5.1986 | 5.6399 | 6.0784 | 6.4027 | 6.7332 | 7.076 | 8.9046 | 10.2827
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.2745 | 0.36371 | 0.46327 | 0.57638 | 0.67741 | 0.80888 | 1.0275 | 1.3593 | 1.6315 | 1.9484 | 2.2474 | 2.5364 | 2.816 | 3.0462 | 3.2303 | 3.3653 | 4.0742 | 4.3821 | 0.62467 | 0.82156 | 1.0362 | 1.2794 | 1.4959 | 1.7712 | 2.2624 | 3.0141 | 3.6255 | 4.3421 | 5.003 | 5.6406 | 6.2551 | 6.7494 | 7.1504 | 7.4534 | 9.0519 | 9.7532
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.26237 | 0.33893 | 0.42976 | 0.53735 | 0.63309 | 0.74758 | 0.86443 | 1.0833 | 1.2939 | 1.5674 | 1.8201 | 2.0566 | 2.2824 | 2.4701 | 2.6136 | 2.713 | 3.2904 | 3.8463 | 0.59315 | 0.758 | 0.95056 | 1.1781 | 1.3795 | 1.6166 | 1.8562 | 2.3287 | 2.7894 | 3.4004 | 3.9533 | 4.4671 | 4.9521 | 5.3488 | 5.6564 | 5.8787 | 7.2016 | 8.5079
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.8002 | 2.8621 | 2.9461 | 3.0404 | 3.145 | 3.2644 | 3.4007 | 3.5971 | 3.7443 | 3.9065 | 4.1195 | 4.3293 | 4.5533 | 4.7564 | 4.9297 | 5.1071 | 5.6015 | 5.479 | 6.7961 | 6.926 | 7.1005 | 7.2962 | 7.5125 | 7.7596 | 8.0414 | 8.4477 | 8.7557 | 9.0964 | 9.5603 | 10.0125 | 10.49 | 10.9161 | 11.2694 | 11.631 | 12.6622 | 12.2684
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.8652 | 3.0065 | 3.2415 | 3.4535 | 3.6953 | 3.9853 | 4.3482 | 4.7714 | 5.2168 | 5.503 | 5.655 | 5.7345 | 5.8087 | 5.8668 | 5.9276 | 5.9771 | 6.2877 | 4.3749 | 6.9361 | 7.234 | 7.7413 | 8.1819 | 8.6842 | 9.2979 | 10.0682 | 10.9648 | 11.9363 | 12.538 | 12.8676 | 13.046 | 13.2142 | 13.3442 | 13.4795 | 13.5912 | 14.3032 | 9.4738
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.8412 | 2.9559 | 3.0906 | 3.2454 | 3.5001 | 3.7048 | 3.9651 | 4.3048 | 4.5987 | 4.858 | 5.1167 | 5.3766 | 5.6342 | 5.8643 | 6.0208 | 6.0978 | 6.4716 | 4.5388 | 6.8933 | 7.1496 | 7.4391 | 7.7741 | 8.352 | 8.7936 | 9.3625 | 10.1013 | 10.7435 | 11.2901 | 11.8284 | 12.3725 | 12.9124 | 13.392 | 13.7238 | 13.8961 | 14.7463 | 9.8526
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.8206 | 2.9023 | 3.0651 | 3.2018 | 3.355 | 3.6071 | 3.8309 | 4.1322 | 4.4487 | 4.728 | 4.9865 | 5.2297 | 5.4675 | 5.6778 | 5.8073 | 5.8501 | 6.1063 | 4.1723 | 6.8403 | 7.0135 | 7.3725 | 7.6594 | 7.9809 | 8.5407 | 9.0155 | 9.6543 | 10.3489 | 10.9412 | 11.4761 | 11.9765 | 12.464 | 12.8935 | 13.1611 | 13.2541 | 13.8288 | 8.9319
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.4896 | 1.5468 | 1.615 | 1.6969 | 1.798 | 1.9239 | 2.0668 | 2.2685 | 2.465 | 2.6053 | 2.7449 | 2.4309 | 2.5996 | 2.7646 | 2.9255 | 3.0868 | 3.4923 | 3.7167 | 3.6161 | 3.7354 | 3.8768 | 4.0462 | 4.2587 | 4.5278 | 4.8338 | 5.2618 | 5.6938 | 5.9853 | 6.273 | 5.4232 | 5.7673 | 6.1037 | 6.4315 | 6.7597 | 7.6035 | 8.0883
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.5502 | 1.6761 | 1.9115 | 2.1802 | 2.5355 | 2.8984 | 3.1803 | 3.5337 | 3.8687 | 4.1371 | 4.2824 | 3.4855 | 3.5918 | 3.6759 | 3.7769 | 3.8363 | 4.2066 | 4.5398 | 3.7473 | 4.011 | 4.5335 | 5.125 | 5.9215 | 6.7327 | 7.3213 | 8.0612 | 8.769 | 9.3365 | 9.6548 | 7.644 | 7.8922 | 8.0866 | 8.3039 | 8.4386 | 9.2717 | 10.045
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.528 | 1.6097 | 1.7742 | 1.9946 | 2.2368 | 2.5044 | 2.6935 | 2.9554 | 3.1843 | 3.4237 | 3.654 | 2.9714 | 3.2095 | 3.4334 | 3.6221 | 3.7036 | 4.1305 | 4.4991 | 3.7076 | 3.8856 | 4.2619 | 4.7719 | 5.3296 | 5.9406 | 6.3441 | 6.8984 | 7.3823 | 7.8873 | 8.3624 | 6.56 | 7.0588 | 7.5277 | 7.9255 | 8.1087 | 9.0626 | 9.9077
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.5088 | 1.5767 | 1.7131 | 1.8674 | 2.0891 | 2.3534 | 2.5108 | 2.7404 | 2.943 | 3.1686 | 3.395 | 3.1618 | 3.3834 | 3.5871 | 3.7316 | 3.8021 | 4.0722 | 4.3447 | 3.6583 | 3.8012 | 4.1074 | 4.4477 | 4.9511 | 5.5559 | 5.8811 | 6.3544 | 6.7736 | 7.2415 | 7.7079 | 7.026 | 7.4819 | 7.9001 | 8.1995 | 8.3607 | 8.9578 | 9.5673
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.27519 | 0.36235 | 0.45277 | 0.55057 | 0.67101 | 0.81319 | 0.95649 | 1.1811 | 1.3715 | 1.5862 | 1.7989 | 2.0128 | 2.2592 | 2.5023 | 2.7433 | 2.9831 | 3.6016 | 3.9005 | 0.61359 | 0.7954 | 0.98255 | 1.1847 | 1.4335 | 1.7272 | 2.0219 | 2.4821 | 2.8755 | 3.3205 | 3.7598 | 4.1987 | 4.7031 | 5.2005 | 5.6933 | 6.1831 | 7.473 | 8.1212
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.36021 | 0.54453 | 0.76243 | 1.0039 | 1.292 | 1.6241 | 2.0056 | 2.4597 | 2.8622 | 3.1987 | 3.3715 | 3.4623 | 3.5577 | 3.6572 | 3.7553 | 3.8499 | 4.307 | 4.7075 | 0.79771 | 1.1842 | 1.6364 | 2.1364 | 2.7337 | 3.424 | 4.2105 | 5.1434 | 5.971 | 6.668 | 7.0378 | 7.2417 | 7.4568 | 7.6788 | 7.8973 | 8.1082 | 9.1301 | 10.0345
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.32866 | 0.45783 | 0.60783 | 0.77855 | 0.98023 | 1.2164 | 1.459 | 1.792 | 2.0785 | 2.3976 | 2.7295 | 3.0589 | 3.3954 | 3.7104 | 3.9207 | 4.0311 | 4.5635 | 4.9997 | 0.74138 | 1.0219 | 1.3436 | 1.7091 | 2.1403 | 2.6437 | 3.1576 | 3.8545 | 4.4548 | 5.1232 | 5.8144 | 6.5014 | 7.2042 | 7.8615 | 8.3085 | 8.555 | 9.746 | 10.7272
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.30154 | 0.41262 | 0.54641 | 0.68609 | 0.8631 | 1.0832 | 1.3053 | 1.6128 | 1.8811 | 2.1821 | 2.4959 | 2.803 | 3.118 | 3.4091 | 3.589 | 3.6699 | 4.0604 | 4.4319 | 0.67161 | 0.90659 | 1.1875 | 1.48 | 1.8521 | 2.3158 | 2.7772 | 3.411 | 3.9649 | 4.5883 | 5.2348 | 5.8667 | 6.5158 | 7.1153 | 7.4918 | 7.67 | 8.5363 | 9.3634
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.401 | 1.4803 | 1.7146 | 1.8236 | 1.9476 | 2.7161 | 2.8752 | 3.1237 | 3.3193 | 3.5264 | 3.7392 | 3.9784 | 4.2539 | 4.5401 | 4.8278 | 5.0896 | 5.5869 | 5.7367 | 3.1973 | 3.363 | 3.9066 | 4.133 | 4.3901 | 6.2519 | 6.5808 | 7.0902 | 7.4915 | 7.9164 | 8.3516 | 8.8417 | 9.4052 | 9.9913 | 10.5807 | 11.1145 | 12.1378 | 12.4635
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.4957 | 1.8193 | 2.0602 | 2.3339 | 2.6454 | 2.9827 | 3.3912 | 3.8882 | 4.3353 | 4.7219 | 4.9393 | 5.036 | 5.1089 | 5.1609 | 5.2016 | 5.2396 | 5.415 | 5.6076 | 3.4023 | 4.1361 | 4.6379 | 5.2079 | 5.8561 | 6.5584 | 7.4033 | 8.4267 | 9.3449 | 10.1458 | 10.6113 | 10.8268 | 10.9914 | 11.1095 | 11.2022 | 11.2888 | 11.6963 | 12.1414
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.5959 | 1.7232 | 1.8809 | 2.0582 | 2.2661 | 2.5039 | 2.7741 | 3.1889 | 3.5405 | 3.8601 | 4.1931 | 4.5067 | 4.7943 | 5.0628 | 5.2228 | 5.281 | 5.5242 | 5.7912 | 3.6781 | 3.9569 | 4.297 | 4.6797 | 5.1273 | 5.6375 | 6.2129 | 7.0878 | 7.8254 | 8.488 | 9.1753 | 9.8238 | 10.4163 | 10.9695 | 11.3048 | 11.437 | 11.9983 | 12.6174
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.43 | 1.6711 | 1.8095 | 1.9675 | 2.1496 | 2.3595 | 2.6112 | 2.9638 | 3.2754 | 3.628 | 3.9932 | 4.3364 | 4.6609 | 4.9569 | 5.1099 | 5.1499 | 5.3356 | 5.5027 | 3.2612 | 3.8241 | 4.1157 | 4.4497 | 4.8345 | 5.2775 | 5.8048 | 6.5355 | 7.1791 | 7.9084 | 8.6611 | 9.3661 | 10.0307 | 10.6367 | 10.9521 | 11.0411 | 11.4584 | 11.8342
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.34316 | 0.45445 | 0.59928 | 0.77352 | 0.95508 | 1.1625 | 1.4017 | 1.7462 | 2.038 | 2.3463 | 2.6711 | 3.0053 | 3.3696 | 3.667 | 3.9766 | 4.2967 | 5.0779 | 5.4674 | 0.77595 | 1.0084 | 1.309 | 1.6699 | 2.0458 | 2.4753 | 2.9702 | 3.6783 | 4.2826 | 4.9215 | 5.596 | 6.2887 | 7.0408 | 7.6481 | 8.285 | 8.947 | 10.573 | 11.4108
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.45031 | 0.69956 | 1.0231 | 1.3925 | 1.8032 | 2.2507 | 2.7833 | 3.4224 | 4.0334 | 4.5681 | 4.9382 | 5.1903 | 5.4156 | 5.5345 | 5.617 | 5.6994 | 6.0621 | 6.4312 | 1.0075 | 1.5317 | 2.2069 | 2.9765 | 3.8317 | 4.7639 | 5.8685 | 7.1887 | 8.4618 | 9.5855 | 10.3905 | 10.9498 | 11.4524 | 11.719 | 11.9058 | 12.0921 | 12.91 | 13.7421
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.41046 | 0.59585 | 0.82523 | 1.0907 | 1.3709 | 1.6932 | 2.0631 | 2.6161 | 3.123 | 3.6557 | 4.1884 | 4.6896 | 5.1109 | 5.462 | 5.6905 | 5.7902 | 6.2427 | 6.6549 | 0.93675 | 1.3404 | 1.8328 | 2.4016 | 3.0014 | 3.6905 | 4.4791 | 5.6496 | 6.7291 | 7.864 | 8.9855 | 10.0409 | 10.9226 | 11.6519 | 12.1359 | 12.358 | 13.3768 | 14.3084
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.37477 | 0.52853 | 0.73667 | 0.98225 | 1.2425 | 1.5418 | 1.8859 | 2.354 | 2.792 | 3.2699 | 3.7648 | 4.2257 | 4.6642 | 5.0248 | 5.2482 | 5.3473 | 5.7791 | 6.1698 | 0.84486 | 1.1711 | 1.6097 | 2.1273 | 2.6759 | 3.3061 | 4.0272 | 5 | 5.9188 | 6.9205 | 7.9556 | 8.9148 | 9.8242 | 10.5664 | 11.0343 | 11.2535 | 12.2075 | 13.0738
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.37656 | 0.48474 | 0.75919 | 0.92433 | 1.1062 | 1.3072 | 1.5378 | 1.8823 | 2.1655 | 2.4423 | 2.7254 | 3.023 | 3.3592 | 3.695 | 4.0196 | 4.3459 | 5.1198 | 5.4602 | 0.84255 | 1.0679 | 1.6284 | 1.9719 | 2.3495 | 2.7662 | 3.2421 | 3.9471 | 4.5319 | 5.0985 | 5.6765 | 6.2823 | 6.965 | 7.646 | 8.3036 | 8.9645 | 10.5522 | 11.2741
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.49546 | 0.88236 | 1.2273 | 1.6188 | 2.0746 | 2.5309 | 3.0619 | 3.7148 | 4.2953 | 4.7549 | 4.9775 | 5.0787 | 5.1705 | 5.2575 | 5.3397 | 5.4177 | 5.7571 | 6.156 | 1.0995 | 1.8971 | 2.6263 | 3.4453 | 4.3983 | 5.3432 | 6.4316 | 7.7665 | 8.9547 | 9.897 | 10.365 | 10.5881 | 10.7929 | 10.9863 | 11.1695 | 11.3437 | 12.1106 | 13.0044
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.45039 | 0.75136 | 0.99292 | 1.2346 | 1.5087 | 1.8103 | 2.1603 | 2.6316 | 3.0371 | 3.4622 | 3.9119 | 4.3569 | 4.8003 | 5.2106 | 5.4713 | 5.5863 | 6.0641 | 6.5216 | 1.0192 | 1.6509 | 2.1815 | 2.7038 | 3.2928 | 3.9336 | 4.6695 | 5.648 | 6.4899 | 7.3698 | 8.2964 | 9.2138 | 10.129 | 10.9761 | 11.5228 | 11.7773 | 12.8503 | 13.884
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.41307 | 0.68832 | 0.90381 | 1.1371 | 1.4107 | 1.7009 | 2.0301 | 2.5062 | 2.9082 | 3.3334 | 3.7762 | 4.218 | 4.6529 | 5.0577 | 5.2989 | 5.3939 | 5.762 | 6.086 | 0.92193 | 1.4875 | 1.9515 | 2.4468 | 3.0268 | 3.6344 | 4.3141 | 5.2906 | 6.1152 | 6.9847 | 7.8862 | 8.7858 | 9.6721 | 10.497 | 10.9938 | 11.1975 | 12.0015 | 12.7193
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Counterfactual | 1.0869 | 1.1388 | 1.3847 | 1.4538 | 1.5401 | 1.6587 | 1.7911 | 1.9855 | 2.1797 | 2.3815 | 2.5549 | 2.7698 | 3.0215 | 3.2738 | 3.5013 | 3.6731 | 4.2406 | 4.6216 | 2.463 | 2.5716 | 3.0677 | 3.2107 | 3.3916 | 3.6404 | 3.9183 | 4.3321 | 4.7587 | 5.2034 | 5.5721 | 6.025 | 6.5516 | 7.0795 | 7.5541 | 7.9092 | 9.1208 | 9.9594
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.1375 | 1.4411 | 1.5792 | 1.8348 | 2.0852 | 2.3917 | 2.6728 | 3.0465 | 3.4114 | 3.8324 | 4.1688 | 4.3538 | 4.5052 | 4.6486 | 4.7737 | 4.9032 | 5.6763 | 6.1416 | 2.5726 | 3.194 | 3.4829 | 4.053 | 4.5966 | 5.2602 | 5.8392 | 6.623 | 7.3972 | 8.3031 | 9.0432 | 9.4581 | 9.8001 | 10.114 | 10.3904 | 10.6772 | 12.4227 | 13.5104
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.119 | 1.4025 | 1.5781 | 1.719 | 1.9203 | 2.1413 | 2.4362 | 2.8185 | 3.1412 | 3.5038 | 3.8007 | 4.1719 | 4.4473 | 4.7121 | 4.8979 | 5.1485 | 5.7785 | 6.1339 | 2.5396 | 3.1269 | 3.5341 | 3.8458 | 4.2965 | 4.7668 | 5.4099 | 6.2447 | 6.9456 | 7.7371 | 8.373 | 9.1996 | 9.7888 | 10.3457 | 10.7437 | 11.3358 | 12.7363 | 13.5347
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.1031 | 1.3595 | 1.4447 | 1.6269 | 1.8036 | 1.9838 | 2.2457 | 2.5285 | 2.8122 | 3.291 | 3.569 | 3.822 | 4.0713 | 4.3031 | 4.4596 | 4.5615 | 5.1799 | 5.6395 | 2.4986 | 3.0207 | 3.2021 | 3.6185 | 4.0118 | 4.3948 | 4.9672 | 5.5643 | 6.1696 | 7.209 | 7.798 | 8.3313 | 8.8535 | 9.3342 | 9.6641 | 9.8859 | 11.2949 | 12.3457
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.7098 | 1.8008 | 1.9116 | 2.0421 | 2.199 | 1.5721 | 1.7457 | 2.0659 | 2.3413 | 2.6649 | 3.0374 | 3.4081 | 3.8006 | 4.1961 | 4.587 | 4.9783 | 6.3102 | 6.9605 | 4.0954 | 4.2857 | 4.5184 | 4.7952 | 5.128 | 3.4907 | 3.8479 | 4.5137 | 5.094 | 5.7804 | 6.5661 | 7.3431 | 8.1607 | 8.9838 | 9.7991 | 10.6155 | 13.4495 | 14.8692
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.802 | 2.0258 | 2.3225 | 2.6393 | 3.0066 | 2.643 | 3.1427 | 3.7934 | 4.4164 | 4.9673 | 5.3534 | 5.6336 | 5.9086 | 6.1581 | 6.4596 | 6.7385 | 8.1381 | 8.944 | 4.2951 | 4.7736 | 5.4057 | 6.08 | 6.8637 | 5.7824 | 6.8199 | 8.1836 | 9.4981 | 10.6724 | 11.5187 | 12.1448 | 12.7606 | 13.3139 | 13.9703 | 14.5821 | 17.6959 | 19.5218
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.7682 | 1.9673 | 2.2167 | 2.5207 | 2.8633 | 2.4195 | 2.8358 | 3.3822 | 3.8744 | 4.4043 | 4.9276 | 5.5916 | 6.0918 | 6.5504 | 6.9534 | 7.2226 | 8.4736 | 9.1462 | 4.235 | 4.675 | 5.2225 | 5.8885 | 6.6428 | 5.4108 | 6.3107 | 7.4867 | 8.547 | 9.691 | 10.805 | 12.2774 | 13.3415 | 14.3118 | 15.17 | 15.7599 | 18.5252 | 20.0251
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.7383 | 1.9066 | 2.1362 | 2.3585 | 2.639 | 2.1611 | 2.5173 | 3.0063 | 3.4549 | 3.9514 | 4.4513 | 4.9386 | 5.4103 | 5.8485 | 6.1889 | 6.4167 | 7.5959 | 8.3158 | 4.1579 | 4.5235 | 5.021 | 5.5044 | 6.1168 | 4.804 | 5.5547 | 6.5854 | 7.5365 | 8.5951 | 9.6539 | 10.6816 | 11.6731 | 12.5914 | 13.3132 | 13.8107 | 16.4401 | 18.0568
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.46756 | 0.59144 | 0.72582 | 0.87821 | 1.0501 | 1.2416 | 1.4624 | 1.8011 | 2.0721 | 2.3555 | 2.6491 | 2.985 | 3.3801 | 3.7679 | 4.1319 | 4.4557 | 5.1689 | 5.4034 | 1.071 | 1.3277 | 1.6057 | 1.9207 | 2.2754 | 2.67 | 3.1239 | 3.8153 | 4.3721 | 4.9539 | 5.555 | 6.2439 | 7.0531 | 7.8469 | 8.5893 | 9.2458 | 10.717 | 11.2287
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.59918 | 0.86949 | 1.1931 | 1.5682 | 1.9941 | 2.4479 | 2.997 | 3.6801 | 4.3166 | 4.863 | 5.1559 | 5.2579 | 5.3284 | 5.3968 | 5.4675 | 5.5301 | 5.833 | 6.1936 | 1.3557 | 1.9184 | 2.5882 | 3.3645 | 4.2445 | 5.1806 | 6.3068 | 7.7049 | 9.0142 | 10.1469 | 10.7737 | 11.0036 | 11.166 | 11.3226 | 11.4834 | 11.6273 | 12.3248 | 13.1457
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.55032 | 0.7459 | 0.95061 | 1.1844 | 1.4597 | 1.7809 | 2.162 | 2.7056 | 3.1658 | 3.5917 | 4.0461 | 4.4783 | 4.9109 | 5.3188 | 5.5627 | 5.6561 | 6.0732 | 6.4889 | 1.2689 | 1.6911 | 2.1295 | 2.6293 | 3.2157 | 3.8978 | 4.7041 | 5.8406 | 6.8043 | 7.687 | 8.6241 | 9.5159 | 10.4098 | 11.2522 | 11.7654 | 11.9772 | 12.9318 | 13.8824
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.50622 | 0.66016 | 0.83767 | 1.0496 | 1.2897 | 1.5575 | 1.8915 | 2.3736 | 2.8379 | 3.3421 | 3.7976 | 4.2395 | 4.6605 | 5.0527 | 5.2671 | 5.3352 | 5.6314 | 5.9162 | 1.1555 | 1.4777 | 1.8481 | 2.2912 | 2.7924 | 3.3502 | 4.0422 | 5.0347 | 5.9981 | 7.0443 | 7.976 | 8.8792 | 9.7374 | 10.5367 | 10.9799 | 11.1303 | 11.7942 | 12.4343
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.37497 | 0.44838 | 0.5426 | 0.65964 | 0.78467 | 0.92024 | 1.0627 | 1.2453 | 1.4311 | 1.6266 | 1.8247 | 2.0305 | 2.2507 | 2.4658 | 2.6786 | 2.8851 | 3.4094 | 3.4989 | 0.79396 | 0.9479 | 1.1443 | 1.3875 | 1.6477 | 1.9302 | 2.2275 | 2.6063 | 2.9954 | 3.4051 | 3.8208 | 4.2518 | 4.7117 | 5.1609 | 5.6049 | 6.0358 | 7.1371 | 7.326
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.41461 | 0.53941 | 0.70203 | 0.89937 | 1.1175 | 1.3521 | 1.6193 | 1.9241 | 2.2353 | 2.5123 | 2.7227 | 2.8865 | 3.0458 | 3.2076 | 3.3712 | 3.5247 | 3.9733 | 4.0666 | 0.8804 | 1.1454 | 1.4885 | 1.9047 | 2.3661 | 2.8636 | 3.4267 | 4.0651 | 4.7211 | 5.3083 | 5.7621 | 6.1208 | 6.4696 | 6.8234 | 7.1805 | 7.5173 | 8.5049 | 8.7162
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.4008 | 0.50125 | 0.63018 | 0.78845 | 0.96209 | 1.1572 | 1.3662 | 1.6181 | 1.8742 | 2.1303 | 2.3984 | 2.6627 | 2.9274 | 3.1868 | 3.4029 | 3.5677 | 4.0538 | 4.1775 | 0.85579 | 1.0743 | 1.352 | 1.6922 | 2.0666 | 2.4874 | 2.936 | 3.4706 | 4.0174 | 4.5624 | 5.1308 | 5.6917 | 6.2539 | 6.8049 | 7.2693 | 7.6308 | 8.7004 | 8.9804
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.38917 | 0.48046 | 0.60192 | 0.75414 | 0.9218 | 1.109 | 1.3121 | 1.5588 | 1.814 | 2.0888 | 2.3539 | 2.6178 | 2.8826 | 3.1384 | 3.3481 | 3.505 | 3.9548 | 4.0391 | 0.82579 | 1.0213 | 1.28 | 1.6041 | 1.9626 | 2.3637 | 2.7966 | 3.3168 | 3.859 | 4.4415 | 5.0011 | 5.5582 | 6.1171 | 6.6582 | 7.1067 | 7.4494 | 8.4329 | 8.6171
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.1113 | 1.1704 | 1.2609 | 1.3423 | 1.4348 | 1.5405 | 1.6602 | 1.8398 | 1.9938 | 2.1491 | 2.3063 | 2.4653 | 2.6394 | 2.8079 | 2.9694 | 3.1387 | 3.5634 | 3.7303 | 2.7478 | 2.872 | 3.0578 | 3.226 | 3.4168 | 3.635 | 3.8818 | 4.2495 | 4.5696 | 4.8874 | 5.2088 | 5.5325 | 5.8856 | 6.2265 | 6.5532 | 6.8957 | 7.7659 | 8.1163
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.1725 | 1.3061 | 1.4943 | 1.6875 | 1.9136 | 2.1614 | 2.4572 | 2.8125 | 3.1202 | 3.362 | 3.5232 | 3.6287 | 3.7209 | 3.811 | 3.9075 | 3.9928 | 4.4154 | 4.8253 | 2.8798 | 3.1616 | 3.55 | 3.9519 | 4.4232 | 4.939 | 5.5513 | 6.2821 | 6.9122 | 7.4066 | 7.7396 | 7.96 | 8.1533 | 8.3422 | 8.5438 | 8.7226 | 9.6122 | 10.4744
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.1497 | 1.2458 | 1.3723 | 1.5064 | 1.6535 | 1.8308 | 2.0292 | 2.2633 | 2.4638 | 2.6816 | 2.9563 | 3.2273 | 3.4987 | 3.7551 | 3.9404 | 4.0471 | 3.5166 | 4.9545 | 2.8391 | 3.0505 | 3.321 | 3.6101 | 3.9263 | 4.3048 | 4.7251 | 5.2082 | 5.6222 | 6.0711 | 6.6332 | 7.1878 | 7.7443 | 8.2698 | 8.6527 | 8.878 | 7.3702 | 10.8082
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.1309 | 1.2081 | 1.3344 | 1.4569 | 1.6003 | 1.7704 | 1.9651 | 2.228 | 2.4416 | 2.6644 | 2.9161 | 3.1661 | 3.4162 | 3.6427 | 3.7959 | 3.8762 | 4.2362 | 4.5146 | 2.7903 | 2.9541 | 3.215 | 3.4718 | 3.7737 | 4.1319 | 4.5382 | 5.0805 | 5.5184 | 5.9713 | 6.4817 | 6.9894 | 7.4974 | 7.9578 | 8.2711 | 8.4385 | 9.1912 | 9.7739
Enderby 132kV | HINCKLEY 11kV S STN | Bulk Supply Point | 11 | Counterfactual | 8.0653 | 8.3103 | 8.4836 | 8.6846 | 8.9149 | 9.1789 | 9.4734 | 9.9587 | 10.3491 | 10.7687 | 11.1992 | 11.6394 | 12.1188 | 12.5982 | 13.0682 | 13.5364 | 14.8392 | 15.5438 | 19.9148 | 20.4705 | 20.8298 | 21.2461 | 21.7223 | 22.2666 | 22.8732 | 23.8736 | 24.6855 | 25.5613 | 26.4548 | 27.3634 | 28.3469 | 29.3298 | 30.2927 | 31.2517 | 33.9814 | 35.5075
Enderby 132kV | HINCKLEY 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | 8.3234 | 8.6582 | 9.0718 | 9.5701 | 10.1323 | 10.7547 | 11.47 | 12.3725 | 13.3065 | 14.1035 | 14.5957 | 14.931 | 15.2509 | 15.4358 | 15.6187 | 15.793 | 16.6613 | 17.3874 | 20.5075 | 21.2144 | 22.0749 | 23.112 | 24.281 | 25.5728 | 27.0458 | 28.9095 | 30.861 | 32.5365 | 33.6019 | 34.3496 | 35.0666 | 35.4789 | 35.8852 | 36.2739 | 38.2218 | 39.8859
Enderby 132kV | HINCKLEY 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | 8.2656 | 8.4994 | 8.7906 | 9.1302 | 9.4932 | 9.9266 | 10.533 | 11.3373 | 12.044 | 12.7903 | 13.5479 | 14.182 | 14.8026 | 15.3768 | 15.7657 | 15.9711 | 16.9426 | 17.7953 | 20.4046 | 20.9189 | 21.5455 | 22.2744 | 23.0511 | 23.9723 | 25.2718 | 26.981 | 28.4804 | 30.0616 | 31.6547 | 32.9803 | 34.278 | 35.4753 | 36.3012 | 36.7589 | 38.9381 | 40.8966
Enderby 132kV | HINCKLEY 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | 8.217 | 8.4115 | 8.65 | 8.9404 | 9.2744 | 9.6741 | 10.1222 | 10.7648 | 11.3515 | 11.9901 | 12.6406 | 13.277 | 13.8941 | 16.2516 | 16.615 | 16.7966 | 17.6435 | 18.4331 | 20.2786 | 20.6931 | 21.1924 | 21.8013 | 22.5014 | 23.3383 | 24.269 | 25.6002 | 26.8227 | 28.1565 | 29.5054 | 30.8236 | 32.0992 | 37.7445 | 38.506 | 38.9047 | 40.7921 | 42.5655
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.36158 | 0.44838 | 0.55944 | 0.67905 | 0.82043 | 0.9736 | 1.1521 | 1.4316 | 1.6746 | 1.956 | 2.285 | 2.666 | 2.9388 | 3.2219 | 3.5386 | 3.8607 | 4.5508 | 4.7838 | 0.81248 | 0.99278 | 1.222 | 1.4695 | 1.7612 | 2.0771 | 2.4444 | 3.0154 | 3.5156 | 4.0962 | 4.7784 | 5.5705 | 6.1256 | 6.7025 | 7.3609 | 8.0373 | 9.4669 | 9.9644
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.45699 | 0.65057 | 0.89936 | 1.1907 | 1.5274 | 1.9117 | 2.3862 | 2.9644 | 3.5 | 3.9772 | 4.3221 | 4.5588 | 4.7392 | 4.8355 | 4.9359 | 5.0298 | 5.4077 | 5.8151 | 1.0187 | 1.4224 | 1.9378 | 2.5414 | 3.2379 | 4.0344 | 5.0156 | 6.2064 | 7.3126 | 8.3114 | 9.0598 | 9.5817 | 9.9825 | 10.1984 | 10.422 | 10.632 | 11.4562 | 12.3452
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.42165 | 0.54708 | 0.71849 | 0.91953 | 1.1472 | 1.4404 | 1.7689 | 2.2441 | 2.6858 | 3.1629 | 3.6493 | 4.1061 | 4.4855 | 4.8421 | 5.0782 | 5.1812 | 5.6506 | 6.0863 | 0.95599 | 1.2274 | 1.593 | 2.0226 | 2.5088 | 3.1333 | 3.8284 | 4.8253 | 5.761 | 6.7793 | 7.7999 | 8.7592 | 9.5483 | 10.2906 | 10.791 | 11.0163 | 12.0468 | 13.0117
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.38975 | 0.49556 | 0.65161 | 0.82541 | 1.0355 | 1.3103 | 1.6266 | 2.0455 | 2.4278 | 2.847 | 3.3166 | 3.7748 | 4.1667 | 4.5288 | 4.7632 | 4.8855 | 5.2895 | 5.6015 | 0.87394 | 1.0958 | 1.4207 | 1.7847 | 2.2251 | 2.8022 | 3.4627 | 4.3284 | 5.1213 | 5.9928 | 6.976 | 7.9347 | 8.745 | 9.4935 | 9.986 | 10.2539 | 11.1243 | 11.803
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.10107 | 0.10298 | 0.10427 | 0.10615 | 0.10837 | 0.11207 | 0.11585 | 0.12263 | 0.12905 | 0.1363 | 0.14311 | 0.14923 | 0.15603 | 0.16264 | 0.1685 | 0.17488 | 0.20438 | 0.23327 | 0.24112 | 0.24532 | 0.24807 | 0.25198 | 0.25657 | 0.26416 | 0.27195 | 0.28642 | 0.30039 | 0.31637 | 0.33111 | 0.34401 | 0.35813 | 0.3719 | 0.38408 | 0.39731 | 0.46028 | 0.52218
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.10207 | 0.1061 | 0.10985 | 0.11418 | 0.11963 | 0.12678 | 0.13549 | 0.14764 | 0.16031 | 0.17218 | 0.18335 | 0.19311 | 0.20252 | 0.21066 | 0.21931 | 0.22744 | 0.26948 | 0.29574 | 0.24321 | 0.25225 | 0.26014 | 0.26921 | 0.2806 | 0.29541 | 0.31341 | 0.33928 | 0.36661 | 0.39242 | 0.41695 | 0.4384 | 0.45928 | 0.47694 | 0.49563 | 0.51336 | 0.60594 | 0.66684
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.10167 | 0.10559 | 0.10851 | 0.1116 | 0.11575 | 0.12232 | 0.13123 | 0.1441 | 0.15496 | 0.16733 | 0.17874 | 0.19008 | 0.20089 | 0.21047 | 0.22027 | 0.22852 | 0.26861 | 0.29147 | 0.24245 | 0.25164 | 0.25801 | 0.26473 | 0.2737 | 0.28753 | 0.30717 | 0.33576 | 0.35971 | 0.38712 | 0.41197 | 0.43669 | 0.46028 | 0.48081 | 0.50177 | 0.51962 | 0.60749 | 0.65771
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.1017 | 0.10429 | 0.1068 | 0.11019 | 0.11457 | 0.12036 | 0.12703 | 0.13742 | 0.14743 | 0.15974 | 0.1707 | 0.18063 | 0.19134 | 0.1999 | 0.20863 | 0.215 | 0.24706 | 0.27713 | 0.24239 | 0.24816 | 0.25341 | 0.26041 | 0.26949 | 0.28138 | 0.29507 | 0.31701 | 0.33839 | 0.36502 | 0.38844 | 0.40962 | 0.43228 | 0.45029 | 0.46863 | 0.48228 | 0.55299 | 0.61998
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.26721 | 0.33143 | 0.40844 | 0.49897 | 0.60159 | 0.71547 | 0.84352 | 1.0399 | 1.1981 | 1.3647 | 1.5366 | 1.7166 | 1.9142 | 2.1114 | 2.3014 | 2.488 | 2.9531 | 3.1139 | 0.62039 | 0.75515 | 0.91508 | 1.1027 | 1.315 | 1.5504 | 1.8145 | 2.2159 | 2.541 | 2.8831 | 3.2359 | 3.6035 | 4.0053 | 4.4061 | 4.7917 | 5.1698 | 6.1245 | 6.4668
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.3414 | 0.49393 | 0.6846 | 0.90642 | 1.1586 | 1.4365 | 1.7688 | 2.1717 | 2.5296 | 2.8157 | 2.9548 | 3.0121 | 3.0546 | 3.0938 | 3.1339 | 3.1673 | 3.3002 | 3.4805 | 0.7802 | 1.1005 | 1.4959 | 1.9554 | 2.4771 | 3.0516 | 3.7351 | 4.5601 | 5.2932 | 5.8798 | 6.1728 | 6.2991 | 6.395 | 6.4834 | 6.5737 | 6.65 | 6.9638 | 7.3768
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.31321 | 0.4184 | 0.54366 | 0.68914 | 0.85417 | 1.0438 | 1.2615 | 1.5411 | 1.7834 | 2.0332 | 2.299 | 2.5857 | 2.8736 | 3.1403 | 3.3011 | 3.3587 | 3.5883 | 3.8221 | 0.72961 | 0.9597 | 1.2281 | 1.5391 | 1.8908 | 2.2929 | 2.7513 | 3.3296 | 3.832 | 4.3473 | 4.8936 | 5.4819 | 6.0736 | 6.6218 | 6.9573 | 7.086 | 7.6103 | 8.1495
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.29047 | 0.37616 | 0.48546 | 0.61514 | 0.76394 | 0.93422 | 1.1339 | 1.4143 | 1.6499 | 1.894 | 2.1524 | 2.4133 | 2.6659 | 2.8954 | 3.0285 | 3.0727 | 3.2355 | 3.3761 | 0.67069 | 0.85218 | 1.0809 | 1.3524 | 1.6637 | 2.0193 | 2.4341 | 3.01 | 3.4939 | 3.9924 | 4.5191 | 5.0514 | 5.5663 | 6.0339 | 6.3082 | 6.4044 | 6.7676 | 7.0813
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Counterfactual | 0.67452 | 0.8007 | 1.0314 | 1.189 | 1.3694 | 1.5845 | 1.8378 | 2.2108 | 2.5194 | 2.8448 | 3.1811 | 3.5268 | 3.9091 | 4.2804 | 4.6426 | 4.8171 | 5.7478 | 6.1388 | 1.6051 | 1.869 | 2.3408 | 2.6673 | 3.0401 | 3.4832 | 4.0033 | 4.7637 | 5.3955 | 6.0614 | 6.7488 | 7.453 | 8.2295 | 8.9823 | 9.7157 | 9.981 | 11.8859 | 12.7025
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.80442 | 1.0829 | 1.5111 | 1.8957 | 2.3327 | 2.8206 | 3.4253 | 4.1531 | 4.8086 | 5.3421 | 5.7051 | 5.9351 | 6.1384 | 6.3429 | 6.5569 | 6.5739 | 7.5514 | 8.4104 | 1.8853 | 2.4709 | 3.352 | 4.1487 | 5.0525 | 6.06 | 7.3025 | 8.7909 | 10.1322 | 11.2249 | 11.9765 | 12.4572 | 12.8826 | 13.3094 | 13.755 | 13.7139 | 15.7602 | 17.567
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.75616 | 0.95645 | 1.2686 | 1.5206 | 1.8058 | 2.1393 | 2.5497 | 3.0719 | 3.5304 | 4.0047 | 4.5918 | 5.182 | 5.7736 | 6.3388 | 6.747 | 6.804 | 7.885 | 8.7531 | 1.7992 | 2.2372 | 2.8936 | 3.433 | 4.0414 | 4.7483 | 5.6088 | 6.6867 | 7.6352 | 8.6114 | 9.812 | 11.0187 | 12.2297 | 13.3866 | 14.228 | 14.2747 | 16.5543 | 18.4107
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.71516 | 0.87791 | 1.1648 | 1.3938 | 1.6793 | 2.0116 | 2.4027 | 2.9392 | 3.4016 | 3.8909 | 4.4368 | 4.9677 | 5.499 | 5.9839 | 6.3108 | 6.2993 | 7.078 | 7.6769 | 1.6932 | 2.0374 | 2.629 | 3.1074 | 3.7013 | 4.391 | 5.1988 | 6.2975 | 7.2443 | 8.2413 | 9.3511 | 10.4303 | 11.5094 | 12.4944 | 13.1625 | 13.0617 | 14.687 | 15.9394
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | 0.34742 | 0.48844 | 0.65514 | 0.84075 | 1.0594 | 1.302 | 1.5735 | 1.9828 | 2.3151 | 2.6664 | 3.0301 | 3.4112 | 3.8386 | 4.2499 | 4.6495 | 5.0411 | 6.0766 | 6.509 | 0.7765 | 1.0744 | 1.4208 | 1.8064 | 2.2592 | 2.7609 | 3.3211 | 4.1581 | 4.8412 | 5.5625 | 6.3085 | 7.0871 | 7.9575 | 8.7936 | 9.6048 | 10.3985 | 12.5274 | 13.4378
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | 0.49566 | 0.82295 | 1.2182 | 1.6751 | 2.1887 | 2.7583 | 3.4495 | 4.2756 | 5.0262 | 5.6306 | 5.9532 | 6.1166 | 6.2372 | 6.3509 | 6.482 | 6.5924 | 7.1381 | 7.6565 | 1.0959 | 1.7893 | 2.6108 | 3.5592 | 4.6239 | 5.8033 | 7.228 | 8.9221 | 10.4621 | 11.705 | 12.3845 | 12.7379 | 13.0035 | 13.2541 | 13.5394 | 13.7825 | 15.0021 | 16.157
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | 0.44012 | 0.67967 | 0.95226 | 1.2598 | 1.6074 | 2.0209 | 2.4815 | 3.0813 | 3.5961 | 4.1258 | 4.6992 | 5.3017 | 5.9098 | 6.4713 | 6.8505 | 7.0214 | 7.7683 | 8.4421 | 0.99617 | 1.5264 | 2.1119 | 2.7716 | 3.5146 | 4.392 | 5.363 | 6.6056 | 7.6761 | 8.7701 | 9.9505 | 11.1893 | 12.4419 | 13.5997 | 14.3909 | 14.7655 | 16.418 | 17.9247
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | 0.39509 | 0.58268 | 0.82222 | 1.1051 | 1.4279 | 1.7952 | 2.2313 | 2.8343 | 3.3469 | 3.903 | 4.4778 | 5.0233 | 5.5836 | 6.072 | 6.3921 | 6.5198 | 7.0866 | 7.5755 | 0.87962 | 1.2799 | 1.7805 | 2.372 | 3.0464 | 3.8127 | 4.7176 | 5.9561 | 7.0095 | 8.1462 | 9.3193 | 10.4332 | 11.5751 | 12.572 | 13.2316 | 13.5061 | 14.7317 | 15.7817
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Counterfactual | 0.21174 | 0.27371 | 0.34866 | 0.43722 | 0.53816 | 0.65064 | 0.77781 | 0.97379 | 1.1323 | 1.2997 | 1.4731 | 1.651 | 1.8463 | 2.0358 | 2.2206 | 2.4099 | 2.8842 | 3.0695 | 0.47733 | 0.60729 | 0.76275 | 0.94612 | 1.1547 | 1.3868 | 1.6487 | 2.0489 | 2.3744 | 2.7177 | 3.073 | 3.4357 | 3.8322 | 4.2158 | 4.59 | 4.9732 | 5.9457 | 6.3361
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.28432 | 0.43233 | 0.6205 | 0.83807 | 1.0851 | 1.3564 | 1.6838 | 2.0811 | 2.4337 | 2.7085 | 2.8396 | 2.9004 | 2.9482 | 2.9927 | 3.0394 | 3.0776 | 3.2361 | 3.4146 | 0.63399 | 0.9447 | 1.3347 | 1.7852 | 2.2959 | 2.8562 | 3.5293 | 4.3423 | 5.064 | 5.6263 | 5.9011 | 6.0339 | 6.1405 | 6.2394 | 6.3427 | 6.4287 | 6.7952 | 7.2024
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.25727 | 0.35862 | 0.48168 | 0.62338 | 0.78395 | 0.97077 | 1.1848 | 1.4509 | 1.6794 | 1.9289 | 2.1924 | 2.4648 | 2.7379 | 2.9914 | 3.1508 | 3.2136 | 3.4617 | 3.6943 | 0.58559 | 0.80746 | 1.0711 | 1.3739 | 1.716 | 2.1116 | 2.5618 | 3.1106 | 3.583 | 4.0975 | 4.6394 | 5.1987 | 5.7605 | 6.2821 | 6.6145 | 6.7535 | 7.3142 | 7.8462
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.23444 | 0.3174 | 0.42541 | 0.55492 | 0.70331 | 0.87355 | 1.0743 | 1.3571 | 1.5944 | 1.8399 | 2.0972 | 2.3528 | 2.6085 | 2.8386 | 2.9781 | 3.026 | 3.2092 | 3.3567 | 0.52656 | 0.70219 | 0.92781 | 1.1984 | 1.508 | 1.8627 | 2.2786 | 2.8588 | 3.3452 | 3.8452 | 4.3685 | 4.8887 | 5.4091 | 5.8778 | 6.1647 | 6.2682 | 6.6722 | 6.9983
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | 1.1163 | 1.2193 | 1.359 | 1.4966 | 1.6595 | 1.8398 | 2.046 | 2.3486 | 2.6008 | 2.863 | 3.1398 | 3.4158 | 3.7197 | 4.0164 | 4.2994 | 4.59 | 5.3645 | 5.7529 | 2.7254 | 2.9431 | 3.2315 | 3.5168 | 3.8535 | 4.2254 | 4.6499 | 5.2679 | 5.7853 | 6.323 | 6.8898 | 7.4521 | 8.0691 | 8.67 | 9.2433 | 9.832 | 11.4232 | 12.233
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | 1.217 | 1.4503 | 1.75 | 2.0726 | 2.4428 | 2.8435 | 3.3373 | 3.9244 | 4.4591 | 4.8819 | 5.1507 | 5.329 | 5.4725 | 5.6018 | 5.7424 | 5.8682 | 6.5092 | 7.0687 | 2.9425 | 3.4381 | 4.0595 | 4.7288 | 5.4953 | 6.3242 | 7.3412 | 8.5448 | 9.6404 | 10.5073 | 11.0661 | 11.4408 | 11.7452 | 12.0204 | 12.3181 | 12.5853 | 13.9613 | 15.1628
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | 1.1793 | 1.3528 | 1.563 | 1.7863 | 2.0319 | 2.3347 | 2.6738 | 3.0886 | 3.445 | 3.8392 | 4.2872 | 4.716 | 5.147 | 5.5569 | 5.857 | 6.0277 | 5.9572 | 7.4431 | 2.875 | 3.2606 | 3.7097 | 4.1879 | 4.7126 | 5.3534 | 6.0663 | 6.9222 | 7.6598 | 8.4732 | 9.3931 | 10.2748 | 11.1627 | 12.0072 | 12.6309 | 12.9956 | 12.5533 | 16.0548
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | 1.1482 | 1.2827 | 1.4812 | 1.6899 | 1.9319 | 2.2053 | 2.5314 | 2.9766 | 3.3605 | 3.7667 | 4.1994 | 4.6147 | 5.0467 | 5.4189 | 5.6855 | 5.8184 | 6.4198 | 6.9014 | 2.7944 | 3.0819 | 3.4939 | 3.9289 | 4.4324 | 5.0006 | 5.6749 | 6.5877 | 7.374 | 8.2009 | 9.0803 | 9.9257 | 10.8049 | 11.5637 | 12.1107 | 12.39 | 13.6597 | 14.6748
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.032872 | 0.061682 | 0.11396 | 0.15109 | 0.19382 | 0.24189 | 0.29581 | 0.37763 | 0.4452 | 0.5138 | 0.58507 | 0.65709 | 0.73609 | 0.81284 | 0.88725 | 0.96335 | 1.1716 | 1.2786 | 0.071413 | 0.13284 | 0.23998 | 0.31708 | 0.40569 | 0.50552 | 0.61744 | 0.78534 | 0.92542 | 1.0661 | 1.2123 | 1.3592 | 1.5198 | 1.6755 | 1.8263 | 1.9806 | 2.4084 | 2.6318
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.059656 | 0.12573 | 0.22324 | 0.31465 | 0.42304 | 0.53387 | 0.66233 | 0.81797 | 0.954 | 1.0599 | 1.1166 | 1.1485 | 1.173 | 1.1957 | 1.2192 | 1.2381 | 1.3144 | 1.4007 | 0.12876 | 0.27042 | 0.4716 | 0.66318 | 0.8919 | 1.1228 | 1.3878 | 1.707 | 1.9861 | 2.2033 | 2.3223 | 2.3909 | 2.4446 | 2.4946 | 2.5463 | 2.5885 | 2.7654 | 2.9619
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.049474 | 0.10057 | 0.1779 | 0.2452 | 0.31479 | 0.39331 | 0.48134 | 0.58857 | 0.68002 | 0.77959 | 0.88421 | 0.9894 | 1.0944 | 1.1921 | 1.2587 | 1.2916 | 1.4154 | 1.5386 | 0.11035 | 0.22505 | 0.38949 | 0.53643 | 0.68583 | 0.85259 | 1.0384 | 1.2599 | 1.4495 | 1.6554 | 1.8713 | 2.0883 | 2.3055 | 2.5076 | 2.6473 | 2.7194 | 2.9982 | 3.2766
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.042262 | 0.081076 | 0.14812 | 0.20633 | 0.27728 | 0.35332 | 0.43684 | 0.55361 | 0.65091 | 0.7513 | 0.85536 | 0.95802 | 1.0608 | 1.1527 | 1.2138 | 1.2412 | 1.336 | 1.4317 | 0.091452 | 0.17506 | 0.31336 | 0.43651 | 0.58804 | 0.74842 | 0.92162 | 1.1612 | 1.3607 | 1.5652 | 1.777 | 1.9862 | 2.1958 | 2.3834 | 2.5092 | 2.5675 | 2.7745 | 2.9801
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.61864 | 0.72435 | 0.83927 | 0.96389 | 1.1264 | 1.34 | 1.5791 | 1.9532 | 2.2966 | 2.6366 | 2.9722 | 3.3047 | 3.6812 | 4.0566 | 4.4265 | 4.794 | 5.8747 | 6.5272 | 1.373 | 1.5955 | 1.834 | 2.092 | 2.4315 | 2.8784 | 3.3791 | 4.1633 | 4.9011 | 5.6186 | 6.3206 | 7.0092 | 7.784 | 8.5565 | 9.317 | 10.0721 | 12.3505 | 13.7692
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.73642 | 1.0407 | 1.3986 | 1.7337 | 2.1313 | 2.6027 | 3.1616 | 3.8616 | 4.507 | 5.0705 | 5.4151 | 5.6378 | 5.8698 | 6.0838 | 6.3023 | 6.5143 | 7.6798 | 8.495 | 1.6273 | 2.292 | 3.0613 | 3.7577 | 4.5839 | 5.5617 | 6.7129 | 8.163 | 9.5072 | 10.6912 | 11.4391 | 11.9377 | 12.4581 | 12.9322 | 13.414 | 13.8836 | 16.4486 | 18.3132
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.69309 | 0.97183 | 1.1687 | 1.3963 | 1.6635 | 2.0041 | 2.4145 | 2.9819 | 3.4703 | 4.0177 | 4.5724 | 5.1157 | 5.6699 | 6.179 | 6.5507 | 6.7856 | 8.0135 | 8.8089 | 1.5502 | 2.1939 | 2.6181 | 3.1099 | 3.6825 | 4.4066 | 5.2875 | 6.4983 | 7.5383 | 8.7064 | 9.8773 | 11.0257 | 12.197 | 13.2669 | 14.0605 | 14.5796 | 17.2856 | 19.0661
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.65528 | 0.82362 | 1.1028 | 1.2934 | 1.5337 | 1.8332 | 2.1731 | 2.6682 | 3.1025 | 3.6099 | 4.1223 | 4.6163 | 5.1191 | 5.5786 | 5.8873 | 6.0589 | 6.9595 | 7.7652 | 1.4528 | 1.8202 | 2.4492 | 2.8496 | 3.3549 | 3.9826 | 4.6879 | 5.7178 | 6.6254 | 7.6938 | 8.7624 | 9.7903 | 10.8353 | 11.7867 | 12.4357 | 12.8108 | 14.7973 | 16.6011
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.45724 | 0.49515 | 0.53951 | 0.59066 | 0.65513 | 0.74619 | 0.83084 | 0.96362 | 1.0849 | 1.215 | 1.3409 | 1.4598 | 1.5881 | 1.7165 | 1.8423 | 1.9688 | 2.387 | 2.6743 | 1.0813 | 1.1636 | 1.2593 | 1.3703 | 1.5103 | 1.7057 | 1.8824 | 2.1628 | 2.4248 | 2.7075 | 2.9765 | 3.2265 | 3.4928 | 3.7593 | 4.0205 | 4.2828 | 5.1803 | 5.8155
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.50194 | 0.60147 | 0.72969 | 0.88103 | 1.0637 | 1.2899 | 1.4961 | 1.7566 | 2.0152 | 2.2516 | 2.4228 | 2.5475 | 2.6726 | 2.7805 | 2.8917 | 3.0568 | 3.7148 | 4.0936 | 1.1805 | 1.4 | 1.682 | 2.0154 | 2.4188 | 2.913 | 3.3426 | 3.8888 | 4.4371 | 4.9428 | 5.3194 | 5.5994 | 5.881 | 6.1185 | 6.3624 | 6.7149 | 8.1782 | 9.0605
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.4883 | 0.56682 | 0.6609 | 0.77729 | 0.91461 | 1.102 | 1.287 | 1.5266 | 1.7326 | 1.9672 | 2.1946 | 2.5296 | 2.743 | 2.931 | 3.0792 | 3.2359 | 3.7844 | 4.083 | 1.1562 | 1.3371 | 1.552 | 1.8192 | 2.1333 | 2.5527 | 2.9614 | 3.4857 | 3.9338 | 4.446 | 4.9345 | 5.697 | 6.155 | 6.5532 | 6.8712 | 7.2058 | 8.4157 | 9.0827
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.47605 | 0.54019 | 0.62835 | 0.73343 | 0.86316 | 1.0302 | 1.163 | 1.3452 | 1.5148 | 1.7214 | 1.9182 | 2.1047 | 2.291 | 2.4539 | 2.574 | 2.6762 | 3.1541 | 3.5427 | 1.1247 | 1.2696 | 1.47 | 1.7083 | 2.0033 | 2.3773 | 2.6586 | 3.0433 | 3.4046 | 3.8504 | 4.2687 | 4.6636 | 5.0556 | 5.3954 | 5.6494 | 5.8685 | 6.9491 | 7.8312
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.55382 | 0.6001 | 0.66312 | 0.73204 | 0.80284 | 0.89921 | 1.0026 | 1.1783 | 1.3428 | 1.5183 | 1.6854 | 1.8422 | 2.0051 | 2.1682 | 2.328 | 2.4884 | 3.028 | 3.3933 | 1.1712 | 1.2688 | 1.3996 | 1.5427 | 1.6896 | 1.8882 | 2.1012 | 2.4728 | 2.8283 | 3.2106 | 3.5685 | 3.8986 | 4.2371 | 4.5758 | 4.9076 | 5.2403 | 6.3992 | 7.2093
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.60104 | 0.70815 | 0.84617 | 1.0132 | 1.1881 | 1.4014 | 1.6546 | 2.001 | 2.3453 | 2.6576 | 2.8863 | 3.0545 | 3.2172 | 3.3513 | 3.4886 | 3.6283 | 4.5793 | 5.0578 | 1.2732 | 1.5004 | 1.788 | 2.1409 | 2.5069 | 2.9468 | 3.4667 | 4.1945 | 4.9262 | 5.5955 | 6.0991 | 6.4771 | 6.8443 | 7.1404 | 7.442 | 7.7499 | 9.8023 | 10.9227
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.58355 | 0.66182 | 0.77039 | 0.88246 | 0.99328 | 1.1526 | 1.3787 | 1.7004 | 1.9786 | 2.2897 | 2.5884 | 2.8728 | 3.1484 | 3.3889 | 3.5736 | 3.7018 | 4.5866 | 4.939 | 1.2421 | 1.4151 | 1.6525 | 1.8943 | 2.1313 | 2.4661 | 2.9604 | 3.6661 | 4.272 | 4.9527 | 5.5951 | 6.2071 | 6.7985 | 7.3072 | 7.7036 | 7.9869 | 9.8996 | 10.6907
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.56841 | 0.63176 | 0.71599 | 0.82336 | 0.92936 | 1.0678 | 1.2218 | 1.4645 | 1.6925 | 1.9636 | 2.2203 | 2.4659 | 2.7022 | 2.9094 | 3.0594 | 3.1558 | 3.7824 | 4.2663 | 1.203 | 1.3385 | 1.5156 | 1.7461 | 1.9713 | 2.2598 | 2.5786 | 3.0922 | 3.579 | 4.1655 | 4.7122 | 5.2328 | 5.7305 | 6.1626 | 6.4797 | 6.691 | 8.0671 | 9.1717
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.11286 | 0.17266 | 0.2512 | 0.33134 | 0.41975 | 0.52342 | 0.63534 | 0.80404 | 0.94019 | 1.0869 | 1.2384 | 1.418 | 1.6155 | 1.8239 | 2.0577 | 2.2932 | 3.1314 | 3.7369 | 0.24502 | 0.37253 | 0.53528 | 0.70183 | 0.88536 | 1.0998 | 1.3312 | 1.6766 | 1.957 | 2.2586 | 2.57 | 2.9395 | 3.3448 | 3.7735 | 4.2573 | 4.744 | 6.5025 | 7.7898
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.16759 | 0.3023 | 0.47261 | 0.656 | 0.86018 | 1.0908 | 1.3682 | 1.6954 | 2.0429 | 2.3842 | 2.7456 | 3.1031 | 3.4418 | 3.7775 | 4.1184 | 4.4452 | 6.088 | 6.7293 | 0.36249 | 0.65102 | 1.0048 | 1.3862 | 1.8103 | 2.2883 | 2.8612 | 3.5337 | 4.2548 | 4.9721 | 5.7495 | 6.5267 | 7.2655 | 7.9981 | 8.7409 | 9.4551 | 13.0548 | 14.45
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.14693 | 0.25218 | 0.37012 | 0.49627 | 0.64092 | 0.81295 | 1.0025 | 1.4684 | 1.9054 | 2.3477 | 2.8298 | 3.3252 | 3.8187 | 4.2992 | 4.7127 | 5.0453 | 6.6355 | 7.044 | 0.32531 | 0.56114 | 0.81428 | 1.0856 | 1.3952 | 1.7607 | 2.1611 | 3.156 | 4.0924 | 5.0377 | 6.0621 | 7.1133 | 8.1619 | 9.1837 | 10.0708 | 10.7961 | 14.276 | 15.1645
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.13166 | 0.21117 | 0.32463 | 0.4431 | 0.57748 | 0.73295 | 0.91663 | 1.1637 | 1.409 | 1.7061 | 2.021 | 2.3308 | 2.6433 | 2.9267 | 3.1519 | 3.3007 | 4.008 | 4.6505 | 0.28526 | 0.45647 | 0.69246 | 0.94015 | 1.2208 | 1.5449 | 1.9261 | 2.4339 | 2.9431 | 3.5611 | 4.2152 | 4.8594 | 5.5084 | 6.0986 | 6.5722 | 6.893 | 8.4226 | 9.8134
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | 0.61308 | 0.81302 | 1.0497 | 1.3229 | 1.6351 | 1.9822 | 2.3771 | 2.986 | 3.4773 | 3.9973 | 4.5363 | 5.0936 | 5.7117 | 6.3221 | 6.9095 | 7.4935 | 8.8618 | 9.3454 | 1.3926 | 1.8121 | 2.3029 | 2.8688 | 3.5138 | 4.2302 | 5.0434 | 6.2858 | 7.2934 | 8.3585 | 9.4618 | 10.5987 | 11.8551 | 13.0945 | 14.2856 | 15.4678 | 18.2777 | 19.3033
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | 0.84263 | 1.3141 | 1.898 | 2.5698 | 3.3325 | 4.161 | 5.1711 | 6.3917 | 7.487 | 8.3569 | 8.7782 | 8.9525 | 9.0843 | 9.209 | 9.3435 | 9.4541 | 9.9589 | 10.4746 | 1.8879 | 2.8798 | 4.0907 | 5.4826 | 7.0599 | 8.7722 | 10.8494 | 13.347 | 15.5899 | 17.3751 | 18.2636 | 18.6482 | 18.9442 | 19.2243 | 19.5236 | 19.7741 | 20.9379 | 22.1198
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | 0.75717 | 1.0848 | 1.4673 | 1.9035 | 2.3974 | 2.9719 | 3.6272 | 4.4895 | 5.233 | 5.9969 | 6.8024 | 7.5896 | 8.3804 | 9.1154 | 9.5786 | 9.7561 | 10.4917 | 11.2152 | 1.7353 | 2.4548 | 3.276 | 4.2103 | 5.2642 | 6.4826 | 7.8617 | 9.6465 | 11.1892 | 12.7649 | 14.4218 | 16.0416 | 17.6715 | 19.1869 | 20.1565 | 20.5535 | 22.2256 | 23.8773
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | 0.68351 | 0.94678 | 1.2776 | 1.6718 | 2.1237 | 2.6405 | 3.2562 | 4.1181 | 4.8568 | 5.643 | 6.4513 | 7.2348 | 8.0218 | 8.7197 | 9.1355 | 9.26 | 9.7935 | 10.2566 | 1.5456 | 2.1038 | 2.7954 | 3.6193 | 4.5628 | 5.64 | 6.9156 | 8.6834 | 10.1993 | 11.8053 | 13.4519 | 15.0482 | 16.6513 | 18.0729 | 18.9291 | 19.202 | 20.3825 | 21.4002
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Counterfactual | 0.62181 | 0.78262 | 0.98198 | 1.2021 | 1.4512 | 1.7309 | 2.049 | 2.5438 | 2.9414 | 3.3594 | 3.7898 | 4.2429 | 4.7475 | 5.2427 | 5.7204 | 6.1876 | 7.227 | 7.5032 | 1.3886 | 1.7242 | 2.1366 | 2.592 | 3.1065 | 3.6833 | 4.338 | 5.3479 | 6.1638 | 7.0213 | 7.9028 | 8.8283 | 9.8556 | 10.8617 | 11.8305 | 12.7766 | 14.9144 | 15.5169
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Electric Engagement | 0.81583 | 1.1957 | 1.6773 | 2.2259 | 2.8502 | 3.5317 | 4.3537 | 5.3544 | 6.2445 | 6.958 | 7.2878 | 7.4044 | 7.4884 | 7.5743 | 7.6569 | 7.7364 | 8.0858 | 8.4986 | 1.808 | 2.6025 | 3.6001 | 4.7359 | 6.0261 | 7.4335 | 9.1226 | 11.1696 | 12.9923 | 14.4577 | 15.1562 | 15.4198 | 15.6148 | 15.8122 | 16.0026 | 16.186 | 17.0034 | 17.9555
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Holistic Transition | 0.74364 | 0.99873 | 1.3098 | 1.6585 | 2.0529 | 2.5056 | 3.0301 | 3.7333 | 4.3457 | 4.9609 | 5.6173 | 6.2709 | 6.9314 | 7.5396 | 7.8993 | 8.0153 | 8.5276 | 9.0459 | 1.6797 | 2.2354 | 2.9017 | 3.648 | 4.4891 | 5.4497 | 6.5543 | 8.0126 | 9.2856 | 10.5562 | 11.9066 | 13.2514 | 14.612 | 15.865 | 16.619 | 16.8844 | 18.0684 | 19.2702
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Hydrogen Evolution | 0.68044 | 0.89096 | 1.1612 | 1.4682 | 1.821 | 2.2278 | 2.7108 | 3.3917 | 3.9786 | 4.5944 | 5.2529 | 5.8739 | 6.4864 | 7.0563 | 7.3619 | 7.4478 | 7.7965 | 8.104 | 1.5164 | 1.9604 | 2.5249 | 3.1676 | 3.9052 | 4.7543 | 5.7559 | 7.1538 | 8.3597 | 9.6208 | 10.967 | 12.2314 | 13.4788 | 14.6389 | 15.2692 | 15.4597 | 16.2472 | 16.9416
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.58711 | 0.64406 | 0.70643 | 0.7777 | 0.86289 | 0.96602 | 1.0872 | 1.2778 | 1.4708 | 1.6123 | 1.7635 | 1.9375 | 2.1368 | 2.3274 | 2.5027 | 2.6717 | 3.0915 | 3.2948 | 1.4233 | 1.5425 | 1.6719 | 1.8194 | 1.9965 | 2.2139 | 2.4706 | 2.8702 | 3.2934 | 3.5833 | 3.8949 | 4.2531 | 4.6625 | 5.0531 | 5.4102 | 5.7527 | 6.6176 | 7.0456
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.6481 | 0.7776 | 0.94761 | 1.1411 | 1.3923 | 1.7141 | 2.0279 | 2.4032 | 2.7746 | 3.0532 | 3.2047 | 3.2713 | 3.3179 | 3.4483 | 3.5041 | 3.5539 | 3.8102 | 4.0249 | 1.5547 | 1.8269 | 2.1852 | 2.5925 | 3.1328 | 3.8413 | 4.5033 | 5.2908 | 6.0777 | 6.6586 | 6.9801 | 7.1249 | 7.2276 | 7.5373 | 7.6589 | 7.7682 | 8.3368 | 8.8162
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.62548 | 0.72293 | 0.83575 | 0.98378 | 1.1686 | 1.4649 | 1.7126 | 1.9941 | 2.3942 | 2.6082 | 2.8364 | 3.0511 | 3.2657 | 3.4743 | 3.6171 | 3.6879 | 4.0056 | 4.281 | 1.5144 | 1.728 | 1.9741 | 2.301 | 2.7114 | 3.3803 | 3.9205 | 4.5232 | 5.4397 | 5.8823 | 6.3516 | 6.7939 | 7.2365 | 7.6674 | 7.9666 | 8.1217 | 8.8242 | 9.4373
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.60593 | 0.67922 | 0.78138 | 0.90481 | 1.07 | 1.3198 | 1.539 | 1.8437 | 2.1305 | 2.3952 | 2.6219 | 2.8361 | 3.0561 | 3.3314 | 3.4617 | 3.5084 | 3.7414 | 3.9553 | 1.464 | 1.6191 | 1.8381 | 2.1012 | 2.4633 | 3.0288 | 3.4996 | 4.1457 | 4.7608 | 5.312 | 5.7732 | 6.2091 | 6.6563 | 7.254 | 7.5225 | 7.6236 | 8.1293 | 8.5911
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.71078 | 0.79764 | 0.89916 | 1.0114 | 1.1393 | 1.3096 | 1.5057 | 1.806 | 2.0667 | 2.3397 | 2.6322 | 2.9358 | 3.2619 | 3.572 | 3.8641 | 4.1359 | 4.8817 | 5.2863 | 1.6519 | 1.8345 | 2.046 | 2.2793 | 2.5447 | 2.897 | 3.3035 | 3.9274 | 4.4752 | 5.0518 | 5.6696 | 6.3055 | 6.9838 | 7.6262 | 8.2297 | 8.7897 | 10.3463 | 11.2239
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.79889 | 0.99588 | 1.2432 | 1.5188 | 1.8351 | 2.2419 | 2.7301 | 3.3428 | 3.9177 | 4.422 | 4.7655 | 4.9884 | 5.1912 | 5.3687 | 5.539 | 5.6863 | 6.3053 | 6.8144 | 1.8406 | 2.2536 | 2.7709 | 3.3414 | 3.9961 | 4.8411 | 5.854 | 7.1288 | 8.3323 | 9.3921 | 10.1336 | 10.6247 | 11.0742 | 11.4641 | 11.8373 | 12.1611 | 13.5404 | 14.7077
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.76468 | 0.90551 | 1.0639 | 1.249 | 1.4679 | 1.7667 | 2.1397 | 2.6301 | 3.0693 | 3.5311 | 4.0105 | 4.6102 | 5.14 | 5.6212 | 5.9462 | 6.112 | 6.7738 | 7.2399 | 1.7797 | 2.086 | 2.4248 | 2.8202 | 3.2905 | 3.9286 | 4.731 | 5.7764 | 6.7124 | 7.696 | 8.7056 | 9.9879 | 11.0965 | 12.0984 | 12.7846 | 13.1477 | 14.6116 | 15.6716
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.7396 | 0.85873 | 1.0077 | 1.1688 | 1.3537 | 1.6261 | 1.9241 | 2.3504 | 2.7331 | 3.1431 | 3.5762 | 4.0118 | 4.4212 | 4.7935 | 5.0404 | 5.1676 | 5.6481 | 6.0819 | 1.7137 | 1.9664 | 2.2831 | 2.6211 | 3.009 | 3.5899 | 4.2149 | 5.1078 | 5.9142 | 6.7798 | 7.6898 | 8.6012 | 9.4543 | 10.2267 | 10.7462 | 11.0227 | 12.1006 | 13.0833
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.76278 | 0.96572 | 1.0487 | 1.1451 | 1.2558 | 1.3795 | 1.5171 | 1.7246 | 1.9014 | 2.0803 | 2.2546 | 2.4244 | 2.6207 | 2.8177 | 3.0077 | 3.1986 | 3.6924 | 3.9544 | 1.7808 | 2.1926 | 2.3645 | 2.5641 | 2.7932 | 3.0493 | 3.3339 | 3.763 | 4.1335 | 4.5082 | 4.87 | 5.2171 | 5.6172 | 6.0178 | 6.4046 | 6.7925 | 7.8169 | 8.3818
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.97279 | 1.1245 | 1.3276 | 1.5534 | 1.8105 | 2.0784 | 2.3954 | 2.7803 | 3.1379 | 3.4301 | 3.5825 | 3.664 | 3.7414 | 3.8088 | 3.8774 | 3.9346 | 4.036 | 4.3974 | 2.212 | 2.5315 | 2.9569 | 3.4258 | 3.9594 | 4.5133 | 5.1645 | 5.954 | 6.6907 | 7.2955 | 7.6207 | 7.8024 | 7.9773 | 8.127 | 8.2791 | 8.4061 | 8.5919 | 9.4223
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.94612 | 1.0582 | 1.1827 | 1.32 | 1.4749 | 1.656 | 1.8777 | 2.1797 | 2.4397 | 2.721 | 3.0047 | 3.2965 | 3.5898 | 3.8591 | 4.0354 | 4.121 | 4.3274 | 4.6851 | 2.1643 | 2.4103 | 2.6785 | 2.9723 | 3.3023 | 3.6857 | 4.1557 | 4.7903 | 5.3364 | 5.9264 | 6.5135 | 7.1185 | 7.7287 | 8.2869 | 8.659 | 8.8495 | 9.2689 | 10.0772
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.92381 | 1.0133 | 1.132 | 1.2663 | 1.4149 | 1.5773 | 1.7652 | 2.0441 | 2.2852 | 2.5534 | 2.824 | 3.0913 | 3.356 | 3.5962 | 3.7418 | 3.7974 | 3.8279 | 4.1631 | 2.1067 | 2.2965 | 2.549 | 2.8304 | 3.1412 | 3.4791 | 3.8673 | 4.444 | 4.9422 | 5.4972 | 6.0538 | 6.6027 | 7.1462 | 7.6379 | 7.94 | 8.0603 | 8.0658 | 8.8235
Enderby 132kV | WIGSTON 11kV S STN | Bulk Supply Point | 11 | Counterfactual | 0.67541 | 0.79841 | 0.94159 | 1.1086 | 1.2955 | 1.5101 | 1.75 | 2.105 | 2.4052 | 2.7163 | 3.0263 | 3.3358 | 3.6867 | 4.0293 | 4.3663 | 4.7045 | 5.5257 | 5.8749 | 1.5764 | 1.8334 | 2.1305 | 2.4766 | 2.8636 | 3.3072 | 3.8021 | 4.5291 | 5.1482 | 5.7895 | 6.427 | 7.059 | 7.7734 | 8.4698 | 9.1543 | 9.8411 | 11.5352 | 12.2861
Enderby 132kV | WIGSTON 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | 0.80693 | 1.0796 | 1.4192 | 1.8135 | 2.2637 | 2.7587 | 3.3593 | 4.0582 | 4.6846 | 5.192 | 5.4252 | 5.5378 | 5.6397 | 5.7426 | 5.8485 | 5.9424 | 6.4268 | 6.9024 | 1.8603 | 2.432 | 3.1369 | 3.9553 | 4.8885 | 5.9142 | 7.1534 | 8.5859 | 9.8715 | 10.9164 | 11.4099 | 11.6599 | 11.8895 | 12.1206 | 12.3568 | 12.5684 | 13.6822 | 14.7571
Enderby 132kV | WIGSTON 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | 0.75801 | 0.94733 | 1.1789 | 1.4457 | 1.7454 | 2.0799 | 2.4685 | 2.9771 | 3.4128 | 3.8773 | 4.3665 | 4.9767 | 5.4952 | 5.978 | 6.2907 | 6.4275 | 7.0398 | 7.6064 | 1.7731 | 2.1854 | 2.6816 | 3.2528 | 3.893 | 4.6027 | 5.4227 | 6.4811 | 7.3875 | 8.3522 | 9.3634 | 10.6655 | 11.7384 | 12.7375 | 13.3952 | 13.7002 | 15.0789 | 16.3609
Enderby 132kV | WIGSTON 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | 0.71617 | 0.87194 | 1.0722 | 1.3088 | 1.5787 | 1.8979 | 2.2431 | 2.7226 | 3.1389 | 3.5807 | 4.0438 | 4.4977 | 4.9544 | 5.3722 | 5.623 | 5.7151 | 6.1577 | 6.5715 | 1.6649 | 1.9935 | 2.4126 | 2.9088 | 3.475 | 4.1432 | 4.8595 | 5.8443 | 6.7005 | 7.6068 | 8.5535 | 9.4814 | 10.4153 | 11.2699 | 11.7895 | 11.9913 | 12.9876 | 13.9047
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.8854 | 1.066 | 1.2821 | 1.5232 | 1.797 | 2.1002 | 2.4427 | 2.9828 | 3.4204 | 3.8867 | 4.4123 | 4.946 | 5.5332 | 6.1112 | 6.66 | 7.2099 | 8.5643 | 9.0846 | 1.9896 | 2.3672 | 2.8147 | 3.3136 | 3.8788 | 4.5038 | 5.2083 | 6.3117 | 7.2121 | 8.1718 | 9.266 | 10.3712 | 11.5802 | 12.7639 | 13.8799 | 14.9976 | 17.7998 | 18.9248
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.0971 | 1.52 | 2.0474 | 2.6492 | 3.3331 | 4.0782 | 5.0064 | 6.1574 | 7.3 | 8.1949 | 8.6249 | 8.8433 | 9.0344 | 9.1849 | 9.3347 | 9.4767 | 10.1452 | 10.7872 | 2.4471 | 3.3328 | 4.4254 | 5.6704 | 7.083 | 8.62 | 10.5392 | 12.9169 | 15.3116 | 17.1765 | 18.0939 | 18.5823 | 19.0126 | 19.352 | 19.6885 | 20.0092 | 21.5322 | 22.9949
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.0183 | 1.3035 | 1.6408 | 2.0212 | 2.452 | 2.9809 | 3.6747 | 4.5754 | 5.3428 | 6.1195 | 6.9313 | 7.7268 | 8.5042 | 9.2336 | 9.685 | 9.8731 | 10.7179 | 11.4097 | 2.3066 | 2.9284 | 3.6511 | 4.4642 | 5.3816 | 6.516 | 8.009 | 9.9139 | 11.5358 | 13.1567 | 14.8421 | 16.4866 | 18.0931 | 19.5998 | 20.5488 | 20.9703 | 22.8858 | 24.4705
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.951 | 1.1882 | 1.4858 | 1.8248 | 2.2151 | 2.6602 | 3.2097 | 4.0077 | 4.7573 | 5.5145 | 6.2535 | 6.9888 | 7.7037 | 8.3695 | 8.7528 | 8.893 | 9.5013 | 10.0468 | 2.1327 | 2.6337 | 3.2554 | 3.9641 | 4.7791 | 5.7061 | 6.8531 | 8.5109 | 10.0946 | 11.6734 | 13.1865 | 14.6902 | 16.1508 | 17.5112 | 18.305 | 18.6125 | 19.97 | 21.1931
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.60544 | 0.62928 | 0.65496 | 0.68221 | 0.71652 | 0.76867 | 0.82467 | 0.93921 | 0.70563 | 0.83896 | 0.95637 | 1.0572 | 1.1597 | 1.2625 | 1.3628 | 1.4642 | 1.8532 | 2.1538 | 1.4799 | 1.5306 | 1.584 | 1.6407 | 1.7119 | 1.8193 | 1.9345 | 2.1847 | 1.5723 | 1.876 | 2.1376 | 2.3561 | 2.5737 | 2.7919 | 3.0047 | 3.2198 | 4.0856 | 4.7766
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.63142 | 0.68957 | 0.75555 | 0.8293 | 0.91696 | 1.0331 | 1.1685 | 1.3861 | 1.2702 | 1.49 | 1.6665 | 1.8031 | 1.9423 | 2.0476 | 2.1554 | 2.2661 | 2.8652 | 3.3324 | 1.536 | 1.6606 | 1.7984 | 1.9515 | 2.1335 | 2.3731 | 2.6506 | 3.1206 | 2.761 | 3.2495 | 3.6541 | 3.9728 | 4.2984 | 4.5381 | 4.7822 | 5.0337 | 6.394 | 7.5125
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.6218 | 0.66569 | 0.70773 | 0.75396 | 0.81053 | 0.90083 | 1.0628 | 1.3057 | 1.1586 | 1.3956 | 1.6046 | 1.8044 | 2.0027 | 2.1626 | 2.2931 | 2.3916 | 2.9239 | 3.1931 | 1.5189 | 1.6179 | 1.7089 | 1.8086 | 1.93 | 2.1203 | 2.4869 | 3.0418 | 2.627 | 3.1665 | 3.6317 | 4.0772 | 4.5176 | 4.8645 | 5.1523 | 5.3758 | 6.5845 | 7.1965
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.61336 | 0.64527 | 0.68189 | 0.72293 | 0.77247 | 0.84492 | 0.92848 | 1.0851 | 0.88987 | 1.0929 | 1.2714 | 1.4353 | 1.5962 | 1.7268 | 1.8281 | 1.8982 | 2.3429 | 2.7946 | 1.4971 | 1.5661 | 1.6437 | 1.7295 | 1.8332 | 1.9836 | 2.1566 | 2.4984 | 1.9662 | 2.4233 | 2.8171 | 3.1766 | 3.5252 | 3.8035 | 4.023 | 4.1816 | 5.2053 | 6.2654
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.27434 | 0.37312 | 0.49965 | 0.6233 | 0.76198 | 0.91826 | 1.0961 | 1.3767 | 1.601 | 1.8401 | 2.085 | 2.3457 | 2.6385 | 2.928 | 3.2146 | 3.5049 | 4.2118 | 4.4993 | 0.59358 | 0.80011 | 1.0614 | 1.3172 | 1.6033 | 1.9248 | 2.2895 | 2.8603 | 3.3181 | 3.8058 | 4.3048 | 4.8347 | 5.4281 | 6.0143 | 6.5942 | 7.1818 | 8.6363 | 9.252
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.39114 | 0.62469 | 0.9205 | 1.2396 | 1.597 | 1.9869 | 2.4596 | 3.0385 | 3.5559 | 3.9707 | 4.1744 | 4.2688 | 4.3488 | 4.4351 | 4.519 | 4.6016 | 5.0406 | 5.4969 | 0.84597 | 1.3359 | 1.9475 | 2.6064 | 3.3426 | 4.1445 | 5.112 | 6.291 | 7.3462 | 8.1944 | 8.6198 | 8.8248 | 9.0005 | 9.1893 | 9.3725 | 9.5538 | 10.5246 | 11.5261
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.34865 | 0.50806 | 0.69489 | 0.88672 | 1.1048 | 1.354 | 1.6397 | 2.0439 | 2.3883 | 2.7597 | 3.1791 | 3.6007 | 4.0153 | 4.4094 | 4.6634 | 4.7732 | 5.3227 | 5.8266 | 0.77068 | 1.1193 | 1.519 | 1.9295 | 2.3933 | 2.9194 | 3.5172 | 4.3505 | 5.062 | 5.8269 | 6.6879 | 7.5541 | 8.4061 | 9.2171 | 9.7471 | 9.989 | 11.2063 | 12.3292
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.30978 | 0.44058 | 0.61287 | 0.78827 | 0.98548 | 1.2126 | 1.4871 | 1.8773 | 2.2112 | 2.5699 | 2.9603 | 3.3457 | 3.7232 | 4.077 | 4.2807 | 4.3518 | 4.7122 | 5.0579 | 0.67067 | 0.94736 | 1.3055 | 1.6708 | 2.0808 | 2.5512 | 3.1163 | 3.9119 | 4.593 | 5.3227 | 6.1147 | 6.8968 | 7.6626 | 8.3812 | 8.7993 | 8.9523 | 9.7363 | 10.491
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.61076 | 0.68278 | 0.76903 | 0.86084 | 0.96962 | 1.056 | 1.1537 | 1.3026 | 1.4292 | 1.5656 | 1.7032 | 1.8445 | 1.9943 | 2.131 | 2.2624 | 2.3979 | 2.7397 | 2.8952 | 1.405 | 1.5558 | 1.7355 | 1.9265 | 2.1524 | 2.3304 | 2.5316 | 2.8379 | 3.1006 | 3.3843 | 3.6691 | 3.9599 | 4.2664 | 4.5443 | 4.811 | 5.0863 | 5.7965 | 6.1352
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.66287 | 0.80604 | 0.98126 | 1.1647 | 1.3879 | 1.5861 | 1.8211 | 2.1099 | 2.3757 | 2.5961 | 2.7184 | 2.7883 | 2.8486 | 2.885 | 2.9229 | 2.9608 | 3.2295 | 3.4555 | 1.5177 | 1.8213 | 2.1901 | 2.5727 | 3.0392 | 3.4493 | 3.9325 | 4.527 | 5.0766 | 5.535 | 5.7976 | 5.9538 | 6.0898 | 6.1724 | 6.2576 | 6.3433 | 6.9665 | 7.4769
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.64362 | 0.75159 | 0.87867 | 1.0081 | 1.1662 | 1.2982 | 1.4582 | 1.6779 | 1.8679 | 2.0751 | 2.2932 | 2.5096 | 2.8408 | 3.0179 | 3.1293 | 3.1789 | 3.43 | 3.6351 | 1.4836 | 1.7193 | 1.9943 | 2.2714 | 2.6103 | 2.8903 | 3.2302 | 3.6927 | 4.0926 | 4.5281 | 4.9834 | 5.4353 | 6.1769 | 6.5431 | 6.7775 | 6.8883 | 7.4535 | 7.9166
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.62624 | 0.724 | 0.84543 | 0.96341 | 1.1169 | 1.2421 | 1.3872 | 1.5965 | 1.7775 | 1.9749 | 2.1842 | 2.3873 | 2.5799 | 2.743 | 2.8359 | 2.87 | 3.1131 | 3.2901 | 1.4388 | 1.6486 | 1.9071 | 2.1561 | 2.4809 | 2.7426 | 3.0438 | 3.4761 | 3.8516 | 4.2617 | 4.6935 | 5.1123 | 5.5082 | 5.8405 | 6.0321 | 6.1067 | 6.6646 | 7.0639
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.49253 | 0.71353 | 1.1018 | 1.375 | 1.6467 | 1.9564 | 2.2911 | 2.734 | 3.1155 | 3.519 | 3.8688 | 4.1987 | 4.5658 | 4.9305 | 5.2891 | 5.6521 | 6.67 | 7.027 | 1.1163 | 1.58 | 2.441 | 3.0081 | 3.5724 | 4.2159 | 4.9112 | 5.8248 | 6.6173 | 7.4556 | 8.1777 | 8.8546 | 9.6048 | 10.3497 | 11.0817 | 11.8231 | 13.9432 | 14.7083
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.62228 | 1.1422 | 1.6237 | 2.143 | 2.7012 | 3.3086 | 3.997 | 4.7883 | 5.5204 | 6.142 | 6.4382 | 6.5957 | 6.7431 | 6.8957 | 7.047 | 7.199 | 8.0057 | 8.4794 | 1.3981 | 2.5495 | 3.5628 | 4.6531 | 5.8249 | 7.1002 | 8.535 | 10.1741 | 11.6944 | 12.9919 | 13.6212 | 13.9676 | 14.2931 | 14.6289 | 14.9609 | 15.2955 | 17.0752 | 18.1318
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.70173 | 1.0154 | 1.3921 | 1.7844 | 2.1899 | 2.6522 | 3.1439 | 3.7506 | 4.2945 | 4.8679 | 5.3925 | 5.8959 | 6.3951 | 6.868 | 7.1964 | 7.3751 | 8.2647 | 8.7998 | 1.6301 | 2.3129 | 3.1247 | 3.9672 | 4.8388 | 5.8297 | 6.8774 | 8.1526 | 9.299 | 10.5042 | 11.5942 | 12.6395 | 13.6759 | 14.6588 | 15.3521 | 15.7462 | 17.7156 | 18.9145
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.53497 | 0.94574 | 1.2969 | 1.6705 | 2.0605 | 2.4941 | 2.966 | 3.552 | 4.0824 | 4.6431 | 5.1406 | 5.6131 | 6.083 | 6.5165 | 6.7955 | 6.9285 | 7.6146 | 8.0344 | 1.2102 | 2.1356 | 2.8817 | 3.6751 | 4.5041 | 5.4259 | 6.4213 | 7.6427 | 8.7514 | 9.9206 | 10.9445 | 11.9148 | 12.8794 | 13.7709 | 14.3529 | 14.6438 | 16.1494 | 17.0706
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.11414 | 0.13031 | 0.15006 | 0.19321 | 0.2514 | 0.32215 | 0.38412 | 0.4576 | 0.52902 | 0.60148 | 0.67506 | 0.74135 | 0.77378 | 0.80515 | 0.83518 | 0.86787 | 0.9825 | 1.0655 | 0.26912 | 0.30431 | 0.34869 | 0.44512 | 0.57537 | 0.73093 | 0.86209 | 1.017 | 1.1694 | 1.3233 | 1.4795 | 1.6191 | 1.6853 | 1.7493 | 1.8106 | 1.8772 | 2.1162 | 2.2913
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.12432 | 0.17611 | 0.23537 | 0.33861 | 0.46795 | 0.622 | 0.72673 | 0.83968 | 0.95059 | 1.0526 | 1.1375 | 1.2023 | 1.2237 | 1.2433 | 1.2644 | 1.2823 | 1.3769 | 1.4458 | 0.291 | 0.40981 | 0.54651 | 0.78454 | 1.0815 | 1.4342 | 1.6588 | 1.899 | 2.1357 | 2.3545 | 2.5394 | 2.681 | 2.728 | 2.7705 | 2.8158 | 2.855 | 3.0665 | 3.224
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.12092 | 0.16759 | 0.22724 | 0.31584 | 0.42845 | 0.57334 | 0.66557 | 0.76888 | 0.86363 | 0.96356 | 1.0642 | 1.1547 | 1.2056 | 1.2529 | 1.2913 | 1.3154 | 1.4225 | 1.5009 | 0.28496 | 0.39467 | 0.53724 | 0.74376 | 1.0052 | 1.3401 | 1.5419 | 1.7648 | 1.9695 | 2.1851 | 2.4014 | 2.5949 | 2.7016 | 2.8004 | 2.8812 | 2.9335 | 3.1698 | 3.3428
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.11786 | 0.15974 | 0.2079 | 0.30181 | 0.41972 | 0.56296 | 0.65083 | 0.74982 | 0.84413 | 0.9454 | 1.0447 | 1.1282 | 1.1752 | 1.2137 | 1.245 | 1.2597 | 1.3342 | 1.411 | 0.27711 | 0.37481 | 0.48851 | 0.70704 | 0.98037 | 1.3114 | 1.5014 | 1.7125 | 1.9143 | 2.1309 | 2.3427 | 2.5203 | 2.617 | 2.6963 | 2.761 | 2.7929 | 2.9572 | 3.126
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.34274 | 0.3647 | 0.38911 | 0.41745 | 0.45108 | 0.51346 | 0.57479 | 0.67721 | 0.76982 | 0.86859 | 0.96686 | 1.0583 | 1.1538 | 1.2496 | 1.3432 | 1.4398 | 1.814 | 2.1308 | 0.7409 | 0.78706 | 0.83764 | 0.89615 | 0.96547 | 1.0924 | 1.2169 | 1.4313 | 1.6289 | 1.8426 | 2.0513 | 2.2429 | 2.4401 | 2.6382 | 2.831 | 3.0302 | 3.8221 | 4.5026
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.36732 | 0.41842 | 0.48578 | 0.56117 | 0.64726 | 0.78514 | 0.94297 | 1.1584 | 1.3766 | 1.5855 | 1.7601 | 1.8936 | 2.0243 | 2.245 | 2.3653 | 2.49 | 3.2072 | 3.5333 | 0.79416 | 0.90189 | 1.0423 | 1.1978 | 1.3751 | 1.6561 | 1.9764 | 2.4255 | 2.8848 | 3.3273 | 3.7021 | 3.9917 | 4.2758 | 4.7322 | 4.9874 | 5.2533 | 6.7744 | 7.5231
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.35829 | 0.3954 | 0.43634 | 0.48363 | 0.53691 | 0.64129 | 0.78362 | 0.98036 | 1.1559 | 1.3568 | 1.5588 | 1.7436 | 1.9211 | 2.183 | 2.3159 | 2.4222 | 3.0407 | 3.2913 | 0.77802 | 0.86049 | 0.94801 | 1.0486 | 1.1615 | 1.3767 | 1.6839 | 2.1115 | 2.4893 | 2.924 | 3.3545 | 3.7484 | 4.1253 | 4.6634 | 4.9431 | 5.1701 | 6.4873 | 7.0353
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.3512 | 0.3799 | 0.41856 | 0.46162 | 0.5126 | 0.60179 | 0.69591 | 0.84115 | 0.98227 | 1.1524 | 1.3153 | 1.4717 | 1.621 | 1.8072 | 1.9139 | 1.9963 | 2.4271 | 2.7849 | 0.75939 | 0.82029 | 0.90181 | 0.99107 | 1.0967 | 1.279 | 1.4705 | 1.7738 | 2.0717 | 2.4362 | 2.7798 | 3.1077 | 3.4189 | 3.7998 | 4.0217 | 4.1969 | 5.1268 | 5.9244
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.15811 | 0.17647 | 0.19746 | 0.22037 | 0.24646 | 0.27635 | 0.3099 | 0.37328 | 0.42967 | 0.494 | 0.55425 | 0.61258 | 0.6743 | 0.73591 | 0.79568 | 0.85737 | 1.0556 | 1.1781 | 0.36708 | 0.40553 | 0.44913 | 0.49657 | 0.55046 | 0.61203 | 0.68099 | 0.81471 | 0.9364 | 1.0766 | 1.2055 | 1.3279 | 1.4554 | 1.5828 | 1.7062 | 1.8336 | 2.2598 | 2.5353
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.1799 | 0.2236 | 0.2775 | 0.33783 | 0.40638 | 0.48335 | 0.57708 | 0.70822 | 0.83564 | 0.94711 | 1.0165 | 1.0607 | 1.1014 | 1.1317 | 1.162 | 1.1926 | 1.3583 | 1.5252 | 0.41394 | 0.50546 | 0.61698 | 0.74148 | 0.88258 | 1.0406 | 1.2323 | 1.5069 | 1.7771 | 2.016 | 2.1715 | 2.2746 | 2.3707 | 2.4412 | 2.5111 | 2.5825 | 2.972 | 3.3694
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.17165 | 0.20154 | 0.23595 | 0.27374 | 0.31642 | 0.36727 | 0.44539 | 0.56271 | 0.66009 | 0.77104 | 0.87828 | 0.98952 | 1.0963 | 1.1889 | 1.2524 | 1.2863 | 1.4597 | 1.5733 | 0.3992 | 0.46443 | 0.53806 | 0.61872 | 0.70933 | 0.81626 | 0.98747 | 1.2446 | 1.4569 | 1.6998 | 1.9304 | 2.1686 | 2.3969 | 2.592 | 2.7289 | 2.8063 | 3.2084 | 3.4694
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.16493 | 0.18922 | 0.21898 | 0.25259 | 0.29101 | 0.33619 | 0.39014 | 0.48053 | 0.5631 | 0.66324 | 0.75859 | 0.84988 | 0.9372 | 1.0118 | 1.0593 | 1.0816 | 1.2152 | 1.3661 | 0.38179 | 0.43309 | 0.49519 | 0.56516 | 0.64497 | 0.73847 | 0.84946 | 1.0397 | 1.2151 | 1.431 | 1.6332 | 1.8258 | 2.0089 | 2.1639 | 2.2645 | 2.3155 | 2.6284 | 2.9829
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.2784 | 2.3267 | 2.3957 | 2.4735 | 2.5357 | 2.604 | 2.6783 | 2.8075 | 2.9163 | 3.0367 | 3.154 | 3.2714 | 3.3984 | 3.5249 | 3.6482 | 3.7778 | 4.1497 | 4.3619 | 5.598 | 5.703 | 5.8523 | 6.022 | 6.1506 | 6.2915 | 6.4444 | 6.7137 | 6.9437 | 7.2001 | 7.4466 | 7.69 | 7.9505 | 8.21 | 8.4624 | 8.7285 | 9.5164 | 9.9866
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.3385 | 2.4665 | 2.7324 | 2.9806 | 3.2305 | 3.4839 | 3.7542 | 4.1145 | 4.4755 | 4.7586 | 4.9342 | 5.0739 | 5.2487 | 5.3755 | 5.4413 | 5.5524 | 6.0557 | 6.5079 | 5.7322 | 6.0147 | 6.6257 | 7.1865 | 7.7453 | 8.3055 | 8.8902 | 9.6784 | 10.4782 | 11.1026 | 11.5038 | 11.8383 | 12.2617 | 12.5652 | 12.7154 | 12.9794 | 14.169 | 15.2525
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.3209 | 2.4186 | 2.5851 | 2.7497 | 2.919 | 3.0728 | 3.2335 | 3.4679 | 3.6637 | 3.8723 | 4.0914 | 4.3196 | 4.5456 | 4.7503 | 4.8952 | 4.9806 | 5.4093 | 5.7375 | 5.7008 | 5.9252 | 6.3108 | 6.6892 | 7.0778 | 7.4186 | 7.7689 | 8.2788 | 8.703 | 9.1527 | 9.6231 | 10.1121 | 10.5958 | 11.0312 | 11.3463 | 11.5426 | 12.5337 | 13.298
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.3059 | 2.3925 | 2.522 | 2.6143 | 2.7046 | 2.8031 | 2.9177 | 3.0976 | 3.2583 | 3.4464 | 3.6303 | 3.8072 | 3.9858 | 4.1433 | 4.2437 | 4.2906 | 4.5429 | 4.8144 | 5.6619 | 5.8587 | 6.1518 | 6.3483 | 6.5387 | 6.7431 | 6.9788 | 7.3529 | 7.6896 | 8.0873 | 8.4713 | 8.8394 | 9.2099 | 9.535 | 9.7453 | 9.85 | 10.4238 | 11.0458
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.25171 | 0.39162 | 0.56249 | 0.73806 | 0.92109 | 1.127 | 1.3066 | 1.5803 | 1.8354 | 2.0991 | 2.3691 | 2.6537 | 2.9694 | 3.2454 | 3.515 | 3.7942 | 4.5255 | 4.8826 | 0.54455 | 0.83935 | 1.1945 | 1.5588 | 1.9388 | 2.3668 | 2.7378 | 3.2967 | 3.8246 | 4.3664 | 4.9211 | 5.5037 | 6.1482 | 6.7074 | 7.2536 | 7.8193 | 9.3264 | 10.0837
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.35754 | 0.65392 | 0.98981 | 1.3569 | 1.7795 | 2.2128 | 2.658 | 3.2033 | 3.7386 | 4.1768 | 4.4285 | 4.5787 | 4.7107 | 4.8078 | 4.9029 | 4.9923 | 5.4805 | 5.9442 | 0.77287 | 1.4039 | 2.1051 | 2.8768 | 3.7659 | 4.6683 | 5.5814 | 6.6941 | 7.7944 | 8.6987 | 9.23 | 9.5554 | 9.8441 | 10.0555 | 10.2622 | 10.4583 | 11.5419 | 12.5647
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.31842 | 0.55076 | 0.80092 | 1.0591 | 1.3294 | 1.6356 | 1.9131 | 2.3024 | 2.6746 | 3.0742 | 3.5222 | 3.9699 | 4.4105 | 4.7885 | 5.046 | 5.1713 | 5.7705 | 6.3106 | 0.70311 | 1.2142 | 1.7582 | 2.3182 | 2.8975 | 3.5506 | 4.1325 | 4.9366 | 5.7127 | 6.5429 | 7.4703 | 8.3979 | 9.3116 | 10.0919 | 10.6308 | 10.9055 | 12.2328 | 13.4333
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.28548 | 0.48458 | 0.7045 | 0.94801 | 1.2236 | 1.513 | 1.7797 | 2.1602 | 2.5304 | 2.926 | 3.3476 | 3.76 | 4.1677 | 4.5039 | 4.714 | 4.796 | 5.1971 | 5.594 | 0.61764 | 1.0447 | 1.5075 | 2.0259 | 2.613 | 3.2236 | 3.7729 | 4.5496 | 5.3119 | 6.1241 | 6.9876 | 7.8325 | 8.6679 | 9.3524 | 9.7845 | 9.9607 | 10.8341 | 11.6956
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.3717 | 2.1902 | 2.3408 | 2.5021 | 2.6689 | 2.8645 | 3.0718 | 3.3662 | 3.5819 | 3.8749 | 4.1825 | 4.4822 | 4.7955 | 5.1082 | 5.4472 | 5.6506 | 6.2381 | 6.6778 | 3.2667 | 5.1201 | 5.4348 | 5.7705 | 6.1178 | 6.5239 | 6.9547 | 7.5716 | 8.0307 | 8.6681 | 9.3211 | 9.9518 | 10.606 | 11.259 | 11.9688 | 12.3868 | 13.6066 | 14.5655
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.4377 | 2.3504 | 2.6465 | 2.9424 | 3.2619 | 3.7593 | 4.2547 | 4.8432 | 5.3383 | 5.7851 | 6.1139 | 6.3199 | 6.536 | 6.7549 | 6.9715 | 7.109 | 7.6662 | 8.0001 | 3.409 | 5.4652 | 6.0905 | 6.712 | 7.3828 | 8.4585 | 9.498 | 10.7404 | 11.7867 | 12.7382 | 13.4551 | 13.8995 | 14.3744 | 14.855 | 15.329 | 15.6319 | 16.8108 | 17.5643
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.4136 | 1.9032 | 2.1592 | 2.4389 | 2.7933 | 3.1502 | 3.5336 | 4.0068 | 4.3773 | 4.786 | 5.1948 | 5.5909 | 5.9759 | 6.3267 | 6.6229 | 6.76 | 7.4593 | 7.8484 | 3.3661 | 4.3805 | 4.9329 | 5.5342 | 6.3184 | 7.0834 | 7.9038 | 8.921 | 9.7189 | 10.6015 | 11.4741 | 12.3194 | 13.1398 | 13.8808 | 14.5298 | 14.8305 | 16.3779 | 17.2517
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.3924 | 2.265 | 2.5062 | 2.7342 | 2.9932 | 3.3248 | 3.7661 | 4.2076 | 4.5478 | 4.9359 | 5.3148 | 5.6535 | 5.9872 | 6.2961 | 6.5195 | 6.6167 | 7.3509 | 7.8315 | 3.3114 | 5.286 | 5.8008 | 6.2848 | 6.8364 | 7.543 | 8.5066 | 9.4429 | 10.1636 | 10.9927 | 11.7932 | 12.4961 | 13.1872 | 13.8273 | 14.2988 | 14.5104 | 16.2092 | 17.2999
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.21046 | 0.2442 | 0.28956 | 0.35066 | 0.4336 | 0.52732 | 0.62406 | 0.69686 | 0.77326 | 0.84919 | 0.94478 | 1.0392 | 1.1225 | 1.1968 | 1.2491 | 1.2685 | 1.3595 | 1.4526 | 0.49965 | 0.57383 | 0.67278 | 0.80235 | 0.98539 | 1.1936 | 1.4106 | 1.5689 | 1.7369 | 1.9029 | 2.1174 | 2.3287 | 2.5108 | 2.6718 | 2.7828 | 2.8223 | 3.0109 | 3.2024
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.22206 | 0.28247 | 0.3658 | 0.5685 | 0.74709 | 0.92981 | 1.0595 | 1.2047 | 1.3816 | 1.4991 | 1.6058 | 1.6907 | 1.7719 | 1.8526 | 1.924 | 1.9449 | 2.0647 | 2.1203 | 0.52801 | 0.66802 | 0.85867 | 1.3392 | 1.7579 | 2.1852 | 2.4797 | 2.8137 | 3.2251 | 3.4897 | 3.7282 | 3.912 | 4.0885 | 4.2638 | 4.4174 | 4.4615 | 4.7195 | 4.8426
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.22161 | 0.28249 | 0.47255 | 0.65311 | 0.81009 | 0.94816 | 1.1027 | 1.2539 | 1.3755 | 1.488 | 1.5745 | 1.6609 | 1.7469 | 1.8317 | 1.9099 | 1.9376 | 2.0599 | 2.1407 | 0.52717 | 0.66922 | 1.1279 | 1.554 | 1.9202 | 2.2349 | 2.5942 | 2.9435 | 3.2204 | 3.4731 | 3.6607 | 3.8483 | 4.0351 | 4.2194 | 4.3876 | 4.446 | 4.707 | 4.8791
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.22175 | 0.27815 | 0.35862 | 0.56069 | 0.7399 | 0.92676 | 1.0488 | 1.1921 | 1.3633 | 1.4993 | 1.6099 | 1.694 | 1.7853 | 1.8644 | 1.9383 | 1.9545 | 2.0418 | 2.1157 | 0.52731 | 0.65801 | 0.84249 | 1.3197 | 1.7387 | 2.1754 | 2.4514 | 2.7786 | 3.1762 | 3.4825 | 3.7275 | 3.9092 | 4.1054 | 4.2769 | 4.4354 | 4.4698 | 4.656 | 4.8124
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Counterfactual | 2.31 | 2.494 | 2.6204 | 2.7814 | 2.9526 | 3.1683 | 3.4731 | 3.8404 | 4.3125 | 4.5813 | 4.8656 | 5.1515 | 5.4056 | 5.6567 | 5.8899 | 6.1248 | 6.8782 | 7.389 | 5.6643 | 6.0479 | 6.3178 | 6.6629 | 7.0292 | 7.4943 | 8.1792 | 8.9848 | 10.0707 | 10.6595 | 11.2805 | 11.8996 | 12.426 | 12.9447 | 13.424 | 13.9065 | 15.4941 | 16.5968
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.3936 | 2.7456 | 3.0272 | 3.5285 | 4.1815 | 4.8251 | 5.4376 | 6.1111 | 6.7096 | 7.1706 | 7.4726 | 7.6338 | 7.7889 | 7.9247 | 8.06 | 8.193 | 8.7801 | 9.2487 | 5.8483 | 6.6179 | 7.2246 | 8.3643 | 9.8715 | 11.3337 | 12.6905 | 14.1631 | 15.4639 | 16.4647 | 17.1376 | 17.4963 | 17.8451 | 18.1454 | 18.444 | 18.7401 | 20.0066 | 21.0579
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.3668 | 2.672 | 3.0484 | 3.5563 | 3.8608 | 4.3594 | 4.8928 | 5.4704 | 5.9571 | 6.4171 | 6.7732 | 7.0956 | 7.4282 | 7.7388 | 7.9675 | 8.1012 | 8.7595 | 9.6902 | 5.8007 | 6.4816 | 7.3618 | 8.5581 | 9.2439 | 10.3837 | 11.6006 | 12.8927 | 13.9769 | 14.9992 | 15.7519 | 16.4149 | 17.1046 | 17.7466 | 18.2256 | 18.5146 | 19.933 | 22.1134
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.3443 | 2.63 | 2.8337 | 3.2378 | 3.7682 | 4.3126 | 4.9103 | 5.4917 | 5.9936 | 6.4706 | 6.8956 | 7.2186 | 7.5529 | 7.8448 | 8.0506 | 8.1648 | 9.6058 | 10.1749 | 5.7423 | 6.3738 | 6.821 | 7.7553 | 8.999 | 10.2581 | 11.639 | 12.9327 | 14.0457 | 15.0956 | 16.0166 | 16.6886 | 17.3816 | 17.9851 | 18.4157 | 18.6653 | 22.0971 | 23.3747
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.12615 | 0.14508 | 0.1667 | 0.19036 | 0.21702 | 0.25259 | 0.29149 | 0.36838 | 0.43956 | 0.52081 | 0.59544 | 0.66317 | 0.73242 | 0.80214 | 0.87023 | 0.9397 | 1.1757 | 1.3396 | 0.28936 | 0.32896 | 0.37375 | 0.42269 | 0.47769 | 0.5505 | 0.62996 | 0.79389 | 0.94957 | 1.1296 | 1.2915 | 1.4352 | 1.5795 | 1.7248 | 1.8666 | 2.0112 | 2.5261 | 2.898
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.14838 | 0.19282 | 0.24755 | 0.309 | 0.37851 | 0.46469 | 0.56821 | 0.7213 | 0.87481 | 1.0141 | 1.1151 | 1.1862 | 1.256 | 1.3105 | 1.3646 | 1.4211 | 1.7261 | 1.9579 | 0.33732 | 0.43061 | 0.54381 | 0.67066 | 0.81373 | 0.99022 | 1.2014 | 1.5255 | 1.8554 | 2.1585 | 2.386 | 2.5507 | 2.7129 | 2.8359 | 2.9579 | 3.0862 | 3.7784 | 4.3335
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.14013 | 0.1706 | 0.20534 | 0.24316 | 0.28551 | 0.34463 | 0.44411 | 0.59291 | 0.71684 | 0.8594 | 0.99314 | 1.1196 | 1.2404 | 1.3432 | 1.4191 | 1.4701 | 1.7427 | 1.8788 | 0.32262 | 0.38935 | 0.46374 | 0.54449 | 0.63438 | 0.75788 | 0.97857 | 1.3106 | 1.5848 | 1.9023 | 2.1944 | 2.4705 | 2.7336 | 2.9525 | 3.1174 | 3.2324 | 3.8515 | 4.1617
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.13292 | 0.15746 | 0.18744 | 0.22132 | 0.25983 | 0.31161 | 0.37162 | 0.47643 | 0.5757 | 0.70026 | 0.81503 | 0.92341 | 1.0253 | 1.1133 | 1.1731 | 1.21 | 1.4247 | 1.6477 | 0.30407 | 0.35592 | 0.4184 | 0.48893 | 0.56883 | 0.67543 | 0.79845 | 1.0215 | 1.2356 | 1.5093 | 1.7566 | 1.9885 | 2.2048 | 2.3888 | 2.5162 | 2.5993 | 3.0947 | 3.6177
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.68501 | 0.78199 | 1.0399 | 1.2182 | 1.4162 | 1.6657 | 1.9124 | 2.2555 | 2.586 | 2.9703 | 3.2525 | 3.5103 | 3.7517 | 3.9891 | 4.2158 | 4.4567 | 5.2134 | 5.7191 | 1.6104 | 1.8136 | 2.3412 | 2.7116 | 3.1245 | 3.6457 | 4.1622 | 4.8929 | 5.6206 | 6.4841 | 7.0933 | 7.6402 | 8.1437 | 8.6375 | 9.1063 | 9.6048 | 11.2348 | 12.3672
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.76287 | 1.079 | 1.3665 | 1.7574 | 2.194 | 2.7801 | 3.3092 | 3.9696 | 4.6086 | 5.1168 | 5.4467 | 5.6708 | 5.8724 | 6.0361 | 6.2036 | 6.3749 | 7.34 | 8.0501 | 1.7785 | 2.433 | 3.0372 | 3.8788 | 4.8176 | 6.1053 | 7.2297 | 8.6535 | 10.0424 | 11.1405 | 11.8737 | 12.3858 | 12.8508 | 13.2186 | 13.5928 | 13.9783 | 16.1549 | 17.8281
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.73362 | 0.99936 | 1.2644 | 1.5597 | 1.9638 | 2.3714 | 2.8729 | 3.4704 | 3.94 | 4.4327 | 4.8813 | 5.3189 | 5.8026 | 6.1572 | 6.4181 | 6.586 | 7.4699 | 7.9721 | 1.7263 | 2.2848 | 2.872 | 3.5175 | 4.427 | 5.3198 | 6.4449 | 7.7761 | 8.8074 | 9.8889 | 10.8571 | 11.8009 | 12.8659 | 13.6149 | 14.1753 | 14.5504 | 16.5335 | 17.6655
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.70849 | 0.95499 | 1.1555 | 1.4543 | 1.78 | 2.1408 | 2.6005 | 3.0988 | 3.5741 | 4.0495 | 4.4471 | 4.8165 | 5.1591 | 5.4583 | 5.6656 | 5.7833 | 6.5016 | 7.1982 | 1.6614 | 2.1716 | 2.5975 | 3.2496 | 3.9611 | 4.7422 | 5.7661 | 6.852 | 7.9006 | 8.941 | 9.7886 | 10.5723 | 11.2922 | 11.9144 | 12.3519 | 12.6144 | 14.2513 | 15.8565
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.22304 | 0.25858 | 0.30238 | 0.35338 | 0.41001 | 0.47472 | 0.54598 | 0.65153 | 0.73846 | 0.83606 | 0.93001 | 1.0212 | 1.119 | 1.2159 | 1.3098 | 1.4094 | 1.7042 | 1.89 | 0.47451 | 0.54898 | 0.63987 | 0.74542 | 0.86251 | 0.99601 | 1.1429 | 1.3635 | 1.5486 | 1.7582 | 1.9568 | 2.1466 | 2.3474 | 2.5466 | 2.7395 | 2.9443 | 3.572 | 3.9828
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.25611 | 0.334 | 0.43467 | 0.55052 | 0.68026 | 0.82756 | 0.9755 | 1.1747 | 1.367 | 1.5319 | 1.6338 | 1.6983 | 1.7613 | 1.8117 | 1.8642 | 1.9156 | 2.1861 | 2.4198 | 0.54583 | 0.70991 | 0.9196 | 1.1606 | 1.4303 | 1.7365 | 2.0387 | 2.4534 | 2.858 | 3.2085 | 3.4341 | 3.5819 | 3.7277 | 3.8418 | 3.9599 | 4.0768 | 4.6946 | 5.2445
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.24392 | 0.30009 | 0.36978 | 0.44951 | 0.53805 | 0.64699 | 0.76341 | 0.93514 | 1.078 | 1.2389 | 1.3953 | 1.5486 | 1.6993 | 1.832 | 1.928 | 1.9845 | 2.2648 | 2.4484 | 0.52415 | 0.64685 | 0.79638 | 0.96695 | 1.1561 | 1.3873 | 1.6399 | 2.0124 | 2.3208 | 2.6697 | 3.0033 | 3.3309 | 3.652 | 3.9314 | 4.1368 | 4.2637 | 4.8989 | 5.3139
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.23313 | 0.27882 | 0.33894 | 0.41062 | 0.49117 | 0.58597 | 0.69484 | 0.84369 | 0.97253 | 1.1265 | 1.2736 | 1.412 | 1.5516 | 1.6712 | 1.7525 | 1.7923 | 2.011 | 2.2358 | 0.49641 | 0.59345 | 0.71963 | 0.8698 | 1.0386 | 1.2368 | 1.4631 | 1.7745 | 2.0457 | 2.3736 | 2.6826 | 2.9723 | 3.2629 | 3.5102 | 3.6807 | 3.7695 | 4.2668 | 4.7844
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.71554 | 0.73729 | 0.76429 | 0.78742 | 0.80927 | 0.84171 | 0.8873 | 0.94932 | 1.0145 | 1.0603 | 1.1046 | 1.1478 | 1.1982 | 1.2451 | 1.2876 | 1.3336 | 1.5122 | 1.6716 | 1.4655 | 1.5161 | 1.5794 | 1.6311 | 1.678 | 1.7484 | 1.8507 | 1.9883 | 2.1366 | 2.2353 | 2.3291 | 2.4188 | 2.5235 | 2.6207 | 2.7082 | 2.8026 | 3.1792 | 3.5183
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.73648 | 0.82728 | 0.90261 | 1.0136 | 1.1811 | 1.3215 | 1.3951 | 1.4895 | 1.5827 | 1.6692 | 1.7416 | 1.7995 | 1.8517 | 1.8975 | 1.9477 | 1.9932 | 2.2335 | 2.3735 | 1.5145 | 1.7331 | 1.9081 | 2.1704 | 2.5716 | 2.8995 | 3.0537 | 3.2542 | 3.4515 | 3.6365 | 3.794 | 3.9203 | 4.0354 | 4.1341 | 4.2416 | 4.3402 | 4.8665 | 5.1899
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.73336 | 0.81902 | 0.97865 | 1.0934 | 1.1825 | 1.2365 | 1.3098 | 1.4089 | 1.4791 | 1.5602 | 1.6396 | 1.7152 | 1.7886 | 1.8544 | 1.9184 | 1.9681 | 2.2008 | 2.3253 | 1.509 | 1.7187 | 2.11 | 2.3881 | 2.6004 | 2.7167 | 2.8785 | 3.0963 | 3.2481 | 3.4243 | 3.5945 | 3.7571 | 3.9146 | 4.0537 | 4.1891 | 4.2959 | 4.8023 | 5.0736
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.73038 | 0.81042 | 0.87364 | 0.96664 | 1.1109 | 1.2674 | 1.3205 | 1.4019 | 1.4744 | 1.5639 | 1.6406 | 1.7092 | 1.783 | 1.8395 | 1.8945 | 1.9288 | 2.1035 | 2.256 | 1.5014 | 1.697 | 1.847 | 2.0678 | 2.4148 | 2.7881 | 2.8994 | 3.072 | 3.2249 | 3.4156 | 3.577 | 3.7214 | 3.8754 | 3.993 | 4.1074 | 4.1812 | 4.5648 | 4.9056
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.55214 | 0.70611 | 0.89991 | 1.1601 | 1.4698 | 1.812 | 2.1889 | 2.9325 | 3.1951 | 3.4073 | 3.6344 | 3.872 | 4.1395 | 4.4012 | 4.6545 | 4.9118 | 5.5715 | 5.8482 | 1.2114 | 1.5346 | 1.9377 | 2.4785 | 3.1237 | 3.8378 | 4.6253 | 6.1832 | 6.727 | 7.163 | 7.6307 | 8.118 | 8.6638 | 9.1962 | 9.7099 | 10.2318 | 11.5956 | 12.1954
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.65905 | 0.96878 | 1.3742 | 1.8551 | 2.4638 | 3.2721 | 4.0233 | 4.8185 | 5.3478 | 5.7364 | 5.925 | 6.0138 | 6.0879 | 6.162 | 6.237 | 6.3153 | 6.7367 | 7.1823 | 1.4428 | 2.0993 | 2.9524 | 3.9642 | 5.253 | 6.98 | 8.5716 | 10.2401 | 11.3359 | 12.1336 | 12.5307 | 12.7265 | 12.8921 | 13.057 | 13.2229 | 13.3963 | 14.3356 | 15.3253
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.62001 | 0.86267 | 1.1817 | 1.6239 | 2.1609 | 2.7329 | 3.3211 | 3.9581 | 4.3224 | 4.6704 | 5.058 | 5.4686 | 5.8719 | 6.2521 | 6.4907 | 6.5968 | 7.1191 | 7.5765 | 1.3733 | 1.9012 | 2.5867 | 3.5376 | 4.6978 | 5.9405 | 7.2113 | 8.567 | 9.3289 | 10.0493 | 10.8479 | 11.6934 | 12.5236 | 13.3063 | 13.8053 | 14.0393 | 15.2029 | 16.2307
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.58623 | 0.80504 | 1.1058 | 1.5301 | 2.047 | 2.5825 | 3.145 | 3.7576 | 4.1162 | 4.4463 | 4.7966 | 5.145 | 5.4828 | 5.8003 | 5.9772 | 6.042 | 6.3831 | 6.733 | 1.286 | 1.7544 | 2.393 | 3.2976 | 4.4075 | 5.5593 | 6.7655 | 8.0619 | 8.8095 | 9.4867 | 10.2001 | 10.9093 | 11.5965 | 12.2426 | 12.607 | 12.7476 | 13.4987 | 14.2716
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.85775 | 0.87434 | 0.89291 | 0.91455 | 0.93945 | 0.97694 | 1.0164 | 1.0822 | 1.1423 | 1.2083 | 1.2731 | 1.3791 | 1.5081 | 1.7639 | 2.0263 | 2.1724 | 2.3824 | 2.5345 | 2.123 | 2.1584 | 2.1972 | 2.2422 | 2.2939 | 2.3708 | 2.4518 | 2.5908 | 2.7205 | 2.8645 | 3.0038 | 3.2293 | 3.5024 | 4.0474 | 4.6312 | 4.9706 | 5.4201 | 5.7531
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.87412 | 0.91248 | 0.95832 | 1.0107 | 1.0698 | 1.1521 | 1.2527 | 1.4013 | 1.5558 | 1.7919 | 2.1062 | 2.2972 | 2.4848 | 2.6581 | 2.7128 | 2.763 | 3.0942 | 3.2784 | 2.1583 | 2.2407 | 2.3364 | 2.4454 | 2.5683 | 2.738 | 2.9458 | 3.2605 | 3.5909 | 4.1238 | 4.853 | 5.2779 | 5.6956 | 6.0744 | 6.1903 | 6.2954 | 7.0122 | 7.441
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.86816 | 0.89603 | 0.92755 | 0.9655 | 1.0293 | 1.1426 | 1.2887 | 1.4577 | 1.6867 | 2.0262 | 2.2002 | 2.3699 | 2.536 | 2.6499 | 2.726 | 2.7817 | 3.0767 | 3.2203 | 2.1477 | 2.2106 | 2.2788 | 2.3607 | 2.4985 | 2.7423 | 3.0628 | 3.4307 | 3.9524 | 4.7465 | 5.1239 | 5.4939 | 5.8543 | 6.0967 | 6.2589 | 6.3801 | 7.0224 | 7.3407
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.86274 | 0.88452 | 0.91096 | 0.94311 | 0.97959 | 1.0337 | 1.1111 | 1.2294 | 1.3628 | 1.5916 | 1.8983 | 2.1491 | 2.3467 | 2.4989 | 2.5605 | 2.5998 | 2.8213 | 3.0174 | 2.1338 | 2.1809 | 2.2366 | 2.3041 | 2.3805 | 2.4927 | 2.6555 | 2.9086 | 3.197 | 3.7061 | 4.41 | 4.9764 | 5.4077 | 5.7348 | 5.864 | 5.9489 | 6.4364 | 6.8781
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.097814 | 0.11522 | 0.13561 | 0.16035 | 0.18856 | 0.23188 | 0.28313 | 0.3743 | 0.4514 | 0.53344 | 0.61657 | 0.69411 | 0.77852 | 0.86395 | 0.94731 | 1.0347 | 1.3311 | 1.5345 | 0.22063 | 0.25733 | 0.29962 | 0.3507 | 0.40884 | 0.4974 | 0.60188 | 0.78938 | 0.94994 | 1.122 | 1.2944 | 1.4533 | 1.625 | 1.7988 | 1.9683 | 2.1465 | 2.7606 | 3.1802
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.11496 | 0.1549 | 0.20653 | 0.27225 | 0.35823 | 0.47175 | 0.60228 | 0.76787 | 0.91915 | 1.053 | 1.1535 | 1.2277 | 1.2942 | 1.3526 | 1.4177 | 1.4803 | 1.806 | 1.9452 | 0.25766 | 0.34233 | 0.44937 | 0.58499 | 0.76149 | 0.99347 | 1.2594 | 1.5998 | 1.9128 | 2.1912 | 2.4032 | 2.5616 | 2.7044 | 2.8277 | 2.9655 | 3.0985 | 3.7912 | 4.1052
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.10815 | 0.13448 | 0.16873 | 0.20683 | 0.24657 | 0.31993 | 0.41365 | 0.54708 | 0.66244 | 0.78929 | 0.9166 | 1.0343 | 1.1486 | 1.2551 | 1.3415 | 1.4032 | 1.6973 | 1.8139 | 0.24546 | 0.30404 | 0.37748 | 0.45892 | 0.54337 | 0.69481 | 0.8926 | 1.1746 | 1.4176 | 1.6856 | 1.9514 | 2.1974 | 2.4362 | 2.6567 | 2.8373 | 2.9686 | 3.5977 | 3.8496
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.10328 | 0.12614 | 0.15677 | 0.19324 | 0.24739 | 0.32992 | 0.41763 | 0.54496 | 0.65758 | 0.78596 | 0.91373 | 1.0368 | 1.1577 | 1.2669 | 1.3578 | 1.4224 | 1.6827 | 1.834 | 0.23247 | 0.28132 | 0.34526 | 0.42129 | 0.53308 | 0.70207 | 0.88073 | 1.1418 | 1.374 | 1.6409 | 1.904 | 2.1567 | 2.4039 | 2.6261 | 2.8129 | 2.9471 | 3.5004 | 3.8305
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.1298 | 1.228 | 1.3488 | 1.5021 | 1.6645 | 1.8465 | 2.0422 | 2.318 | 2.5137 | 2.7035 | 2.8776 | 3.0515 | 3.2443 | 3.4369 | 3.6918 | 3.965 | 4.4658 | 4.7586 | 2.3442 | 2.5504 | 2.8017 | 3.1197 | 3.457 | 3.8348 | 4.2407 | 4.8123 | 5.22 | 5.6158 | 5.9751 | 6.3313 | 6.724 | 7.1159 | 7.6651 | 8.2587 | 9.3025 | 9.9365
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.2047 | 1.3988 | 1.649 | 1.9447 | 2.2707 | 2.6305 | 3.0365 | 3.5207 | 3.9202 | 4.3457 | 4.6357 | 4.7149 | 4.7877 | 4.851 | 4.916 | 4.9809 | 5.3198 | 5.6544 | 2.5067 | 2.9181 | 3.4452 | 4.0645 | 4.7479 | 5.502 | 6.3473 | 7.3548 | 8.1845 | 9.1167 | 9.7865 | 9.9644 | 10.1296 | 10.2716 | 10.4167 | 10.5627 | 11.3288 | 12.0985
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.1776 | 1.3251 | 1.5076 | 1.7286 | 1.9639 | 2.229 | 2.5346 | 2.9203 | 3.3282 | 3.8036 | 4.091 | 4.3615 | 4.624 | 4.8654 | 5.0243 | 5.1016 | 5.4846 | 5.8182 | 2.4585 | 2.7811 | 3.1732 | 3.6477 | 4.1544 | 4.7219 | 5.3779 | 6.198 | 7.104 | 8.1762 | 8.7761 | 9.3407 | 9.8881 | 10.3895 | 10.7257 | 10.8989 | 11.7641 | 12.5207
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.1548 | 1.284 | 1.4526 | 1.6597 | 1.8827 | 2.1353 | 2.4106 | 2.7709 | 3.0492 | 3.379 | 3.7834 | 4.1021 | 4.3515 | 4.58 | 4.7167 | 4.7713 | 5.0383 | 5.3557 | 2.3995 | 2.6757 | 3.0322 | 3.4708 | 3.9441 | 4.4797 | 5.0592 | 5.8129 | 6.3931 | 7.0999 | 7.9919 | 8.6726 | 9.1831 | 9.6495 | 9.9324 | 10.052 | 10.6513 | 11.3663
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.1718 | 2.5053 | 2.778 | 3.0699 | 3.3959 | 3.7808 | 4.2051 | 4.8223 | 5.3229 | 5.8591 | 6.3865 | 6.9791 | 7.3837 | 8.0545 | 8.7836 | 9.5533 | 11.1719 | 11.9555 | 4.8669 | 5.5549 | 6.1212 | 6.7258 | 7.3998 | 8.1951 | 9.0702 | 10.3356 | 11.3709 | 12.4818 | 13.567 | 14.7834 | 15.4888 | 16.8597 | 18.3904 | 20.0271 | 23.4045 | 25.0972
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.5187 | 3.0245 | 3.6827 | 4.404 | 5.2211 | 6.1125 | 7.1487 | 8.4215 | 9.6219 | 10.6918 | 11.3522 | 11.6522 | 11.4338 | 11.6947 | 11.9451 | 12.1986 | 13.1527 | 14.1519 | 5.5973 | 6.6621 | 8.04 | 9.5457 | 11.2477 | 13.1019 | 15.2394 | 17.8628 | 20.3535 | 22.6094 | 24.0765 | 24.7708 | 24.1788 | 24.7869 | 25.3647 | 25.9566 | 28.1533 | 30.4475
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.4326 | 2.7899 | 3.2427 | 3.7152 | 4.2368 | 4.9113 | 5.7154 | 6.6819 | 7.5207 | 8.515 | 9.4224 | 10.358 | 10.7585 | 11.6312 | 12.22 | 12.4774 | 13.6757 | 14.7267 | 5.4441 | 6.2266 | 7.2054 | 8.2233 | 9.3427 | 10.7842 | 12.5002 | 14.5319 | 16.3127 | 18.4583 | 20.3672 | 22.3377 | 22.973 | 24.8103 | 26.0779 | 26.6557 | 29.3751 | 31.7641
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.358 | 2.6549 | 3.0374 | 3.4475 | 3.913 | 4.4639 | 5.1126 | 6.0309 | 6.855 | 7.769 | 8.6892 | 9.5858 | 10.1782 | 10.9705 | 11.4662 | 11.7003 | 12.5062 | 13.3731 | 5.2514 | 5.8816 | 6.6846 | 7.5432 | 8.5165 | 9.6684 | 11.0161 | 12.9126 | 14.6228 | 16.5309 | 18.4636 | 20.3438 | 21.4604 | 23.1064 | 24.1578 | 24.6887 | 26.4944 | 28.4399
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.052124 | 0.064579 | 0.081259 | 0.10354 | 0.1298 | 0.16502 | 0.20176 | 0.26357 | 0.32541 | 0.39551 | 0.45883 | 0.51509 | 0.57056 | 0.62582 | 0.67902 | 0.73361 | 0.95723 | 1.1414 | 0.11839 | 0.14459 | 0.1793 | 0.22557 | 0.2801 | 0.35284 | 0.4288 | 0.56234 | 0.69893 | 0.85589 | 0.99503 | 1.1162 | 1.2336 | 1.3507 | 1.4634 | 1.5788 | 2.0689 | 2.48
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.063257 | 0.090172 | 0.12693 | 0.17368 | 0.22751 | 0.2977 | 0.37855 | 0.49524 | 0.61841 | 0.73543 | 0.83432 | 0.91524 | 0.99507 | 1.0597 | 1.1252 | 1.1902 | 1.5329 | 1.7828 | 0.14232 | 0.19933 | 0.27619 | 0.37407 | 0.48698 | 0.63342 | 0.80128 | 1.0529 | 1.3221 | 1.5803 | 1.803 | 1.9871 | 2.1694 | 2.3134 | 2.4587 | 2.604 | 3.3707 | 3.9573
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.059073 | 0.079491 | 0.10764 | 0.14512 | 0.18847 | 0.24975 | 0.34286 | 0.47183 | 0.5823 | 0.70741 | 0.82162 | 0.93063 | 1.0355 | 1.1241 | 1.2003 | 1.2613 | 1.5769 | 1.7525 | 0.13484 | 0.1797 | 0.24023 | 0.3206 | 0.41372 | 0.54368 | 0.75179 | 1.0428 | 1.29 | 1.5716 | 1.8243 | 2.0653 | 2.2963 | 2.4878 | 2.654 | 2.7896 | 3.4944 | 3.8858
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.055567 | 0.072164 | 0.096108 | 0.12976 | 0.16903 | 0.22089 | 0.27701 | 0.36502 | 0.4524 | 0.56076 | 0.65702 | 0.74691 | 0.83366 | 0.9061 | 0.96687 | 1.0131 | 1.2696 | 1.5179 | 0.12584 | 0.16127 | 0.21184 | 0.28288 | 0.36605 | 0.47525 | 0.59298 | 0.78377 | 0.97521 | 1.2166 | 1.4276 | 1.6236 | 1.8109 | 1.9656 | 2.0966 | 2.1995 | 2.7806 | 3.3531
Grendon 132kV | Hayfield | Primary Substation | 11 | Counterfactual | 0.067057 | 0.10124 | 0.14722 | 0.2507 | 0.35693 | 0.46585 | 0.57759 | 0.69615 | 0.81671 | 0.94299 | 1.0689 | 1.1977 | 1.3298 | 1.459 | 1.5909 | 1.7229 | 2.3248 | 2.3299 | 0.136 | 0.20783 | 0.30411 | 0.51981 | 0.74233 | 0.97148 | 1.2076 | 1.4587 | 1.7152 | 1.9844 | 2.254 | 2.5295 | 2.8115 | 3.0876 | 3.3693 | 3.651 | 4.9373 | 4.9485
Grendon 132kV | Hayfield | Primary Substation | 11 | Electric Engagement | 0.068358 | 0.11036 | 0.16808 | 0.29651 | 0.43364 | 0.57938 | 0.72892 | 0.88293 | 1.0364 | 1.1916 | 1.3443 | 1.4985 | 1.6525 | 1.8095 | 1.9666 | 2.1236 | 2.8389 | 2.8452 | 0.1388 | 0.22953 | 0.35427 | 0.63134 | 0.92995 | 1.2499 | 1.5774 | 1.9141 | 2.2496 | 2.5887 | 2.9228 | 3.2598 | 3.5964 | 3.9391 | 4.2819 | 4.6244 | 6.1872 | 6.2019
Grendon 132kV | Hayfield | Primary Substation | 11 | Holistic Transition | 0.067797 | 0.10888 | 0.16528 | 0.29228 | 0.4278 | 0.57192 | 0.71977 | 0.87209 | 1.0236 | 1.1786 | 1.3336 | 1.4925 | 1.6514 | 1.8125 | 1.9746 | 2.1319 | 2.8485 | 2.8536 | 0.13777 | 0.22674 | 0.34887 | 0.62313 | 0.91855 | 1.2353 | 1.5597 | 1.8932 | 2.225 | 2.5637 | 2.9023 | 3.2489 | 3.5955 | 3.9463 | 4.2991 | 4.6424 | 6.2077 | 6.2196
Grendon 132kV | Hayfield | Primary Substation | 11 | Hydrogen Evolution | 0.067414 | 0.10825 | 0.16447 | 0.29132 | 0.4266 | 0.57035 | 0.71746 | 0.86915 | 1.0202 | 1.1747 | 1.3293 | 1.4867 | 1.6439 | 1.804 | 1.9653 | 2.1222 | 2.837 | 2.8423 | 0.13678 | 0.22517 | 0.34682 | 0.62068 | 0.91552 | 1.2314 | 1.554 | 1.8859 | 2.2165 | 2.5541 | 2.892 | 3.2352 | 3.5781 | 3.9268 | 4.2779 | 4.6202 | 6.1815 | 6.1939
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.73343 | 0.84542 | 0.97737 | 1.1186 | 1.2793 | 1.4606 | 1.6634 | 2.0018 | 2.2806 | 2.5795 | 2.8804 | 3.2257 | 3.6134 | 4.0053 | 4.3713 | 4.7254 | 5.6817 | 6.1565 | 1.6876 | 1.9227 | 2.1974 | 2.491 | 2.8235 | 3.1971 | 3.6139 | 4.3096 | 4.8894 | 5.5116 | 6.1339 | 6.8445 | 7.6386 | 8.4408 | 9.1886 | 9.9104 | 11.9042 | 12.9377
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.86476 | 1.1479 | 1.469 | 1.838 | 2.2547 | 2.7103 | 3.2612 | 3.9712 | 4.6445 | 5.2295 | 5.5543 | 5.7059 | 5.8458 | 5.974 | 6.0983 | 6.2208 | 6.8238 | 7.4485 | 1.971 | 2.572 | 3.2363 | 4.0019 | 4.8621 | 5.7987 | 6.9256 | 8.3838 | 9.7758 | 10.9949 | 11.6949 | 12.0363 | 12.3547 | 12.6427 | 12.9219 | 13.1992 | 14.5774 | 16.009
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.81573 | 1.0126 | 1.2256 | 1.4481 | 1.6988 | 2.0416 | 2.4772 | 3.039 | 3.491 | 3.9809 | 4.4881 | 5.0449 | 5.6003 | 6.1198 | 6.4573 | 6.616 | 7.3813 | 8.0117 | 1.8839 | 2.3199 | 2.7784 | 3.2547 | 3.787 | 4.5142 | 5.4426 | 6.6272 | 7.5768 | 8.6055 | 9.6612 | 10.8191 | 11.9744 | 13.0516 | 13.7638 | 14.1192 | 15.8473 | 17.2789
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.77388 | 0.94128 | 1.1216 | 1.326 | 1.559 | 1.8257 | 2.1575 | 2.6729 | 3.1388 | 3.6484 | 4.1217 | 4.5883 | 5.0603 | 5.4997 | 5.76 | 5.8709 | 6.3967 | 6.941 | 1.7754 | 2.137 | 2.5129 | 2.9424 | 3.4289 | 3.9823 | 4.668 | 5.7337 | 6.7022 | 7.7648 | 8.7384 | 9.6958 | 10.6643 | 11.564 | 12.1049 | 12.3489 | 13.5296 | 14.7613
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.0438 | 1.1188 | 1.1974 | 1.2908 | 1.3754 | 1.4649 | 1.5617 | 1.7366 | 1.8894 | 2.059 | 2.2213 | 2.3786 | 2.5461 | 2.7615 | 2.9419 | 3.1062 | 3.6567 | 4.0104 | 2.5348 | 2.6945 | 2.8606 | 3.0566 | 3.2322 | 3.4156 | 3.6135 | 3.9796 | 4.3062 | 4.6722 | 5.0168 | 5.3447 | 5.6894 | 6.1537 | 6.5317 | 6.8695 | 8.0381 | 8.8131
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.0933 | 1.2768 | 1.4435 | 1.6309 | 1.8212 | 2.0357 | 2.2852 | 2.6263 | 2.9575 | 3.364 | 3.5654 | 3.7021 | 3.829 | 3.9256 | 4.072 | 4.1685 | 4.8557 | 5.2339 | 2.6424 | 3.0507 | 3.4019 | 3.794 | 4.1899 | 4.6314 | 5.1421 | 5.8557 | 6.5569 | 7.4664 | 7.9114 | 8.2215 | 8.5129 | 8.73 | 9.0447 | 9.2618 | 10.8486 | 11.7509
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.0738 | 1.2236 | 1.3384 | 1.4654 | 1.6132 | 1.7545 | 1.9568 | 2.2532 | 2.5874 | 2.8741 | 3.1502 | 3.7317 | 3.9875 | 4.207 | 4.4144 | 4.5081 | 5.0023 | 5.2548 | 2.6074 | 2.9526 | 3.2002 | 3.4734 | 3.7994 | 4.0958 | 4.5362 | 5.1827 | 5.9353 | 6.5605 | 7.1527 | 8.5094 | 9.055 | 9.5162 | 9.9527 | 10.1621 | 11.2751 | 11.854
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.0628 | 1.2 | 1.3078 | 1.4291 | 1.5472 | 1.6799 | 1.8325 | 2.0796 | 2.3042 | 2.6906 | 2.951 | 3.197 | 3.4301 | 3.6327 | 3.796 | 3.8737 | 4.4332 | 4.7939 | 2.5763 | 2.8874 | 3.1142 | 3.3686 | 3.6148 | 3.8877 | 4.2003 | 4.7167 | 5.1903 | 6.0595 | 6.6092 | 7.1244 | 7.6099 | 8.0276 | 8.3663 | 8.5354 | 9.8344 | 10.6712
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Counterfactual | 0.33581 | 0.41082 | 0.50103 | 0.5959 | 0.70152 | 0.82322 | 0.9606 | 1.2593 | 1.5537 | 1.9641 | 2.5481 | 3.2981 | 3.5804 | 3.8633 | 4.2229 | 4.6069 | 5.3543 | 5.7501 | 0.74518 | 0.90184 | 1.0887 | 1.2848 | 1.5024 | 1.7523 | 2.0338 | 2.6526 | 3.2704 | 4.1379 | 5.3759 | 6.9658 | 7.5463 | 8.1279 | 8.9064 | 9.7495 | 11.3211 | 12.1798
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.42354 | 0.60631 | 0.85444 | 1.0953 | 1.3679 | 1.7932 | 2.4034 | 3.1857 | 3.9407 | 4.7102 | 5.3992 | 5.7445 | 5.8689 | 5.9797 | 6.092 | 6.203 | 6.646 | 7.0503 | 0.93473 | 1.3178 | 1.834 | 2.3308 | 2.8917 | 3.7823 | 5.0663 | 6.7179 | 8.3198 | 9.9902 | 11.546 | 12.3286 | 12.6172 | 12.8724 | 13.13 | 13.3861 | 14.391 | 15.3255
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.39096 | 0.5424 | 0.74026 | 1.0264 | 1.3769 | 1.8432 | 2.338 | 2.9269 | 3.53 | 4.2992 | 4.8545 | 5.2701 | 5.6476 | 5.9958 | 6.2345 | 6.3411 | 6.852 | 7.2431 | 0.87667 | 1.2066 | 1.6316 | 2.2458 | 3.0005 | 4.0068 | 5.0765 | 6.3396 | 7.659 | 9.3819 | 10.5814 | 11.463 | 12.2607 | 12.9944 | 13.5082 | 13.7466 | 14.8993 | 15.7862
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.36281 | 0.48215 | 0.6622 | 0.82881 | 1.0669 | 1.4013 | 1.8363 | 2.3952 | 2.9215 | 3.518 | 4.1892 | 4.7369 | 5.1017 | 5.4352 | 5.6569 | 5.775 | 6.244 | 6.6694 | 0.8039 | 1.0571 | 1.4372 | 1.7863 | 2.2891 | 3.0007 | 3.926 | 5.1092 | 6.229 | 7.5107 | 8.9826 | 10.1762 | 10.9389 | 11.6356 | 12.1084 | 12.3754 | 13.4232 | 14.3837
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.21478 | 0.2303 | 0.24784 | 0.26752 | 0.2901 | 0.31592 | 0.34469 | 0.39485 | 0.43724 | 0.48414 | 0.53061 | 0.57711 | 0.62747 | 0.67748 | 0.72602 | 0.77749 | 0.92781 | 1.0193 | 0.47224 | 0.50491 | 0.54131 | 0.58203 | 0.62861 | 0.68168 | 0.74071 | 0.84475 | 0.93406 | 1.0335 | 1.1308 | 1.227 | 1.3302 | 1.4325 | 1.5318 | 1.6373 | 1.9542 | 2.1538
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.2319 | 0.26834 | 0.31324 | 0.36347 | 0.42036 | 0.48386 | 0.56087 | 0.66161 | 0.75619 | 0.83623 | 0.88316 | 0.9114 | 0.93855 | 0.96093 | 0.98385 | 1.0058 | 1.1152 | 1.2226 | 0.50905 | 0.58577 | 0.67866 | 0.78234 | 0.89939 | 1.0298 | 1.1874 | 1.3959 | 1.5932 | 1.7617 | 1.8643 | 1.9284 | 1.9908 | 2.0414 | 2.0929 | 2.143 | 2.3952 | 2.6453
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.22538 | 0.25084 | 0.27928 | 0.31093 | 0.34636 | 0.38885 | 0.44542 | 0.52785 | 0.59656 | 0.67306 | 0.74907 | 0.82733 | 0.90473 | 0.97464 | 1.0239 | 1.0513 | 1.1795 | 1.2743 | 0.49743 | 0.55351 | 0.61443 | 0.68199 | 0.75718 | 0.84656 | 0.96822 | 1.1447 | 1.2914 | 1.4552 | 1.6158 | 1.7812 | 1.9446 | 2.091 | 2.196 | 2.2572 | 2.5483 | 2.7633
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.22018 | 0.24039 | 0.26568 | 0.29463 | 0.32776 | 0.36692 | 0.4133 | 0.48517 | 0.54919 | 0.62328 | 0.69571 | 0.76508 | 0.83507 | 0.89645 | 0.93736 | 0.95751 | 1.0535 | 1.1547 | 0.48388 | 0.52676 | 0.57942 | 0.63952 | 0.70818 | 0.78907 | 0.88442 | 1.0334 | 1.167 | 1.3229 | 1.4736 | 1.6175 | 1.7624 | 1.8889 | 1.9743 | 2.0187 | 2.2362 | 2.4672
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Counterfactual | 2.8678 | 2.9182 | 2.9756 | 3.0412 | 3.1187 | 3.2185 | 3.3213 | 3.544 | 3.7804 | 4.0594 | 4.3017 | 4.5043 | 4.7118 | 4.923 | 5.1347 | 5.3416 | 6.0798 | 6.6717 | 7.0486 | 7.1544 | 7.2736 | 7.4094 | 7.5695 | 7.7746 | 7.9852 | 8.4649 | 8.9863 | 9.6087 | 10.1397 | 10.5737 | 11.0098 | 11.4541 | 11.9027 | 12.3419 | 13.9608 | 15.299
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.9254 | 3.048 | 3.2058 | 3.3798 | 3.5804 | 3.846 | 4.1895 | 4.6617 | 5.1148 | 5.5632 | 5.9155 | 6.1483 | 6.3672 | 6.5331 | 6.6909 | 6.8561 | 7.3516 | 7.891 | 7.1724 | 7.4301 | 7.7585 | 8.1186 | 8.5332 | 9.0821 | 9.7936 | 10.8038 | 11.788 | 12.7776 | 13.581 | 14.1224 | 14.6363 | 15.0144 | 15.3752 | 15.7559 | 16.8319 | 18.0879
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.9034 | 3.0067 | 3.1172 | 3.2487 | 3.4112 | 3.6164 | 3.9308 | 4.3801 | 4.7678 | 5.2294 | 5.6305 | 5.9083 | 6.2059 | 6.4693 | 6.6529 | 6.7582 | 7.2391 | 8.4103 | 7.1331 | 7.3593 | 7.5965 | 7.8777 | 8.2254 | 8.6594 | 9.3627 | 10.3752 | 11.2462 | 12.2909 | 13.1741 | 13.7453 | 14.3694 | 14.9114 | 15.2971 | 15.5255 | 16.5635 | 19.3901
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.8862 | 2.9617 | 3.0589 | 3.1607 | 3.2878 | 3.4631 | 3.6721 | 3.9948 | 4.3026 | 4.7001 | 5.0602 | 5.3876 | 5.68 | 5.9303 | 6.1044 | 6.2211 | 8.0786 | 8.8374 | 7.0883 | 7.2486 | 7.4524 | 7.6648 | 7.9308 | 8.2967 | 8.7323 | 9.4261 | 10.0961 | 10.9806 | 11.7706 | 12.4801 | 13.1058 | 13.6323 | 14.0062 | 14.2699 | 18.8027 | 20.5904
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.30141 | 0.43065 | 0.61548 | 0.75521 | 0.89647 | 1.0297 | 1.1832 | 1.4259 | 1.6178 | 1.8315 | 2.0604 | 2.3009 | 2.5682 | 2.8346 | 3.0973 | 3.3579 | 4.0066 | 4.2533 | 0.67545 | 0.9462 | 1.3305 | 1.6201 | 1.9122 | 2.187 | 2.5028 | 2.9973 | 3.3906 | 3.8277 | 4.2964 | 4.7875 | 5.3317 | 5.8736 | 6.408 | 6.9374 | 8.2755 | 8.8021
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.39967 | 0.65864 | 1.0007 | 1.3104 | 1.6428 | 1.9742 | 2.3754 | 2.8684 | 3.347 | 3.7419 | 3.9542 | 4.0754 | 4.1821 | 4.2517 | 4.3251 | 4.3891 | 4.7408 | 5.0903 | 0.88817 | 1.4354 | 2.1526 | 2.7997 | 3.4898 | 4.1721 | 4.9934 | 5.9978 | 6.9805 | 7.7941 | 8.2422 | 8.5065 | 8.7416 | 8.895 | 9.0558 | 9.1968 | 9.9746 | 10.7458
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.36405 | 0.55977 | 0.82401 | 1.0252 | 1.2328 | 1.446 | 1.7305 | 2.1152 | 2.4494 | 2.8071 | 3.198 | 3.5509 | 3.8949 | 4.2249 | 4.4375 | 4.5266 | 4.9642 | 5.3558 | 0.82494 | 1.251 | 1.822 | 2.2538 | 2.6961 | 3.1461 | 3.7455 | 4.5439 | 5.2395 | 5.9814 | 6.7904 | 7.5159 | 8.2234 | 8.9031 | 9.3476 | 9.5439 | 10.5146 | 11.3908
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.33176 | 0.50542 | 0.745 | 0.93836 | 1.1369 | 1.3344 | 1.5711 | 1.9042 | 2.2132 | 2.5438 | 2.8965 | 3.2407 | 3.5859 | 3.9059 | 4.1016 | 4.1798 | 4.5109 | 4.7933 | 0.74186 | 1.1124 | 1.6195 | 2.0287 | 2.4462 | 2.8567 | 3.3442 | 4.0239 | 4.6579 | 5.334 | 6.0535 | 6.7559 | 7.4601 | 8.1141 | 8.5194 | 8.6885 | 9.4091 | 10.0256
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.73135 | 0.78678 | 0.84501 | 0.91194 | 0.98593 | 1.0695 | 1.1677 | 1.3281 | 1.4598 | 1.6069 | 1.7535 | 1.9132 | 2.0953 | 2.2723 | 2.4411 | 2.6167 | 3.0948 | 3.3672 | 1.7628 | 1.8772 | 1.9963 | 2.133 | 2.2839 | 2.4542 | 2.654 | 2.9816 | 3.2532 | 3.5575 | 3.8585 | 4.1864 | 4.558 | 4.9191 | 5.2633 | 5.6208 | 6.6158 | 7.1986
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.79738 | 0.93297 | 1.0859 | 1.2601 | 1.4543 | 1.6671 | 1.9306 | 2.2667 | 2.5829 | 2.8496 | 3.007 | 3.0914 | 3.1709 | 3.2399 | 3.3133 | 3.3831 | 3.7293 | 4.0338 | 1.9073 | 2.1928 | 2.5093 | 2.8687 | 3.2685 | 3.7058 | 4.245 | 4.9354 | 5.5888 | 6.1442 | 6.4814 | 6.6679 | 6.8456 | 6.9983 | 7.1597 | 7.3146 | 8.0928 | 8.7853
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.7755 | 0.87258 | 0.97044 | 1.0778 | 1.2078 | 1.3683 | 1.5609 | 1.8214 | 2.037 | 2.2748 | 2.5223 | 2.7672 | 3.013 | 3.2377 | 3.4024 | 3.4899 | 3.8993 | 4.221 | 1.8684 | 2.0811 | 2.2907 | 2.52 | 2.7961 | 3.1353 | 3.5446 | 4.0922 | 4.5454 | 5.0449 | 5.5601 | 6.0712 | 6.5843 | 7.0517 | 7.3986 | 7.5916 | 8.5035 | 9.2211
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.75628 | 0.83653 | 0.9254 | 1.0263 | 1.1415 | 1.2781 | 1.4432 | 1.6947 | 1.9166 | 2.1683 | 2.4108 | 2.6392 | 2.876 | 3.0823 | 3.2224 | 3.282 | 3.5774 | 3.875 | 1.8188 | 1.989 | 2.1738 | 2.3832 | 2.6217 | 2.9036 | 3.2433 | 3.7614 | 4.2205 | 4.7427 | 5.2408 | 5.7096 | 6.1951 | 6.6176 | 6.9075 | 7.0375 | 7.6904 | 8.3508
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.58878 | 0.66193 | 0.74727 | 0.85026 | 0.96881 | 1.376 | 1.5354 | 1.8113 | 2.0678 | 2.3578 | 2.6366 | 2.9038 | 3.1803 | 3.4555 | 3.6989 | 3.9391 | 4.7461 | 5.3488 | 1.3599 | 1.5138 | 1.6908 | 1.9042 | 2.1494 | 3.0988 | 3.4264 | 4.0112 | 4.5675 | 5.2038 | 5.8062 | 6.3742 | 6.954 | 7.5298 | 8.0355 | 8.5342 | 10.2816 | 11.6314
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.66572 | 0.83268 | 1.0461 | 1.298 | 1.5852 | 1.9361 | 2.3377 | 2.8985 | 3.4741 | 3.9966 | 4.3823 | 4.655 | 4.9169 | 5.1193 | 5.3009 | 5.4937 | 6.5159 | 7.3358 | 1.5261 | 1.879 | 2.3254 | 2.852 | 3.4517 | 4.1801 | 5.0088 | 6.1982 | 7.4395 | 8.5753 | 9.4387 | 10.0641 | 10.6662 | 11.1223 | 11.5295 | 11.9651 | 14.2738 | 16.2171
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.63735 | 0.76421 | 0.91014 | 1.0804 | 1.2827 | 1.5506 | 1.9279 | 2.4543 | 2.9036 | 3.4108 | 3.8925 | 4.3425 | 4.7812 | 5.1519 | 5.4146 | 5.5909 | 6.5277 | 7.0728 | 1.4755 | 1.7549 | 2.0705 | 2.4373 | 2.8723 | 3.4413 | 4.2756 | 5.4451 | 6.4371 | 7.5608 | 8.6088 | 9.586 | 10.535 | 11.324 | 11.8923 | 12.2881 | 14.4035 | 15.6406
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.61325 | 0.71122 | 0.83521 | 0.98225 | 1.1533 | 1.3754 | 1.6211 | 2.0186 | 2.4072 | 2.8734 | 3.2933 | 3.6879 | 4.0604 | 4.3835 | 4.5932 | 4.7233 | 5.4479 | 6.2324 | 1.4132 | 1.622 | 1.882 | 2.1904 | 2.5492 | 3.0122 | 3.522 | 4.3681 | 5.2082 | 6.2297 | 7.1319 | 7.9744 | 8.7619 | 9.4377 | 9.8822 | 10.1718 | 11.8267 | 13.646
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Counterfactual | 0.91048 | 1.0986 | 1.3529 | 1.6375 | 1.9396 | 2.3548 | 2.757 | 3.3558 | 3.8857 | 4.4735 | 5.0414 | 5.5707 | 6.1163 | 6.8275 | 7.4009 | 7.8624 | 9.2791 | 10.1515 | 2.1297 | 2.5273 | 3.0585 | 3.6513 | 4.2803 | 5.1418 | 5.9757 | 7.2462 | 8.3936 | 9.6808 | 10.9046 | 12.0271 | 13.1688 | 14.7334 | 15.9575 | 16.9183 | 19.9931 | 21.9758
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Electric Engagement | 1.051 | 1.4323 | 1.9544 | 3.2523 | 3.8525 | 4.6459 | 5.5 | 6.5999 | 7.6591 | 8.9854 | 9.7325 | 10.3173 | 10.8796 | 11.3082 | 11.7397 | 12.1333 | 14.0149 | 15.2569 | 2.4341 | 3.25 | 4.3612 | 7.3876 | 8.6467 | 10.3109 | 12.0863 | 14.4181 | 16.6876 | 19.6775 | 21.3461 | 22.6832 | 23.9689 | 24.9249 | 25.8834 | 26.7602 | 30.9725 | 33.9461
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Holistic Transition | 0.99895 | 1.2977 | 1.662 | 2.0542 | 2.6454 | 3.2637 | 4.0468 | 5.0821 | 6.1509 | 7.1159 | 8.0614 | 8.9785 | 9.8558 | 10.5835 | 11.1437 | 11.496 | 13.1558 | 13.8991 | 2.341 | 3.0039 | 3.7907 | 4.6346 | 5.9638 | 7.2835 | 9.0077 | 11.2971 | 13.7088 | 15.8384 | 17.8958 | 19.8982 | 21.8039 | 23.3536 | 24.5654 | 25.3506 | 29.0808 | 30.7827
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.95488 | 1.2048 | 1.542 | 1.9143 | 2.321 | 2.8896 | 3.4578 | 4.2536 | 4.9699 | 6.2239 | 7.063 | 7.8838 | 8.6588 | 9.3041 | 9.7726 | 10.032 | 11.3287 | 12.5193 | 2.2275 | 2.7685 | 3.489 | 4.278 | 5.1411 | 6.3464 | 7.5407 | 9.2402 | 10.7816 | 13.6446 | 15.4537 | 17.2212 | 18.8745 | 20.2293 | 21.2288 | 21.8035 | 24.7532 | 27.5337
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Counterfactual | 0.90582 | 1.0275 | 1.1332 | 1.255 | 1.3914 | 1.536 | 1.7009 | 1.957 | 2.1865 | 2.3966 | 2.6106 | 2.8339 | 3.0822 | 3.3299 | 3.5655 | 3.7945 | 4.3918 | 4.6724 | 2.1931 | 2.4447 | 2.6642 | 2.9164 | 3.1993 | 3.5002 | 3.8448 | 4.3744 | 4.8576 | 5.2887 | 5.7269 | 6.1825 | 6.6877 | 7.1911 | 7.669 | 8.1327 | 9.362 | 9.9583
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.99427 | 1.2255 | 1.4718 | 1.7779 | 2.1392 | 2.5118 | 2.9072 | 3.3763 | 3.8069 | 4.1544 | 4.336 | 4.4325 | 4.5179 | 4.6045 | 4.6867 | 4.756 | 5.1187 | 5.4847 | 2.3842 | 2.8673 | 3.3798 | 4.0278 | 4.7992 | 5.5913 | 6.4089 | 7.3688 | 8.2514 | 8.9649 | 9.3456 | 9.5547 | 9.7409 | 9.9297 | 10.1084 | 10.2592 | 11.0585 | 11.863
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.96157 | 1.136 | 1.3297 | 1.5553 | 1.7937 | 2.0179 | 2.2633 | 2.6015 | 2.8999 | 3.2152 | 3.563 | 3.9099 | 4.2484 | 4.5738 | 4.787 | 4.8842 | 5.3378 | 5.1476 | 2.326 | 2.7009 | 3.1264 | 3.6234 | 4.1464 | 4.6256 | 5.1422 | 5.8428 | 6.4619 | 7.1139 | 7.8292 | 8.5436 | 9.2415 | 9.913 | 10.359 | 10.5707 | 11.5704 | 10.9819
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.93381 | 1.0868 | 1.2372 | 1.4362 | 1.6714 | 1.9309 | 2.184 | 2.5227 | 2.8167 | 3.1332 | 3.4652 | 3.7892 | 4.1073 | 4.4036 | 4.5812 | 4.6485 | 4.9667 | 5.2798 | 2.2539 | 2.5744 | 2.8904 | 3.3186 | 3.8307 | 4.3969 | 4.9251 | 5.6193 | 6.2228 | 6.8708 | 7.5479 | 8.2085 | 8.8571 | 9.4619 | 9.8278 | 9.9716 | 10.6625 | 11.3443
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Counterfactual | 4.202 | 4.2576 | 4.3269 | 4.4012 | 4.4819 | 4.5716 | 4.6746 | 4.8458 | 4.9804 | 5.1231 | 5.2697 | 5.4247 | 5.5948 | 5.765 | 5.932 | 6.1045 | 6.5018 | 6.6565 | 10.3789 | 10.4944 | 10.6375 | 10.7907 | 10.9569 | 11.1414 | 11.3529 | 11.7018 | 11.9784 | 12.2705 | 12.5702 | 12.8855 | 13.2306 | 13.5754 | 13.9135 | 14.2629 | 15.0836 | 15.4195
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Electric Engagement | 4.2715 | 4.4043 | 4.5763 | 4.767 | 4.9802 | 5.2098 | 5.486 | 5.8312 | 6.138 | 6.3859 | 6.4994 | 6.5408 | 6.5812 | 6.6186 | 6.6573 | 6.6999 | 6.9244 | 7.1658 | 10.5289 | 10.8057 | 11.1608 | 11.5562 | 11.9961 | 12.4677 | 13.0323 | 13.736 | 14.363 | 14.8714 | 15.1107 | 15.2046 | 15.2963 | 15.3815 | 15.4685 | 15.5639 | 16.0693 | 16.6099
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Holistic Transition | 4.2453 | 4.3319 | 4.446 | 4.5587 | 4.6838 | 4.8277 | 4.9969 | 5.24 | 5.445 | 5.6676 | 5.9071 | 6.1446 | 6.3784 | 6.5982 | 6.7325 | 6.786 | 7.0653 | 7.3174 | 10.4823 | 10.6701 | 10.915 | 11.156 | 11.4217 | 11.7248 | 12.08 | 12.5834 | 13.0085 | 13.469 | 13.9626 | 14.4523 | 14.9343 | 15.3875 | 15.6693 | 15.7893 | 16.4181 | 16.9878
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Hydrogen Evolution | 4.2224 | 4.2946 | 4.3912 | 4.4976 | 4.6141 | 4.7474 | 4.9064 | 5.1348 | 5.3335 | 5.5482 | 5.7738 | 5.999 | 6.2189 | 6.4242 | 6.5335 | 6.5698 | 6.7566 | 6.946 | 10.4232 | 10.5751 | 10.7757 | 10.999 | 11.2423 | 11.5186 | 11.8454 | 12.3118 | 12.7184 | 13.157 | 13.616 | 14.0741 | 14.5209 | 14.9382 | 15.1633 | 15.2426 | 15.6565 | 16.0782
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Counterfactual | 0.21706 | 0.28406 | 0.37048 | 0.45547 | 0.54678 | 0.64715 | 0.76055 | 0.94495 | 1.0935 | 1.2518 | 1.441 | 1.6413 | 1.8766 | 2.1026 | 2.2975 | 2.4955 | 3.0403 | 3.344 | 0.49358 | 0.63293 | 0.81017 | 0.98469 | 1.1717 | 1.3767 | 1.6081 | 1.982 | 2.2848 | 2.6067 | 3.0023 | 3.4211 | 3.9128 | 4.3845 | 4.7806 | 5.1794 | 6.285 | 6.9238
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.28856 | 0.46207 | 0.66638 | 0.88149 | 1.1179 | 1.3742 | 1.723 | 2.1428 | 2.5666 | 2.8896 | 3.0764 | 3.1975 | 3.3041 | 3.403 | 3.4974 | 3.5809 | 4.0241 | 4.3821 | 0.64779 | 1.0195 | 1.4433 | 1.8904 | 2.379 | 2.9065 | 3.6352 | 4.5068 | 5.405 | 6.0808 | 6.4789 | 6.7438 | 6.9791 | 7.1947 | 7.3951 | 7.5744 | 8.5378 | 9.3226
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.26231 | 0.39189 | 0.53132 | 0.66616 | 0.81412 | 1.027 | 1.2709 | 1.5944 | 1.8764 | 2.1666 | 2.4834 | 2.8168 | 3.1384 | 3.4317 | 3.6438 | 3.7563 | 4.2831 | 4.698 | 0.60092 | 0.89007 | 1.1904 | 1.4796 | 1.7941 | 2.2574 | 2.7846 | 3.4726 | 4.0736 | 4.6834 | 5.3437 | 6.0381 | 6.7038 | 7.3076 | 7.7483 | 7.9902 | 9.1345 | 10.0474
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.24026 | 0.34842 | 0.47426 | 0.60638 | 0.75209 | 0.9127 | 1.1281 | 1.4363 | 1.7445 | 2.0547 | 2.3566 | 2.6493 | 2.9491 | 3.2064 | 3.3782 | 3.4511 | 3.8162 | 4.1293 | 0.54373 | 0.77888 | 1.0415 | 1.3183 | 1.6215 | 1.954 | 2.4069 | 3.0494 | 3.7106 | 4.3625 | 4.9854 | 5.59 | 6.2084 | 6.737 | 7.0889 | 7.2434 | 8.0255 | 8.7012
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Counterfactual | 0.67635 | 0.75355 | 0.84964 | 0.95812 | 1.0797 | 1.2363 | 1.4017 | 1.6803 | 1.9329 | 2.2141 | 2.4812 | 2.7354 | 3.0118 | 3.296 | 3.575 | 3.8528 | 4.7277 | 5.3253 | 1.4763 | 1.6404 | 1.8418 | 2.0683 | 2.3204 | 2.6425 | 2.9824 | 3.5702 | 4.1142 | 4.7266 | 5.2983 | 5.8326 | 6.4066 | 6.9991 | 7.5848 | 8.1677 | 10.0437 | 11.3632
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.75067 | 0.9496 | 1.1666 | 1.4123 | 1.6916 | 2.0372 | 2.445 | 2.9899 | 3.5378 | 4.0754 | 4.4909 | 4.7375 | 4.9628 | 5.1431 | 5.3553 | 5.5651 | 6.6774 | 7.4083 | 1.6364 | 2.0695 | 2.5214 | 3.0318 | 3.6116 | 4.3248 | 5.1624 | 6.3071 | 7.4718 | 8.6374 | 9.565 | 10.121 | 10.6328 | 11.0321 | 11.4991 | 11.9635 | 14.4307 | 16.1504
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.72273 | 0.89266 | 1.0425 | 1.2103 | 1.3951 | 1.6461 | 2.0169 | 2.5066 | 2.9489 | 3.4625 | 3.9088 | 4.3324 | 4.7423 | 5.1107 | 5.4055 | 5.6062 | 6.6301 | 7.1577 | 1.5864 | 1.9707 | 2.2931 | 2.6527 | 3.0478 | 3.5752 | 4.3864 | 5.4612 | 6.435 | 7.5742 | 8.5336 | 9.4445 | 10.3235 | 11.1018 | 11.7337 | 12.1771 | 14.4518 | 15.6368
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.69974 | 0.82733 | 0.95819 | 1.1116 | 1.2874 | 1.5153 | 1.772 | 2.1711 | 2.5497 | 3.0257 | 3.4504 | 3.8321 | 4.1884 | 4.4924 | 4.7355 | 4.8845 | 5.6816 | 6.4172 | 1.5269 | 1.8101 | 2.0849 | 2.4063 | 2.7744 | 3.248 | 3.7793 | 4.6222 | 5.4296 | 6.4654 | 7.3787 | 8.1899 | 8.9363 | 9.5663 | 10.079 | 10.4058 | 12.1936 | 13.879
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.20931 | 0.24587 | 0.28595 | 0.3295 | 0.3929 | 0.4657 | 0.54819 | 0.67438 | 0.78598 | 0.90035 | 1.02 | 1.1745 | 1.3392 | 1.5314 | 1.7613 | 1.9931 | 2.8059 | 3.474 | 0.46447 | 0.54046 | 0.62341 | 0.71342 | 0.84475 | 0.99565 | 1.1665 | 1.4278 | 1.6617 | 1.9014 | 2.151 | 2.4732 | 2.815 | 3.2146 | 3.6952 | 4.1794 | 5.9016 | 7.3346
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.25142 | 0.3355 | 0.4372 | 0.55976 | 0.71541 | 0.88086 | 1.0801 | 1.3396 | 1.5894 | 1.8197 | 2.0068 | 2.1692 | 2.3357 | 2.4968 | 2.6614 | 2.8174 | 3.5118 | 4.1985 | 0.55536 | 0.73062 | 0.94082 | 1.1974 | 1.5225 | 1.8659 | 2.2781 | 2.8169 | 3.3392 | 3.825 | 4.2315 | 4.5907 | 4.9594 | 5.3145 | 5.6764 | 6.0204 | 7.5557 | 9.0783
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.23571 | 0.29192 | 0.36315 | 0.43463 | 0.53374 | 0.66164 | 0.86923 | 1.1392 | 1.3853 | 1.6441 | 1.91 | 2.1838 | 2.457 | 2.7202 | 2.9289 | 3.08 | 3.7329 | 4.3397 | 0.52737 | 0.64903 | 0.80421 | 0.95764 | 1.1692 | 1.4431 | 1.8913 | 2.4697 | 2.9969 | 3.5506 | 4.1158 | 4.6976 | 5.278 | 5.8363 | 6.2848 | 6.6177 | 8.061 | 9.4018
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.2221 | 0.26917 | 0.32485 | 0.395 | 0.49264 | 0.59973 | 0.73705 | 0.93412 | 1.1364 | 1.3943 | 1.6604 | 1.9218 | 2.1886 | 2.4412 | 2.6399 | 2.7846 | 3.4193 | 4.0571 | 0.49228 | 0.59102 | 0.70704 | 0.85635 | 1.0635 | 1.2888 | 1.5769 | 1.9899 | 2.4176 | 2.9661 | 3.5287 | 4.081 | 4.6442 | 5.1775 | 5.603 | 5.9199 | 7.3161 | 8.723
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.15276 | 0.1872 | 0.22745 | 0.268 | 0.30444 | 0.3527 | 0.40654 | 0.49341 | 0.58386 | 0.69069 | 0.78171 | 0.85528 | 0.92453 | 0.99439 | 1.0627 | 1.1319 | 1.451 | 1.718 | 0.36196 | 0.43549 | 0.52028 | 0.60534 | 0.6815 | 0.78076 | 0.89188 | 1.0843 | 1.2903 | 1.5377 | 1.7434 | 1.9052 | 2.0534 | 2.2033 | 2.3496 | 2.4977 | 3.2125 | 3.8253
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.16876 | 0.23789 | 0.30675 | 0.38076 | 0.45416 | 0.55403 | 0.67502 | 0.84656 | 1.0364 | 1.2244 | 1.39 | 1.5238 | 1.6553 | 1.7507 | 1.8489 | 1.9512 | 2.5171 | 2.9073 | 0.39641 | 0.54934 | 0.69496 | 0.85064 | 1.0046 | 1.211 | 1.4608 | 1.8346 | 2.2555 | 2.6758 | 3.0539 | 3.3625 | 3.6675 | 3.8824 | 4.1023 | 4.3328 | 5.6056 | 6.5482
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.1628 | 0.22314 | 0.27761 | 0.33468 | 0.38873 | 0.46884 | 0.62466 | 0.83053 | 1.0003 | 1.2032 | 1.3798 | 1.5464 | 1.705 | 1.827 | 1.9306 | 2.0143 | 2.4858 | 2.669 | 0.38577 | 0.52276 | 0.64062 | 0.76347 | 0.87971 | 1.0475 | 1.4008 | 1.8758 | 2.2629 | 2.7283 | 3.1243 | 3.498 | 3.8524 | 4.1175 | 4.3455 | 4.5335 | 5.5962 | 6.0132
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.15793 | 0.21108 | 0.26099 | 0.31491 | 0.36585 | 0.43444 | 0.51412 | 0.63449 | 0.75698 | 0.92536 | 1.0684 | 1.1993 | 1.3202 | 1.4149 | 1.4931 | 1.5543 | 1.9424 | 2.3275 | 0.37318 | 0.49213 | 0.59875 | 0.71321 | 0.82119 | 0.96402 | 1.1301 | 1.395 | 1.668 | 2.0511 | 2.3699 | 2.6594 | 2.9236 | 3.126 | 3.2952 | 3.4327 | 4.3251 | 5.2336
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.79197 | 0.85802 | 0.93209 | 1.014 | 1.1075 | 1.241 | 1.3844 | 1.6764 | 1.9569 | 2.2811 | 2.575 | 2.8291 | 3.0847 | 3.3401 | 3.5892 | 3.8459 | 4.7848 | 5.4732 | 1.7596 | 1.8989 | 2.0527 | 2.2224 | 2.4154 | 2.6887 | 2.9818 | 3.6113 | 4.2325 | 4.9609 | 5.6063 | 6.1506 | 6.6862 | 7.2225 | 7.7448 | 8.2828 | 10.3482 | 11.9157
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.86605 | 1.023 | 1.2197 | 1.4397 | 1.6865 | 2.0034 | 2.3825 | 2.9603 | 3.5614 | 4.1129 | 4.5392 | 4.8603 | 5.1818 | 5.4399 | 5.6815 | 5.9321 | 7.3659 | 8.3608 | 1.9195 | 2.2519 | 2.6629 | 3.1215 | 3.6338 | 4.2862 | 5.0626 | 6.2991 | 7.6066 | 8.8199 | 9.7873 | 10.5316 | 11.28 | 11.8596 | 12.4021 | 12.9692 | 16.1966 | 18.5877
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.83877 | 0.94991 | 1.0778 | 1.2157 | 1.37 | 1.5968 | 1.99 | 2.5843 | 3.0742 | 3.6498 | 4.1728 | 4.6633 | 5.1364 | 5.5423 | 5.8503 | 6.0704 | 7.3268 | 7.8741 | 1.8711 | 2.1176 | 2.3946 | 2.6922 | 3.0233 | 3.4982 | 4.3787 | 5.7204 | 6.8168 | 8.1124 | 9.2648 | 10.3468 | 11.3865 | 12.2552 | 12.9263 | 13.4219 | 16.2472 | 17.4927
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.81462 | 0.90135 | 1.0059 | 1.1275 | 1.2651 | 1.4573 | 1.6762 | 2.0778 | 2.4635 | 2.9622 | 3.4113 | 3.8269 | 4.2258 | 4.5618 | 4.8061 | 4.9618 | 5.9611 | 6.9208 | 1.8088 | 1.9938 | 2.2121 | 2.4653 | 2.7511 | 3.1463 | 3.5949 | 4.458 | 5.2976 | 6.4049 | 7.3823 | 8.281 | 9.1338 | 9.84 | 10.3617 | 10.7108 | 12.9946 | 15.2463
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.26785 | 0.3123 | 0.36492 | 0.42403 | 0.48058 | 0.56569 | 0.65558 | 0.8207 | 0.98244 | 1.166 | 1.3369 | 1.4946 | 1.6639 | 1.832 | 1.9903 | 2.1471 | 2.7176 | 3.1548 | 0.61689 | 0.71022 | 0.8195 | 0.94188 | 1.0583 | 1.232 | 1.4153 | 1.7641 | 2.113 | 2.5137 | 2.88 | 3.2124 | 3.564 | 3.9138 | 4.2425 | 4.5671 | 5.7877 | 6.7437
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.31124 | 0.40917 | 0.53726 | 0.67672 | 0.81928 | 1.0267 | 1.2923 | 1.6366 | 1.9894 | 2.3218 | 2.5834 | 2.7707 | 2.9449 | 3.0877 | 3.24 | 3.3944 | 4.2303 | 4.7448 | 0.71045 | 0.91706 | 1.1835 | 1.4725 | 1.7657 | 2.1915 | 2.737 | 3.4616 | 4.2117 | 4.9254 | 5.4995 | 5.916 | 6.3069 | 6.6196 | 6.9507 | 7.2891 | 9.1165 | 10.3155
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.29525 | 0.39256 | 0.48485 | 0.58981 | 0.69678 | 0.86213 | 1.0808 | 1.3949 | 1.6603 | 1.9701 | 2.2681 | 2.553 | 2.8319 | 3.0722 | 3.2716 | 3.4151 | 4.1808 | 4.5747 | 0.68192 | 0.89502 | 1.093 | 1.3174 | 1.5452 | 1.8901 | 2.3678 | 3.0584 | 3.6372 | 4.3154 | 4.9565 | 5.5699 | 6.1682 | 6.6751 | 7.0995 | 7.4125 | 9.0872 | 9.9538
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.28156 | 0.34203 | 0.42466 | 0.51889 | 0.61535 | 0.76673 | 0.92462 | 1.1761 | 1.4207 | 1.726 | 1.9887 | 2.2262 | 2.473 | 2.6732 | 2.838 | 2.9424 | 3.5437 | 4.1146 | 0.64655 | 0.77519 | 0.94895 | 1.1455 | 1.3458 | 1.6595 | 1.984 | 2.5147 | 3.0363 | 3.6955 | 4.2532 | 4.7556 | 5.2729 | 5.6893 | 6.0345 | 6.2619 | 7.5886 | 8.8738
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.57306 | 0.63551 | 0.71923 | 0.82694 | 0.95533 | 1.0962 | 1.2593 | 1.4892 | 1.7058 | 1.8681 | 2.0162 | 2.1727 | 2.3504 | 2.5232 | 2.6897 | 2.8604 | 3.3255 | 3.584 | 1.367 | 1.4987 | 1.6773 | 1.9106 | 2.1908 | 2.4961 | 2.8502 | 3.3442 | 3.8206 | 4.1584 | 4.4636 | 4.7843 | 5.1465 | 5.4988 | 5.8378 | 6.1852 | 7.1513 | 7.7039
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.6345 | 0.79705 | 1.0136 | 1.3125 | 1.6693 | 2.0297 | 2.4201 | 2.8761 | 3.3132 | 3.5998 | 3.7521 | 3.8346 | 3.9128 | 3.9848 | 4.061 | 4.1325 | 4.5 | 4.7887 | 1.5 | 1.854 | 2.3246 | 2.9906 | 3.7902 | 4.5875 | 5.4338 | 6.4166 | 7.3641 | 7.9617 | 8.2866 | 8.468 | 8.6417 | 8.7999 | 8.9659 | 9.1235 | 9.9377 | 10.5932
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.61228 | 0.73572 | 0.93675 | 1.1725 | 1.4196 | 1.703 | 2.0081 | 2.3837 | 2.7213 | 2.9812 | 3.2261 | 3.4717 | 3.7157 | 3.9426 | 4.1039 | 4.1912 | 4.6026 | 4.9073 | 1.4605 | 1.7399 | 2.2024 | 2.7453 | 3.3076 | 3.9451 | 4.6303 | 5.4599 | 6.2094 | 6.7556 | 7.2645 | 7.7757 | 8.2838 | 8.7546 | 9.0937 | 9.2854 | 10.1957 | 10.8762
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.59285 | 0.70125 | 0.85098 | 1.0776 | 1.3497 | 1.6385 | 1.9231 | 2.2901 | 2.6282 | 2.8915 | 3.1286 | 3.3545 | 3.5843 | 3.7906 | 3.9272 | 3.9841 | 4.2722 | 4.5541 | 1.4104 | 1.652 | 1.9855 | 2.5018 | 3.1266 | 3.7832 | 4.4154 | 5.2169 | 5.9612 | 6.5089 | 6.9953 | 7.4582 | 7.9289 | 8.3508 | 8.6334 | 8.7572 | 9.391 | 10.016
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.69318 | 0.72195 | 0.74412 | 0.77357 | 0.80406 | 0.83547 | 0.8528 | 0.8568 | 0.86066 | 0.86518 | 0.86943 | 0.87335 | 0.87754 | 0.8815 | 0.88529 | 0.88954 | 0.90893 | 0.92761 | 1.7262 | 1.787 | 1.8335 | 1.8948 | 1.9586 | 2.0246 | 2.061 | 2.0695 | 2.0778 | 2.0876 | 2.0967 | 2.1048 | 2.1134 | 2.1216 | 2.1294 | 2.1381 | 2.1789 | 2.2181
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.69649 | 0.73219 | 0.76118 | 0.79855 | 0.83853 | 0.88124 | 0.90583 | 0.91307 | 0.9204 | 0.92711 | 0.93355 | 0.93896 | 0.94369 | 0.9476 | 0.96981 | 0.97194 | 1.0026 | 1.011 | 1.7344 | 1.8121 | 1.8747 | 1.9551 | 2.0418 | 2.1351 | 2.1884 | 2.2037 | 2.2194 | 2.2339 | 2.248 | 2.2598 | 2.2702 | 2.2786 | 2.3326 | 2.3369 | 2.41 | 2.429
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.69632 | 0.73187 | 0.76 | 0.79652 | 0.83547 | 0.87767 | 0.90245 | 0.91009 | 0.91635 | 0.96126 | 0.96779 | 0.97245 | 0.97733 | 1.0221 | 1.0268 | 1.0305 | 1.0435 | 1.0507 | 1.734 | 1.8117 | 1.8725 | 1.9513 | 2.036 | 2.1283 | 2.1828 | 2.1996 | 2.2133 | 2.3235 | 2.3376 | 2.3472 | 2.3575 | 2.4676 | 2.4772 | 2.4849 | 2.512 | 2.5275
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.69625 | 0.7313 | 0.75953 | 0.7966 | 0.83628 | 0.87881 | 0.90293 | 0.91013 | 0.91683 | 0.9251 | 0.93245 | 0.93908 | 0.94582 | 0.95084 | 0.97517 | 0.97905 | 1.0141 | 1.0254 | 1.7339 | 1.8102 | 1.8711 | 1.9508 | 2.0369 | 2.1298 | 2.1821 | 2.1972 | 2.2113 | 2.2289 | 2.2444 | 2.2583 | 2.2723 | 2.2827 | 2.3412 | 2.3494 | 2.4327 | 2.4588
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.8465 | 0.8916 | 0.93896 | 1.0002 | 1.0699 | 1.146 | 1.2323 | 1.3985 | 1.5389 | 1.6951 | 1.8466 | 2.0072 | 1.8319 | 2.0041 | 2.1705 | 2.3331 | 2.8742 | 3.2563 | 1.9824 | 2.0769 | 2.1752 | 2.3019 | 2.446 | 2.6023 | 2.7788 | 3.1246 | 3.4228 | 3.7571 | 4.0764 | 4.4102 | 3.8963 | 4.2506 | 4.5925 | 4.9263 | 6.0677 | 6.8934
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.89116 | 0.99365 | 1.111 | 1.2615 | 1.4456 | 1.6446 | 1.8792 | 2.2015 | 2.5111 | 2.7909 | 2.9841 | 3.1111 | 2.8834 | 2.9768 | 3.1229 | 3.2698 | 3.7397 | 4.1343 | 2.0785 | 2.2936 | 2.5361 | 2.847 | 3.2265 | 3.6333 | 4.1113 | 4.7808 | 5.4319 | 6.0256 | 6.4476 | 6.7313 | 6.1331 | 6.3406 | 6.6528 | 6.9686 | 8.0253 | 8.9437
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.8744 | 0.94658 | 1.0211 | 1.1171 | 1.2321 | 1.3757 | 1.5737 | 1.8624 | 2.0948 | 2.3519 | 2.6052 | 2.865 | 2.7765 | 3.0024 | 3.2225 | 3.3814 | 3.8806 | 4.1879 | 2.0487 | 2.206 | 2.3652 | 2.5698 | 2.8148 | 3.1155 | 3.5431 | 4.1663 | 4.6661 | 5.2214 | 5.76 | 6.3115 | 5.9915 | 6.465 | 6.9257 | 7.2647 | 8.3781 | 9.0687
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.86059 | 0.92182 | 0.98825 | 1.078 | 1.1916 | 1.3219 | 1.475 | 1.7246 | 1.9521 | 2.2209 | 2.4635 | 2.6956 | 2.5836 | 2.7877 | 2.9644 | 3.0832 | 3.507 | 3.88 | 2.0128 | 2.1423 | 2.2805 | 2.4681 | 2.7041 | 2.9713 | 3.2849 | 3.8043 | 4.2827 | 4.8538 | 5.3616 | 5.8455 | 5.4657 | 5.8864 | 6.2521 | 6.5037 | 7.4438 | 8.2967
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Counterfactual | 0.27083 | 0.3269 | 0.39726 | 0.47967 | 0.56984 | 0.67313 | 0.7808 | 0.92346 | 1.0448 | 1.1781 | 1.3168 | 1.4559 | 1.5971 | 1.7279 | 1.8561 | 1.9906 | 2.3637 | 2.5565 | 0.62851 | 0.74592 | 0.89209 | 1.0629 | 1.2497 | 1.4634 | 1.6858 | 1.9801 | 2.233 | 2.5124 | 2.8014 | 3.0891 | 3.3782 | 3.6452 | 3.9068 | 4.1814 | 4.9618 | 5.3785
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Electric Engagement | 0.31732 | 0.42995 | 0.57485 | 0.74296 | 0.93067 | 1.1437 | 1.3873 | 1.6661 | 1.9369 | 2.1695 | 2.3044 | 2.3899 | 2.4711 | 2.5343 | 2.5999 | 2.6647 | 2.9996 | 3.2256 | 0.72887 | 0.96615 | 1.2687 | 1.6193 | 2.0107 | 2.4544 | 2.9583 | 3.5337 | 4.097 | 4.5841 | 4.8743 | 5.0636 | 5.2447 | 5.3842 | 5.528 | 5.671 | 6.4109 | 6.9301
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Holistic Transition | 0.29999 | 0.38217 | 0.48451 | 0.60292 | 0.73367 | 0.89192 | 1.0812 | 1.3105 | 1.5016 | 1.7104 | 1.9236 | 2.1338 | 2.3382 | 2.5169 | 2.6429 | 2.7146 | 3.0685 | 3.2947 | 0.69795 | 0.87698 | 1.0966 | 1.3502 | 1.6301 | 1.9666 | 2.3722 | 2.8585 | 3.2626 | 3.7047 | 4.152 | 4.5938 | 5.0229 | 5.3951 | 5.6614 | 5.8194 | 6.6028 | 7.1103
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Hydrogen Evolution | 0.28498 | 0.35653 | 0.45004 | 0.56178 | 0.68652 | 0.83312 | 0.99239 | 1.1903 | 1.3749 | 1.5812 | 1.7863 | 1.9792 | 2.1713 | 2.3339 | 2.4405 | 2.4919 | 2.7503 | 2.9788 | 0.65927 | 0.81151 | 1.0088 | 1.2442 | 1.5074 | 1.8161 | 2.1489 | 2.559 | 2.9443 | 3.3764 | 3.8024 | 4.2021 | 4.5989 | 4.9329 | 5.1546 | 5.2667 | 5.8376 | 6.3484
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.45804 | 0.49086 | 0.53328 | 0.5746 | 0.62089 | 0.68164 | 0.74797 | 0.87266 | 0.98504 | 1.1117 | 1.2309 | 1.342 | 1.4583 | 1.5748 | 1.6885 | 1.8053 | 2.1928 | 2.4582 | 1.086 | 1.1545 | 1.2425 | 1.3279 | 1.4232 | 1.5475 | 1.6831 | 1.9463 | 2.189 | 2.4657 | 2.7212 | 2.9548 | 3.1952 | 3.4365 | 3.6716 | 3.9133 | 4.7471 | 5.3383
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.49581 | 0.57226 | 0.67347 | 0.78017 | 0.89992 | 1.0474 | 1.2251 | 1.4766 | 1.7247 | 1.9474 | 2.0616 | 2.1332 | 2.2372 | 2.3203 | 2.4047 | 2.4906 | 2.9979 | 3.3345 | 1.1675 | 1.3277 | 1.5376 | 1.7577 | 2.004 | 2.306 | 2.6685 | 3.1963 | 3.7238 | 4.2026 | 4.4444 | 4.5996 | 4.8382 | 5.0242 | 5.2119 | 5.4048 | 6.5575 | 7.3561
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.48206 | 0.5341 | 0.6008 | 0.66745 | 0.74128 | 0.84272 | 0.99994 | 1.2317 | 1.3845 | 1.5697 | 1.7837 | 1.9881 | 2.2791 | 2.4476 | 2.5735 | 2.6547 | 3.0792 | 3.2988 | 1.143 | 1.2566 | 1.3994 | 1.5415 | 1.698 | 1.9098 | 2.2545 | 2.7645 | 3.0852 | 3.4808 | 3.9425 | 4.3832 | 5.0422 | 5.3982 | 5.6687 | 5.85 | 6.8043 | 7.3012
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.46992 | 0.51286 | 0.57201 | 0.63226 | 0.69992 | 0.78973 | 0.89432 | 1.0682 | 1.2308 | 1.4291 | 1.6159 | 1.7936 | 1.9625 | 2.1092 | 2.2101 | 2.269 | 2.6427 | 2.9713 | 1.1118 | 1.2024 | 1.3261 | 1.4514 | 1.5916 | 1.7763 | 1.9907 | 2.357 | 2.7035 | 3.133 | 3.5303 | 3.9062 | 4.261 | 4.5658 | 4.7785 | 4.9093 | 5.7715 | 6.5336
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.48018 | 0.59548 | 0.73281 | 0.88781 | 1.0652 | 1.2648 | 1.486 | 1.8567 | 2.2036 | 2.5946 | 2.9694 | 3.3083 | 3.6849 | 4.0632 | 4.4237 | 4.7904 | 5.7382 | 6.2057 | 1.0552 | 1.2965 | 1.5835 | 1.9075 | 2.2777 | 2.6939 | 3.1522 | 3.9144 | 4.6306 | 5.44 | 6.2133 | 6.9047 | 7.6706 | 8.4393 | 9.1709 | 9.9146 | 11.866 | 12.8578
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.6184 | 0.90239 | 1.2819 | 1.6942 | 2.164 | 2.7273 | 3.4308 | 4.3059 | 4.9595 | 5.5015 | 5.7793 | 5.898 | 6.011 | 6.1196 | 6.2291 | 6.3336 | 6.8225 | 7.3265 | 1.3546 | 1.9527 | 2.7496 | 3.6152 | 4.6007 | 5.7871 | 7.2555 | 9.0776 | 10.4153 | 11.5303 | 12.1171 | 12.3784 | 12.6301 | 12.8708 | 13.1127 | 13.3455 | 14.4494 | 15.5831
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.56862 | 0.78355 | 1.0495 | 1.3645 | 1.7245 | 2.139 | 2.5888 | 3.1725 | 3.6118 | 4.0773 | 4.5657 | 5.0828 | 5.5973 | 6.0847 | 6.3991 | 6.5473 | 7.2089 | 7.7951 | 1.266 | 1.7364 | 2.3149 | 3.0002 | 3.7827 | 4.6809 | 5.6432 | 6.8717 | 7.7819 | 8.7438 | 9.7488 | 10.8147 | 11.8764 | 12.8822 | 13.5408 | 13.868 | 15.346 | 16.664
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.52484 | 0.70372 | 0.9491 | 1.2088 | 1.5271 | 1.9183 | 2.3623 | 2.9615 | 3.4083 | 3.8979 | 4.3768 | 4.8447 | 5.3213 | 5.7591 | 6.0234 | 6.1292 | 6.5783 | 7.042 | 1.153 | 1.5361 | 2.0602 | 2.6162 | 3.2982 | 4.1376 | 5.0759 | 6.3271 | 7.2446 | 8.2488 | 9.2237 | 10.1756 | 11.1465 | 12.039 | 12.5838 | 12.8125 | 13.8021 | 14.826
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.2358 | 1.2698 | 1.3058 | 1.3697 | 1.3926 | 1.4727 | 1.5415 | 1.634 | 1.7358 | 1.8743 | 2.0079 | 2.1638 | 2.3456 | 2.5287 | 2.6901 | 2.812 | 3.2117 | 3.4869 | 3.0015 | 3.0727 | 3.1499 | 3.287 | 3.3352 | 3.5072 | 3.6541 | 3.8519 | 4.0712 | 4.3634 | 4.6434 | 4.97 | 5.3496 | 5.7323 | 6.0684 | 6.3194 | 7.1588 | 7.7479
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.2731 | 1.3121 | 1.4149 | 1.5438 | 1.6908 | 1.8563 | 2.0444 | 2.2598 | 2.4814 | 2.7897 | 3.0315 | 3.1869 | 3.336 | 3.4711 | 3.5643 | 3.6765 | 4.2634 | 4.6836 | 3.0836 | 3.1679 | 3.4023 | 3.6952 | 4.0265 | 4.3951 | 4.8081 | 5.2855 | 5.7803 | 6.4495 | 6.9824 | 7.3334 | 7.6766 | 7.98 | 8.1832 | 8.4358 | 9.7362 | 10.6963
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.2607 | 1.3045 | 1.3898 | 1.5137 | 1.6687 | 1.8479 | 2.0277 | 2.2361 | 2.3396 | 2.5385 | 2.7445 | 2.9508 | 3.1531 | 3.3526 | 3.4995 | 3.6028 | 4.1562 | 4.5487 | 3.0614 | 3.1587 | 3.3564 | 3.6368 | 3.9869 | 4.3827 | 4.778 | 5.2357 | 5.4618 | 5.8864 | 6.3251 | 6.764 | 7.1941 | 7.6157 | 7.9313 | 8.1591 | 9.3736 | 10.2506
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.2508 | 1.2772 | 1.3214 | 1.397 | 1.4846 | 1.5931 | 1.7182 | 1.8892 | 2.0464 | 2.3005 | 2.4824 | 2.6563 | 2.8281 | 2.9909 | 3.1063 | 3.18 | 3.5551 | 3.8829 | 3.0355 | 3.093 | 3.1875 | 3.3495 | 3.5381 | 3.7711 | 4.0397 | 4.4075 | 4.7468 | 5.2893 | 5.6702 | 6.0333 | 6.3913 | 6.7299 | 6.9729 | 7.1326 | 7.9495 | 8.6725
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.69007 | 0.73593 | 0.78572 | 0.84211 | 0.9072 | 0.98561 | 1.0755 | 1.2591 | 1.4273 | 1.6211 | 1.8027 | 1.974 | 2.1535 | 2.3323 | 2.5069 | 2.6849 | 3.3044 | 3.7457 | 1.6581 | 1.7537 | 1.8569 | 1.9734 | 2.1075 | 2.2683 | 2.4522 | 2.8423 | 3.2088 | 3.6359 | 4.0277 | 4.3894 | 4.7621 | 5.1337 | 5.4961 | 5.8657 | 7.2021 | 8.1854
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.74129 | 0.84699 | 0.97727 | 1.1273 | 1.3027 | 1.5058 | 1.7528 | 2.1148 | 2.4791 | 2.8075 | 3.0387 | 3.2036 | 3.435 | 3.5464 | 3.6633 | 3.7772 | 4.3863 | 4.9434 | 1.7686 | 1.9896 | 2.2589 | 2.5682 | 2.9285 | 3.3446 | 3.8486 | 4.6129 | 5.3934 | 6.106 | 6.6268 | 7.0068 | 7.5609 | 7.8166 | 8.0823 | 8.3453 | 9.7513 | 11.0761
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.72199 | 0.79335 | 0.87502 | 0.96497 | 1.0661 | 1.2104 | 1.4497 | 1.9572 | 2.2419 | 2.5749 | 2.8815 | 3.1918 | 3.4957 | 3.7507 | 3.9396 | 4.0604 | 4.6688 | 5.0335 | 1.734 | 1.8892 | 2.0637 | 2.2552 | 2.4695 | 2.7714 | 3.3004 | 4.4712 | 5.0992 | 5.837 | 6.5037 | 7.1769 | 7.8338 | 8.3754 | 8.7839 | 9.0564 | 10.445 | 11.2696
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.70633 | 0.76609 | 0.83895 | 0.92528 | 1.0298 | 1.1603 | 1.3158 | 1.5874 | 1.8444 | 2.163 | 2.4517 | 2.7179 | 3.0644 | 3.2833 | 3.4463 | 3.5398 | 4.0709 | 4.6068 | 1.6933 | 1.819 | 1.9707 | 2.1497 | 2.3656 | 2.6339 | 2.9524 | 3.5272 | 4.0772 | 4.7704 | 5.3874 | 5.9536 | 6.715 | 7.1717 | 7.5165 | 7.7252 | 8.9385 | 10.1876
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.42546 | 0.45957 | 0.50011 | 0.54779 | 0.60273 | 0.68628 | 0.77337 | 0.93784 | 1.096 | 1.2762 | 1.4403 | 1.5748 | 1.71 | 1.847 | 1.9804 | 2.1244 | 2.6791 | 3.1096 | 1.0197 | 1.092 | 1.1763 | 1.2751 | 1.3888 | 1.5599 | 1.7383 | 2.0921 | 2.441 | 2.8445 | 3.2039 | 3.4918 | 3.7751 | 4.0625 | 4.3422 | 4.6443 | 5.8563 | 6.8211
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.46079 | 0.5415 | 0.64304 | 0.75906 | 0.89134 | 1.0755 | 1.2901 | 1.6027 | 1.9226 | 2.2205 | 2.4638 | 2.6504 | 2.8332 | 2.9752 | 3.1342 | 3.2969 | 4.2155 | 4.7843 | 1.0959 | 1.2677 | 1.4787 | 1.7194 | 1.9936 | 2.3724 | 2.812 | 3.479 | 4.172 | 4.8241 | 5.3701 | 5.7952 | 6.2135 | 6.529 | 6.8801 | 7.2414 | 9.2966 | 10.6476
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.44775 | 0.50348 | 0.57215 | 0.64897 | 0.72925 | 0.85511 | 1.0667 | 1.386 | 1.654 | 1.965 | 2.2496 | 2.5174 | 2.878 | 3.0995 | 3.2874 | 3.4318 | 4.1897 | 4.5262 | 1.0726 | 1.197 | 1.3446 | 1.5092 | 1.6804 | 1.942 | 2.4141 | 3.1326 | 3.7301 | 4.4279 | 5.053 | 5.6413 | 6.4623 | 6.9362 | 7.343 | 7.6625 | 9.3484 | 10.1048
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.43674 | 0.48277 | 0.54195 | 0.61308 | 0.69533 | 0.81655 | 0.94202 | 1.1568 | 1.3636 | 1.6297 | 1.8682 | 2.0901 | 2.3022 | 2.4789 | 2.6291 | 2.7389 | 3.3965 | 3.9631 | 1.0441 | 1.1428 | 1.2668 | 1.4155 | 1.5873 | 1.838 | 2.0957 | 2.5566 | 3.0059 | 3.5958 | 4.114 | 4.5927 | 5.0454 | 5.4162 | 5.7361 | 5.9778 | 7.4757 | 8.7898
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Bulk Supply Point | 11 | Counterfactual | 1.6582 | 1.6857 | 1.7142 | 1.7488 | 1.7924 | 1.8482 | 1.9147 | 1.9895 | 2.0503 | 2.1124 | 2.1766 | 2.2475 | 2.3235 | 2.3994 | 2.4761 | 2.5533 | 2.7529 | 2.8492 | 4.1192 | 4.1766 | 4.2357 | 4.307 | 4.3972 | 4.5128 | 4.6502 | 4.8025 | 4.9269 | 5.0539 | 5.185 | 5.3293 | 5.4835 | 5.6373 | 5.7926 | 5.9493 | 6.3604 | 6.5654
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Bulk Supply Point | 11 | Electric Engagement | 1.6868 | 1.7483 | 1.8207 | 1.9046 | 2.0087 | 2.1304 | 2.2757 | 2.4244 | 2.5571 | 2.6669 | 2.7201 | 2.748 | 2.7752 | 2.8019 | 2.8254 | 2.8505 | 3.0463 | 3.4892 | 4.1808 | 4.3096 | 4.4592 | 4.6322 | 4.848 | 5.1013 | 5.4019 | 5.7049 | 5.976 | 6.2008 | 6.3125 | 6.3729 | 6.4326 | 6.4911 | 6.5431 | 6.5985 | 7.0561 | 8.1269
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Bulk Supply Point | 11 | Holistic Transition | 1.6761 | 1.7187 | 1.7644 | 1.8171 | 1.8854 | 1.9713 | 2.0709 | 2.1765 | 2.2663 | 2.3656 | 2.4729 | 2.7377 | 2.8478 | 2.9519 | 3.0208 | 3.056 | 3.8429 | 3.9874 | 4.1618 | 4.2546 | 4.3524 | 4.4645 | 4.6102 | 4.7935 | 5.0041 | 5.2225 | 5.4085 | 5.6133 | 5.8339 | 6.449 | 6.6762 | 6.8912 | 7.0357 | 7.1127 | 9.0359 | 9.3586
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Bulk Supply Point | 11 | Hydrogen Evolution | 1.667 | 1.7024 | 1.7457 | 1.7906 | 1.8571 | 1.9384 | 2.0342 | 2.1372 | 2.2281 | 2.3231 | 2.4252 | 2.5287 | 2.63 | 2.724 | 2.7805 | 2.8075 | 2.9906 | 3.4134 | 4.1383 | 4.2128 | 4.3027 | 4.3961 | 4.5352 | 4.7063 | 4.9063 | 5.1165 | 5.3022 | 5.496 | 5.7035 | 5.9136 | 6.1199 | 6.3115 | 6.4279 | 6.4856 | 6.91 | 7.9334
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.34332 | 0.4348 | 0.54625 | 0.65797 | 0.78659 | 0.9283 | 1.0907 | 1.3618 | 1.5797 | 1.7987 | 2.0258 | 2.2605 | 2.5278 | 2.7921 | 3.0549 | 3.3198 | 3.9126 | 4.1085 | 0.76924 | 0.95928 | 1.1892 | 1.42 | 1.6848 | 1.976 | 2.3087 | 2.8606 | 3.3058 | 3.7518 | 4.214 | 4.6908 | 5.2323 | 5.7672 | 6.2986 | 6.8344 | 8.0538 | 8.4807
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.45425 | 0.66853 | 0.9363 | 1.2309 | 1.5612 | 1.9232 | 2.3598 | 2.9105 | 3.4051 | 3.7834 | 3.9475 | 4.006 | 4.058 | 4.1139 | 4.1668 | 4.2258 | 4.5503 | 4.9062 | 1.0089 | 1.4553 | 2.0085 | 2.616 | 3.2956 | 4.0392 | 4.9316 | 6.0543 | 7.0639 | 7.8362 | 8.1796 | 8.3104 | 8.4275 | 8.5531 | 8.6721 | 8.8036 | 9.5274 | 10.315
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.41247 | 0.55336 | 0.72147 | 0.89902 | 1.0945 | 1.3165 | 1.5766 | 1.9582 | 2.2885 | 2.6246 | 3.0013 | 3.3704 | 3.7337 | 4.0785 | 4.2832 | 4.3622 | 4.7689 | 5.1588 | 0.93451 | 1.2396 | 1.5985 | 1.9773 | 2.3925 | 2.8608 | 3.4042 | 4.192 | 4.8753 | 5.5663 | 6.339 | 7.0966 | 7.8425 | 8.5516 | 8.9798 | 9.1567 | 10.0695 | 10.9483
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.37583 | 0.49399 | 0.64708 | 0.80282 | 0.98082 | 1.1832 | 1.4297 | 1.7964 | 2.1141 | 2.4345 | 2.7818 | 3.1288 | 3.4665 | 3.7833 | 3.9509 | 3.9978 | 4.2588 | 4.5263 | 0.84018 | 1.0882 | 1.4063 | 1.7307 | 2.1006 | 2.5201 | 3.0271 | 3.7767 | 4.4266 | 5.0775 | 5.7817 | 6.485 | 7.1694 | 7.8122 | 8.1562 | 8.259 | 8.8328 | 9.422
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.46567 | 0.61823 | 0.80644 | 1.027 | 1.267 | 1.5177 | 1.7199 | 1.971 | 2.1736 | 2.3725 | 2.5754 | 2.7865 | 3.0154 | 3.2433 | 3.4645 | 3.6888 | 4.2983 | 4.6049 | 1.0428 | 1.3626 | 1.7542 | 2.2123 | 2.7112 | 3.2327 | 3.6508 | 4.1686 | 4.5907 | 5.0058 | 5.4272 | 5.8614 | 6.3292 | 6.794 | 7.2441 | 7.7006 | 8.9714 | 9.6381
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.55208 | 0.83352 | 1.1789 | 1.5703 | 2.0126 | 2.4444 | 2.8617 | 3.3498 | 3.7904 | 4.134 | 4.3173 | 4.4161 | 4.5019 | 4.5813 | 4.6564 | 4.7378 | 5.1713 | 5.5751 | 1.231 | 1.8288 | 2.5562 | 3.3787 | 4.3115 | 5.2184 | 6.0837 | 7.0937 | 8.0098 | 8.7242 | 9.1181 | 9.3398 | 9.5355 | 9.713 | 9.8808 | 10.063 | 11.0366 | 11.9574
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.52094 | 0.74605 | 1.0203 | 1.3311 | 1.6697 | 2.0012 | 2.3036 | 2.6814 | 2.993 | 3.3122 | 3.6486 | 3.9898 | 4.3221 | 4.6279 | 4.8256 | 4.9227 | 5.4023 | 5.7607 | 1.1756 | 1.665 | 2.2541 | 2.9212 | 3.6499 | 4.3642 | 5.0132 | 5.8152 | 6.4731 | 7.1454 | 7.8473 | 8.5583 | 9.2498 | 9.8832 | 10.2999 | 10.5154 | 11.5908 | 12.3993
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.49562 | 0.70524 | 0.96669 | 1.2656 | 1.5942 | 1.9065 | 2.1765 | 2.5284 | 2.8298 | 3.1383 | 3.4534 | 3.7619 | 4.0605 | 4.3347 | 4.4978 | 4.5661 | 4.9192 | 5.2634 | 1.1091 | 1.5584 | 2.1137 | 2.7486 | 3.4496 | 4.1128 | 4.6779 | 5.4092 | 6.0386 | 6.6803 | 7.3288 | 7.9621 | 8.5737 | 9.1336 | 9.4709 | 9.6197 | 10.4062 | 11.1839
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.42225 | 0.5049 | 0.60731 | 0.71946 | 0.85095 | 0.99804 | 1.1677 | 1.4234 | 1.6258 | 1.8301 | 2.0387 | 2.2553 | 2.4989 | 2.7428 | 2.9818 | 3.222 | 3.8017 | 4.0156 | 0.91401 | 1.0868 | 1.2988 | 1.5308 | 1.8023 | 2.1056 | 2.4548 | 2.9763 | 3.3909 | 3.8077 | 4.233 | 4.6732 | 5.1668 | 5.6608 | 6.1443 | 6.6305 | 7.8228 | 8.2814
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.51793 | 0.71651 | 0.95859 | 1.2544 | 1.5959 | 1.9398 | 2.3389 | 2.8216 | 3.2498 | 3.5923 | 3.7503 | 3.8167 | 3.8746 | 3.9279 | 3.9819 | 4.0372 | 4.3343 | 4.6382 | 1.1203 | 1.5381 | 2.0385 | 2.6521 | 3.36 | 4.0693 | 4.8864 | 5.8693 | 6.7421 | 7.442 | 7.7727 | 7.9197 | 8.0489 | 8.1684 | 8.2891 | 8.412 | 9.0789 | 9.755
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.48148 | 0.61692 | 0.79771 | 0.99609 | 1.195 | 1.4032 | 1.6394 | 1.9779 | 2.2713 | 2.5889 | 2.9334 | 3.2798 | 3.6181 | 3.936 | 4.1309 | 4.2084 | 4.6007 | 4.9319 | 1.0553 | 1.3524 | 1.7394 | 2.1636 | 2.5867 | 3.0261 | 3.5199 | 4.2175 | 4.8244 | 5.4793 | 6.1876 | 6.9001 | 7.5955 | 8.2497 | 8.6574 | 8.8297 | 9.7089 | 10.4588
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.4512 | 0.56343 | 0.70114 | 0.86595 | 1.0532 | 1.2707 | 1.5168 | 1.8548 | 2.1338 | 2.4324 | 2.7567 | 3.0783 | 3.3904 | 3.6812 | 3.8459 | 3.899 | 4.162 | 4.4008 | 0.97688 | 1.2155 | 1.5018 | 1.8464 | 2.2376 | 2.6912 | 3.1999 | 3.8909 | 4.4599 | 5.067 | 5.7256 | 6.379 | 7.0126 | 7.6032 | 7.9412 | 8.0557 | 8.6326 | 9.1573
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.7264 | 0.78019 | 0.84308 | 0.91177 | 1.0129 | 1.1294 | 1.262 | 1.4854 | 1.729 | 1.9971 | 2.3078 | 2.5547 | 2.8184 | 3.0507 | 3.2381 | 3.4343 | 3.8704 | 4.1737 | 1.7221 | 1.8348 | 1.9652 | 2.1073 | 2.3167 | 2.558 | 2.8322 | 3.298 | 3.8143 | 4.3846 | 5.0659 | 5.6069 | 6.1804 | 6.6758 | 7.0608 | 7.4643 | 8.3285 | 8.9966
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.79021 | 0.92769 | 1.1155 | 1.3469 | 1.6049 | 1.9299 | 2.4379 | 2.9799 | 3.5945 | 3.9732 | 4.2041 | 4.3679 | 4.5083 | 4.5721 | 4.6432 | 4.7301 | 4.8107 | 5.1803 | 1.8598 | 2.1501 | 2.5438 | 3.0325 | 3.5749 | 4.2596 | 5.3601 | 6.5384 | 7.9213 | 8.7424 | 9.2572 | 9.6333 | 9.9558 | 10.1042 | 10.2661 | 10.4651 | 10.5877 | 11.455
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.76636 | 0.88734 | 1.0788 | 1.2964 | 1.5128 | 1.7978 | 2.212 | 2.6961 | 3.0646 | 3.4102 | 3.7474 | 3.9707 | 4.2163 | 4.4336 | 4.5917 | 4.6878 | 4.8239 | 5.1345 | 1.8174 | 2.083 | 2.4995 | 2.9697 | 3.4367 | 4.0785 | 5.0194 | 6.1114 | 6.9293 | 7.6818 | 8.4061 | 8.866 | 9.3843 | 9.8384 | 10.1765 | 10.3931 | 10.6367 | 11.3449
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.74589 | 0.84361 | 0.97696 | 1.1341 | 1.34 | 1.5609 | 1.8242 | 2.2007 | 2.6734 | 3.0376 | 3.3302 | 3.6063 | 3.8598 | 4.0823 | 4.229 | 4.3122 | 4.5855 | 4.926 | 1.7644 | 1.9739 | 2.255 | 2.5893 | 3.0277 | 3.4965 | 4.0693 | 4.8934 | 5.9723 | 6.7739 | 7.3937 | 7.9762 | 8.5025 | 8.9621 | 9.2704 | 9.4555 | 10.0339 | 10.8139
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.24763 | 0.33308 | 0.42612 | 0.52913 | 0.6465 | 0.7772 | 0.92648 | 1.1671 | 1.3588 | 1.5644 | 1.7807 | 2.0716 | 2.4164 | 2.7647 | 3.0719 | 3.3403 | 4.0585 | 4.439 | 0.54929 | 0.72854 | 0.92136 | 1.1344 | 1.3764 | 1.6453 | 1.9515 | 2.4411 | 2.8333 | 3.2538 | 3.695 | 4.2935 | 5.0031 | 5.7198 | 6.3498 | 6.8952 | 8.3792 | 9.1864
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.34294 | 0.54199 | 0.77982 | 1.0458 | 1.3465 | 1.6753 | 2.0813 | 2.5939 | 3.1047 | 3.5762 | 3.8652 | 3.9951 | 4.0621 | 4.1457 | 4.2364 | 4.3174 | 4.7357 | 5.1323 | 0.75479 | 1.1739 | 1.6663 | 2.2157 | 2.8351 | 3.5116 | 4.3438 | 5.392 | 6.4456 | 7.4276 | 8.0463 | 8.3321 | 8.4813 | 8.6666 | 8.8667 | 9.0472 | 9.9872 | 10.8786
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.30736 | 0.46774 | 0.61943 | 0.78515 | 0.98784 | 1.2309 | 1.5653 | 2.0187 | 2.3766 | 2.7007 | 3.0451 | 3.4002 | 3.7339 | 4.0686 | 4.3005 | 4.4138 | 4.9446 | 5.4316 | 0.69115 | 1.0434 | 1.3687 | 1.7231 | 2.155 | 2.6703 | 3.3795 | 4.3295 | 5.0782 | 5.7478 | 6.4567 | 7.191 | 7.8788 | 8.5721 | 9.0601 | 9.3111 | 10.4976 | 11.5897
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.27762 | 0.38947 | 0.52174 | 0.67131 | 0.84189 | 1.0384 | 1.296 | 1.7161 | 2.1302 | 2.5745 | 2.9191 | 3.2648 | 3.5877 | 3.8997 | 4.0987 | 4.1793 | 4.5597 | 4.9498 | 0.61428 | 0.85128 | 1.1269 | 1.438 | 1.7919 | 2.1983 | 2.7313 | 3.5994 | 4.4628 | 5.3882 | 6.0902 | 6.7964 | 7.4521 | 8.0894 | 8.5014 | 8.6767 | 9.513 | 10.3681
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.20014 | 0.3031 | 0.37911 | 0.50731 | 0.63345 | 0.78284 | 0.91753 | 1.0729 | 1.1943 | 1.3238 | 1.4819 | 1.6452 | 1.8284 | 1.9971 | 2.1398 | 2.2873 | 2.7008 | 2.9218 | 0.45031 | 0.66957 | 0.82763 | 1.0936 | 1.3551 | 1.6649 | 1.9436 | 2.2619 | 2.5129 | 2.7793 | 3.1161 | 3.4614 | 3.846 | 4.1956 | 4.4848 | 4.7836 | 5.6285 | 6.0857
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.2446 | 0.4106 | 0.56516 | 0.79567 | 1.0491 | 1.3143 | 1.6436 | 1.9787 | 2.315 | 2.5384 | 2.6928 | 2.8007 | 2.8957 | 2.9894 | 3.0779 | 3.1642 | 3.5535 | 3.8968 | 0.54589 | 0.90081 | 1.2234 | 1.7079 | 2.2404 | 2.7975 | 3.5077 | 4.221 | 4.9521 | 5.4186 | 5.7379 | 5.9628 | 6.162 | 6.3576 | 6.5426 | 6.723 | 7.5417 | 8.2624
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.22732 | 0.36378 | 0.47481 | 0.65952 | 0.85441 | 1.1398 | 1.4164 | 1.6746 | 1.879 | 2.0592 | 2.2897 | 2.5214 | 2.7456 | 2.9575 | 3.1163 | 3.2202 | 3.6571 | 3.9965 | 0.51466 | 0.8141 | 1.0522 | 1.4483 | 1.8671 | 2.5039 | 3.1187 | 3.6795 | 4.1163 | 4.4878 | 4.9601 | 5.4355 | 5.8956 | 6.3301 | 6.6579 | 6.8758 | 7.7992 | 8.5218
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.21615 | 0.33976 | 0.44698 | 0.63302 | 0.8271 | 1.0317 | 1.2736 | 1.5394 | 1.824 | 2.0618 | 2.2777 | 2.4942 | 2.7026 | 2.8947 | 3.0288 | 3.1169 | 3.4399 | 3.6943 | 0.48459 | 0.75047 | 0.97568 | 1.3693 | 1.7802 | 2.2135 | 2.737 | 3.3059 | 3.9329 | 4.4361 | 4.8746 | 5.3149 | 5.7385 | 6.1288 | 6.4026 | 6.5843 | 7.2574 | 7.7887
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.4672 | 2.5347 | 2.617 | 2.706 | 2.8072 | 2.9224 | 3.0508 | 3.258 | 3.4476 | 3.6548 | 3.8544 | 4.0318 | 4.2327 | 4.4306 | 4.6243 | 4.8204 | 5.2792 | 5.4322 | 6.1042 | 6.2445 | 6.4146 | 6.5988 | 6.8077 | 7.0452 | 7.3089 | 7.7326 | 8.1244 | 8.5527 | 8.964 | 9.3256 | 9.7331 | 10.1344 | 10.5268 | 10.9238 | 11.8717 | 12.2074
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.5489 | 2.7085 | 2.9076 | 3.1488 | 3.4229 | 3.7114 | 4.0784 | 4.5312 | 4.89 | 5.1779 | 5.3083 | 5.3585 | 5.4025 | 5.4425 | 5.4818 | 5.5219 | 5.7632 | 6.0114 | 6.2805 | 6.6139 | 7.0264 | 7.5264 | 8.0944 | 8.6907 | 9.4483 | 10.3804 | 11.1136 | 11.7042 | 11.9798 | 12.0931 | 12.1939 | 12.2848 | 12.3735 | 12.4628 | 13.0048 | 13.5608
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.5186 | 2.6305 | 2.7821 | 2.9527 | 3.1576 | 3.3364 | 3.5479 | 3.8324 | 4.0737 | 4.3336 | 4.6127 | 4.8884 | 5.1623 | 5.417 | 5.5699 | 5.6271 | 5.9291 | 6.2313 | 6.2267 | 6.4698 | 6.7949 | 7.1599 | 7.5988 | 7.9772 | 8.4224 | 9.0124 | 9.5137 | 10.0505 | 10.6236 | 11.1903 | 11.7534 | 12.2773 | 12.5972 | 12.7254 | 13.406 | 14.1003
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.4919 | 2.5841 | 2.7034 | 2.8367 | 3.013 | 3.2105 | 3.4267 | 3.7156 | 3.944 | 4.1911 | 4.4555 | 4.7152 | 4.9673 | 5.2021 | 5.3271 | 6.4689 | 6.6809 | 6.8835 | 6.1578 | 6.3519 | 6.601 | 6.88 | 7.251 | 7.666 | 8.1157 | 8.7095 | 9.1769 | 9.6819 | 10.2205 | 10.7486 | 11.261 | 11.7379 | 11.9944 | 14.8371 | 15.3085 | 15.76
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.67915 | 0.83233 | 1.0199 | 1.1977 | 1.429 | 1.6919 | 1.9903 | 2.448 | 2.8244 | 3.2027 | 3.6561 | 4.1314 | 4.6565 | 5.1688 | 5.6115 | 6.0674 | 7.026 | 7.3574 | 1.5326 | 1.8522 | 2.2387 | 2.6063 | 3.0843 | 3.6274 | 4.2432 | 5.1822 | 5.9597 | 6.7402 | 7.6973 | 8.6974 | 9.7989 | 10.8675 | 11.7734 | 12.7048 | 14.6885 | 15.411
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.84093 | 1.183 | 1.6028 | 2.1156 | 2.7033 | 3.3134 | 4.0803 | 5.0198 | 5.9898 | 6.712 | 7.0798 | 7.2965 | 7.4885 | 7.5904 | 7.6853 | 7.7855 | 8.2402 | 8.6597 | 1.8825 | 2.5995 | 3.4667 | 4.5327 | 5.7548 | 7.0202 | 8.6183 | 10.5759 | 12.6502 | 14.1752 | 14.97 | 15.4615 | 15.9005 | 16.1365 | 16.3534 | 16.5828 | 17.6346 | 18.6043
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.78109 | 1.029 | 1.3587 | 1.7101 | 2.0832 | 2.5518 | 3.1391 | 3.9206 | 4.607 | 5.2377 | 5.8743 | 6.4954 | 7.0634 | 7.5768 | 7.8928 | 8.024 | 8.6063 | 9.0631 | 1.7762 | 2.3152 | 3.0191 | 3.7721 | 4.5693 | 5.5832 | 6.8602 | 8.5441 | 10.0235 | 11.3524 | 12.684 | 13.9816 | 15.1606 | 16.2206 | 16.8862 | 17.1842 | 18.5208 | 19.5794
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.7278 | 0.92886 | 1.173 | 1.4695 | 1.8029 | 2.1789 | 2.64 | 3.302 | 4.0215 | 4.7137 | 5.352 | 5.9797 | 6.5785 | 7.0882 | 7.371 | 7.4601 | 7.8431 | 8.1899 | 1.6388 | 2.064 | 2.5715 | 3.1944 | 3.8944 | 4.683 | 5.6536 | 7.0435 | 8.6045 | 10.0806 | 11.4064 | 12.7095 | 13.9501 | 14.9976 | 15.5848 | 15.7829 | 16.6499 | 17.4377
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.4998 | 1.5521 | 1.6377 | 1.7389 | 1.8394 | 1.9517 | 2.078 | 2.2805 | 2.4674 | 2.6713 | 2.8686 | 3.0403 | 3.2276 | 3.4107 | 3.5816 | 3.7533 | 4.2937 | 4.628 | 3.6447 | 3.7541 | 3.9319 | 4.142 | 4.3503 | 4.583 | 4.845 | 5.2716 | 5.6738 | 6.1139 | 6.5372 | 6.8999 | 7.2902 | 7.6706 | 8.0233 | 8.3774 | 9.5341 | 10.2796
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.5583 | 1.679 | 1.8775 | 2.1355 | 2.4108 | 2.6795 | 3.0237 | 3.4643 | 3.8524 | 4.1786 | 4.3904 | 4.527 | 4.655 | 4.7477 | 4.8425 | 4.9569 | 5.6805 | 6.153 | 3.7709 | 4.024 | 4.4446 | 4.9956 | 5.585 | 6.1496 | 6.876 | 7.815 | 8.6506 | 9.3524 | 9.8249 | 10.1413 | 10.4427 | 10.6573 | 10.8721 | 11.1343 | 12.8258 | 13.9445
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.5364 | 1.619 | 1.7926 | 2.01 | 2.1874 | 2.4067 | 2.6824 | 3.0326 | 3.3174 | 3.6127 | 3.8995 | 4.4869 | 4.7542 | 4.9837 | 5.1574 | 5.2696 | 5.8268 | 6.1674 | 3.7319 | 3.9123 | 4.2934 | 4.7695 | 5.1539 | 5.6313 | 6.2397 | 7.0086 | 7.629 | 8.2725 | 8.8878 | 10.2569 | 10.828 | 11.3116 | 11.6856 | 11.9391 | 13.2066 | 13.9835
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.5175 | 1.5859 | 1.7098 | 1.8776 | 2.0538 | 2.2438 | 2.4745 | 2.761 | 3.0152 | 3.3042 | 3.5751 | 3.8294 | 4.0659 | 4.2656 | 4.3986 | 4.475 | 5.0516 | 5.4766 | 3.683 | 3.8277 | 4.0895 | 4.4481 | 4.8271 | 5.2295 | 5.7194 | 6.3282 | 6.8755 | 7.4977 | 8.0704 | 8.6057 | 9.0992 | 9.5121 | 9.7916 | 9.9629 | 11.3117 | 12.2947
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.23636 | 0.28259 | 0.344 | 0.4094 | 0.47493 | 0.54749 | 0.62394 | 0.75251 | 0.86816 | 0.99016 | 1.1081 | 1.2155 | 1.3319 | 1.4474 | 1.5594 | 1.6765 | 2.0166 | 2.2061 | 0.54128 | 0.63811 | 0.76569 | 0.90124 | 1.0368 | 1.1861 | 1.3433 | 1.611 | 1.8557 | 2.1156 | 2.3644 | 2.5874 | 2.8267 | 3.0641 | 3.2935 | 3.5338 | 4.2552 | 4.6761
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.27876 | 0.38276 | 0.51492 | 0.66721 | 0.82548 | 0.97949 | 1.1865 | 1.4371 | 1.6672 | 1.8605 | 1.972 | 2.0379 | 2.0986 | 2.1453 | 2.2031 | 2.27 | 2.6029 | 2.8601 | 0.63279 | 0.85235 | 1.1287 | 1.4466 | 1.776 | 2.0923 | 2.5202 | 3.0416 | 3.524 | 3.9321 | 4.177 | 4.3284 | 4.4694 | 4.5758 | 4.7053 | 4.8558 | 5.6054 | 6.207
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.26283 | 0.33929 | 0.4524 | 0.5639 | 0.64383 | 0.75829 | 0.91867 | 1.117 | 1.2836 | 1.4689 | 1.6524 | 1.8275 | 1.997 | 2.1461 | 2.257 | 2.3257 | 2.6626 | 2.8773 | 0.60438 | 0.77133 | 1.0143 | 1.2535 | 1.4235 | 1.6665 | 2.0143 | 2.4417 | 2.799 | 3.1973 | 3.5863 | 3.957 | 4.3152 | 4.6268 | 4.8634 | 5.0172 | 5.7759 | 6.261
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.24927 | 0.31556 | 0.40384 | 0.49619 | 0.57937 | 0.68781 | 0.8285 | 0.9994 | 1.1485 | 1.3203 | 1.4882 | 1.6476 | 1.8033 | 1.9386 | 2.026 | 2.0706 | 2.3232 | 2.5733 | 0.56936 | 0.71067 | 0.89692 | 1.0915 | 1.2655 | 1.4923 | 1.7874 | 2.1444 | 2.4582 | 2.8223 | 3.1731 | 3.5052 | 3.8274 | 4.1057 | 4.2881 | 4.3877 | 4.9577 | 5.5292
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.41643 | 0.46901 | 0.52822 | 0.58257 | 0.64071 | 0.74326 | 0.89148 | 1.1266 | 1.3541 | 1.601 | 1.847 | 2.085 | 2.332 | 2.5835 | 2.8373 | 3.0036 | 3.546 | 3.8279 | 0.97587 | 1.0857 | 1.2086 | 1.321 | 1.4408 | 1.6527 | 1.9607 | 2.4546 | 2.939 | 3.4681 | 3.9925 | 4.4956 | 5.0137 | 5.5414 | 6.0738 | 6.4181 | 7.573 | 8.1944
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.46247 | 0.57841 | 0.70549 | 0.83643 | 0.98445 | 1.2059 | 1.5345 | 1.9687 | 2.3844 | 2.7664 | 3.0822 | 3.3629 | 3.6325 | 3.8472 | 4.0423 | 4.1369 | 4.6148 | 4.9778 | 1.075 | 1.319 | 1.5827 | 1.8526 | 2.157 | 2.6175 | 3.3081 | 4.2294 | 5.1176 | 5.9374 | 6.6298 | 7.2513 | 7.8508 | 8.3243 | 8.7553 | 8.9666 | 10.0359 | 10.8817
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.44466 | 0.52968 | 0.61435 | 0.69455 | 0.78383 | 0.96148 | 1.2536 | 1.6803 | 2.0494 | 2.4445 | 2.8349 | 3.22 | 3.5595 | 3.8705 | 4.127 | 4.2226 | 4.7017 | 4.9818 | 1.0431 | 1.2278 | 1.4091 | 1.5798 | 1.7688 | 2.1492 | 2.7867 | 3.7178 | 4.5192 | 5.378 | 6.219 | 7.0476 | 7.7746 | 8.436 | 8.99 | 9.2024 | 10.2717 | 10.9013
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.43027 | 0.50448 | 0.57968 | 0.65336 | 0.7368 | 0.89264 | 1.1359 | 1.4771 | 1.7916 | 2.146 | 2.4972 | 2.8346 | 3.1688 | 3.4792 | 3.7238 | 3.8172 | 4.2268 | 4.5769 | 1.0058 | 1.1634 | 1.3209 | 1.474 | 1.6469 | 1.975 | 2.4927 | 3.2214 | 3.8977 | 4.6621 | 5.4119 | 6.1311 | 6.841 | 7.4982 | 8.0239 | 8.2289 | 9.1455 | 9.9452
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 3.0934 | 3.0961 | 3.0987 | 3.1019 | 3.1058 | 3.1103 | 3.1153 | 3.1235 | 3.1303 | 3.1376 | 3.1507 | 3.1662 | 3.1839 | 3.1994 | 3.21 | 3.2188 | 3.2513 | 3.2736 | 7.7316 | 7.7374 | 7.7428 | 7.7496 | 7.7576 | 7.7669 | 7.7773 | 7.7941 | 7.8081 | 7.8232 | 7.8528 | 7.8872 | 7.9259 | 7.9595 | 7.9812 | 7.9993 | 8.0662 | 8.1126
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 3.0957 | 3.1019 | 3.1089 | 3.117 | 3.126 | 3.1369 | 3.1636 | 3.1905 | 3.2224 | 3.2412 | 3.2553 | 3.2639 | 3.2699 | 2.1412 | 2.1467 | 2.1512 | 2.174 | 2.1906 | 7.7366 | 7.7498 | 7.7644 | 7.781 | 7.7996 | 7.8221 | 7.883 | 7.9428 | 8.0149 | 8.0549 | 8.0852 | 8.1035 | 8.1163 | 5.2929 | 5.3046 | 5.3142 | 5.3649 | 5.4017
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 3.0948 | 3.0996 | 3.1045 | 3.1103 | 3.119 | 3.1528 | 3.1775 | 3.1989 | 3.2128 | 3.2252 | 3.2387 | 3.2548 | 2.1365 | 2.151 | 2.1622 | 2.1689 | 2.1985 | 3.3534 | 7.7348 | 7.7455 | 7.7562 | 7.7686 | 7.7871 | 7.8653 | 7.9224 | 7.9701 | 8.0001 | 8.026 | 8.054 | 8.0874 | 5.285 | 5.3152 | 5.3384 | 5.3527 | 5.417 | 8.2978
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 3.0943 | 3.098 | 3.1024 | 3.108 | 3.1143 | 3.122 | 3.142 | 3.168 | 3.1987 | 3.2205 | 3.234 | 3.2465 | 3.2602 | 2.1369 | 2.1463 | 2.1513 | 3.8744 | 3.8957 | 7.7336 | 7.7416 | 7.7507 | 7.7621 | 7.7752 | 7.7912 | 7.8368 | 7.8948 | 7.9653 | 8.0126 | 8.0403 | 8.0661 | 8.0943 | 5.2814 | 5.3007 | 5.3115 | 9.6111 | 9.6563
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.49314 | 0.63916 | 0.79983 | 0.97119 | 1.1711 | 1.3905 | 1.6421 | 2.0356 | 2.3597 | 2.7163 | 3.0942 | 3.4563 | 3.8767 | 4.3135 | 4.7318 | 5.1534 | 6.245 | 6.728 | 1.1035 | 1.4091 | 1.7425 | 2.0974 | 2.51 | 2.9621 | 3.4794 | 4.2821 | 4.9478 | 5.6817 | 6.458 | 7.1959 | 8.0507 | 8.9403 | 9.7909 | 10.6478 | 12.9049 | 13.9355
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.65155 | 0.97993 | 1.3662 | 1.8069 | 2.4994 | 3.0436 | 3.7205 | 4.5381 | 5.2653 | 5.8704 | 6.1681 | 6.2964 | 6.4162 | 6.5598 | 6.7036 | 6.8276 | 7.424 | 7.9476 | 1.4455 | 2.1347 | 2.9344 | 3.8452 | 5.3564 | 6.4767 | 7.8659 | 9.5366 | 11.0245 | 12.2696 | 12.8998 | 13.1846 | 13.4536 | 13.7746 | 14.0933 | 14.3717 | 15.7259 | 16.9152
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.59259 | 0.82108 | 1.0664 | 1.3328 | 1.6565 | 2.025 | 2.4324 | 3.013 | 3.5103 | 4.0602 | 4.6392 | 5.226 | 5.821 | 6.3989 | 6.776 | 6.9462 | 7.7126 | 8.3224 | 1.3404 | 1.8398 | 2.3658 | 2.9354 | 3.6242 | 4.4032 | 5.2587 | 6.4619 | 7.4941 | 8.6352 | 9.8312 | 11.0421 | 12.2718 | 13.4693 | 14.2623 | 14.6408 | 16.3634 | 17.7444
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.54216 | 0.72944 | 0.94252 | 1.182 | 1.4698 | 1.8112 | 2.1951 | 2.7486 | 3.2249 | 3.7609 | 4.3213 | 4.8461 | 5.3789 | 5.8915 | 6.2009 | 6.3164 | 6.8442 | 7.3262 | 1.2099 | 1.6059 | 2.0502 | 2.5488 | 3.1471 | 3.8572 | 4.6482 | 5.7793 | 6.7537 | 7.8518 | 8.996 | 10.0643 | 11.1496 | 12.1989 | 12.8391 | 13.0911 | 14.2609 | 15.3272
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | 0.77563 | 0.87532 | 0.98803 | 1.108 | 1.2502 | 1.41 | 1.5949 | 1.8946 | 2.1481 | 2.4063 | 2.669 | 2.9437 | 3.2514 | 3.556 | 3.8508 | 4.168 | 5.0413 | 5.5135 | 1.7738 | 1.9824 | 2.2158 | 2.464 | 2.7585 | 3.0895 | 3.4718 | 4.089 | 4.6193 | 5.1536 | 5.6943 | 6.2561 | 6.8824 | 7.5019 | 8.1009 | 8.7473 | 10.5642 | 11.5772
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | 0.88849 | 1.1265 | 1.4272 | 1.7504 | 2.1316 | 2.5258 | 3.0061 | 3.6018 | 4.1486 | 4.6029 | 4.8344 | 4.9527 | 5.052 | 5.1591 | 5.2801 | 5.3926 | 5.9884 | 6.5187 | 2.0175 | 2.5192 | 3.1499 | 3.8227 | 4.6205 | 5.4323 | 6.4161 | 7.6359 | 8.7606 | 9.7005 | 10.1953 | 10.4591 | 10.684 | 10.9233 | 11.191 | 11.4425 | 12.7905 | 13.9955
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | 0.84701 | 1.0214 | 1.2117 | 1.4278 | 1.668 | 1.9308 | 2.2457 | 2.695 | 3.0756 | 3.4925 | 3.9222 | 4.3802 | 4.7991 | 5.2085 | 5.4943 | 5.6396 | 6.333 | 6.9106 | 1.9437 | 2.3276 | 2.739 | 3.2085 | 3.7278 | 4.2813 | 4.9466 | 5.8862 | 6.6825 | 7.5536 | 8.4448 | 9.4117 | 10.2804 | 11.1298 | 11.7329 | 12.0554 | 13.6074 | 14.9033
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | 0.81034 | 0.94729 | 1.1283 | 1.3169 | 1.5426 | 1.7882 | 2.0701 | 2.4905 | 2.8608 | 3.2731 | 3.6885 | 4.0849 | 4.4817 | 4.8537 | 5.0962 | 5.1967 | 5.7235 | 6.2309 | 1.8491 | 2.1393 | 2.5267 | 2.9235 | 3.4027 | 3.9139 | 4.4934 | 5.3559 | 6.1181 | 6.9687 | 7.8197 | 8.6306 | 9.4403 | 10.2019 | 10.7049 | 10.9249 | 12.0983 | 13.2267
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 3.2709 | 3.3734 | 3.4956 | 3.6308 | 3.7829 | 3.9565 | 4.1495 | 4.463 | 4.7227 | 5.0036 | 5.2759 | 5.5765 | 5.9271 | 6.2635 | 6.5665 | 6.8558 | 7.5543 | 7.9733 | 6.8273 | 7.0414 | 7.2942 | 7.5737 | 7.8872 | 8.2443 | 8.6407 | 9.2844 | 9.8234 | 10.4081 | 10.9695 | 11.5876 | 12.3055 | 12.993 | 13.6079 | 14.1928 | 15.6397 | 16.5496
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 3.392 | 3.6373 | 3.9458 | 4.2959 | 4.6899 | 5.08 | 5.5593 | 6.1705 | 6.7507 | 7.2465 | 7.4965 | 7.5854 | 7.6654 | 7.7425 | 8.1128 | 8.2172 | 8.7552 | 9.2641 | 7.0894 | 7.6042 | 8.2448 | 8.9705 | 9.7859 | 10.5871 | 11.5679 | 12.8232 | 14.0226 | 15.0562 | 15.5955 | 15.7966 | 15.9795 | 16.1553 | 16.9224 | 17.1582 | 18.3808 | 19.549
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 3.3492 | 3.5522 | 3.7557 | 3.9866 | 4.2654 | 4.5563 | 4.9147 | 5.3498 | 5.7105 | 6.1056 | 6.5089 | 6.8832 | 7.2744 | 7.658 | 8.1771 | 8.3055 | 8.9286 | 9.4476 | 7.0132 | 7.4561 | 7.8924 | 8.3864 | 8.9822 | 9.5984 | 10.3617 | 11.2727 | 12.0239 | 12.8476 | 13.6806 | 14.4544 | 15.2695 | 16.0679 | 17.1376 | 17.4256 | 18.8351 | 20.0079
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 3.3057 | 3.438 | 3.6045 | 3.793 | 4.0072 | 4.2579 | 4.5762 | 5.063 | 5.5009 | 5.9705 | 6.374 | 6.7569 | 7.1336 | 7.4803 | 7.817 | 7.8871 | 8.2952 | 8.7719 | 6.9035 | 7.1829 | 7.5307 | 7.9239 | 8.3702 | 8.8909 | 9.5513 | 10.5619 | 11.4747 | 12.4555 | 13.2832 | 14.0654 | 14.8326 | 15.5394 | 16.227 | 16.3817 | 17.2999 | 18.3728
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.4526 | 0.52333 | 0.62714 | 0.72468 | 0.81393 | 0.9142 | 1.0345 | 1.2234 | 1.3883 | 1.559 | 1.7984 | 2.0503 | 2.3244 | 2.5731 | 2.7443 | 2.9206 | 3.4127 | 3.6512 | 0.98597 | 1.1333 | 1.3455 | 1.5467 | 1.73 | 1.9351 | 2.1816 | 2.5674 | 2.9062 | 3.257 | 3.7757 | 4.3221 | 4.9186 | 5.455 | 5.8014 | 6.1587 | 7.1691 | 7.6679
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.51362 | 0.65574 | 0.84352 | 1.0414 | 1.2385 | 1.4567 | 1.8172 | 2.2534 | 2.7794 | 3.1411 | 3.4117 | 3.624 | 3.8129 | 3.9607 | 4.1157 | 4.266 | 5.0246 | 5.6644 | 1.1191 | 1.4185 | 1.8039 | 2.2144 | 2.6197 | 3.0675 | 3.8363 | 4.7688 | 5.9323 | 6.7107 | 7.291 | 7.7531 | 8.1596 | 8.4662 | 8.7866 | 9.0982 | 10.6735 | 12.0024
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.49232 | 0.60175 | 0.72731 | 0.86748 | 0.98988 | 1.2366 | 1.5582 | 1.9537 | 2.305 | 2.615 | 2.9903 | 3.352 | 3.6725 | 3.9766 | 4.2186 | 4.3861 | 5.1721 | 5.7611 | 1.081 | 1.319 | 1.5833 | 1.8819 | 2.1406 | 2.6869 | 3.4075 | 4.2813 | 5.0567 | 5.726 | 6.5176 | 7.2731 | 7.9295 | 8.5514 | 9.0488 | 9.3976 | 11.0368 | 12.27
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.47494 | 0.56801 | 0.70726 | 0.84805 | 0.96824 | 1.1188 | 1.3662 | 1.7114 | 2.1445 | 2.5117 | 2.8617 | 3.1935 | 3.5047 | 3.7592 | 3.9455 | 4.0695 | 4.6453 | 5.0777 | 1.0359 | 1.2327 | 1.5178 | 1.8114 | 2.0592 | 2.3689 | 2.8983 | 3.6396 | 4.6083 | 5.4105 | 6.1489 | 6.8476 | 7.4951 | 8.0121 | 8.3919 | 8.6478 | 9.8389 | 10.738
Ratcliffe 132kV | NOTTINGHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | 0.6751 | 0.83986 | 1.0258 | 1.2567 | 1.522 | 1.7916 | 2.1187 | 2.6296 | 3.0352 | 3.4636 | 3.9293 | 4.4017 | 4.9381 | 5.465 | 5.9628 | 6.4746 | 7.7149 | 8.1902 | 1.5574 | 1.902 | 2.2872 | 2.7652 | 3.3134 | 3.8683 | 4.5414 | 5.5833 | 6.4141 | 7.2907 | 8.2507 | 9.2201 | 10.3175 | 11.3917 | 12.4011 | 13.4394 | 15.9913 | 16.9991
Ratcliffe 132kV | NOTTINGHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | 0.86854 | 1.2574 | 1.7298 | 2.2968 | 2.9438 | 3.606 | 4.4943 | 5.5466 | 6.4915 | 7.2343 | 7.5961 | 7.776 | 7.9357 | 8.0817 | 8.2262 | 8.3539 | 8.9378 | 9.4309 | 1.9746 | 2.7897 | 3.7669 | 4.9406 | 6.2783 | 7.6401 | 9.4837 | 11.648 | 13.5983 | 15.1234 | 15.8852 | 16.2805 | 16.6357 | 16.9606 | 17.2807 | 17.5668 | 18.8929 | 20.0184
Ratcliffe 132kV | NOTTINGHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | 0.79619 | 1.0603 | 1.3584 | 1.7243 | 2.1478 | 2.6558 | 3.2405 | 4.0028 | 4.6374 | 5.3044 | 6.0269 | 6.7542 | 7.4606 | 8.117 | 8.5369 | 8.7184 | 9.5231 | 10.1205 | 1.8454 | 2.423 | 3.0615 | 3.8439 | 4.7468 | 5.8399 | 7.0832 | 8.6714 | 9.9904 | 11.3683 | 12.8588 | 14.3611 | 15.8195 | 17.1749 | 18.0551 | 18.4584 | 20.2796 | 21.6427
Ratcliffe 132kV | NOTTINGHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | 0.73474 | 0.94974 | 1.2098 | 1.5453 | 1.9277 | 2.3219 | 2.8557 | 3.5957 | 4.2496 | 4.9207 | 5.6136 | 6.2995 | 6.9773 | 7.585 | 7.9452 | 8.0693 | 8.5775 | 9.0349 | 1.6867 | 2.1406 | 2.6823 | 3.3836 | 4.1813 | 4.9976 | 6.1143 | 7.642 | 9.0015 | 10.3773 | 11.7897 | 13.1905 | 14.5729 | 15.8128 | 16.5555 | 16.826 | 17.9485 | 18.9582
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.47551 | 0.58987 | 0.73319 | 0.89233 | 1.068 | 1.2671 | 1.4893 | 1.8483 | 2.1554 | 2.4631 | 2.7549 | 3.1481 | 3.6158 | 4.0883 | 4.5146 | 4.8593 | 5.7618 | 6.2244 | 1.0584 | 1.2975 | 1.5947 | 1.9241 | 2.2872 | 2.698 | 3.1556 | 3.8996 | 4.5449 | 5.1944 | 5.803 | 6.6224 | 7.5937 | 8.5746 | 9.4592 | 10.1691 | 12.0747 | 13.1018
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.59838 | 0.85653 | 1.1846 | 1.5546 | 1.9703 | 2.4339 | 2.9928 | 3.7309 | 4.4762 | 5.2063 | 5.7006 | 5.8913 | 6.0169 | 6.1389 | 6.268 | 6.3961 | 7.0744 | 7.7101 | 1.3239 | 1.8656 | 2.5483 | 3.3155 | 4.1765 | 5.1355 | 6.286 | 7.8191 | 9.3838 | 10.9392 | 12.0264 | 12.4624 | 12.757 | 13.0359 | 13.3297 | 13.6224 | 15.1745 | 16.6574
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.5525 | 0.76929 | 0.98326 | 1.2343 | 1.5938 | 2.0224 | 2.5122 | 3.1505 | 3.7024 | 4.2544 | 4.7348 | 5.1967 | 5.6527 | 6.0878 | 6.3773 | 6.5208 | 7.2542 | 7.8115 | 1.2424 | 1.7151 | 2.1742 | 2.7117 | 3.4836 | 4.4015 | 5.4586 | 6.8273 | 8.0123 | 9.1987 | 10.2083 | 11.1791 | 12.1365 | 13.0458 | 13.6639 | 13.9902 | 15.6643 | 16.9375
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.51194 | 0.66158 | 0.85172 | 1.0677 | 1.3114 | 1.5962 | 1.9751 | 2.56 | 3.1547 | 3.8936 | 4.3711 | 4.8099 | 5.2255 | 5.6238 | 5.8663 | 5.9674 | 6.5221 | 7.098 | 1.1379 | 1.4547 | 1.8536 | 2.3066 | 2.8172 | 3.4124 | 4.2049 | 5.4342 | 6.6963 | 8.2782 | 9.2769 | 10.1871 | 11.0429 | 11.862 | 12.3703 | 12.5969 | 13.8613 | 15.1852
Ratcliffe 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.070337 | 0.094449 | 0.15006 | 0.24353 | 0.34365 | 0.46656 | 0.60397 | 0.77737 | 0.95776 | 1.1539 | 1.3431 | 1.5147 | 1.6896 | 1.864 | 1.9444 | 2.0047 | 2.2173 | 2.3689 | 0.15705 | 0.20757 | 0.3237 | 0.51823 | 0.72724 | 0.98441 | 1.2728 | 1.6417 | 2.0296 | 2.4546 | 2.8624 | 3.2295 | 3.6013 | 3.9725 | 4.1412 | 4.267 | 4.7297 | 5.0708
Ratcliffe 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.086938 | 0.1377 | 0.24551 | 0.39661 | 0.57434 | 0.7811 | 1.0159 | 1.2741 | 1.5229 | 1.7603 | 1.9674 | 2.1537 | 2.3417 | 2.5131 | 2.5649 | 2.612 | 2.8641 | 3.0744 | 0.19287 | 0.30068 | 0.53007 | 0.85186 | 1.2328 | 1.6781 | 2.1821 | 2.7411 | 3.283 | 3.8035 | 4.2645 | 4.6816 | 5.1023 | 5.4833 | 5.6003 | 5.7079 | 6.2838 | 6.7827
Ratcliffe 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.080519 | 0.12518 | 0.22185 | 0.37583 | 0.54342 | 0.7261 | 0.93432 | 1.1815 | 1.4071 | 1.649 | 1.881 | 2.1077 | 2.3357 | 2.5446 | 2.6146 | 2.6642 | 2.9065 | 3.0445 | 0.18135 | 0.27918 | 0.48805 | 0.81999 | 1.1837 | 1.5808 | 2.0408 | 2.589 | 3.0875 | 3.6237 | 4.1331 | 4.631 | 5.131 | 5.586 | 5.7388 | 5.8502 | 6.4003 | 6.7124
Ratcliffe 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.075502 | 0.11345 | 0.20586 | 0.34923 | 0.51048 | 0.69947 | 0.88299 | 1.099 | 1.3088 | 1.5419 | 1.7658 | 1.9814 | 2.1995 | 2.399 | 2.4587 | 2.4932 | 2.6983 | 2.9024 | 0.16823 | 0.24946 | 0.44762 | 0.75486 | 1.103 | 1.5129 | 1.9094 | 2.3786 | 2.8366 | 3.3488 | 3.837 | 4.3064 | 4.7791 | 5.2107 | 5.3386 | 5.4159 | 5.8841 | 6.3585
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.93144 | 1.0566 | 1.2323 | 1.459 | 1.7077 | 1.9936 | 2.3134 | 2.7472 | 3.1751 | 3.5834 | 4.0042 | 4.5533 | 5.1843 | 5.7412 | 6.1346 | 6.4047 | 7.1335 | 7.5428 | 2.2457 | 2.5098 | 2.8782 | 3.3529 | 3.8756 | 4.4782 | 5.1607 | 6.0868 | 7.021 | 7.9078 | 8.8184 | 9.9958 | 11.3406 | 12.5175 | 13.3378 | 13.894 | 15.4283 | 16.3243
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.0261 | 1.3006 | 1.6745 | 2.1241 | 2.6653 | 3.2525 | 3.9501 | 4.7888 | 5.6587 | 6.5664 | 7.3125 | 7.794 | 8.1378 | 8.3501 | 8.4655 | 8.5785 | 9.105 | 9.5792 | 2.451 | 3.0402 | 3.8386 | 4.7989 | 5.9676 | 7.2391 | 8.754 | 10.566 | 12.4571 | 14.4491 | 16.1162 | 17.2116 | 18.0024 | 18.4868 | 18.7448 | 18.9989 | 20.1667 | 21.2556
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.99155 | 1.2553 | 1.5369 | 1.914 | 2.4143 | 2.9942 | 3.7055 | 4.4959 | 5.2233 | 5.9511 | 6.6085 | 7.1976 | 7.7514 | 8.1793 | 8.4041 | 8.5231 | 9.13 | 9.7307 | 2.3895 | 2.9726 | 3.5878 | 4.4133 | 5.5182 | 6.7991 | 8.3888 | 10.137 | 11.7509 | 13.3674 | 14.8056 | 16.0859 | 17.2874 | 18.2003 | 18.6754 | 18.9385 | 20.2943 | 21.6839
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.96139 | 1.1503 | 1.4227 | 1.7683 | 2.1757 | 2.6325 | 3.2106 | 3.9623 | 4.7539 | 5.6976 | 6.371 | 6.9954 | 7.5453 | 7.9618 | 8.1636 | 8.2555 | 8.9898 | 9.4893 | 2.3118 | 2.7221 | 3.3134 | 4.0622 | 4.9564 | 5.9644 | 7.2446 | 8.889 | 10.628 | 12.7052 | 14.1747 | 15.5303 | 16.7167 | 17.5997 | 18.0212 | 18.2239 | 19.934 | 21.071
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.65544 | 0.92897 | 1.0164 | 1.0912 | 1.1772 | 1.2642 | 1.3614 | 1.5197 | 1.6492 | 1.8103 | 1.9699 | 2.1786 | 2.4274 | 2.6703 | 2.8766 | 3.0432 | 3.4903 | 3.7065 | 1.4362 | 1.989 | 2.1711 | 2.3262 | 2.504 | 2.6832 | 2.8832 | 3.2054 | 3.4708 | 3.8111 | 4.1447 | 4.5821 | 5.1022 | 5.6076 | 6.0317 | 6.3698 | 7.2904 | 7.7441
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.72273 | 1.0845 | 1.2838 | 1.4633 | 1.6691 | 1.9061 | 2.18 | 2.5306 | 2.9171 | 3.2437 | 3.4596 | 3.5549 | 3.6175 | 3.6749 | 3.7567 | 3.8419 | 4.2578 | 4.598 | 1.5841 | 2.3291 | 2.7519 | 3.1235 | 3.5493 | 4.048 | 4.6153 | 5.3393 | 6.1577 | 6.8424 | 7.3052 | 7.5125 | 7.6502 | 7.7764 | 7.9506 | 8.132 | 9.0232 | 9.7515
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.70041 | 1.0305 | 1.1595 | 1.3014 | 1.4577 | 1.6764 | 2.0285 | 2.323 | 2.5372 | 2.7575 | 2.9938 | 3.2397 | 3.4782 | 3.6999 | 3.8682 | 3.9764 | 4.453 | 4.8071 | 1.5441 | 2.2328 | 2.51 | 2.8215 | 3.1578 | 3.6315 | 4.3947 | 5.0181 | 5.4665 | 5.9224 | 6.4106 | 6.919 | 7.4119 | 7.87 | 8.2207 | 8.4515 | 9.4745 | 10.2418
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.68317 | 0.99061 | 1.1248 | 1.2357 | 1.3618 | 1.5189 | 1.7156 | 2.0216 | 2.3425 | 2.6557 | 2.8885 | 3.1143 | 3.3397 | 3.5368 | 3.6656 | 3.7219 | 4.0596 | 4.3259 | 1.4991 | 2.1306 | 2.4198 | 2.6514 | 2.9142 | 3.25 | 3.6632 | 4.3038 | 4.9915 | 5.6487 | 6.1245 | 6.5862 | 7.0464 | 7.4491 | 7.7147 | 7.8353 | 8.5504 | 9.1153
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.17392 | 0.18657 | 0.20015 | 0.21494 | 0.23222 | 0.27526 | 0.31683 | 0.41993 | 0.53256 | 0.66656 | 0.77837 | 0.86674 | 0.94776 | 1.0304 | 1.1101 | 1.1899 | 1.5998 | 1.9801 | 0.41313 | 0.44015 | 0.46847 | 0.49922 | 0.53501 | 0.62236 | 0.70675 | 0.9382 | 1.198 | 1.5126 | 1.7687 | 1.9658 | 2.1416 | 2.3213 | 2.4942 | 2.6675 | 3.5935 | 4.4641
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.1875 | 0.21797 | 0.25427 | 0.2963 | 0.34384 | 0.43786 | 0.54655 | 0.75091 | 0.98786 | 1.2326 | 1.4668 | 1.6585 | 1.8485 | 2.0003 | 2.1468 | 2.3018 | 3.1504 | 3.7045 | 0.44243 | 0.50777 | 0.58321 | 0.67022 | 0.76845 | 0.95965 | 1.1801 | 1.631 | 2.1624 | 2.7146 | 3.2491 | 3.69 | 4.1281 | 4.4652 | 4.7909 | 5.1372 | 7.0303 | 8.3638
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.18266 | 0.21293 | 0.23664 | 0.26365 | 0.29379 | 0.36941 | 0.54106 | 0.80483 | 1.0223 | 1.285 | 1.511 | 1.7202 | 1.9191 | 2.0794 | 2.2179 | 2.3416 | 3.0336 | 3.2878 | 0.43381 | 0.50141 | 0.55251 | 0.61032 | 0.67453 | 0.8297 | 1.224 | 1.8393 | 2.3399 | 2.9483 | 3.4603 | 3.9349 | 4.384 | 4.7335 | 5.0386 | 5.3144 | 6.8614 | 7.4341
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.17808 | 0.19499 | 0.21422 | 0.23854 | 0.2659 | 0.32657 | 0.3912 | 0.5358 | 0.68974 | 0.90589 | 1.0808 | 1.2393 | 1.385 | 1.5043 | 1.6065 | 1.6984 | 2.2633 | 2.8158 | 0.42214 | 0.45866 | 0.49895 | 0.54954 | 0.6064 | 0.72997 | 0.86175 | 1.1843 | 1.5318 | 2.0301 | 2.4256 | 2.7809 | 3.103 | 3.3598 | 3.5822 | 3.7873 | 5.0794 | 6.3788
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.24855 | 0.33084 | 0.46985 | 0.649 | 0.82893 | 1.0338 | 1.2846 | 1.6243 | 1.8758 | 2.1355 | 2.4168 | 2.7317 | 3.1166 | 3.5045 | 3.8303 | 4.0796 | 4.7364 | 5.0359 | 0.54941 | 0.72313 | 1.0114 | 1.3832 | 1.7564 | 2.1817 | 2.7032 | 3.4042 | 3.9243 | 4.4602 | 5.0498 | 5.7104 | 6.5195 | 7.335 | 8.011 | 8.5169 | 9.8666 | 10.4952
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.33423 | 0.526 | 0.818 | 1.1719 | 1.554 | 1.9744 | 2.5152 | 3.1422 | 3.7157 | 4.3021 | 4.7314 | 4.9124 | 5.0387 | 5.1575 | 5.2525 | 5.3336 | 5.7076 | 6.0196 | 0.73393 | 1.1406 | 1.7504 | 2.4919 | 3.2916 | 4.1718 | 5.3101 | 6.623 | 7.838 | 9.0861 | 10.0168 | 10.4159 | 10.6977 | 10.9634 | 11.1689 | 11.3467 | 12.176 | 12.8671
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.30179 | 0.44011 | 0.64907 | 0.9239 | 1.2361 | 1.6335 | 2.1317 | 2.6902 | 3.1559 | 3.6451 | 4.0769 | 4.4713 | 4.8514 | 5.1849 | 5.4117 | 5.5249 | 5.9947 | 6.3689 | 0.67566 | 0.98242 | 1.4319 | 2.0222 | 2.6938 | 3.5561 | 4.6362 | 5.8322 | 6.8318 | 7.8752 | 8.7829 | 9.6067 | 10.4011 | 11.0896 | 11.5637 | 11.8106 | 12.8494 | 13.6846
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.27718 | 0.38797 | 0.58732 | 0.84636 | 1.1089 | 1.4082 | 1.8109 | 2.3146 | 2.791 | 3.4768 | 3.9085 | 4.2751 | 4.6325 | 4.958 | 5.1527 | 5.2355 | 5.5671 | 5.8371 | 0.6111 | 0.84758 | 1.2667 | 1.8148 | 2.3695 | 3.0025 | 3.8597 | 4.9207 | 5.9411 | 7.412 | 8.3126 | 9.0716 | 9.8113 | 10.4857 | 10.8863 | 11.0633 | 11.7803 | 12.3644
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.4465 | 1.5432 | 1.6548 | 1.7744 | 1.9168 | 2.0894 | 2.2884 | 2.6149 | 2.9306 | 3.1986 | 3.4677 | 3.8771 | 4.4396 | 5.0104 | 5.5442 | 5.9236 | 6.298 | 6.7509 | 3.5177 | 3.7198 | 3.9506 | 4.1976 | 4.4937 | 4.8549 | 5.273 | 5.9569 | 6.6416 | 7.2012 | 7.7581 | 8.6107 | 9.7855 | 10.9778 | 12.1093 | 12.9135 | 13.5057 | 14.4899
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.5602 | 1.8001 | 2.1386 | 2.4717 | 2.8685 | 3.3249 | 3.8548 | 4.5271 | 5.2292 | 5.5075 | 6.1294 | 6.4321 | 6.7303 | 6.8473 | 6.9704 | 7.0906 | 7.7122 | 8.2871 | 3.7637 | 4.2719 | 4.9973 | 5.6948 | 6.532 | 7.5001 | 8.607 | 10.0052 | 11.4836 | 11.9255 | 13.314 | 13.9868 | 14.6524 | 14.9147 | 15.1894 | 15.459 | 16.8637 | 18.1782
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.5184 | 1.7518 | 1.9593 | 2.2088 | 2.5632 | 3.0624 | 3.5684 | 4.1738 | 4.7464 | 4.9049 | 5.4077 | 5.8879 | 6.3555 | 6.7535 | 7.0304 | 7.1777 | 7.8795 | 8.4393 | 3.6893 | 4.2063 | 4.6614 | 5.2111 | 5.9834 | 7.077 | 8.1811 | 9.4781 | 10.7365 | 10.9473 | 12.0034 | 13.0129 | 13.9955 | 14.8247 | 15.412 | 15.7399 | 17.3191 | 18.5791
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.4819 | 1.6131 | 1.8336 | 2.0273 | 2.2693 | 2.5788 | 2.9739 | 3.5684 | 4.1649 | 4.4067 | 5.0456 | 5.5924 | 6.1132 | 6.4869 | 6.7267 | 6.827 | 7.3536 | 7.875 | 3.5953 | 3.8744 | 4.359 | 4.7706 | 5.2899 | 5.9625 | 6.8062 | 8.0606 | 9.3321 | 9.6822 | 11.0604 | 12.2195 | 13.305 | 14.0716 | 14.5708 | 14.7915 | 15.9684 | 17.1423
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.047931 | 0.065277 | 0.083333 | 0.10469 | 0.12859 | 0.15515 | 0.18589 | 0.23711 | 0.27889 | 0.3232 | 0.37851 | 0.46236 | 0.56562 | 0.66635 | 0.74669 | 0.79883 | 0.93774 | 1.0105 | 0.099735 | 0.13632 | 0.17372 | 0.21779 | 0.26694 | 0.32148 | 0.3845 | 0.4887 | 0.57421 | 0.66476 | 0.78196 | 0.95984 | 1.1783 | 1.39 | 1.5564 | 1.6621 | 1.9473 | 2.0988
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.064905 | 0.10437 | 0.15098 | 0.20325 | 0.26219 | 0.3261 | 0.41316 | 0.53879 | 0.69221 | 0.81724 | 0.91218 | 0.94849 | 0.96714 | 0.98448 | 1.0013 | 1.015 | 1.0724 | 1.1216 | 0.13611 | 0.21977 | 0.31616 | 0.42399 | 0.54526 | 0.67661 | 0.85908 | 1.125 | 1.4597 | 1.7252 | 1.9302 | 2.0091 | 2.0499 | 2.0879 | 2.1246 | 2.1551 | 2.2864 | 2.3983
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.058365 | 0.086954 | 0.11686 | 0.15289 | 0.22013 | 0.36583 | 0.47638 | 0.57679 | 0.64655 | 0.7117 | 0.78139 | 0.84855 | 0.91344 | 0.97354 | 1.0147 | 1.0359 | 1.1164 | 1.1829 | 0.12432 | 0.1878 | 0.25177 | 0.32867 | 0.47311 | 0.79282 | 1.0371 | 1.2554 | 1.4034 | 1.538 | 1.682 | 1.821 | 1.9553 | 2.0797 | 2.1661 | 2.2125 | 2.3934 | 2.5438
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.053898 | 0.076856 | 0.10387 | 0.13461 | 0.16976 | 0.21054 | 0.2859 | 0.41497 | 0.56128 | 0.69013 | 0.76329 | 0.83351 | 0.90097 | 0.96227 | 1.0017 | 1.0198 | 1.0788 | 1.1351 | 0.11249 | 0.1614 | 0.21747 | 0.28115 | 0.35381 | 0.43797 | 0.59844 | 0.87513 | 1.1973 | 1.4725 | 1.622 | 1.7653 | 1.9029 | 2.0279 | 2.1089 | 2.1474 | 2.2763 | 2.3978
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Counterfactual | 0.49566 | 0.6108 | 0.75736 | 0.9161 | 1.0899 | 1.2823 | 1.4983 | 1.8649 | 2.1833 | 2.5589 | 3.0371 | 3.5252 | 4.0459 | 4.5671 | 5.0228 | 5.482 | 6.4382 | 6.6834 | 1.1191 | 1.3593 | 1.663 | 1.992 | 2.3508 | 2.7477 | 3.1917 | 3.9412 | 4.5974 | 5.375 | 6.379 | 7.4004 | 8.4856 | 9.5681 | 10.5066 | 11.4522 | 13.439 | 13.9732
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.63156 | 0.91308 | 1.2575 | 1.6425 | 2.0772 | 2.6056 | 3.3166 | 4.1751 | 4.9722 | 5.6082 | 5.9678 | 6.1969 | 6.418 | 6.6231 | 6.8074 | 6.9921 | 7.5318 | 7.936 | 1.4128 | 2.0053 | 2.719 | 3.5153 | 4.4134 | 5.5106 | 7.0057 | 8.7964 | 10.47 | 11.7964 | 12.566 | 13.0734 | 13.564 | 14.0194 | 14.4288 | 14.8384 | 16.0457 | 16.95
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.58073 | 0.77969 | 1.0201 | 1.281 | 1.6696 | 2.1341 | 2.6362 | 3.2553 | 3.7979 | 4.3613 | 4.9622 | 5.5608 | 6.1516 | 6.6964 | 7.0591 | 7.2546 | 7.864 | 8.2962 | 1.3223 | 1.7577 | 2.2719 | 2.8297 | 3.6632 | 4.6778 | 5.7602 | 7.0678 | 8.2118 | 9.3925 | 10.6462 | 11.8954 | 13.1278 | 14.2644 | 15.0338 | 15.4682 | 16.8369 | 17.8206
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.53641 | 0.70496 | 0.91471 | 1.135 | 1.4457 | 1.8279 | 2.3065 | 2.9218 | 3.4951 | 4.0546 | 4.6257 | 5.1938 | 5.7512 | 6.2633 | 6.5834 | 6.7496 | 7.1985 | 7.5008 | 1.2079 | 1.5676 | 2.0058 | 2.4669 | 3.1216 | 3.9298 | 4.9502 | 6.2433 | 7.4613 | 8.6301 | 9.8134 | 10.99 | 12.1444 | 13.2043 | 13.8776 | 14.2425 | 15.2347 | 15.9068
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 3.4083 | 3.5328 | 3.7081 | 3.8515 | 4.0143 | 4.2021 | 4.4263 | 4.7614 | 5.0099 | 5.2619 | 5.5901 | 5.9416 | 6.3277 | 6.6973 | 7.0105 | 7.3311 | 8.2558 | 8.7033 | 6.9993 | 7.2606 | 7.6234 | 7.9206 | 8.2574 | 8.6455 | 9.1089 | 9.7959 | 10.3074 | 10.8249 | 11.5278 | 12.2768 | 13.0961 | 13.8721 | 14.5103 | 15.1615 | 17.0729 | 18.0295
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 3.5305 | 3.8029 | 4.1692 | 4.5746 | 5.0188 | 5.4587 | 6.0504 | 6.7928 | 7.5931 | 8.1326 | 8.3865 | 8.5195 | 8.6292 | 8.7251 | 8.8357 | 8.9743 | 9.6115 | 10.242 | 7.263 | 7.836 | 8.5968 | 9.4405 | 10.3629 | 11.2696 | 12.5119 | 14.0709 | 15.8137 | 16.9511 | 17.4899 | 17.7857 | 18.0337 | 18.2469 | 18.4885 | 18.7911 | 20.1954 | 21.5862
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 3.4843 | 3.6769 | 3.9764 | 4.2577 | 4.4983 | 4.8431 | 5.2985 | 5.9264 | 6.4191 | 6.8546 | 7.3252 | 7.845 | 8.3456 | 8.8065 | 9.1249 | 9.3073 | 10.1144 | 10.7703 | 7.1799 | 7.6002 | 8.2402 | 8.8422 | 9.3534 | 10.1092 | 11.1138 | 12.4818 | 13.5482 | 14.4568 | 15.4299 | 16.5017 | 17.5304 | 18.4732 | 19.1373 | 19.5351 | 21.3138 | 22.7794
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 3.4474 | 3.6121 | 3.8461 | 4.0775 | 4.3183 | 4.6035 | 4.9886 | 5.5329 | 6.1191 | 6.6245 | 7.0634 | 7.5017 | 7.9298 | 8.3142 | 8.5375 | 8.6851 | 9.2314 | 9.747 | 7.0839 | 7.434 | 7.9239 | 8.41 | 8.9137 | 9.5092 | 10.3286 | 11.4833 | 12.7834 | 13.8665 | 14.7683 | 15.6679 | 16.5461 | 17.3308 | 17.7882 | 18.1125 | 19.3054 | 20.4376
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Counterfactual | 0.73001 | 0.76328 | 0.79634 | 0.83301 | 0.87529 | 0.95201 | 1.0355 | 1.2138 | 1.3865 | 1.5842 | 1.7636 | 1.9283 | 2.0972 | 2.2667 | 2.428 | 2.5892 | 3.287 | 3.8878 | 1.7392 | 1.8097 | 1.8785 | 1.9545 | 2.0417 | 2.1979 | 2.3677 | 2.7511 | 3.133 | 3.5768 | 3.9699 | 4.3223 | 4.6764 | 5.0326 | 5.3709 | 5.7089 | 7.2216 | 8.543
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.75815 | 0.83315 | 0.91469 | 1.0138 | 1.1374 | 1.3263 | 1.5496 | 1.8673 | 2.2053 | 2.5292 | 2.8137 | 3.0347 | 3.2365 | 3.3926 | 3.5838 | 3.7867 | 4.9551 | 5.6229 | 1.7998 | 1.9599 | 2.1287 | 2.3329 | 2.5865 | 2.9705 | 3.4241 | 4.0926 | 4.8152 | 5.5116 | 6.1329 | 6.619 | 7.0664 | 7.3994 | 7.8151 | 8.2621 | 10.8339 | 12.4158
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.74722 | 0.80437 | 0.85752 | 0.91716 | 0.98865 | 1.1593 | 1.3868 | 1.7128 | 1.9814 | 2.2915 | 2.5534 | 2.9064 | 3.203 | 3.4483 | 3.6673 | 3.8476 | 4.8426 | 5.2404 | 1.7802 | 1.9074 | 2.0213 | 2.1485 | 2.3006 | 2.6555 | 3.1522 | 3.8737 | 4.4611 | 5.1429 | 5.6968 | 6.4852 | 7.1341 | 7.6582 | 8.1296 | 8.5244 | 10.7058 | 11.5892
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.73954 | 0.78608 | 0.83207 | 0.89104 | 0.96972 | 1.1031 | 1.2553 | 1.5269 | 1.7739 | 2.0841 | 2.4333 | 2.702 | 2.9624 | 3.1772 | 3.3678 | 3.5194 | 4.3669 | 5.0617 | 1.7597 | 1.8597 | 1.9555 | 2.0775 | 2.2392 | 2.5105 | 2.8208 | 3.4014 | 3.9291 | 4.6033 | 5.3779 | 5.9562 | 6.5104 | 6.961 | 7.3632 | 7.6915 | 9.5803 | 11.1803
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.45699 | 0.61952 | 0.82642 | 1.0468 | 1.284 | 1.5464 | 1.8034 | 2.2235 | 2.5667 | 2.9289 | 3.3053 | 3.6867 | 4.1219 | 4.5544 | 4.9707 | 5.4002 | 6.434 | 6.8309 | 1.0205 | 1.3608 | 1.789 | 2.2451 | 2.7352 | 3.2764 | 3.8034 | 4.6589 | 5.3615 | 6.1021 | 6.8713 | 7.6476 | 8.5314 | 9.409 | 10.2527 | 11.124 | 13.25 | 14.0911
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.61637 | 0.97301 | 1.4233 | 1.9198 | 2.4704 | 3.0763 | 3.7572 | 4.5943 | 5.3437 | 5.9509 | 6.2762 | 6.4502 | 6.6095 | 6.7598 | 6.9059 | 7.0484 | 7.7151 | 8.2698 | 1.3644 | 2.1148 | 3.0494 | 4.0792 | 5.2186 | 6.4719 | 7.8664 | 9.5748 | 11.1054 | 12.3505 | 13.032 | 13.4094 | 13.7574 | 14.0851 | 14.4028 | 14.7132 | 16.1754 | 17.3922
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.55665 | 0.80959 | 1.1176 | 1.4488 | 1.8279 | 2.2646 | 2.6859 | 3.2728 | 3.7991 | 4.3551 | 4.9825 | 5.6061 | 6.2133 | 6.7787 | 7.1535 | 7.3352 | 8.1342 | 8.7464 | 1.258 | 1.8109 | 2.4694 | 3.1775 | 3.9867 | 4.9139 | 5.7955 | 7.0071 | 8.0978 | 9.2464 | 10.5389 | 11.8256 | 13.0775 | 14.2435 | 15.0264 | 15.4228 | 17.1804 | 18.5432
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.50591 | 0.71864 | 1.0048 | 1.3107 | 1.6468 | 2.0346 | 2.4364 | 3.0189 | 3.5265 | 4.0783 | 4.6707 | 5.2626 | 5.8444 | 6.3673 | 6.6883 | 6.8191 | 7.3742 | 7.8255 | 1.1267 | 1.578 | 2.1756 | 2.8158 | 3.5177 | 4.327 | 5.1534 | 6.3427 | 7.3806 | 8.5065 | 9.7131 | 10.9209 | 12.1064 | 13.172 | 13.8325 | 14.1124 | 15.3093 | 16.2827
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.45258 | 0.46172 | 0.47102 | 0.48281 | 0.49622 | 0.51136 | 0.5283 | 0.55622 | 0.57826 | 0.60192 | 0.62644 | 0.65273 | 0.68223 | 0.71162 | 0.74031 | 0.76917 | 0.85729 | 0.9091 | 1.1231 | 1.1424 | 1.1618 | 1.1861 | 1.2137 | 1.2448 | 1.2796 | 1.3363 | 1.3813 | 1.4296 | 1.4795 | 1.5329 | 1.5927 | 1.6522 | 1.7102 | 1.7685 | 1.9481 | 2.0545
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.46096 | 0.48187 | 0.51254 | 0.54789 | 0.58646 | 0.62846 | 0.67748 | 0.73865 | 0.79542 | 0.84257 | 0.87077 | 0.8899 | 0.9064 | 0.91873 | 0.92776 | 0.93694 | 0.97215 | 1.0014 | 1.1412 | 1.1858 | 1.2514 | 1.3267 | 1.4084 | 1.4968 | 1.5987 | 1.7258 | 1.8443 | 1.9424 | 2.0022 | 2.0441 | 2.0816 | 2.1097 | 2.1294 | 2.1507 | 2.234 | 2.3038
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.45755 | 0.47244 | 0.49281 | 0.51524 | 0.53991 | 0.5672 | 0.59688 | 0.63864 | 0.6757 | 0.71594 | 0.7584 | 0.79959 | 0.83783 | 0.87213 | 0.89562 | 0.90658 | 0.94689 | 0.97533 | 1.1351 | 1.1686 | 1.2138 | 1.263 | 1.3169 | 1.3753 | 1.4375 | 1.524 | 1.6009 | 1.6838 | 1.7714 | 1.8564 | 1.9355 | 2.0066 | 2.0561 | 2.0804 | 2.1728 | 2.24
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.45543 | 0.46733 | 0.48284 | 0.50135 | 0.52212 | 0.547 | 0.57702 | 0.62061 | 0.65898 | 0.70202 | 0.74619 | 0.78845 | 0.82822 | 0.86243 | 0.88508 | 1.0299 | 1.0589 | 1.0756 | 1.1292 | 1.1548 | 1.187 | 1.2253 | 1.2682 | 1.3194 | 1.3809 | 1.4695 | 1.5475 | 1.6348 | 1.7243 | 1.8099 | 1.8905 | 1.9599 | 2.006 | 2.3641 | 2.4266 | 2.464
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.40844 | 0.43491 | 0.46397 | 0.49893 | 0.53822 | 0.58852 | 0.63377 | 0.69854 | 0.75837 | 0.82326 | 0.88326 | 0.93794 | 0.99496 | 1.0508 | 1.105 | 1.1616 | 1.3928 | 1.5488 | 1.0047 | 1.0623 | 1.124 | 1.1979 | 1.2812 | 1.3873 | 1.4836 | 1.6229 | 1.7544 | 1.8981 | 2.028 | 2.1438 | 2.2626 | 2.3789 | 2.4919 | 2.6097 | 3.1053 | 3.4498
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.42494 | 0.48019 | 0.54577 | 0.84825 | 0.93227 | 1.0368 | 1.1444 | 1.2714 | 1.3982 | 1.5148 | 1.6124 | 1.6925 | 1.7644 | 1.8196 | 1.8757 | 1.9192 | 2.1758 | 2.3296 | 1.0408 | 1.1626 | 1.3045 | 2.0342 | 2.2145 | 2.4377 | 2.6651 | 2.9352 | 3.2071 | 3.4595 | 3.6743 | 3.852 | 4.0132 | 4.1349 | 4.2582 | 4.3509 | 4.9094 | 5.2719
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.41953 | 0.46833 | 0.51345 | 0.57033 | 0.63151 | 0.71711 | 0.81011 | 0.92618 | 1.026 | 1.1373 | 1.2471 | 1.3391 | 1.433 | 1.5142 | 1.5868 | 1.6418 | 1.961 | 2.0929 | 1.0311 | 1.1433 | 1.2422 | 1.3672 | 1.5015 | 1.6867 | 1.8926 | 2.1484 | 2.3676 | 2.612 | 2.8498 | 3.0451 | 3.2457 | 3.4165 | 3.5705 | 3.689 | 4.4063 | 4.7047
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.41504 | 0.44964 | 0.49082 | 0.54235 | 0.60142 | 0.67787 | 0.74942 | 0.84255 | 0.92861 | 1.0335 | 1.1288 | 1.2163 | 1.3038 | 1.3753 | 1.4382 | 1.4818 | 1.7005 | 1.8883 | 1.0194 | 1.096 | 1.185 | 1.2956 | 1.4231 | 1.5877 | 1.7403 | 1.9393 | 2.1243 | 2.3516 | 2.5547 | 2.7405 | 2.9249 | 3.0744 | 3.2064 | 3.3004 | 3.787 | 4.2176
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.5191 | 2.5505 | 2.5839 | 2.6218 | 2.6645 | 2.7216 | 2.7868 | 2.9071 | 3.019 | 3.1428 | 3.2601 | 3.3717 | 3.4883 | 3.6054 | 3.7187 | 3.8296 | 4.2836 | 4.656 | 6.0748 | 6.1472 | 6.2228 | 6.3076 | 6.402 | 6.5254 | 6.6648 | 6.9248 | 7.1718 | 7.4477 | 7.7047 | 7.9449 | 8.1923 | 8.441 | 8.6817 | 8.917 | 9.9106 | 10.7386
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.5376 | 2.5942 | 2.661 | 2.7424 | 2.8453 | 2.9771 | 3.1291 | 3.3408 | 3.5512 | 3.7481 | 3.9126 | 4.0416 | 4.1595 | 2.5942 | 2.694 | 2.7913 | 3.3041 | 3.6711 | 6.1148 | 6.2408 | 6.3852 | 6.559 | 6.7762 | 7.0513 | 7.3667 | 7.8165 | 8.2696 | 8.697 | 9.0612 | 9.3501 | 9.6169 | 5.6777 | 5.8997 | 6.1179 | 7.2739 | 8.1551
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.5308 | 2.5771 | 2.627 | 2.6825 | 2.749 | 2.8532 | 2.9981 | 3.2027 | 3.3751 | 3.5701 | 3.7502 | 3.9258 | 2.4459 | 2.5939 | 2.7194 | 2.8173 | 4.9764 | 5.2367 | 6.1025 | 6.2105 | 6.323 | 6.447 | 6.5944 | 6.8169 | 7.1373 | 7.5909 | 7.9715 | 8.4034 | 8.7945 | 9.1762 | 5.4212 | 5.7393 | 6.0123 | 6.2307 | 11.5136 | 12.1209
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.5253 | 2.556 | 2.593 | 2.6384 | 2.7022 | 2.795 | 2.8992 | 3.0691 | 3.2246 | 3.4121 | 4.4344 | 4.5981 | 4.7556 | 4.8893 | 5.0014 | 5.0857 | 5.4651 | 5.7659 | 6.0884 | 6.157 | 6.2368 | 6.3339 | 6.4683 | 6.6606 | 6.8761 | 7.2359 | 7.5679 | 7.9738 | 10.4662 | 10.8144 | 11.1467 | 11.426 | 11.6622 | 11.844 | 12.6902 | 13.3886
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.21062 | 0.24795 | 0.30204 | 0.35747 | 0.42956 | 0.50475 | 0.57448 | 0.69965 | 0.8233 | 0.96861 | 1.098 | 1.2199 | 1.3397 | 1.4593 | 1.5731 | 1.6851 | 2.0834 | 2.375 | 0.49641 | 0.57545 | 0.68847 | 0.80398 | 0.95398 | 1.1091 | 1.2526 | 1.5254 | 1.8029 | 2.1338 | 2.4226 | 2.6912 | 2.95 | 3.2084 | 3.4527 | 3.6924 | 4.5816 | 5.2592
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.24053 | 0.32382 | 0.42802 | 0.54032 | 0.68092 | 0.8351 | 1.0014 | 1.2437 | 1.4988 | 1.781 | 1.9968 | 2.1481 | 2.2866 | 2.373 | 2.4608 | 2.563 | 3.1347 | 3.5858 | 0.56081 | 0.74073 | 0.95929 | 1.1939 | 1.4889 | 1.8093 | 2.1512 | 2.6734 | 3.2334 | 3.8727 | 4.3743 | 4.7314 | 5.0582 | 5.2551 | 5.4536 | 5.6888 | 7.0027 | 8.0995
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.22886 | 0.29325 | 0.36947 | 0.4487 | 0.55148 | 0.66841 | 0.85886 | 1.1258 | 1.3555 | 1.6296 | 1.8558 | 2.0812 | 2.296 | 2.4542 | 2.5765 | 2.664 | 3.154 | 3.3614 | 0.53982 | 0.68424 | 0.84849 | 1.0186 | 1.2396 | 1.487 | 1.9172 | 2.5271 | 3.0502 | 3.6789 | 4.1832 | 4.6899 | 5.1712 | 5.5143 | 5.7844 | 5.9851 | 7.1121 | 7.592
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.21959 | 0.27431 | 0.34351 | 0.41784 | 0.51586 | 0.62166 | 0.72561 | 0.89573 | 1.0617 | 1.2852 | 1.5057 | 1.7102 | 1.8965 | 2.0445 | 2.1506 | 2.2143 | 2.6302 | 3.0577 | 0.5159 | 0.63598 | 0.78264 | 0.93949 | 1.1476 | 1.3695 | 1.5851 | 1.9548 | 2.3204 | 2.8246 | 3.3182 | 3.7739 | 4.1837 | 4.503 | 4.7354 | 4.8809 | 5.8525 | 6.8723
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.50479 | 0.52992 | 0.55598 | 0.58563 | 0.61916 | 0.66281 | 0.71285 | 0.83505 | 0.95871 | 1.1061 | 1.2324 | 1.3391 | 1.4423 | 1.546 | 1.6475 | 1.7507 | 2.1884 | 2.5554 | 1.1318 | 1.1874 | 1.2434 | 1.3067 | 1.3779 | 1.4693 | 1.5736 | 1.8435 | 2.1243 | 2.4632 | 2.7477 | 2.9809 | 3.2013 | 3.423 | 3.6399 | 3.8603 | 4.8386 | 5.6789
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.52601 | 0.58182 | 0.64495 | 0.72093 | 0.81148 | 0.92294 | 1.0542 | 1.2794 | 1.5163 | 1.744 | 1.9355 | 2.089 | 2.2978 | 2.388 | 2.4861 | 2.6887 | 3.2 | 3.6767 | 1.1775 | 1.2994 | 1.4324 | 1.5913 | 1.7794 | 2.0094 | 2.2791 | 2.7692 | 3.2953 | 3.8067 | 4.2487 | 4.6077 | 5.0577 | 5.2659 | 5.4928 | 5.931 | 7.1354 | 8.3002
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.51826 | 0.5626 | 0.6057 | 0.65485 | 0.70903 | 0.7883 | 0.95691 | 1.1725 | 1.3857 | 1.6378 | 1.8516 | 2.0572 | 2.355 | 2.501 | 2.6225 | 2.8194 | 3.3242 | 3.5448 | 1.1637 | 1.2656 | 1.3601 | 1.467 | 1.584 | 1.7512 | 2.1362 | 2.6231 | 3.1097 | 3.6885 | 4.1694 | 4.6316 | 5.2749 | 5.5953 | 5.8668 | 6.289 | 7.4795 | 7.9998
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.51162 | 0.54261 | 0.57836 | 0.62174 | 0.67633 | 0.75161 | 0.83789 | 1.0121 | 1.1808 | 1.4048 | 1.5986 | 1.7776 | 2.0154 | 2.142 | 2.2426 | 2.3693 | 2.7784 | 3.1938 | 1.1466 | 1.2148 | 1.2905 | 1.3816 | 1.4952 | 1.6504 | 1.8274 | 2.2071 | 2.5795 | 3.085 | 3.5133 | 3.9059 | 4.4214 | 4.6914 | 4.9093 | 5.1818 | 6.1444 | 7.1472
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.33203 | 0.3722 | 0.56149 | 0.62206 | 0.67946 | 0.74831 | 0.8292 | 0.99817 | 1.1472 | 1.3217 | 1.477 | 1.6166 | 1.7587 | 1.9013 | 2.0414 | 2.1839 | 2.6847 | 3.0371 | 0.74198 | 0.82707 | 1.21 | 1.3357 | 1.4544 | 1.596 | 1.7624 | 2.1254 | 2.4548 | 2.8452 | 3.1856 | 3.4834 | 3.7807 | 4.0793 | 4.3723 | 4.6703 | 5.768 | 6.5719
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.37532 | 1.0329 | 1.166 | 1.3055 | 1.5685 | 1.7457 | 1.9511 | 2.2634 | 2.5789 | 2.868 | 3.0773 | 3.2287 | 3.37 | 3.465 | 3.5645 | 3.7185 | 4.2388 | 4.7266 | 0.83538 | 2.3751 | 2.6533 | 2.9425 | 3.5352 | 3.9001 | 4.3199 | 4.9843 | 5.6668 | 6.2996 | 6.7757 | 7.1293 | 7.4631 | 7.6838 | 7.9139 | 8.2554 | 9.4759 | 10.6568
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.35912 | 0.56449 | 1.0823 | 1.186 | 1.2752 | 1.391 | 1.5976 | 1.9122 | 2.1734 | 2.478 | 2.7512 | 3.0138 | 3.2612 | 3.458 | 3.6072 | 3.7567 | 4.2461 | 4.5054 | 0.80661 | 1.2329 | 2.4955 | 2.7177 | 2.9075 | 3.1506 | 3.6121 | 4.319 | 4.9009 | 5.5831 | 6.1827 | 6.7586 | 7.3007 | 7.7232 | 8.0508 | 8.3796 | 9.5202 | 10.1242
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.34523 | 0.53578 | 1.0446 | 1.1408 | 1.2232 | 1.3278 | 1.452 | 1.6772 | 1.8907 | 2.1619 | 2.408 | 2.6381 | 2.8487 | 3.021 | 3.1407 | 3.2388 | 3.6491 | 4.0877 | 0.77064 | 1.1595 | 2.3988 | 2.6008 | 2.7719 | 2.9876 | 3.2428 | 3.7246 | 4.1866 | 4.7848 | 5.317 | 5.8113 | 6.2604 | 6.6221 | 6.8788 | 7.0951 | 8.0608 | 9.1097
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Counterfactual | 0.38354 | 0.39028 | 0.39673 | 0.4048 | 0.4149 | 0.43067 | 0.4469 | 0.49432 | 0.54624 | 0.61068 | 0.66233 | 0.72657 | 0.79863 | 0.87236 | 0.93281 | 0.96691 | 1.0923 | 1.197 | 0.94407 | 0.9585 | 0.97195 | 0.98869 | 1.0096 | 1.0418 | 1.075 | 1.1825 | 1.3035 | 1.4556 | 1.5751 | 1.7171 | 1.8731 | 2.0328 | 2.164 | 2.2386 | 2.5159 | 2.7537
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.38918 | 0.40413 | 0.42123 | 0.44154 | 0.46464 | 0.49829 | 0.5378 | 0.63092 | 0.75693 | 0.90064 | 1.0406 | 1.0992 | 1.1429 | 1.1645 | 1.2095 | 1.2245 | 1.3794 | 1.5685 | 0.95626 | 0.98855 | 1.0241 | 1.0663 | 1.1141 | 1.1832 | 1.2639 | 1.4724 | 1.7578 | 2.0843 | 2.4058 | 2.5394 | 2.6408 | 2.6868 | 2.7813 | 2.8102 | 3.149 | 3.6101
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.38678 | 0.39804 | 0.40894 | 0.42278 | 0.44895 | 0.49688 | 0.5748 | 0.69377 | 0.79432 | 0.86703 | 0.90375 | 0.9478 | 1.0004 | 1.0382 | 1.0909 | 1.1165 | 1.3471 | 1.4387 | 0.95192 | 0.9776 | 1.0012 | 1.0309 | 1.0874 | 1.1898 | 1.3637 | 1.6336 | 1.8588 | 2.0241 | 2.0989 | 2.1932 | 2.3091 | 2.3887 | 2.4994 | 2.5558 | 3.0914 | 3.3048
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.38562 | 0.39429 | 0.40425 | 0.41742 | 0.43269 | 0.45595 | 0.49008 | 0.5709 | 0.69608 | 0.85317 | 0.93287 | 0.98377 | 1.0305 | 1.0607 | 1.0953 | 1.1026 | 1.2278 | 1.3607 | 0.94853 | 0.96732 | 0.98813 | 1.0155 | 1.0473 | 1.0951 | 1.1663 | 1.3476 | 1.6285 | 1.9865 | 2.1685 | 2.2803 | 2.3811 | 2.4428 | 2.5135 | 2.5249 | 2.8069 | 3.119
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.11975 | 0.14778 | 0.18924 | 0.26831 | 0.35483 | 0.45428 | 0.56959 | 0.70939 | 0.86156 | 0.92969 | 1.0073 | 1.0842 | 1.1633 | 1.2384 | 1.3082 | 1.3785 | 1.6566 | 1.8282 | 0.25412 | 0.31306 | 0.39956 | 0.56408 | 0.74631 | 0.95857 | 1.207 | 1.5109 | 1.8508 | 1.9964 | 2.1652 | 2.3314 | 2.5009 | 2.6608 | 2.8075 | 2.9551 | 3.5492 | 3.921
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.13112 | 0.1911 | 0.31469 | 0.45117 | 0.62861 | 0.81222 | 1.0013 | 1.2061 | 1.3572 | 1.4531 | 1.5257 | 1.585 | 1.6429 | 1.6964 | 1.7514 | 1.8055 | 2.0703 | 2.2722 | 0.27856 | 0.40953 | 0.69157 | 0.98875 | 1.3836 | 1.7952 | 2.2162 | 2.6707 | 2.9979 | 3.2043 | 3.3642 | 3.4966 | 3.6265 | 3.7457 | 3.868 | 3.9886 | 4.5817 | 5.0368
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.12664 | 0.19263 | 0.26882 | 0.41728 | 0.59992 | 0.76002 | 0.93112 | 1.1204 | 1.2483 | 1.3421 | 1.4352 | 1.5289 | 1.6207 | 1.707 | 1.7789 | 1.8354 | 2.1088 | 2.2887 | 0.27045 | 0.4211 | 0.59067 | 0.9224 | 1.3384 | 1.6995 | 2.0858 | 2.5112 | 2.7899 | 2.9939 | 3.1945 | 3.3962 | 3.5939 | 3.7787 | 3.9349 | 4.0604 | 4.6704 | 5.0714
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.12325 | 0.16867 | 0.28563 | 0.41324 | 0.57004 | 0.75036 | 0.91573 | 1.0991 | 1.2254 | 1.3174 | 1.4081 | 1.4968 | 1.5835 | 1.665 | 1.7326 | 1.786 | 2.0472 | 2.2368 | 0.26164 | 0.36067 | 0.63194 | 0.9112 | 1.2621 | 1.6735 | 2.0448 | 2.4545 | 2.7285 | 2.9272 | 3.1212 | 3.3107 | 3.4958 | 3.6694 | 3.8152 | 3.9331 | 4.5141 | 4.9395
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | 1.309 | 1.3825 | 1.4852 | 1.6069 | 1.7447 | 1.8987 | 2.0659 | 2.3109 | 2.5339 | 2.7717 | 2.9845 | 3.1695 | 3.3627 | 3.5579 | 3.7492 | 3.9398 | 4.5277 | 4.7887 | 2.9805 | 3.1346 | 3.3484 | 3.601 | 3.8873 | 4.2072 | 4.5549 | 5.0712 | 5.5487 | 6.0634 | 6.5178 | 6.9069 | 7.3088 | 7.715 | 8.1128 | 8.5091 | 9.7672 | 10.3505
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | 1.3566 | 1.4902 | 1.6763 | 1.8974 | 2.1572 | 2.4609 | 2.7923 | 3.2143 | 3.6184 | 3.9784 | 4.2312 | 4.3983 | 4.6667 | 4.8077 | 4.938 | 5.0681 | 5.6985 | 6.0074 | 3.0839 | 3.3665 | 3.7579 | 4.222 | 4.7684 | 5.4105 | 6.1035 | 6.9976 | 7.8617 | 8.6378 | 9.1976 | 9.5763 | 10.1949 | 10.5086 | 10.8001 | 11.0929 | 12.5367 | 13.285
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | 1.3391 | 1.4412 | 1.5832 | 1.7492 | 1.9488 | 2.1784 | 2.4755 | 3.0128 | 3.3489 | 3.706 | 4.0343 | 4.4537 | 4.7712 | 5.0282 | 5.2172 | 5.3441 | 5.8822 | 6.0513 | 3.0527 | 3.2748 | 3.5801 | 3.9361 | 4.3683 | 4.8599 | 5.5104 | 6.7339 | 7.4675 | 8.2498 | 8.959 | 9.906 | 10.5835 | 11.128 | 11.5364 | 11.8204 | 13.0383 | 13.4317
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | 1.3247 | 1.4174 | 1.552 | 1.7119 | 1.9038 | 2.128 | 2.3817 | 2.7153 | 3.0235 | 3.3636 | 3.6761 | 3.952 | 4.3063 | 4.546 | 4.7166 | 4.8316 | 5.3718 | 5.6498 | 3.0154 | 3.2135 | 3.4996 | 3.8389 | 4.2472 | 4.7238 | 5.2639 | 5.9744 | 6.6354 | 7.3716 | 8.0388 | 8.6238 | 9.3987 | 9.9002 | 10.2632 | 10.5168 | 11.7547 | 12.4181
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | 0.65191 | 0.92464 | 1.0532 | 1.1957 | 1.3729 | 1.5818 | 1.8124 | 2.1623 | 2.4546 | 2.8995 | 3.2386 | 3.5558 | 3.9044 | 4.2534 | 4.6846 | 5.166 | 6.0975 | 6.565 | 1.5423 | 2.1036 | 2.3768 | 2.6803 | 3.0572 | 3.4997 | 3.9869 | 4.7196 | 5.3379 | 6.3315 | 7.053 | 7.7098 | 8.4249 | 9.1409 | 10.0684 | 11.1226 | 13.0966 | 14.1185
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | 0.93313 | 1.2151 | 1.559 | 1.9563 | 2.4321 | 3.0327 | 3.7184 | 4.5123 | 5.2342 | 5.9296 | 6.4713 | 6.7482 | 7.0042 | 7.231 | 7.4645 | 7.6899 | 8.5629 | 9.0869 | 2.1296 | 2.7384 | 3.4743 | 4.3294 | 5.3541 | 6.6653 | 8.1425 | 9.8335 | 11.3655 | 12.8768 | 14.1119 | 14.7476 | 15.3389 | 15.8563 | 16.3855 | 16.9009 | 18.8397 | 20.0785
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | 0.89051 | 1.1124 | 1.3572 | 1.6321 | 2.0327 | 2.5201 | 3.0815 | 3.7502 | 4.3404 | 5.089 | 5.6741 | 6.232 | 6.7758 | 7.2697 | 7.6445 | 7.8179 | 8.6637 | 9.1115 | 2.0533 | 2.5517 | 3.0981 | 3.7133 | 4.6216 | 5.7162 | 6.9801 | 8.4514 | 9.7528 | 11.4336 | 12.6918 | 13.8909 | 15.0582 | 16.1113 | 16.9263 | 17.3091 | 19.1916 | 20.2034
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | 0.85511 | 1.0335 | 1.2499 | 1.51 | 1.8322 | 2.2057 | 2.6881 | 3.2886 | 3.798 | 4.4021 | 5.0454 | 5.6627 | 6.1783 | 6.6327 | 6.9515 | 7.125 | 7.7098 | 8.2343 | 1.9621 | 2.3551 | 2.8297 | 3.4039 | 4.1152 | 4.9348 | 6.0008 | 7.2954 | 8.3864 | 9.6945 | 11.0992 | 12.4456 | 13.5362 | 14.4948 | 15.1814 | 15.5794 | 16.8901 | 18.0883
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.70762 | 0.77268 | 0.84791 | 0.93797 | 1.0461 | 1.173 | 0.99506 | 1.2331 | 1.4429 | 1.6764 | 1.9016 | 2.1101 | 2.3372 | 2.5639 | 2.7823 | 2.9982 | 3.6934 | 4.0973 | 1.6963 | 1.833 | 1.989 | 2.1753 | 2.3987 | 2.66 | 2.1541 | 2.6519 | 3.0984 | 3.5997 | 4.0763 | 4.5099 | 4.9772 | 5.4435 | 5.8925 | 6.3354 | 7.8126 | 8.7035
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.78266 | 0.94359 | 1.1376 | 1.358 | 1.6144 | 1.9068 | 1.9458 | 2.4118 | 2.8558 | 3.238 | 3.4804 | 3.6292 | 3.7701 | 3.8784 | 3.9946 | 4.1086 | 4.7196 | 5.2019 | 1.8584 | 2.1977 | 2.5998 | 3.0556 | 3.5855 | 4.1884 | 4.1274 | 5.0986 | 6.0324 | 6.8439 | 7.378 | 7.7165 | 8.0408 | 8.2852 | 8.5457 | 8.8035 | 10.1943 | 11.3336
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.75536 | 0.86911 | 0.9956 | 1.1373 | 1.2968 | 1.5 | 1.4535 | 1.8464 | 2.18 | 2.5577 | 2.9243 | 3.2835 | 3.632 | 3.9367 | 4.1574 | 4.2893 | 4.9121 | 5.2765 | 1.8097 | 2.0598 | 2.331 | 2.6338 | 2.9732 | 3.4014 | 3.1958 | 4.0463 | 4.7654 | 5.5823 | 6.3631 | 7.1276 | 7.868 | 8.5077 | 8.9791 | 9.2742 | 10.6831 | 11.5118
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.73154 | 0.81771 | 0.92599 | 1.0615 | 1.2223 | 1.4144 | 1.3123 | 1.6437 | 1.9415 | 2.2941 | 2.6311 | 2.9501 | 3.2626 | 3.5296 | 3.7078 | 3.8042 | 4.294 | 4.7547 | 1.7484 | 1.9313 | 2.1571 | 2.4398 | 2.7752 | 3.1746 | 2.826 | 3.5187 | 4.1454 | 4.8962 | 5.6034 | 6.2702 | 6.9202 | 7.4711 | 7.8442 | 8.0575 | 9.1694 | 10.2326
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Counterfactual | 2.9267 | 3.0436 | 3.1951 | 3.4047 | 3.6442 | 3.916 | 4.2246 | 4.6688 | 5.0687 | 5.4778 | 5.8569 | 6.215 | 6.5998 | 6.9722 | 7.3415 | 7.7143 | 8.7735 | 9.1618 | 7.1187 | 7.3689 | 7.6898 | 8.1333 | 8.6406 | 9.2174 | 9.8724 | 10.8127 | 11.6719 | 12.5553 | 13.3589 | 14.1031 | 14.897 | 15.664 | 16.4246 | 17.1926 | 19.4301 | 20.2869
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Electric Engagement | 3.0542 | 3.3442 | 3.7179 | 4.1993 | 4.7693 | 5.3944 | 6.1049 | 6.955 | 7.7594 | 8.4366 | 8.809 | 9.0277 | 9.2308 | 9.3935 | 9.5989 | 9.7648 | 10.451 | 10.8809 | 7.3983 | 8.026 | 8.8283 | 9.8648 | 11.095 | 12.4486 | 13.9726 | 15.7916 | 17.5248 | 18.998 | 19.8241 | 20.3206 | 20.7859 | 21.1559 | 21.6107 | 21.9888 | 23.5511 | 24.5577
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Holistic Transition | 3.0107 | 3.2262 | 3.4942 | 3.8562 | 4.2821 | 4.7658 | 5.3242 | 6.033 | 6.6657 | 7.3156 | 7.8918 | 8.3968 | 8.8962 | 9.3452 | 9.7032 | 9.8837 | 10.6627 | 11.2386 | 7.3205 | 7.8071 | 8.4036 | 9.2077 | 10.1555 | 11.231 | 12.4726 | 14.0291 | 15.4225 | 16.8514 | 18.0845 | 19.1434 | 20.1929 | 21.1321 | 21.892 | 22.2962 | 24.0555 | 25.4135
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.9746 | 3.1586 | 3.4 | 3.7401 | 4.145 | 4.6053 | 5.112 | 5.7693 | 6.3732 | 7.0019 | 7.5573 | 8.0597 | 8.5479 | 8.9764 | 9.2863 | 9.4382 | 11.2372 | 11.6615 | 7.227 | 7.6341 | 8.1626 | 8.9086 | 9.7998 | 10.8154 | 11.9237 | 13.3455 | 14.6607 | 16.0301 | 17.2061 | 18.2551 | 19.2717 | 20.1602 | 20.8133 | 21.1509 | 25.4818 | 26.4642
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.51915 | 0.62805 | 0.66133 | 0.70485 | 0.74786 | 0.80628 | 0.86672 | 0.98062 | 1.0908 | 1.2179 | 1.336 | 1.4417 | 1.5513 | 1.6585 | 1.7588 | 1.8573 | 2.2386 | 2.5174 | 1.2648 | 1.527 | 1.5965 | 1.687 | 1.7762 | 1.8963 | 2.0208 | 2.2658 | 2.5087 | 2.7924 | 3.052 | 3.2791 | 3.5101 | 3.736 | 3.9464 | 4.1527 | 4.9845 | 5.611
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.62818 | 0.69115 | 0.77693 | 0.87514 | 0.97671 | 1.1067 | 1.2599 | 1.4808 | 1.7119 | 1.9246 | 2.0906 | 2.2137 | 2.333 | 2.4199 | 2.511 | 2.6014 | 3.1857 | 3.5594 | 1.528 | 1.6629 | 1.8451 | 2.0503 | 2.2616 | 2.531 | 2.8473 | 3.3194 | 3.8203 | 4.286 | 4.6599 | 4.9423 | 5.2172 | 5.4132 | 5.6176 | 5.8216 | 7.1597 | 8.0498
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.61814 | 0.67325 | 0.72833 | 0.80159 | 0.88539 | 0.98647 | 1.1395 | 1.3634 | 1.5513 | 1.7702 | 1.9678 | 2.3184 | 2.5021 | 2.6535 | 2.7767 | 2.8683 | 3.3331 | 3.5734 | 1.5101 | 1.634 | 1.7531 | 1.9113 | 2.0949 | 2.3078 | 2.6488 | 3.1513 | 3.5695 | 4.0591 | 4.4921 | 5.3085 | 5.7103 | 6.0351 | 6.3028 | 6.5079 | 7.5545 | 8.097
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.60958 | 0.64592 | 0.70061 | 0.76651 | 0.83219 | 0.92427 | 1.0225 | 1.1884 | 1.3481 | 1.5487 | 1.7234 | 1.884 | 2.0433 | 2.169 | 2.2671 | 2.3307 | 2.7948 | 3.1657 | 1.488 | 1.5664 | 1.6846 | 1.8231 | 1.9607 | 2.154 | 2.3578 | 2.7144 | 3.061 | 3.503 | 3.8812 | 4.2273 | 4.5668 | 4.8316 | 5.0409 | 5.1831 | 6.2565 | 7.118
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.14717 | 0.1621 | 0.17993 | 0.20672 | 0.23007 | 0.25958 | 0.29203 | 0.35086 | 0.40437 | 0.46453 | 0.52134 | 0.5809 | 0.64503 | 0.70786 | 0.76656 | 0.81566 | 0.97332 | 1.0644 | 0.35361 | 0.38504 | 0.42206 | 0.47768 | 0.52597 | 0.58664 | 0.65328 | 0.77751 | 0.89297 | 1.0242 | 1.146 | 1.2715 | 1.4041 | 1.5336 | 1.6547 | 1.7549 | 2.0872 | 2.2857
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.16461 | 0.20057 | 0.24521 | 0.30514 | 0.36416 | 0.43711 | 0.52206 | 0.63303 | 0.74537 | 0.84923 | 0.92305 | 0.96233 | 0.99866 | 1.032 | 1.0672 | 1.1027 | 1.2973 | 1.4395 | 0.39125 | 0.46727 | 0.55991 | 0.68485 | 0.80699 | 0.95714 | 1.1314 | 1.3615 | 1.597 | 1.8164 | 1.9768 | 2.0641 | 2.1464 | 2.2216 | 2.3004 | 2.3804 | 2.8201 | 3.1584
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.15826 | 0.20024 | 0.23283 | 0.27565 | 0.31925 | 0.37381 | 0.43722 | 0.52642 | 0.60233 | 0.68776 | 0.77542 | 0.86857 | 0.95865 | 1.0356 | 1.0932 | 1.1299 | 1.3126 | 1.4096 | 0.37994 | 0.47228 | 0.54194 | 0.63382 | 0.72709 | 0.84234 | 0.97823 | 1.1697 | 1.3314 | 1.5137 | 1.6996 | 1.8999 | 2.0932 | 2.2558 | 2.3796 | 2.4619 | 2.8744 | 3.0947
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.15258 | 0.17253 | 0.20046 | 0.23882 | 0.27404 | 0.31824 | 0.37403 | 0.46802 | 0.55144 | 0.64739 | 0.72562 | 0.7987 | 0.87041 | 0.92971 | 0.96942 | 0.98537 | 1.1266 | 1.2648 | 0.36538 | 0.40785 | 0.46604 | 0.54677 | 0.62028 | 0.712 | 0.8278 | 1.0272 | 1.2035 | 1.4078 | 1.5712 | 1.7231 | 1.8712 | 1.992 | 2.0737 | 2.1065 | 2.4281 | 2.7489
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Counterfactual | 3.6509 | 3.7508 | 3.8591 | 3.9963 | 4.1734 | 4.4032 | 4.6605 | 5.0696 | 5.4385 | 5.8129 | 6.2075 | 6.5904 | 6.9947 | 7.3784 | 7.6917 | 7.9907 | 8.8312 | 9.3264 | 9.0192 | 9.2308 | 9.4568 | 9.7413 | 10.1085 | 10.5853 | 11.1191 | 11.979 | 12.7682 | 13.5746 | 14.4267 | 15.2421 | 16.0928 | 16.8956 | 17.5372 | 18.1475 | 19.9143 | 20.9961
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 3.7588 | 4.0022 | 4.3894 | 4.7214 | 5.1337 | 5.6255 | 6.2056 | 6.9529 | 7.6736 | 8.2216 | 8.5673 | 8.8034 | 9.0184 | 9.1819 | 9.3105 | 9.3959 | 9.8881 | 10.4476 | 9.2521 | 9.7725 | 10.6248 | 11.3136 | 12.1714 | 13.1999 | 14.4061 | 15.978 | 17.5093 | 18.6646 | 19.418 | 19.9465 | 20.4327 | 20.795 | 21.0808 | 21.2695 | 22.4002 | 23.7165
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 3.719 | 3.945 | 4.1268 | 4.3577 | 4.7096 | 5.0702 | 5.5115 | 6.1156 | 6.635 | 7.1667 | 7.6599 | 8.1561 | 8.6542 | 9.095 | 9.3733 | 9.4895 | 7.535 | 8.0446 | 9.1809 | 9.6991 | 10.0927 | 10.5911 | 11.3698 | 12.1386 | 13.0892 | 14.3874 | 15.4988 | 16.6361 | 17.6649 | 18.7063 | 19.7576 | 20.6811 | 21.2724 | 21.5277 | 16.5088 | 17.6802
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 3.6863 | 3.8259 | 4.0973 | 4.3002 | 4.5653 | 4.923 | 5.3111 | 5.8744 | 6.3927 | 6.9107 | 7.4235 | 7.9162 | 8.3915 | 8.801 | 9.0336 | 9.108 | 9.5407 | 10.0548 | 9.0965 | 9.3978 | 10.0136 | 10.438 | 10.9951 | 11.7555 | 12.5688 | 13.759 | 14.8617 | 15.9579 | 17.0315 | 18.0597 | 19.0479 | 19.8929 | 20.376 | 20.5326 | 21.515 | 22.6923
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.19599 | 0.21819 | 0.24753 | 0.28058 | 0.30756 | 0.35432 | 0.40238 | 0.51438 | 0.63229 | 0.77191 | 0.89073 | 0.98175 | 1.0672 | 1.153 | 1.2368 | 1.3229 | 1.7213 | 2.0552 | 0.43727 | 0.4846 | 0.54578 | 0.61453 | 0.67046 | 0.76602 | 0.86428 | 1.1127 | 1.3815 | 1.705 | 1.9739 | 2.1746 | 2.3579 | 2.5425 | 2.7224 | 2.9072 | 3.8033 | 4.5725
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.21495 | 0.26321 | 0.32573 | 0.39852 | 0.46645 | 0.57349 | 0.69616 | 0.90798 | 1.1417 | 1.3695 | 1.5718 | 1.736 | 1.8998 | 2.0177 | 2.2097 | 2.3386 | 3.0475 | 3.5467 | 0.47809 | 0.58181 | 0.7129 | 0.86515 | 1.006 | 1.2253 | 1.4759 | 1.9396 | 2.46 | 2.9726 | 3.4372 | 3.8185 | 4.2 | 4.4667 | 4.8811 | 5.1722 | 6.7725 | 7.9793
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.20776 | 0.24555 | 0.29386 | 0.34665 | 0.38927 | 0.46567 | 0.63068 | 0.88833 | 1.0996 | 1.3528 | 1.5701 | 1.7741 | 1.9694 | 2.119 | 2.319 | 2.4282 | 3.0225 | 3.2583 | 0.46521 | 0.55003 | 0.65394 | 0.76749 | 0.85855 | 1.0168 | 1.3944 | 1.9912 | 2.4751 | 3.0585 | 3.5484 | 4.0089 | 4.4478 | 4.7746 | 5.2017 | 5.4478 | 6.7906 | 7.3268
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.20187 | 0.23096 | 0.27323 | 0.32206 | 0.36369 | 0.43138 | 0.50306 | 0.65221 | 0.80254 | 1.011 | 1.1874 | 1.3481 | 1.4985 | 1.6145 | 1.7469 | 1.8271 | 2.3238 | 2.817 | 0.45001 | 0.51293 | 0.6021 | 0.70503 | 0.79191 | 0.93119 | 1.078 | 1.4075 | 1.7441 | 2.2205 | 2.6157 | 2.973 | 3.3028 | 3.5518 | 3.8332 | 4.0136 | 5.1578 | 6.3222
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.43177 | 0.48796 | 0.54626 | 0.61516 | 0.69732 | 0.78929 | 0.89408 | 1.0626 | 1.2013 | 1.3508 | 1.503 | 1.6806 | 1.8837 | 2.1179 | 2.4078 | 2.7181 | 3.1449 | 3.3359 | 1.0037 | 1.1217 | 1.2424 | 1.3848 | 1.5543 | 1.7437 | 1.9591 | 2.3045 | 2.5911 | 2.9005 | 3.2141 | 3.5803 | 3.9979 | 4.482 | 5.0859 | 5.7333 | 6.6191 | 7.0297
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.4916 | 0.62036 | 0.76997 | 0.94551 | 1.1487 | 1.3728 | 1.6402 | 1.9815 | 2.2915 | 2.5638 | 2.7503 | 2.8861 | 3.0166 | 3.1396 | 3.2662 | 3.4065 | 3.6421 | 3.8391 | 1.1328 | 1.4042 | 1.7136 | 2.0767 | 2.4966 | 2.959 | 3.5081 | 4.2098 | 4.8496 | 5.4166 | 5.8188 | 6.1198 | 6.4105 | 6.6832 | 6.9638 | 7.2895 | 7.8272 | 8.2829
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.46931 | 0.55956 | 0.65753 | 0.76975 | 0.91114 | 1.083 | 1.2924 | 1.5811 | 1.8376 | 2.1146 | 2.4919 | 2.7667 | 3.0367 | 3.2893 | 3.4739 | 3.5394 | 3.8246 | 4.0354 | 1.093 | 1.2916 | 1.5011 | 1.7411 | 2.0429 | 2.4086 | 2.8545 | 3.4633 | 4.0052 | 4.5899 | 5.4198 | 5.9972 | 6.5645 | 7.0945 | 7.4887 | 7.6353 | 8.282 | 8.7649
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.45026 | 0.52379 | 0.60932 | 0.70923 | 0.82864 | 0.96608 | 1.136 | 1.3828 | 1.612 | 1.8955 | 2.1853 | 2.4693 | 2.7479 | 3.0061 | 3.2095 | 3.3059 | 3.5109 | 3.6933 | 1.0439 | 1.2001 | 1.3779 | 1.5862 | 1.8351 | 2.121 | 2.4732 | 2.9826 | 3.4588 | 4.0521 | 4.6558 | 5.2474 | 5.8272 | 6.3648 | 6.797 | 7.0227 | 7.4814 | 7.8915
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.12057 | 0.13449 | 0.14987 | 0.1673 | 0.18731 | 0.2138 | 0.24267 | 0.31175 | 0.38172 | 0.46551 | 0.54764 | 0.6266 | 0.69605 | 0.75436 | 0.81087 | 0.87007 | 1.112 | 1.3041 | 0.27868 | 0.30828 | 0.34025 | 0.37638 | 0.41771 | 0.47204 | 0.53112 | 0.68309 | 0.84158 | 1.0339 | 1.2172 | 1.3888 | 1.5366 | 1.6607 | 1.7809 | 1.9068 | 2.4474 | 2.8902
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.13587 | 0.17007 | 0.21045 | 0.25667 | 0.30849 | 0.37247 | 0.45079 | 0.58319 | 0.72605 | 0.861 | 0.98231 | 1.0899 | 1.1835 | 1.2221 | 1.2791 | 1.3388 | 1.6584 | 1.9417 | 0.31166 | 0.38474 | 0.46862 | 0.56423 | 0.67112 | 0.80232 | 0.96226 | 1.2498 | 1.5657 | 1.868 | 2.1472 | 2.3969 | 2.6169 | 2.7046 | 2.8362 | 2.9751 | 3.7196 | 4.4069
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.13012 | 0.15527 | 0.18126 | 0.21039 | 0.24277 | 0.28936 | 0.38761 | 0.54139 | 0.66516 | 0.81375 | 0.95407 | 1.0835 | 1.2107 | 1.2968 | 1.3696 | 1.4239 | 1.7132 | 1.8528 | 0.30137 | 0.35774 | 0.41376 | 0.4761 | 0.54508 | 0.64246 | 0.86655 | 1.2203 | 1.5026 | 1.8433 | 2.1577 | 2.4435 | 2.7278 | 2.9157 | 3.0775 | 3.2024 | 3.8722 | 4.1937
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.12538 | 0.14433 | 0.16678 | 0.19457 | 0.22578 | 0.26713 | 0.31514 | 0.41302 | 0.50958 | 0.64092 | 0.76594 | 0.88953 | 0.99775 | 1.0696 | 1.1265 | 1.1653 | 1.4195 | 1.6902 | 0.28908 | 0.32986 | 0.37677 | 0.43451 | 0.4992 | 0.58431 | 0.68259 | 0.8963 | 1.11 | 1.4063 | 1.6827 | 1.9545 | 2.1899 | 2.3433 | 2.4667 | 2.5559 | 3.1506 | 3.7944
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.61824 | 0.65597 | 0.69733 | 0.74504 | 0.80669 | 0.88513 | 0.96737 | 1.0997 | 1.2194 | 1.355 | 1.4906 | 1.6177 | 1.7494 | 1.8775 | 1.9996 | 2.1228 | 2.5099 | 2.7248 | 1.4779 | 1.5584 | 1.6451 | 1.7448 | 1.8732 | 2.0361 | 2.2065 | 2.4877 | 2.7479 | 3.0462 | 3.3422 | 3.6143 | 3.8918 | 4.1603 | 4.414 | 4.67 | 5.5097 | 5.9868
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.65807 | 0.7454 | 0.88282 | 1.0022 | 1.1496 | 1.3234 | 1.5183 | 1.7591 | 1.9901 | 2.1863 | 2.3076 | 2.3837 | 2.4999 | 2.4797 | 2.5508 | 2.6208 | 2.9794 | 3.3213 | 1.5638 | 1.7497 | 2.0499 | 2.2978 | 2.6042 | 2.9653 | 3.3666 | 3.866 | 4.351 | 4.765 | 5.0312 | 5.2043 | 5.4575 | 5.3945 | 5.5579 | 5.7203 | 6.5591 | 7.3823
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.64296 | 0.71686 | 0.78346 | 0.86282 | 0.98397 | 1.1085 | 1.2592 | 1.4667 | 1.6396 | 1.8317 | 1.9969 | 2.168 | 2.3842 | 2.5521 | 2.6747 | 2.7469 | 3.3317 | 3.5486 | 1.5368 | 1.7047 | 1.8486 | 2.0205 | 2.2886 | 2.5535 | 2.8792 | 3.3286 | 3.6998 | 4.1133 | 4.4553 | 4.8131 | 5.2623 | 5.6192 | 5.8857 | 6.0513 | 7.4516 | 7.9563
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.63071 | 0.67903 | 0.77009 | 0.83786 | 0.92791 | 1.0419 | 1.1625 | 1.3468 | 1.5018 | 1.683 | 2.0308 | 2.2141 | 2.4089 | 2.5546 | 2.6528 | 2.7041 | 2.9776 | 3.2801 | 1.505 | 1.6085 | 1.8129 | 1.9546 | 2.1436 | 2.3825 | 2.6324 | 3.0223 | 3.3481 | 3.7338 | 4.5327 | 4.9213 | 5.3291 | 5.6322 | 5.8411 | 5.9571 | 6.5978 | 7.3142
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.57 | 0.59876 | 0.62921 | 0.66325 | 0.70199 | 0.75381 | 0.8104 | 0.94403 | 1.0791 | 1.2404 | 1.3783 | 1.4945 | 1.6072 | 1.7202 | 1.8309 | 1.9433 | 2.3868 | 2.7317 | 1.2958 | 1.3572 | 1.4206 | 1.4914 | 1.5716 | 1.6781 | 1.7942 | 2.0878 | 2.3933 | 2.7633 | 3.0726 | 3.3255 | 3.5648 | 3.8051 | 4.0404 | 4.2791 | 5.2723 | 6.0721
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.60034 | 0.66923 | 0.74868 | 0.839 | 0.94019 | 1.067 | 1.22 | 1.4771 | 1.7508 | 2.0092 | 2.2153 | 2.3747 | 2.5283 | 2.6313 | 2.7371 | 2.8448 | 3.5349 | 4.0569 | 1.3612 | 1.5087 | 1.674 | 1.8611 | 2.07 | 2.3304 | 2.6434 | 3.2008 | 3.8058 | 4.3838 | 4.8606 | 5.2365 | 5.6016 | 5.8411 | 6.086 | 6.3369 | 7.9135 | 9.1844
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.58879 | 0.64012 | 0.69187 | 0.74899 | 0.81265 | 0.90394 | 1.0928 | 1.3874 | 1.6261 | 1.9091 | 2.1524 | 2.3843 | 2.6038 | 2.7723 | 2.9081 | 3.0049 | 3.6261 | 3.8701 | 1.3405 | 1.456 | 1.5678 | 1.6904 | 1.8263 | 2.0178 | 2.4481 | 3.1247 | 3.6683 | 4.3168 | 4.8619 | 5.3817 | 5.873 | 6.2405 | 6.5425 | 6.7665 | 8.1784 | 8.746
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.57943 | 0.61786 | 0.66213 | 0.71429 | 0.77306 | 0.85248 | 0.945 | 1.1329 | 1.3161 | 1.5623 | 1.7741 | 1.969 | 2.1478 | 2.2876 | 2.3928 | 2.4621 | 2.9607 | 3.4422 | 1.3162 | 1.3991 | 1.4918 | 1.6005 | 1.7225 | 1.8863 | 2.0762 | 2.4866 | 2.8921 | 3.4481 | 3.9171 | 4.3453 | 4.734 | 5.0322 | 5.2611 | 5.4206 | 6.5784 | 7.7332
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.85698 | 0.8857 | 0.91492 | 0.9492 | 0.99033 | 1.0497 | 1.1132 | 1.2498 | 1.3868 | 1.5479 | 1.6886 | 1.809 | 1.9301 | 2.0514 | 2.1956 | 2.3066 | 2.7637 | 3.1219 | 2.0208 | 2.0822 | 2.1431 | 2.2144 | 2.2997 | 2.4216 | 2.5519 | 2.8503 | 3.1577 | 3.5245 | 3.8377 | 4.0985 | 4.355 | 4.6123 | 4.9288 | 5.1633 | 6.1769 | 6.9939
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.88636 | 0.95444 | 1.071 | 1.1688 | 1.2782 | 1.4202 | 1.5886 | 1.8583 | 2.1492 | 2.4243 | 2.6529 | 2.8262 | 3.0807 | 3.2026 | 3.3248 | 3.5728 | 4.3215 | 4.8382 | 2.084 | 2.2302 | 2.4895 | 2.6958 | 2.9251 | 3.2197 | 3.5665 | 4.1509 | 4.792 | 5.404 | 5.9253 | 6.3273 | 6.8937 | 7.1711 | 7.4461 | 8.0112 | 9.7004 | 10.9481
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.87548 | 0.9276 | 0.98484 | 1.0507 | 1.141 | 1.2515 | 1.452 | 1.7598 | 1.998 | 2.2796 | 2.662 | 2.896 | 3.2037 | 3.3803 | 3.5285 | 3.6949 | 4.342 | 4.6073 | 2.0645 | 2.1822 | 2.3079 | 2.4516 | 2.6537 | 2.8868 | 3.3398 | 4.0413 | 4.5793 | 5.2191 | 6.1067 | 6.6272 | 7.2918 | 7.6738 | 7.9988 | 8.361 | 9.8157 | 10.4195
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.86647 | 0.90451 | 0.94656 | 1.0003 | 1.0634 | 1.1521 | 1.2539 | 1.4504 | 1.6431 | 1.9262 | 2.137 | 2.33 | 2.5536 | 2.6962 | 2.8089 | 2.9835 | 3.4986 | 3.9921 | 2.0412 | 2.1235 | 2.2116 | 2.3238 | 2.4555 | 2.6386 | 2.848 | 3.2755 | 3.6995 | 4.3421 | 4.8058 | 5.2273 | 5.7034 | 6.0058 | 6.2484 | 6.6514 | 7.8326 | 8.9958
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.27248 | 0.30626 | 0.3364 | 0.36832 | 0.40686 | 0.45316 | 0.51207 | 0.64271 | 0.76484 | 0.91041 | 1.0371 | 1.1478 | 1.2581 | 1.3694 | 1.4772 | 1.586 | 1.9868 | 2.281 | 0.60744 | 0.68057 | 0.74297 | 0.80882 | 0.88821 | 0.98325 | 1.1041 | 1.3873 | 1.6602 | 1.9895 | 2.2698 | 2.5079 | 2.7397 | 2.9741 | 3.2007 | 3.4293 | 4.3166 | 4.9921
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.30885 | 0.39495 | 0.46772 | 0.55332 | 0.66098 | 0.78351 | 0.93608 | 1.179 | 1.4234 | 1.6504 | 1.8246 | 1.9552 | 2.0784 | 2.1584 | 2.2381 | 2.317 | 2.7761 | 3.1688 | 0.6885 | 0.87815 | 1.0285 | 1.2046 | 1.4259 | 1.6772 | 1.9896 | 2.5124 | 3.0485 | 3.5533 | 3.9551 | 4.263 | 4.5569 | 4.7446 | 4.9312 | 5.1188 | 6.1974 | 7.1638
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.29815 | 0.36565 | 0.41114 | 0.46186 | 0.52373 | 0.60656 | 0.78152 | 1.0477 | 1.2567 | 1.5027 | 1.718 | 1.9207 | 2.1106 | 2.2551 | 2.367 | 2.4406 | 2.8577 | 3.0177 | 0.66943 | 0.82382 | 0.92106 | 1.029 | 1.1603 | 1.3337 | 1.7291 | 2.335 | 2.8074 | 3.3672 | 3.8466 | 4.2983 | 4.7206 | 5.0339 | 5.2822 | 5.4538 | 6.4249 | 6.8029
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.28884 | 0.34856 | 0.38876 | 0.43557 | 0.50005 | 0.58144 | 0.68231 | 0.86737 | 1.0404 | 1.2666 | 1.467 | 1.6517 | 1.8206 | 1.9553 | 2.0522 | 2.114 | 2.4854 | 2.8369 | 0.64552 | 0.78033 | 0.86389 | 0.96092 | 1.0944 | 1.2619 | 1.4693 | 1.8685 | 2.2467 | 2.7518 | 3.1899 | 3.5908 | 3.954 | 4.2386 | 4.4471 | 4.5883 | 5.4617 | 6.3185
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.13968 | 0.15627 | 0.17386 | 0.19534 | 0.22125 | 0.26054 | 0.30169 | 0.38849 | 0.47473 | 0.57484 | 0.66328 | 0.73501 | 0.80559 | 0.87647 | 0.94548 | 1.0161 | 1.3134 | 1.5477 | 0.32852 | 0.36356 | 0.40006 | 0.44451 | 0.49798 | 0.57837 | 0.66248 | 0.85127 | 1.044 | 1.2712 | 1.4673 | 1.6223 | 1.7713 | 1.9212 | 2.0669 | 2.216 | 2.8723 | 3.4034
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.15677 | 0.19527 | 0.24127 | 0.29644 | 0.35941 | 0.44761 | 0.55161 | 0.71549 | 0.88786 | 1.0514 | 1.1878 | 1.2947 | 1.4001 | 1.4771 | 1.5573 | 1.6485 | 2.1019 | 2.4172 | 0.36543 | 0.44722 | 0.54254 | 0.65675 | 0.78694 | 0.96788 | 1.1804 | 1.5334 | 1.9109 | 2.273 | 2.5824 | 2.8285 | 3.0725 | 3.2458 | 3.4253 | 3.6286 | 4.6495 | 5.4087
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.15018 | 0.17774 | 0.20734 | 0.24315 | 0.28179 | 0.34329 | 0.4602 | 0.63995 | 0.78962 | 0.96716 | 1.1244 | 1.2721 | 1.413 | 1.5242 | 1.6175 | 1.6995 | 2.0883 | 2.2513 | 0.35365 | 0.41509 | 0.47868 | 0.55527 | 0.63749 | 0.76513 | 1.0287 | 1.4382 | 1.7756 | 2.1782 | 2.5271 | 2.8552 | 3.167 | 3.4071 | 3.6111 | 3.793 | 4.6692 | 5.0393
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.14544 | 0.16718 | 0.19299 | 0.22603 | 0.26523 | 0.32313 | 0.38602 | 0.50314 | 0.61711 | 0.76792 | 0.90143 | 1.0244 | 1.1401 | 1.2328 | 1.3065 | 1.3667 | 1.6896 | 2.0006 | 0.34098 | 0.38742 | 0.44118 | 0.50988 | 0.59143 | 0.71067 | 0.83946 | 1.0932 | 1.3432 | 1.681 | 1.974 | 2.242 | 2.4914 | 2.6876 | 2.8456 | 2.9789 | 3.7183 | 4.4496
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.1775 | 1.2937 | 1.4357 | 1.5887 | 1.7556 | 1.943 | 2.1414 | 2.448 | 2.6937 | 2.2059 | 2.4885 | 2.7872 | 3.1198 | 3.4519 | 3.7746 | 4.0977 | 4.9052 | 5.2005 | 2.8408 | 3.0838 | 3.3779 | 3.6949 | 4.0398 | 4.4266 | 4.8346 | 5.4596 | 5.9625 | 4.6226 | 5.2017 | 5.8121 | 6.4899 | 7.1657 | 7.8216 | 8.4786 | 10.1442 | 10.778
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.3025 | 1.5672 | 1.8967 | 2.2601 | 2.6534 | 3.0941 | 3.6189 | 4.2633 | 4.8439 | 4.5749 | 4.8149 | 4.9375 | 5.0464 | 5.1538 | 5.2624 | 5.3652 | 5.8404 | 6.2702 | 3.1114 | 3.6666 | 4.3509 | 5.1039 | 5.9164 | 6.8247 | 7.9022 | 9.2193 | 10.4079 | 9.5198 | 10.0247 | 10.2945 | 10.5357 | 10.7735 | 11.013 | 11.2405 | 12.2964 | 13.2504
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.2562 | 1.4409 | 1.6638 | 1.9002 | 2.1476 | 2.4419 | 2.7944 | 3.2731 | 3.6741 | 3.3505 | 3.8271 | 4.331 | 4.8239 | 5.2869 | 5.5805 | 5.7156 | 6.3058 | 6.771 | 3.0286 | 3.4305 | 3.9073 | 4.4127 | 4.939 | 5.5622 | 6.3035 | 7.2972 | 8.1293 | 7.1348 | 8.1184 | 9.1576 | 10.1736 | 11.1288 | 11.7442 | 12.0421 | 13.3551 | 14.405
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.217 | 1.3739 | 1.5758 | 1.7921 | 2.0149 | 2.281 | 2.5922 | 3.0355 | 3.4105 | 3.0635 | 3.507 | 3.9524 | 4.3782 | 4.7758 | 5.0143 | 5.1111 | 5.5135 | 5.8498 | 2.9272 | 3.2593 | 3.6821 | 4.1354 | 4.6006 | 5.155 | 5.7998 | 6.7091 | 7.4787 | 6.4267 | 7.3334 | 8.2445 | 9.1145 | 9.9264 | 10.42 | 10.6301 | 11.5113 | 12.2505
Stoke Bardolph 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.50122 | 0.57293 | 0.65998 | 0.74979 | 0.85141 | 0.96537 | 1.0993 | 1.3209 | 1.5009 | 1.6909 | 1.8885 | 2.0909 | 2.3223 | 2.5535 | 2.7764 | 3.0028 | 3.5044 | 3.6518 | 1.1342 | 1.2835 | 1.4631 | 1.6485 | 1.8576 | 2.0916 | 2.3661 | 2.817 | 3.1852 | 3.5736 | 3.9771 | 4.3891 | 4.8591 | 5.3283 | 5.7801 | 6.2389 | 7.2711 | 7.5899
Stoke Bardolph 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.59153 | 0.76318 | 0.97756 | 1.2138 | 1.4809 | 1.7746 | 2.1385 | 2.589 | 2.9945 | 3.3234 | 3.473 | 3.5347 | 3.592 | 3.6472 | 3.6979 | 3.7451 | 3.9728 | 4.1517 | 1.3294 | 1.6877 | 2.1304 | 2.6175 | 3.1665 | 3.7701 | 4.5145 | 5.4332 | 6.2611 | 6.9354 | 7.2511 | 7.3896 | 7.5194 | 7.6434 | 7.7577 | 7.8649 | 8.3836 | 8.7953
Stoke Bardolph 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.5578 | 0.67798 | 0.81179 | 0.95448 | 1.1237 | 1.3181 | 1.5376 | 1.8486 | 2.1246 | 2.4181 | 2.7348 | 3.0448 | 3.3461 | 3.6257 | 3.7975 | 3.8598 | 4.1412 | 4.3617 | 1.2692 | 1.5306 | 1.8164 | 2.121 | 2.4808 | 2.8914 | 3.3506 | 3.9923 | 4.5641 | 5.1701 | 5.8229 | 6.4628 | 7.0844 | 7.6613 | 8.0216 | 8.1629 | 8.8048 | 9.314
Stoke Bardolph 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.52901 | 0.62199 | 0.73872 | 0.86459 | 1.008 | 1.1774 | 1.3835 | 1.6867 | 1.9514 | 2.238 | 2.5394 | 2.8395 | 3.1327 | 3.3996 | 3.5465 | 3.5891 | 3.7685 | 3.927 | 1.1951 | 1.3906 | 1.6333 | 1.8951 | 2.1926 | 2.5432 | 2.9675 | 3.5871 | 4.1289 | 4.7141 | 5.3281 | 5.9404 | 6.5379 | 7.0816 | 7.3844 | 7.4785 | 7.8805 | 8.2332
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.49822 | 0.63594 | 0.79871 | 0.97563 | 1.1759 | 1.3954 | 1.6505 | 2.0463 | 2.3844 | 2.7006 | 3.0644 | 3.5057 | 4.0205 | 4.5137 | 4.9401 | 5.3175 | 6.2169 | 6.5503 | 1.1344 | 1.4252 | 1.7644 | 2.1329 | 2.5488 | 3.0034 | 3.5306 | 4.3419 | 5.0422 | 5.6893 | 6.4505 | 7.3782 | 8.4556 | 9.4797 | 10.3516 | 11.117 | 12.9679 | 13.6774
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.65333 | 0.98654 | 1.3757 | 1.8844 | 2.4247 | 2.9501 | 3.5717 | 4.3765 | 5.2284 | 5.9495 | 6.3752 | 6.531 | 6.6451 | 6.7474 | 6.8514 | 6.9449 | 7.3671 | 7.7102 | 1.4733 | 2.1849 | 2.9977 | 4.0777 | 5.2121 | 6.2993 | 7.5833 | 9.249 | 11.0544 | 12.5821 | 13.5095 | 13.853 | 14.1074 | 14.336 | 14.5666 | 14.7762 | 15.7344 | 16.5169
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.6002 | 0.85245 | 1.1903 | 1.5336 | 1.9061 | 2.3427 | 2.8454 | 3.5266 | 4.1215 | 4.6741 | 5.2053 | 5.7371 | 6.2589 | 6.7393 | 7.0443 | 7.1728 | 7.7181 | 8.1454 | 1.3787 | 1.9387 | 2.6804 | 3.4258 | 4.226 | 5.1664 | 6.2494 | 7.7029 | 8.981 | 10.1501 | 11.2461 | 12.3444 | 13.421 | 14.4129 | 15.0523 | 15.3385 | 16.5704 | 17.5479
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.55324 | 0.75949 | 0.992 | 1.301 | 1.6121 | 1.9389 | 2.3652 | 2.9959 | 3.673 | 4.3731 | 4.9359 | 5.4378 | 5.9313 | 6.3776 | 6.6363 | 6.7212 | 7.0821 | 7.3848 | 1.2577 | 1.706 | 2.1977 | 2.8657 | 3.5283 | 4.2129 | 5.1067 | 6.4265 | 7.8816 | 9.3742 | 10.5457 | 11.5705 | 12.5769 | 13.487 | 14.0206 | 14.2068 | 15.0064 | 15.6762
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.54253 | 0.64422 | 0.76598 | 0.89885 | 1.0486 | 1.2174 | 1.408 | 1.7225 | 1.9772 | 2.2451 | 2.524 | 2.8056 | 3.123 | 3.4404 | 3.751 | 4.075 | 4.8492 | 5.098 | 1.261 | 1.4731 | 1.7253 | 2.0002 | 2.3092 | 2.6568 | 3.0482 | 3.6889 | 4.2108 | 4.759 | 5.3294 | 5.9019 | 6.5456 | 7.1883 | 7.8171 | 8.4743 | 10.0677 | 10.604
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.67136 | 0.92055 | 1.228 | 1.5764 | 1.9702 | 2.4012 | 2.9279 | 3.5771 | 4.1505 | 4.6117 | 4.8119 | 4.9015 | 4.9856 | 5.0608 | 5.1332 | 5.1996 | 5.5089 | 5.8018 | 1.5389 | 2.0585 | 2.6938 | 3.413 | 4.2235 | 5.1093 | 6.1872 | 7.5104 | 8.6795 | 9.6218 | 10.0418 | 10.242 | 10.4323 | 10.6028 | 10.7665 | 10.918 | 11.6321 | 12.3037
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.62295 | 0.78726 | 0.98132 | 1.191 | 1.4235 | 1.6899 | 2.0016 | 2.4514 | 2.8529 | 3.2803 | 3.7438 | 4.228 | 4.702 | 5.1401 | 5.4014 | 5.4987 | 5.9307 | 6.2728 | 1.4526 | 1.809 | 2.2242 | 2.6718 | 3.1651 | 3.7268 | 4.3782 | 5.3062 | 6.1377 | 7.0202 | 7.9756 | 8.9736 | 9.9494 | 10.852 | 11.3996 | 11.6188 | 12.6053 | 13.4002
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.58151 | 0.71833 | 0.88545 | 1.0731 | 1.288 | 1.5344 | 1.8229 | 2.2444 | 2.6045 | 2.9934 | 3.4231 | 3.8588 | 4.2836 | 4.6717 | 4.8857 | 4.9494 | 5.2211 | 5.452 | 1.3456 | 1.6331 | 1.9813 | 2.3727 | 2.8194 | 3.3305 | 3.9241 | 4.7834 | 5.518 | 6.3093 | 7.1847 | 8.0735 | 8.9392 | 9.7299 | 10.1713 | 10.3119 | 10.9217 | 11.4413
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 7.301 | 7.4389 | 7.601 | 9.2283 | 9.4326 | 9.6618 | 9.9557 | 10.3445 | 10.6733 | 11.0412 | 11.4256 | 11.8093 | 12.2364 | 12.6534 | 13.0587 | 13.47 | 14.5731 | 15.0814 | 17.9445 | 18.2336 | 18.5698 | 22.5613 | 22.984 | 23.4576 | 24.0891 | 24.8851 | 25.5658 | 26.327 | 27.126 | 27.9176 | 28.7942 | 29.6467 | 30.4716 | 31.3093 | 33.5956 | 34.6845
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 7.452 | 7.7679 | 8.2332 | 8.7775 | 9.3659 | 10.0483 | 10.8198 | 11.7522 | 12.596 | 13.2562 | 13.6068 | 13.8257 | 14.0524 | 14.2358 | 14.3765 | 14.5499 | 15.4487 | 16.1476 | 18.2703 | 18.9335 | 19.929 | 21.1001 | 22.3547 | 23.8212 | 25.4489 | 27.4116 | 29.2034 | 30.5926 | 31.356 | 31.8595 | 32.3919 | 32.8175 | 33.1336 | 33.5333 | 35.5736 | 37.1952
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 7.3943 | 7.6113 | 7.9454 | 8.2862 | 8.7192 | 9.1772 | 9.6742 | 10.2936 | 10.8248 | 11.3858 | 11.9789 | 12.6017 | 13.2128 | 13.7824 | 14.1652 | 14.3545 | 15.3462 | 16.0768 | 18.167 | 18.6413 | 19.3848 | 20.1359 | 21.1027 | 22.1008 | 23.171 | 24.4773 | 25.5953 | 26.7648 | 27.9984 | 29.2929 | 30.5631 | 31.7465 | 32.5576 | 32.9828 | 35.1924 | 36.8846
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 7.3489 | 7.5292 | 7.7569 | 8.0284 | 8.3271 | 8.6805 | 9.1853 | 9.7723 | 10.2896 | 10.8273 | 11.3766 | 11.9241 | 12.4594 | 12.9457 | 13.2448 | 14.2033 | 14.8244 | 15.3211 | 18.0484 | 18.4301 | 18.9066 | 19.4817 | 20.1099 | 20.8491 | 21.9333 | 23.1507 | 24.2349 | 25.3466 | 26.4732 | 27.5956 | 28.6914 | 29.6858 | 30.3059 | 32.6592 | 34.0279 | 35.1407
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.792 | 1.9097 | 2.0545 | 2.2151 | 2.3548 | 2.4964 | 2.6448 | 2.8853 | 3.0835 | 3.3067 | 3.5299 | 3.7624 | 4.017 | 4.2722 | 4.5256 | 4.7795 | 4.4393 | 4.6916 | 4.3558 | 4.6021 | 4.9032 | 5.2365 | 5.5259 | 5.819 | 6.125 | 6.6184 | 7.0303 | 7.4923 | 7.9526 | 8.4297 | 8.9492 | 9.4694 | 9.986 | 10.5036 | 9.3854 | 9.9349
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.8927 | 2.1269 | 2.423 | 2.7783 | 3.1149 | 3.4478 | 3.8488 | 4.3532 | 4.7997 | 5.1787 | 5.3826 | 5.4859 | 5.5779 | 5.6644 | 5.7993 | 5.9595 | 5.3596 | 5.6895 | 4.5754 | 5.0685 | 5.6878 | 6.4379 | 7.1407 | 7.8266 | 8.6486 | 9.6822 | 10.5993 | 11.3833 | 11.819 | 12.0508 | 12.259 | 12.4532 | 12.7438 | 13.1227 | 11.5355 | 12.2914
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.8575 | 2.0289 | 2.2591 | 2.498 | 2.7056 | 2.9288 | 3.1846 | 3.5483 | 3.8746 | 4.2328 | 4.7618 | 5.1418 | 5.512 | 5.8558 | 6.127 | 6.2268 | 5.7006 | 6.0208 | 4.5129 | 4.8853 | 5.3873 | 5.9016 | 6.3445 | 6.8162 | 7.3563 | 8.1166 | 8.8002 | 9.5503 | 10.7151 | 11.5049 | 12.2738 | 12.9866 | 13.5536 | 13.7772 | 12.354 | 13.0901
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.826 | 1.9769 | 2.1692 | 2.4043 | 2.6096 | 2.8106 | 3.045 | 3.3871 | 3.6851 | 4.0132 | 4.3605 | 4.6977 | 5.0261 | 5.3307 | 5.539 | 5.689 | 5.0251 | 5.2936 | 4.4315 | 4.7526 | 5.1592 | 5.6634 | 6.0991 | 6.5189 | 7.0037 | 7.7077 | 8.3222 | 9.0008 | 9.715 | 10.4074 | 11.0806 | 11.7044 | 12.1356 | 12.4882 | 10.7481 | 11.3575
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.4542 | 0.5782 | 0.74965 | 0.96334 | 1.1697 | 1.4133 | 1.6768 | 2.0702 | 2.3991 | 2.7311 | 3.0818 | 3.436 | 3.8199 | 4.2051 | 4.5806 | 4.973 | 5.9548 | 6.3 | 1.0234 | 1.2824 | 1.6376 | 2.0806 | 2.5077 | 3.0119 | 3.5572 | 4.3634 | 5.0476 | 5.7319 | 6.456 | 7.1828 | 7.9633 | 8.7449 | 9.5058 | 10.3028 | 12.3245 | 13.0632
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.60559 | 0.90188 | 1.2956 | 1.788 | 2.3179 | 2.9125 | 3.5989 | 4.4153 | 5.1262 | 5.7065 | 5.9914 | 6.1301 | 6.2607 | 6.3836 | 6.4981 | 6.6106 | 7.1073 | 7.5709 | 1.3498 | 1.9687 | 2.785 | 3.8115 | 4.9168 | 6.1562 | 7.5787 | 9.2573 | 10.72 | 11.9154 | 12.518 | 12.8231 | 13.1133 | 13.3859 | 13.64 | 13.8899 | 15.0063 | 16.0418
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.54807 | 0.74567 | 1.0148 | 1.3603 | 1.7055 | 2.1112 | 2.5414 | 3.1263 | 3.6396 | 4.1841 | 4.7666 | 5.4013 | 6.0216 | 6.5959 | 6.9511 | 7.1038 | 7.7552 | 8.259 | 1.2468 | 1.6761 | 2.2541 | 2.9982 | 3.7392 | 4.6101 | 5.5225 | 6.7412 | 7.8141 | 8.9476 | 10.1488 | 11.4563 | 12.7332 | 13.9159 | 14.6584 | 14.9957 | 16.453 | 17.5994
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.50118 | 0.66473 | 0.89972 | 1.2098 | 1.5281 | 1.909 | 2.3094 | 2.8548 | 3.3211 | 3.8174 | 4.362 | 4.906 | 5.4302 | 5.9112 | 6.1897 | 6.2984 | 6.724 | 7.0776 | 1.1252 | 1.4696 | 1.9607 | 2.6157 | 3.2893 | 4.0966 | 4.9357 | 6.0615 | 7.0265 | 8.0473 | 9.1655 | 10.277 | 11.3469 | 12.3287 | 12.904 | 13.1395 | 14.0766 | 14.8572
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.41464 | 0.51687 | 0.6794 | 0.80889 | 0.95379 | 1.1221 | 1.304 | 1.603 | 1.8428 | 2.1097 | 2.3823 | 2.6798 | 3.02 | 3.3615 | 3.6918 | 4.0204 | 4.8201 | 5.0837 | 0.94315 | 1.1565 | 1.491 | 1.7589 | 2.0579 | 2.4045 | 2.7781 | 3.387 | 3.8778 | 4.4242 | 4.982 | 5.5896 | 6.283 | 6.9784 | 7.6502 | 8.3178 | 9.9652 | 10.5327
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.54095 | 0.78694 | 1.1387 | 1.4735 | 1.8529 | 2.2804 | 2.8014 | 3.443 | 4.0192 | 4.5044 | 4.7598 | 4.8737 | 4.9691 | 5.0626 | 5.1498 | 5.2344 | 5.6146 | 5.9701 | 1.2158 | 1.7299 | 2.4566 | 3.1476 | 3.9284 | 4.8075 | 5.8744 | 7.1836 | 8.3602 | 9.3563 | 9.8966 | 10.1494 | 10.3634 | 10.5726 | 10.7682 | 10.9584 | 11.82 | 12.621
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.49353 | 0.66439 | 0.90607 | 1.1094 | 1.3502 | 1.6309 | 1.9461 | 2.4004 | 2.8157 | 3.2586 | 3.7294 | 4.2413 | 4.7371 | 5.2021 | 5.4841 | 5.599 | 6.0941 | 6.4872 | 1.1309 | 1.5026 | 2.015 | 2.449 | 2.9605 | 3.5543 | 4.2138 | 5.1528 | 6.0152 | 6.9329 | 7.904 | 8.959 | 9.9802 | 10.9385 | 11.5295 | 11.786 | 12.9042 | 13.8057
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.45411 | 0.58999 | 0.80826 | 0.99022 | 1.1946 | 1.4419 | 1.7388 | 2.1745 | 2.5578 | 2.9833 | 3.4241 | 3.8653 | 4.2904 | 4.6878 | 4.912 | 4.9953 | 5.3213 | 5.6002 | 1.0289 | 1.315 | 1.7684 | 2.1474 | 2.5722 | 3.0856 | 3.6984 | 4.5905 | 5.3771 | 6.2499 | 7.1507 | 8.0515 | 8.9191 | 9.73 | 10.194 | 10.376 | 11.0999 | 11.7195
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Counterfactual | 0.57165 | 0.6708 | 0.7877 | 0.8981 | 1.0139 | 1.1627 | 1.4586 | 1.7474 | 2.0067 | 2.2976 | 2.5719 | 2.8345 | 3.1125 | 3.3934 | 3.6656 | 3.9344 | 4.735 | 5.1897 | 1.3422 | 1.5496 | 1.7921 | 2.0204 | 2.2592 | 2.5639 | 3.1785 | 3.7868 | 4.3456 | 4.9796 | 5.5663 | 6.1177 | 6.693 | 7.2747 | 7.8376 | 8.3927 | 10.1183 | 11.1502
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.66549 | 0.89263 | 1.1804 | 1.4532 | 1.795 | 2.1917 | 2.623 | 3.2154 | 3.8037 | 4.3305 | 4.6376 | 4.8739 | 5.1032 | 5.2803 | 5.4572 | 5.6393 | 6.5931 | 7.2325 | 1.5456 | 2.0249 | 2.6271 | 3.193 | 3.9044 | 4.725 | 5.6069 | 6.8495 | 8.0996 | 9.2306 | 9.8995 | 10.4423 | 10.9719 | 11.3707 | 11.7665 | 12.1772 | 14.328 | 15.8695
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.63127 | 0.79876 | 1.0029 | 1.2022 | 1.4234 | 1.6908 | 2.0671 | 2.6063 | 3.0103 | 3.5239 | 4.0138 | 4.4763 | 4.9207 | 5.2992 | 5.5742 | 5.7371 | 6.5857 | 6.9657 | 1.4846 | 1.8497 | 2.2889 | 2.716 | 3.1891 | 3.752 | 4.576 | 5.7611 | 6.626 | 7.7524 | 8.8079 | 9.8039 | 10.7579 | 11.5565 | 12.1476 | 12.5143 | 14.4335 | 15.3065
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.60166 | 0.74733 | 0.93109 | 1.1125 | 1.3137 | 1.5472 | 1.7985 | 2.1996 | 2.5772 | 3.0464 | 3.4257 | 3.8338 | 4.2217 | 4.5576 | 4.7752 | 4.8887 | 5.5209 | 6.126 | 1.4084 | 1.7188 | 2.1068 | 2.4879 | 2.9101 | 3.3946 | 3.9114 | 4.7561 | 5.5601 | 6.5758 | 7.3624 | 8.2247 | 9.0383 | 9.7348 | 10.1937 | 10.448 | 11.9006 | 13.3254
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.36719 | 0.4157 | 0.46954 | 0.53831 | 0.6091 | 0.69623 | 0.78367 | 0.91432 | 1.03 | 1.1587 | 1.2821 | 1.4016 | 1.5281 | 1.6537 | 1.7757 | 1.9004 | 2.3291 | 2.6057 | 0.85244 | 0.95545 | 1.0678 | 1.2109 | 1.3581 | 1.5385 | 1.7192 | 1.9939 | 2.2417 | 2.5202 | 2.7832 | 3.0328 | 3.294 | 3.5532 | 3.8052 | 4.0625 | 4.9711 | 5.5746
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.40581 | 0.51455 | 0.64119 | 0.78716 | 0.93318 | 1.1147 | 1.3329 | 1.5986 | 1.8642 | 2.1064 | 2.2746 | 2.3986 | 2.5175 | 2.6175 | 2.7065 | 2.7885 | 3.2395 | 3.5483 | 0.93588 | 1.1698 | 1.4358 | 1.7411 | 2.045 | 2.4217 | 2.8716 | 3.4259 | 3.9847 | 4.4977 | 4.8639 | 5.1388 | 5.4031 | 5.6212 | 5.8166 | 5.998 | 6.9979 | 7.7216
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.39164 | 0.47898 | 0.57251 | 0.68125 | 0.78284 | 0.925 | 1.1117 | 1.353 | 1.5636 | 1.8044 | 2.0338 | 2.2606 | 2.4848 | 2.6847 | 2.8251 | 2.9104 | 3.3488 | 3.6071 | 0.9105 | 1.1052 | 1.3074 | 1.5409 | 1.7584 | 2.059 | 2.4633 | 2.9858 | 3.4391 | 3.958 | 4.4445 | 4.9257 | 5.4007 | 5.8195 | 6.119 | 6.3083 | 7.2812 | 7.8616
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.37982 | 0.44487 | 0.51817 | 0.62248 | 0.73138 | 0.86681 | 1.0102 | 1.2061 | 1.3889 | 1.6106 | 1.8202 | 2.0177 | 2.2117 | 2.3747 | 2.4883 | 2.5454 | 2.8807 | 3.1959 | 0.88007 | 1.0212 | 1.1763 | 1.3963 | 1.6259 | 1.9101 | 2.208 | 2.619 | 3.0041 | 3.4754 | 3.9161 | 4.33 | 4.734 | 5.0716 | 5.3099 | 5.4355 | 6.1843 | 6.9007
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.40339 | 0.45837 | 0.53244 | 0.61229 | 0.68806 | 0.76911 | 0.85433 | 0.99856 | 1.1203 | 1.2514 | 1.3861 | 1.5332 | 1.6976 | 1.8616 | 2.0157 | 2.1625 | 2.6029 | 2.8343 | 0.96773 | 1.0833 | 1.2374 | 1.4029 | 1.5598 | 1.7271 | 1.9025 | 2.1995 | 2.4535 | 2.7267 | 3.0065 | 3.3097 | 3.647 | 3.9833 | 4.2982 | 4.597 | 5.5078 | 5.9988
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.45603 | 0.57474 | 0.73247 | 0.92074 | 1.1115 | 1.3196 | 1.5702 | 1.8854 | 2.1932 | 2.4697 | 2.6421 | 2.7461 | 2.8268 | 2.8909 | 2.9554 | 3.0099 | 3.2798 | 3.4802 | 1.0816 | 1.3326 | 1.6621 | 2.0568 | 2.4536 | 2.8824 | 3.3965 | 4.0444 | 4.6808 | 5.2542 | 5.6202 | 5.8448 | 6.022 | 6.1624 | 6.3035 | 6.4243 | 7.0272 | 7.4908
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.43672 | 0.52316 | 0.64201 | 0.77017 | 0.89948 | 1.0703 | 1.2656 | 1.5242 | 1.7446 | 1.992 | 2.24 | 2.4871 | 2.7172 | 2.921 | 3.0596 | 3.1252 | 3.4262 | 3.6397 | 1.047 | 1.2369 | 1.495 | 1.7694 | 2.0447 | 2.4072 | 2.8218 | 3.3653 | 3.8263 | 4.3431 | 4.8574 | 5.3698 | 5.8475 | 6.27 | 6.5615 | 6.7071 | 7.3798 | 7.8629
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.42081 | 0.49279 | 0.59366 | 0.71937 | 0.8385 | 0.97373 | 1.134 | 1.3704 | 1.5959 | 1.8512 | 2.0857 | 2.3123 | 2.524 | 2.7046 | 2.8203 | 2.8635 | 3.0727 | 3.2687 | 1.006 | 1.1595 | 1.3724 | 1.6388 | 1.8893 | 2.1701 | 2.5008 | 2.9893 | 3.458 | 3.9877 | 4.4692 | 4.934 | 5.3676 | 5.7374 | 5.9769 | 6.0714 | 6.5363 | 6.9758
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.39277 | 0.41541 | 0.44095 | 0.46899 | 0.5009 | 0.54198 | 0.58807 | 0.67284 | 0.74783 | 0.83089 | 0.91046 | 0.98961 | 1.0733 | 1.1567 | 1.2383 | 1.3207 | 1.6105 | 1.7965 | 0.95559 | 1.0034 | 1.0563 | 1.1144 | 1.1802 | 1.2645 | 1.3589 | 1.5365 | 1.6967 | 1.8759 | 2.0447 | 2.2095 | 2.3815 | 2.5532 | 2.7211 | 2.8903 | 3.5006 | 3.9025
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.41866 | 0.47312 | 0.53841 | 0.61746 | 0.70579 | 0.81608 | 0.95306 | 1.1354 | 1.3175 | 1.4869 | 1.604 | 1.6889 | 1.76 | 1.8106 | 1.8623 | 1.9085 | 2.1513 | 2.3221 | 1.0114 | 1.1266 | 1.2619 | 1.4248 | 1.6065 | 1.8325 | 2.1119 | 2.4904 | 2.8716 | 3.2281 | 3.4807 | 3.667 | 3.8257 | 3.9375 | 4.0512 | 4.1541 | 4.6978 | 5.1035
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.40872 | 0.44681 | 0.48799 | 0.53848 | 0.59509 | 0.67533 | 0.78874 | 0.95118 | 1.0946 | 1.2615 | 1.42 | 1.5733 | 1.7136 | 1.8288 | 1.9139 | 1.961 | 1.9934 | 2.1222 | 0.99347 | 1.0779 | 1.1663 | 1.2736 | 1.3933 | 1.5606 | 1.8044 | 2.1542 | 2.4606 | 2.8177 | 3.1521 | 3.4755 | 3.772 | 4.0133 | 4.1942 | 4.2991 | 4.3196 | 4.6117
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.40067 | 0.4306 | 0.46639 | 0.51383 | 0.56655 | 0.63814 | 0.72524 | 0.86 | 0.98747 | 1.1439 | 1.2927 | 1.4323 | 1.5601 | 1.6627 | 1.7341 | 1.7668 | 1.9466 | 2.116 | 0.97275 | 1.0366 | 1.1113 | 1.2095 | 1.3184 | 1.4655 | 1.6436 | 1.9243 | 2.1909 | 2.521 | 2.8317 | 3.1223 | 3.3872 | 3.5988 | 3.7478 | 3.8196 | 4.2248 | 4.6148
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.57838 | 0.66966 | 0.76939 | 0.88855 | 1.0238 | 1.2133 | 1.4148 | 1.7283 | 2.0036 | 2.2794 | 2.5563 | 2.8332 | 3.1309 | 3.43 | 3.7229 | 4.02 | 4.9733 | 5.5823 | 1.3767 | 1.569 | 1.7759 | 2.0226 | 2.3026 | 2.6927 | 3.1076 | 3.7568 | 4.3351 | 4.9156 | 5.4926 | 6.0645 | 6.6747 | 7.2876 | 7.8878 | 8.496 | 10.4864 | 11.7845
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.66611 | 0.86635 | 1.1058 | 1.406 | 1.7414 | 2.1696 | 2.6728 | 3.3018 | 3.9104 | 4.4406 | 4.7963 | 5.0472 | 5.2779 | 5.4863 | 5.7021 | 5.9128 | 7.017 | 7.6131 | 1.5665 | 1.9906 | 2.4877 | 3.1169 | 3.8161 | 4.7008 | 5.7348 | 7.0358 | 8.301 | 9.407 | 10.1631 | 10.7056 | 11.2069 | 11.6544 | 12.1159 | 12.5678 | 14.936 | 16.2912
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.63324 | 0.7775 | 0.94907 | 1.1433 | 1.3752 | 1.7047 | 2.0932 | 2.6133 | 3.0793 | 3.5752 | 4.0676 | 4.5435 | 5.0027 | 5.4232 | 5.7406 | 5.9443 | 6.9742 | 7.5393 | 1.5076 | 1.8261 | 2.1994 | 2.616 | 3.1112 | 3.8047 | 4.632 | 5.7361 | 6.7222 | 7.7708 | 8.8008 | 9.7964 | 10.7566 | 11.6312 | 12.2987 | 12.7385 | 14.9642 | 16.217
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.60702 | 0.72592 | 0.86602 | 1.0591 | 1.2772 | 1.5701 | 1.8963 | 2.3526 | 2.773 | 3.232 | 3.6785 | 4.1101 | 4.5298 | 4.9045 | 5.1736 | 5.3289 | 6.0905 | 6.7232 | 1.4395 | 1.6934 | 1.9867 | 2.3961 | 2.8565 | 3.4674 | 4.1435 | 5.0916 | 5.9687 | 6.9287 | 7.854 | 8.7467 | 9.612 | 10.3826 | 10.9411 | 11.2729 | 12.922 | 14.3186
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.1109 | 1.164 | 1.2291 | 1.3108 | 1.4027 | 1.4806 | 1.5645 | 1.6744 | 1.7635 | 1.8623 | 1.9657 | 2.0688 | 2.1834 | 2.297 | 2.4079 | 2.5221 | 2.5261 | 2.6793 | 2.748 | 2.8597 | 2.9964 | 3.1688 | 3.3628 | 3.5264 | 3.7018 | 3.9252 | 4.107 | 4.3091 | 4.5204 | 4.7294 | 4.9614 | 5.1911 | 5.4152 | 5.6461 | 5.5091 | 5.8267
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.1539 | 1.2716 | 1.4136 | 1.5904 | 1.7917 | 1.9896 | 2.2214 | 2.4613 | 2.6811 | 2.5563 | 2.6589 | 2.7224 | 2.7738 | 2.8146 | 2.8553 | 2.8867 | 3.0757 | 3.1804 | 2.8412 | 3.0953 | 3.3968 | 3.7719 | 4.2001 | 4.6193 | 5.1041 | 5.5919 | 6.039 | 5.6387 | 5.8508 | 5.9846 | 6.0946 | 6.1828 | 6.2706 | 6.3395 | 6.7703 | 7.0078
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.1384 | 1.2287 | 1.3325 | 1.4657 | 1.614 | 1.7603 | 1.9206 | 2.0949 | 2.2542 | 2.1217 | 2.3088 | 2.5776 | 2.7475 | 2.8986 | 2.9991 | 3.0421 | 3.2235 | 3.3643 | 2.8132 | 3.015 | 3.2421 | 3.5322 | 3.8563 | 4.1737 | 4.5166 | 4.8745 | 5.2019 | 4.7895 | 5.1735 | 5.7634 | 6.1127 | 6.4239 | 6.6335 | 6.728 | 7.131 | 7.4486
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.1255 | 1.2063 | 1.3027 | 1.4306 | 1.5742 | 1.7147 | 1.8696 | 2.0402 | 2.1937 | 2.0508 | 2.2287 | 2.4045 | 2.5679 | 2.7075 | 2.7937 | 2.8219 | 2.9754 | 3.0781 | 2.7803 | 2.9579 | 3.1659 | 3.4414 | 3.7519 | 4.0542 | 4.3823 | 4.7288 | 5.0406 | 4.6022 | 4.9632 | 5.3203 | 5.6523 | 5.9363 | 6.1132 | 6.1743 | 6.5234 | 6.7484
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.36617 | 0.38561 | 0.40832 | 0.43555 | 0.48333 | 0.538 | 0.59883 | 0.68118 | 0.75417 | 0.8312 | 0.90984 | 0.99318 | 1.0806 | 1.1675 | 1.2527 | 1.339 | 1.7049 | 1.9236 | 0.90067 | 0.9443 | 0.99435 | 1.0535 | 1.1555 | 1.2719 | 1.4013 | 1.5742 | 1.7288 | 1.892 | 2.0586 | 2.2342 | 2.4178 | 2.6001 | 2.7791 | 2.9603 | 3.7355 | 4.2042
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.3805 | 0.41883 | 0.4685 | 0.53187 | 0.63004 | 0.74217 | 0.87251 | 1.0245 | 1.1699 | 1.3086 | 1.4126 | 1.5011 | 1.5742 | 1.6354 | 1.6989 | 1.7521 | 2.0018 | 2.1557 | 0.93147 | 1.0146 | 1.12 | 1.2529 | 1.4607 | 1.6976 | 1.9709 | 2.2878 | 2.5917 | 2.8818 | 3.1028 | 3.2924 | 3.4513 | 3.5861 | 3.7254 | 3.8441 | 4.4065 | 4.7602
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.37515 | 0.40269 | 0.4367 | 0.48178 | 0.55922 | 0.65193 | 0.75652 | 0.88464 | 1.0073 | 1.1428 | 1.2763 | 1.408 | 1.5258 | 1.6291 | 1.7164 | 1.7772 | 2.0555 | 2.2187 | 0.92189 | 0.98459 | 1.0596 | 1.1569 | 1.3244 | 1.5236 | 1.7468 | 2.0173 | 2.2765 | 2.5618 | 2.8428 | 3.1201 | 3.3695 | 3.5895 | 3.7775 | 3.9123 | 4.5363 | 4.9119
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.37073 | 0.39114 | 0.41958 | 0.46083 | 0.53443 | 0.62291 | 0.72392 | 0.85066 | 0.97119 | 1.1046 | 1.2359 | 1.3649 | 1.4809 | 1.5799 | 1.6608 | 1.7147 | 1.9439 | 2.0584 | 0.91048 | 0.95492 | 1.0151 | 1.1013 | 1.2574 | 1.4445 | 1.6566 | 1.9204 | 2.1716 | 2.4486 | 2.7213 | 2.9893 | 3.2312 | 3.439 | 3.6104 | 3.7276 | 4.2323 | 4.4871
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.81082 | 0.88883 | 0.98066 | 1.0834 | 1.1901 | 1.3451 | 1.5114 | 1.7741 | 2.0013 | 2.2373 | 2.4795 | 2.7178 | 2.974 | 3.2314 | 3.4839 | 3.741 | 4.5622 | 5.0881 | 1.8901 | 2.0545 | 2.2451 | 2.4579 | 2.6784 | 2.9954 | 3.3358 | 3.8781 | 4.3538 | 4.8499 | 5.3537 | 5.8448 | 6.3684 | 6.8948 | 7.4106 | 7.9356 | 9.6451 | 10.7612
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.88891 | 1.0637 | 1.28 | 1.5397 | 1.8175 | 2.2351 | 2.6704 | 3.2185 | 3.7536 | 4.2395 | 4.5881 | 4.8378 | 5.1192 | 5.6486 | 5.8827 | 6.1051 | 7.3537 | 7.8697 | 2.059 | 2.4294 | 2.8792 | 3.4224 | 3.9995 | 4.8521 | 5.7399 | 6.8675 | 7.9741 | 8.9835 | 9.72 | 10.2547 | 10.8758 | 11.9603 | 12.4534 | 12.9242 | 15.557 | 16.7269
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.86003 | 0.98641 | 1.1413 | 1.308 | 1.4838 | 1.755 | 2.0854 | 2.6304 | 3.0342 | 3.4864 | 3.9478 | 4.383 | 4.8034 | 5.5039 | 5.8129 | 6.0158 | 7.133 | 7.6223 | 2.0074 | 2.2868 | 2.6232 | 2.9807 | 3.3549 | 3.9189 | 4.6184 | 5.8074 | 6.6576 | 7.6108 | 8.574 | 9.4832 | 10.3603 | 11.7895 | 12.4349 | 12.8679 | 15.2429 | 16.318
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.83564 | 0.9375 | 1.0642 | 1.2262 | 1.3928 | 1.6237 | 1.8847 | 2.261 | 2.6093 | 3.0129 | 3.4134 | 3.8008 | 4.2256 | 4.6048 | 4.8567 | 5.1265 | 5.8925 | 6.4732 | 1.9446 | 2.1622 | 2.428 | 2.7707 | 3.1206 | 3.5955 | 4.1304 | 4.907 | 5.6288 | 6.4708 | 7.2995 | 8.099 | 8.9934 | 9.7685 | 10.2884 | 10.8451 | 12.4811 | 13.752
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.38185 | 0.43566 | 0.50609 | 0.58933 | 0.68372 | 0.77802 | 0.88197 | 1.0485 | 1.1855 | 1.3303 | 1.4782 | 1.6722 | 1.9361 | 2.2039 | 2.4942 | 2.7327 | 3.1413 | 3.2975 | 0.87631 | 0.98882 | 1.1348 | 1.3071 | 1.5025 | 1.6971 | 1.911 | 2.2521 | 2.5358 | 2.8347 | 3.1385 | 3.539 | 4.0859 | 4.641 | 5.2654 | 5.7825 | 6.6259 | 6.9605
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.44578 | 0.57372 | 0.74211 | 0.94807 | 1.1757 | 1.4046 | 1.6783 | 2.0338 | 2.3712 | 2.7546 | 3.0984 | 3.2505 | 3.4024 | 3.467 | 3.5166 | 3.5592 | 3.7657 | 3.9241 | 1.014 | 1.282 | 1.6312 | 2.0623 | 2.5359 | 3.0074 | 3.5672 | 4.2964 | 4.9923 | 5.822 | 6.6106 | 6.9479 | 7.2846 | 7.4253 | 7.5354 | 7.6313 | 8.1018 | 8.4714
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.42134 | 0.50766 | 0.62736 | 0.75871 | 0.92556 | 1.1287 | 1.3597 | 1.6687 | 2.0133 | 2.4825 | 2.752 | 3.0134 | 3.2584 | 3.4901 | 3.632 | 3.6896 | 3.9452 | 4.1357 | 0.97019 | 1.1588 | 1.4187 | 1.7005 | 2.0571 | 2.49 | 2.9814 | 3.6319 | 4.3865 | 5.4442 | 6.0062 | 6.5493 | 7.0573 | 7.5343 | 7.8319 | 7.9606 | 8.5393 | 8.9754
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.40127 | 0.4714 | 0.56873 | 0.69615 | 0.83622 | 0.97754 | 1.1559 | 1.4201 | 1.6739 | 2.0259 | 2.433 | 2.7672 | 3.0539 | 3.2604 | 3.3777 | 3.4122 | 3.5699 | 3.7143 | 0.91844 | 1.0665 | 1.2701 | 1.5406 | 1.8359 | 2.1298 | 2.4992 | 3.0446 | 3.5727 | 4.3229 | 5.2185 | 5.9355 | 6.5302 | 6.9505 | 7.1922 | 7.2681 | 7.6223 | 7.9477
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 6.8405 | 7.4802 | 8.0177 | 8.0943 | 7.744 | 7.8301 | 7.93 | 8.0831 | 8.2134 | 8.3411 | 8.4867 | 8.6446 | 8.8305 | 9.0122 | 9.1896 | 9.3687 | 9.7406 | 9.9705 | 17.0417 | 18.5624 | 19.8787 | 20.0375 | 19.1295 | 19.308 | 19.515 | 19.8292 | 20.0995 | 20.3616 | 20.6665 | 20.9978 | 21.3889 | 21.7706 | 22.1449 | 22.5242 | 23.2864 | 23.762
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 7.4821 | 7.5977 | 8.2211 | 8.4137 | 8.1817 | 8.3865 | 8.8777 | 9.1976 | 9.758 | 10.0647 | 10.2888 | 10.3778 | 10.4485 | 10.4995 | 10.5525 | 10.6335 | 10.8396 | 10.9983 | 18.5696 | 18.8134 | 20.3088 | 20.7167 | 20.0582 | 20.482 | 21.4834 | 22.1464 | 23.3056 | 23.9702 | 24.4772 | 24.6762 | 24.8355 | 24.9469 | 25.0612 | 25.2508 | 25.7082 | 26.0633
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 7.9349 | 8.0174 | 8.1386 | 8.2642 | 7.961 | 8.1247 | 8.5537 | 8.8202 | 9.3391 | 9.6601 | 9.9741 | 10.2064 | 10.4168 | 10.6128 | 10.7477 | 10.8092 | 11.0871 | 11.3146 | 19.7155 | 19.8966 | 20.1629 | 20.4335 | 19.6305 | 19.9814 | 20.869 | 21.4367 | 22.5328 | 23.2436 | 23.9338 | 24.4189 | 24.8523 | 25.2566 | 25.5385 | 25.6732 | 26.293 | 26.7994
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 7.4464 | 7.5143 | 7.6072 | 8.2108 | 7.9098 | 8.0462 | 8.2284 | 8.4664 | 8.7426 | 9.0169 | 9.3524 | 9.5993 | 9.9882 | 10.1625 | 12.2908 | 12.3678 | 13.4795 | 13.6512 | 18.493 | 18.6373 | 18.8325 | 20.2954 | 19.4961 | 19.7815 | 20.1603 | 20.6557 | 21.2424 | 21.8307 | 22.5526 | 23.0774 | 23.8707 | 24.2264 | 29.4975 | 29.6777 | 32.4048 | 32.7757
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.46439 | 0.54799 | 0.64788 | 0.7674 | 0.88401 | 1.0245 | 1.1788 | 1.4179 | 1.6132 | 1.8142 | 2.0249 | 2.2468 | 2.4985 | 2.7513 | 2.9913 | 3.2211 | 3.7985 | 4.0386 | 1.1032 | 1.2777 | 1.4845 | 1.7317 | 1.9721 | 2.2607 | 2.5774 | 3.0646 | 3.4648 | 3.8761 | 4.3068 | 4.7596 | 5.2719 | 5.7865 | 6.2736 | 6.7387 | 7.9199 | 8.4242
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.55144 | 0.73601 | 0.97062 | 1.2457 | 1.5363 | 1.8766 | 2.2824 | 2.779 | 3.2403 | 3.6303 | 3.847 | 3.9562 | 4.0518 | 4.1402 | 4.2291 | 4.3105 | 4.7087 | 4.9386 | 1.2914 | 1.6782 | 2.1651 | 2.7352 | 3.335 | 4.0359 | 4.8673 | 5.8819 | 6.8265 | 7.627 | 8.0813 | 8.3158 | 8.5224 | 8.7134 | 8.9047 | 9.0809 | 9.9426 | 10.4622
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.5189 | 0.64774 | 0.80244 | 0.98666 | 1.1787 | 1.4277 | 1.7102 | 2.088 | 2.4047 | 2.7441 | 3.104 | 3.4606 | 3.8053 | 4.1252 | 4.3325 | 4.4268 | 4.8622 | 5.1503 | 1.233 | 1.5131 | 1.8442 | 2.2371 | 2.6455 | 3.1711 | 3.7639 | 4.548 | 5.2033 | 5.9036 | 6.6449 | 7.379 | 8.0883 | 8.747 | 9.1795 | 9.3852 | 10.3399 | 10.9905
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.49212 | 0.60114 | 0.74092 | 0.91103 | 1.0814 | 1.2948 | 1.5403 | 1.8967 | 2.2196 | 2.5547 | 2.8841 | 3.2124 | 3.5291 | 3.8179 | 3.9909 | 4.0563 | 4.3266 | 4.5516 | 1.164 | 1.3946 | 1.6874 | 2.0438 | 2.399 | 2.8423 | 3.3487 | 4.0805 | 4.7453 | 5.4318 | 6.1023 | 6.7706 | 7.4151 | 8.0031 | 8.3586 | 8.4992 | 9.0841 | 9.5766
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.36823 | 0.45016 | 0.54887 | 0.66299 | 0.79967 | 0.94205 | 1.1047 | 1.3613 | 1.5676 | 1.7855 | 2.0222 | 2.2761 | 2.5595 | 2.8467 | 3.1348 | 3.4192 | 4.2081 | 4.6407 | 0.86009 | 1.032 | 1.2376 | 1.4761 | 1.7599 | 2.0534 | 2.3881 | 2.9117 | 3.3347 | 3.7812 | 4.2724 | 4.7975 | 5.3813 | 5.971 | 6.5603 | 7.1411 | 8.7774 | 9.6989
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.46024 | 0.66082 | 0.91232 | 1.1992 | 1.5254 | 1.8711 | 2.307 | 2.8437 | 3.3513 | 3.7562 | 3.9676 | 4.0894 | 4.2009 | 4.3064 | 4.4095 | 4.5208 | 4.9423 | 5.3629 | 1.0582 | 1.483 | 2.0092 | 2.6094 | 3.2861 | 4.0001 | 4.9032 | 6.0111 | 7.0721 | 7.9138 | 8.3614 | 8.6291 | 8.8761 | 9.1104 | 9.3391 | 9.593 | 10.5447 | 11.4902
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.42495 | 0.56541 | 0.73167 | 0.91884 | 1.1461 | 1.4241 | 1.7512 | 2.1833 | 2.5628 | 2.9382 | 3.3631 | 3.7516 | 4.1297 | 4.4845 | 4.7191 | 4.8329 | 5.3252 | 5.7844 | 0.99479 | 1.3052 | 1.6656 | 2.0711 | 2.5576 | 3.1556 | 3.856 | 4.7684 | 5.5711 | 6.3526 | 7.2499 | 8.0552 | 8.8393 | 9.5759 | 10.0715 | 10.3246 | 11.4331 | 12.4706
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.39715 | 0.51423 | 0.66386 | 0.83675 | 1.0341 | 1.2505 | 1.5243 | 1.9124 | 2.286 | 2.689 | 3.0628 | 3.4342 | 3.7953 | 4.1285 | 4.3376 | 4.4504 | 4.8394 | 5.2265 | 0.92275 | 1.1739 | 1.4914 | 1.8588 | 2.2731 | 2.7238 | 3.2965 | 4.1017 | 4.8909 | 5.7339 | 6.5012 | 7.2635 | 8.005 | 8.69 | 9.1261 | 9.3785 | 10.2402 | 11.0955
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Counterfactual | 0.31252 | 0.39056 | 0.4704 | 0.5664 | 0.66214 | 0.78171 | 0.92485 | 1.1616 | 1.4038 | 1.5883 | 1.7769 | 1.9725 | 2.1878 | 2.404 | 2.6147 | 2.8274 | 3.4171 | 3.7198 | 0.72619 | 0.88941 | 1.0547 | 1.2527 | 1.4509 | 1.7005 | 2.0016 | 2.4992 | 3.0306 | 3.4127 | 3.801 | 4.2012 | 4.6393 | 5.0792 | 5.5079 | 5.94 | 7.1581 | 7.7986
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.38266 | 0.54531 | 0.73824 | 1.0205 | 1.3408 | 1.6831 | 2.0769 | 2.5306 | 2.9121 | 3.2359 | 3.4163 | 3.5222 | 3.609 | 3.6827 | 3.7573 | 3.8228 | 4.1434 | 4.3936 | 0.87822 | 1.2205 | 1.62 | 2.228 | 2.9233 | 3.6584 | 4.4928 | 5.4402 | 6.224 | 6.8926 | 7.2751 | 7.5066 | 7.6992 | 7.8625 | 8.0269 | 8.1728 | 8.8935 | 9.4712
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.3553 | 0.46855 | 0.64432 | 0.84778 | 1.0461 | 1.2927 | 1.5567 | 1.8715 | 2.146 | 2.4494 | 2.7595 | 3.0612 | 3.3486 | 3.6105 | 3.7854 | 3.8676 | 4.2387 | 4.5059 | 0.82907 | 1.0769 | 1.4717 | 1.9268 | 2.367 | 2.9108 | 3.4834 | 4.1414 | 4.7149 | 5.3483 | 5.9912 | 6.6173 | 7.2137 | 7.7566 | 8.1249 | 8.3076 | 9.1405 | 9.7483
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.33619 | 0.43519 | 0.55009 | 0.74152 | 0.95527 | 1.2136 | 1.4847 | 1.8303 | 2.0992 | 2.4026 | 2.7119 | 3.011 | 3.2967 | 3.5515 | 3.7127 | 3.7797 | 4.0664 | 4.3014 | 0.778 | 0.98807 | 1.2276 | 1.6478 | 2.1225 | 2.6934 | 3.2788 | 4.0059 | 4.5587 | 5.1836 | 5.8174 | 6.4299 | 7.014 | 7.5346 | 7.8676 | 8.0122 | 8.6449 | 9.1732
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.38246 | 0.48855 | 0.614 | 0.76651 | 0.92494 | 1.1016 | 1.3022 | 1.6082 | 1.8659 | 2.1384 | 2.4181 | 2.7069 | 3.0267 | 3.3357 | 3.6379 | 3.9413 | 4.7783 | 5.2046 | 0.87262 | 1.095 | 1.3552 | 1.6712 | 1.9991 | 2.3647 | 2.7793 | 3.4086 | 3.9435 | 4.5085 | 5.0869 | 5.6814 | 6.3368 | 6.9689 | 7.5868 | 8.2068 | 9.949 | 10.8647
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.48624 | 0.71626 | 0.99781 | 1.3482 | 1.7278 | 2.1377 | 2.6275 | 3.2247 | 3.7752 | 4.2439 | 4.5069 | 4.6642 | 4.8085 | 4.9529 | 5.0718 | 5.1822 | 5.7194 | 6.1968 | 1.0967 | 1.5813 | 2.1666 | 2.9 | 3.6908 | 4.5407 | 5.5504 | 6.7786 | 7.9144 | 8.8863 | 9.4475 | 9.7949 | 10.1163 | 10.4325 | 10.6967 | 10.9437 | 12.152 | 13.2355
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.44682 | 0.61046 | 0.80994 | 1.0412 | 1.2891 | 1.578 | 1.917 | 2.3755 | 2.781 | 3.2207 | 3.6761 | 4.1243 | 4.5632 | 4.9835 | 5.2478 | 5.3812 | 6.0042 | 6.5309 | 1.0258 | 1.3841 | 1.816 | 2.3119 | 2.841 | 3.4545 | 4.1724 | 5.133 | 5.9834 | 6.904 | 7.853 | 8.787 | 9.7023 | 10.5753 | 11.1355 | 11.4336 | 12.8339 | 14.0238
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.41511 | 0.55204 | 0.7201 | 0.94159 | 1.1728 | 1.4347 | 1.7419 | 2.1703 | 2.5517 | 2.9705 | 3.4041 | 3.8258 | 4.2382 | 4.6154 | 4.8445 | 4.9465 | 5.4229 | 5.8798 | 0.944 | 1.235 | 1.5878 | 2.0576 | 2.5454 | 3.0943 | 3.7334 | 4.6189 | 5.4089 | 6.2762 | 7.1712 | 8.0407 | 8.891 | 9.6667 | 10.1455 | 10.3699 | 11.4296 | 12.4466
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Counterfactual | 0.57096 | 0.7698 | 0.92979 | 1.0959 | 1.274 | 1.4928 | 1.7415 | 2.1444 | 2.4872 | 2.8512 | 3.2064 | 3.5735 | 3.9806 | 4.4478 | 4.9277 | 5.3669 | 6.3404 | 6.7818 | 1.2837 | 1.6942 | 2.0259 | 2.3697 | 2.7371 | 3.1878 | 3.6992 | 4.5336 | 5.2537 | 6.0221 | 6.7636 | 7.5225 | 8.3575 | 9.3216 | 10.3305 | 11.2547 | 13.3057 | 14.2856
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.71248 | 1.0772 | 1.4506 | 1.857 | 2.3078 | 2.824 | 3.4504 | 4.2518 | 5.0071 | 5.7176 | 6.1956 | 6.4241 | 6.637 | 6.8411 | 6.9896 | 7.1294 | 7.8503 | 8.4134 | 1.5897 | 2.3505 | 3.1261 | 3.9675 | 4.8978 | 5.9632 | 7.2493 | 8.908 | 10.4829 | 12.008 | 13.0864 | 13.6063 | 14.0944 | 14.5538 | 14.889 | 15.2081 | 16.8609 | 18.199
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.66022 | 0.93411 | 1.1825 | 1.4417 | 1.7275 | 2.0947 | 2.5714 | 3.2325 | 3.8759 | 4.62 | 5.2212 | 5.7947 | 6.3524 | 6.861 | 7.1912 | 7.3498 | 8.1133 | 8.61 | 1.4965 | 2.0844 | 2.6178 | 3.1724 | 3.7815 | 4.5591 | 5.5842 | 6.9977 | 8.3989 | 10.0379 | 11.3063 | 12.5172 | 13.693 | 14.7578 | 15.4608 | 15.8198 | 17.564 | 18.7026
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.61478 | 0.85324 | 1.0715 | 1.308 | 1.5673 | 1.8885 | 2.2704 | 2.8346 | 3.3486 | 3.9722 | 4.6527 | 5.2501 | 5.7933 | 6.2857 | 6.564 | 6.6666 | 7.2151 | 7.7452 | 1.3796 | 1.8778 | 2.3352 | 2.8292 | 3.3692 | 4.0375 | 4.8278 | 6 | 7.0751 | 8.4017 | 9.8615 | 11.1219 | 12.2467 | 13.264 | 13.8442 | 14.0745 | 15.3286 | 16.5541
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.7901 | 1.8183 | 1.8481 | 1.8836 | 1.9248 | 1.9738 | 2.0284 | 2.1137 | 2.1812 | 2.252 | 2.3305 | 2.4155 | 2.5089 | 2.6002 | 2.6876 | 2.7758 | 3.0272 | 3.1533 | 4.4516 | 4.5105 | 4.5719 | 4.6452 | 4.73 | 4.8305 | 4.9424 | 5.1158 | 5.2533 | 5.3974 | 5.5592 | 5.7338 | 5.9251 | 6.1113 | 6.2884 | 6.467 | 6.9809 | 7.2422
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.82 | 1.8836 | 2.0129 | 2.1697 | 2.3351 | 2.5138 | 2.7165 | 2.9657 | 3.2157 | 3.4086 | 3.5263 | 3.6216 | 3.7292 | 3.8075 | 3.8638 | 3.9249 | 4.2375 | 4.4238 | 4.516 | 4.6491 | 4.9395 | 5.2903 | 5.657 | 6.0488 | 6.4876 | 7.0264 | 7.573 | 7.9876 | 8.2459 | 8.4635 | 8.7167 | 8.9001 | 9.028 | 9.1709 | 9.9084 | 10.3532
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.8086 | 1.852 | 1.9454 | 2.0495 | 2.1658 | 2.2917 | 2.4082 | 2.5608 | 2.6964 | 2.8693 | 3.0215 | 3.2852 | 3.4229 | 3.5474 | 3.6344 | 3.6803 | 3.8858 | 4.0421 | 4.4956 | 4.5899 | 4.8063 | 5.0439 | 5.3084 | 5.588 | 5.8372 | 6.1586 | 6.443 | 6.8147 | 7.1319 | 7.7301 | 8.0179 | 8.279 | 8.4648 | 8.5682 | 9.0358 | 9.401
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.7992 | 1.8362 | 1.8777 | 1.9329 | 1.996 | 2.0754 | 2.1773 | 2.3153 | 2.4457 | 2.5804 | 2.7152 | 2.8475 | 2.9702 | 3.0782 | 3.1626 | 3.1889 | 3.3482 | 3.4271 | 4.4715 | 4.5494 | 4.6356 | 4.7502 | 4.8811 | 5.0449 | 5.2574 | 5.5417 | 5.8128 | 6.0882 | 6.3621 | 6.6311 | 6.8807 | 7.1007 | 7.2817 | 7.338 | 7.7021 | 7.8741
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.20182 | 0.23144 | 0.2657 | 0.30617 | 0.35313 | 0.41537 | 0.48831 | 0.62413 | 0.74329 | 0.87534 | 1.0042 | 1.1265 | 1.259 | 1.3915 | 1.5224 | 1.6607 | 2.1157 | 2.4503 | 0.45894 | 0.52129 | 0.59236 | 0.67608 | 0.77294 | 0.90055 | 1.0496 | 1.3326 | 1.5854 | 1.8681 | 2.1397 | 2.3934 | 2.6651 | 2.9369 | 3.2074 | 3.4936 | 4.451 | 5.1677
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.23388 | 0.30361 | 0.39171 | 0.49806 | 0.63097 | 0.79241 | 0.98635 | 1.2432 | 1.4927 | 1.7217 | 1.8907 | 2.0066 | 2.1082 | 2.1894 | 2.2808 | 2.3671 | 2.8224 | 3.1238 | 0.528 | 0.67533 | 0.85793 | 1.0774 | 1.3506 | 1.6813 | 2.0771 | 2.611 | 3.1348 | 3.6226 | 3.9923 | 4.2475 | 4.4743 | 4.6517 | 4.8506 | 5.0401 | 6.0429 | 6.7446
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.22183 | 0.26935 | 0.32698 | 0.39125 | 0.46129 | 0.57643 | 0.73613 | 0.96257 | 1.1589 | 1.3862 | 1.5939 | 1.7912 | 1.9824 | 2.1511 | 2.288 | 2.3788 | 2.8189 | 3.0635 | 0.50646 | 0.61154 | 0.73508 | 0.87236 | 1.0211 | 1.2608 | 1.6048 | 2.0935 | 2.5176 | 3.0118 | 3.4525 | 3.8714 | 4.277 | 4.6304 | 4.9203 | 5.1181 | 6.0857 | 6.6268
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.21191 | 0.25127 | 0.30195 | 0.3653 | 0.45026 | 0.56578 | 0.69578 | 0.89645 | 1.0796 | 1.304 | 1.52 | 1.7143 | 1.9075 | 2.0678 | 2.2013 | 2.2825 | 2.6754 | 2.9992 | 0.4808 | 0.56462 | 0.67038 | 0.80202 | 0.97743 | 1.2145 | 1.4801 | 1.8969 | 2.2802 | 2.756 | 3.2106 | 3.6167 | 4.0163 | 4.3459 | 4.6227 | 4.7962 | 5.6551 | 6.3842
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.63768 | 0.65021 | 0.66431 | 0.68032 | 0.69989 | 0.72271 | 0.74875 | 0.78972 | 0.82605 | 0.85935 | 0.89391 | 0.9312 | 0.97297 | 1.0142 | 1.0885 | 1.1719 | 1.2863 | 1.3444 | 1.5688 | 1.5952 | 1.6245 | 1.6577 | 1.6985 | 1.7464 | 1.8009 | 1.8858 | 1.9627 | 2.031 | 2.1017 | 2.1777 | 2.2624 | 2.3461 | 2.5132 | 2.702 | 2.9366 | 3.057
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.6522 | 0.68219 | 0.72219 | 0.78512 | 0.8463 | 0.90311 | 0.97146 | 1.0553 | 1.1343 | 1.2606 | 1.3719 | 1.394 | 1.4136 | 1.4304 | 1.5251 | 1.5385 | 1.4516 | 1.4955 | 1.6 | 1.6633 | 1.7474 | 1.8864 | 2.0184 | 2.1368 | 2.2777 | 2.4502 | 2.6131 | 2.9006 | 3.1645 | 3.2123 | 3.2556 | 3.2926 | 3.5235 | 3.5531 | 3.3202 | 3.4217
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.64689 | 0.66795 | 0.71054 | 0.74442 | 0.77706 | 0.81556 | 0.85829 | 0.91872 | 1.0311 | 1.341 | 1.4009 | 1.4621 | 1.5211 | 1.5762 | 1.4649 | 1.4839 | 1.5616 | 1.6177 | 1.5905 | 1.637 | 1.7349 | 1.8099 | 1.8801 | 1.9616 | 2.051 | 2.1759 | 2.4342 | 3.1838 | 3.3069 | 3.4327 | 3.5543 | 3.6677 | 3.3731 | 3.4146 | 3.5875 | 3.7141
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.64243 | 0.659 | 0.68002 | 0.72126 | 0.76081 | 0.79786 | 0.83903 | 0.89843 | 0.95104 | 1.0361 | 1.1682 | 1.2568 | 1.3141 | 1.3627 | 1.4739 | 1.4847 | 1.5305 | 1.5699 | 1.579 | 1.6142 | 1.658 | 1.7504 | 1.8367 | 1.9146 | 1.9991 | 2.1203 | 2.2278 | 2.4132 | 2.7154 | 2.9104 | 3.0268 | 3.1257 | 3.3892 | 3.4122 | 3.5124 | 3.5985
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.37383 | 0.40107 | 0.42937 | 0.45286 | 0.47699 | 0.50831 | 0.54397 | 0.60279 | 0.65753 | 0.7101 | 0.76307 | 0.81604 | 0.87357 | 0.92994 | 0.9845 | 1.0416 | 1.2485 | 1.3992 | 0.89146 | 0.9493 | 1.0084 | 1.0571 | 1.1074 | 1.1728 | 1.2473 | 1.3706 | 1.4883 | 1.5994 | 1.7101 | 1.8193 | 1.9368 | 2.0521 | 2.1637 | 2.2804 | 2.7102 | 3.0262
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.39015 | 0.44085 | 0.49946 | 0.57811 | 0.65028 | 0.72365 | 0.81373 | 0.92772 | 1.0398 | 1.1414 | 1.2148 | 1.2714 | 1.3179 | 1.3561 | 1.3965 | 1.4301 | 1.6026 | 1.7137 | 0.92705 | 1.0361 | 1.159 | 1.3315 | 1.486 | 1.6373 | 1.8216 | 2.0568 | 2.2894 | 2.5012 | 2.657 | 2.778 | 2.8791 | 2.9611 | 3.0476 | 3.1204 | 3.4989 | 3.7534
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.38474 | 0.42648 | 0.49079 | 0.53657 | 0.57621 | 0.6332 | 0.70335 | 0.80231 | 0.889 | 0.98817 | 1.0849 | 1.1781 | 1.2652 | 1.3414 | 1.4048 | 1.4455 | 1.6282 | 1.7396 | 0.91736 | 1.0102 | 1.1558 | 1.2558 | 1.3398 | 1.4588 | 1.6077 | 1.8174 | 2.0003 | 2.2096 | 2.4116 | 2.6065 | 2.7891 | 2.9481 | 3.0815 | 3.1692 | 3.5682 | 3.8143
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.38033 | 0.41517 | 0.45583 | 0.51563 | 0.56818 | 0.62369 | 0.68547 | 0.77716 | 0.8612 | 0.96181 | 1.0582 | 1.1477 | 1.2351 | 1.3051 | 1.3618 | 1.3911 | 1.5305 | 1.6506 | 0.90599 | 0.98141 | 1.0673 | 1.2 | 1.3141 | 1.4299 | 1.5564 | 1.7456 | 1.9194 | 2.1285 | 2.3277 | 2.5123 | 2.692 | 2.836 | 2.9533 | 3.0157 | 3.3195 | 3.5847
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.21893 | 0.24419 | 0.27349 | 0.30994 | 0.3519 | 0.4035 | 0.46047 | 0.56507 | 0.66141 | 0.77069 | 0.87158 | 0.96695 | 1.0659 | 1.1649 | 1.2608 | 1.3573 | 1.6803 | 1.8935 | 0.48428 | 0.53738 | 0.59825 | 0.67366 | 0.7603 | 0.86672 | 0.98399 | 1.2065 | 1.4163 | 1.657 | 1.8751 | 2.0769 | 2.283 | 2.4893 | 2.6891 | 2.8899 | 3.5894 | 4.0693
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.24516 | 0.30311 | 0.37722 | 0.46303 | 0.56155 | 0.67699 | 0.814 | 1.0085 | 1.2017 | 1.374 | 1.4929 | 1.5786 | 1.6592 | 1.7186 | 1.7779 | 1.8359 | 2.1336 | 2.4126 | 0.54099 | 0.66338 | 0.81708 | 0.99481 | 1.1987 | 1.4378 | 1.72 | 2.1324 | 2.5481 | 2.9237 | 3.1935 | 3.3936 | 3.5835 | 3.7209 | 3.8576 | 3.9926 | 4.6894 | 5.3583
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.23483 | 0.27494 | 0.32357 | 0.3799 | 0.44473 | 0.52789 | 0.65746 | 0.84664 | 1.0043 | 1.1826 | 1.3471 | 1.5101 | 1.6667 | 1.7989 | 1.8969 | 1.9569 | 2.2539 | 2.4313 | 0.52248 | 0.61122 | 0.71561 | 0.83613 | 0.97448 | 1.1508 | 1.4385 | 1.8599 | 2.2091 | 2.606 | 2.9656 | 3.3207 | 3.6612 | 3.9436 | 4.1573 | 4.2947 | 4.9827 | 5.3903
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.22795 | 0.2609 | 0.30513 | 0.35848 | 0.42085 | 0.49894 | 0.58852 | 0.73628 | 0.87353 | 1.0409 | 1.1955 | 1.3411 | 1.4803 | 1.5984 | 1.6815 | 1.7297 | 1.9884 | 2.244 | 0.50376 | 0.57377 | 0.66603 | 0.77723 | 0.9073 | 1.0702 | 1.256 | 1.5705 | 1.8658 | 2.2317 | 2.5639 | 2.8751 | 3.1703 | 3.4181 | 3.5955 | 3.704 | 4.304 | 4.9084
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.1806 | 0.1989 | 0.21746 | 0.23937 | 0.2647 | 0.30024 | 0.3389 | 0.41017 | 0.47416 | 0.54579 | 0.61434 | 0.67952 | 0.748 | 0.81612 | 0.8826 | 0.95057 | 1.2049 | 1.3886 | 0.4339 | 0.47293 | 0.5116 | 0.557 | 0.60929 | 0.68218 | 0.76138 | 0.91145 | 1.049 | 1.2047 | 1.3511 | 1.4872 | 1.6285 | 1.7689 | 1.9061 | 2.0462 | 2.5832 | 2.9786
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.19763 | 0.23959 | 0.28855 | 0.34729 | 0.41352 | 0.50037 | 0.60713 | 0.7499 | 0.89485 | 1.0301 | 1.1311 | 1.209 | 1.2757 | 1.3257 | 1.3788 | 1.4268 | 1.6864 | 1.8545 | 0.47074 | 0.56084 | 0.66254 | 0.78392 | 0.92057 | 1.0988 | 1.317 | 1.6148 | 1.92 | 2.2064 | 2.4252 | 2.5961 | 2.7445 | 2.8539 | 2.9695 | 3.0747 | 3.6471 | 4.0428
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.19087 | 0.22202 | 0.25354 | 0.29159 | 0.33472 | 0.40147 | 0.49466 | 0.62755 | 0.74336 | 0.87811 | 1.0038 | 1.124 | 1.2358 | 1.3292 | 1.4043 | 1.4529 | 1.6966 | 1.8253 | 0.45862 | 0.52907 | 0.59707 | 0.67825 | 0.76993 | 0.90928 | 1.1107 | 1.3991 | 1.6485 | 1.9391 | 2.2056 | 2.4608 | 2.6988 | 2.8956 | 3.0554 | 3.1622 | 3.7002 | 3.9888
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.18624 | 0.20996 | 0.23814 | 0.27608 | 0.31869 | 0.37917 | 0.45039 | 0.56215 | 0.66722 | 0.79681 | 0.91813 | 1.0306 | 1.1367 | 1.221 | 1.2868 | 1.3229 | 1.5198 | 1.6941 | 0.44613 | 0.49736 | 0.55614 | 0.63461 | 0.72262 | 0.84686 | 0.99255 | 1.2265 | 1.4472 | 1.7223 | 1.9769 | 2.2122 | 2.433 | 2.6073 | 2.7445 | 2.8225 | 3.2586 | 3.6554
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.22309 | 0.25014 | 0.4735 | 0.51651 | 0.56396 | 0.62059 | 0.68336 | 0.79883 | 0.90669 | 1.0278 | 1.1406 | 1.2448 | 1.3518 | 1.4586 | 1.5628 | 1.6685 | 2.0522 | 2.3422 | 0.49298 | 0.55005 | 1.094 | 1.1832 | 1.2815 | 1.3979 | 1.5268 | 1.772 | 2.0062 | 2.2725 | 2.5158 | 2.7362 | 2.9589 | 3.1817 | 3.3985 | 3.6186 | 4.4452 | 5.0845
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.24745 | 0.49522 | 0.57241 | 0.66788 | 0.78029 | 0.91263 | 1.0682 | 1.2861 | 1.5047 | 1.7052 | 1.8611 | 1.9818 | 2.0968 | 2.1886 | 2.2822 | 2.3757 | 2.8641 | 3.2099 | 0.54548 | 1.1427 | 1.3038 | 1.5027 | 1.7364 | 2.0093 | 2.3288 | 2.7899 | 3.2587 | 3.6933 | 4.04 | 4.3122 | 4.5734 | 4.7772 | 4.9841 | 5.1921 | 6.28 | 7.094
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.42726 | 0.47116 | 0.52653 | 0.5931 | 0.66757 | 0.76905 | 0.9201 | 1.1361 | 1.3176 | 1.5236 | 1.7146 | 1.8973 | 2.0744 | 2.2254 | 2.348 | 2.4374 | 2.8888 | 3.1241 | 1.0015 | 1.0985 | 1.2175 | 1.3603 | 1.5199 | 1.7331 | 2.0657 | 2.5445 | 2.9439 | 3.3999 | 3.8149 | 4.2121 | 4.5959 | 4.9173 | 5.1815 | 5.3792 | 6.384 | 6.9111
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.23058 | 0.45512 | 0.5039 | 0.56618 | 0.64171 | 0.73531 | 0.83916 | 1.005 | 1.1606 | 1.3507 | 1.5257 | 1.69 | 1.8505 | 1.9873 | 2.0956 | 2.1711 | 2.5568 | 2.9008 | 0.50921 | 1.0578 | 1.1606 | 1.2917 | 1.4501 | 1.6443 | 1.859 | 2.2112 | 2.545 | 2.9594 | 3.3344 | 3.6848 | 4.0243 | 4.3107 | 4.5396 | 4.7042 | 5.5673 | 6.3596
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.46497 | 0.60875 | 0.75944 | 0.9106 | 1.0786 | 1.262 | 1.486 | 1.8202 | 2.1258 | 2.4617 | 2.7964 | 3.1203 | 3.4995 | 3.929 | 4.3188 | 4.642 | 5.3865 | 5.6156 | 1.07 | 1.3706 | 1.6817 | 1.9941 | 2.3404 | 2.7173 | 3.1776 | 3.8587 | 4.4876 | 5.1804 | 5.8689 | 6.5315 | 7.3064 | 8.189 | 8.9865 | 9.6408 | 11.1738 | 11.6689
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.59754 | 0.89742 | 1.249 | 1.6203 | 2.0428 | 2.533 | 3.1609 | 3.8584 | 4.4811 | 5.0189 | 5.3192 | 5.463 | 5.5854 | 5.7134 | 5.8018 | 5.8897 | 6.3469 | 6.7078 | 1.3574 | 1.988 | 2.7167 | 3.4844 | 4.3571 | 5.3714 | 6.6697 | 8.0977 | 9.3752 | 10.4868 | 11.1247 | 11.4413 | 11.7115 | 11.9939 | 12.1883 | 12.381 | 13.389 | 14.1944
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.54907 | 0.77562 | 1.0199 | 1.2989 | 1.6081 | 1.952 | 2.3173 | 2.8568 | 3.3228 | 3.7602 | 4.2377 | 4.696 | 5.1449 | 5.5646 | 5.8156 | 5.9183 | 6.4353 | 6.8092 | 1.2711 | 1.7643 | 2.287 | 2.8839 | 3.5441 | 4.2749 | 5.0443 | 6.1711 | 7.1452 | 8.0511 | 9.0349 | 9.9799 | 10.9057 | 11.7714 | 12.2958 | 12.5225 | 13.6725 | 14.5177
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.50675 | 0.70037 | 0.92625 | 1.1574 | 1.4236 | 1.7395 | 2.0938 | 2.5445 | 2.9572 | 3.43 | 3.9295 | 4.4185 | 4.8693 | 5.291 | 5.5082 | 5.5789 | 5.9302 | 6.2072 | 1.1622 | 1.5735 | 2.0462 | 2.5298 | 3.0874 | 3.7487 | 4.4844 | 5.4054 | 6.2538 | 7.2285 | 8.2543 | 9.2576 | 10.1783 | 11.0396 | 11.4852 | 11.6373 | 12.4035 | 13.0132
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.16645 | 0.21255 | 0.27442 | 0.33191 | 0.40027 | 0.47347 | 0.55986 | 0.69564 | 0.80676 | 0.92562 | 1.0454 | 1.1726 | 1.3122 | 1.4545 | 1.5938 | 1.73 | 2.0674 | 2.1923 | 0.36512 | 0.46163 | 0.58905 | 0.70775 | 0.84832 | 0.99871 | 1.1756 | 1.4518 | 1.6789 | 1.9219 | 2.1663 | 2.4249 | 2.7079 | 2.9961 | 3.2782 | 3.5538 | 4.2473 | 4.5128
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.21991 | 0.32902 | 0.47011 | 0.61784 | 0.78815 | 0.97223 | 1.1919 | 1.4668 | 1.7118 | 1.9086 | 2.0105 | 2.0581 | 2.1013 | 2.1416 | 2.1816 | 2.2167 | 2.4021 | 2.5693 | 0.48036 | 0.70955 | 1.0007 | 1.3054 | 1.6557 | 2.0337 | 2.4829 | 3.0429 | 3.5431 | 3.9464 | 4.1597 | 4.2634 | 4.358 | 4.4461 | 4.5332 | 4.6105 | 5.0221 | 5.3922
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.19996 | 0.27431 | 0.36344 | 0.45357 | 0.55524 | 0.67412 | 0.80998 | 1.0057 | 1.1708 | 1.3503 | 1.5473 | 1.7344 | 1.9143 | 2.0854 | 2.1948 | 2.2422 | 2.4715 | 2.6513 | 0.44477 | 0.60796 | 0.7979 | 0.99031 | 1.2061 | 1.4564 | 1.741 | 2.1455 | 2.4874 | 2.8582 | 3.2631 | 3.6478 | 4.0179 | 4.3696 | 4.5976 | 4.7014 | 5.2103 | 5.6127
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.18319 | 0.24352 | 0.32574 | 0.41001 | 0.50322 | 0.61384 | 0.74609 | 0.93716 | 1.1011 | 1.2756 | 1.4672 | 1.6508 | 1.8323 | 1.9969 | 2.0922 | 2.127 | 2.2851 | 2.4182 | 0.40137 | 0.52893 | 0.69929 | 0.87424 | 1.0674 | 1.2959 | 1.5674 | 1.9569 | 2.2916 | 2.6474 | 3.0367 | 3.4094 | 3.7776 | 4.1114 | 4.3065 | 4.3802 | 4.7236 | 5.0133
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.4977 | 2.603 | 2.7252 | 2.9487 | 3.1972 | 3.4729 | 3.7792 | 4.215 | 4.586 | 4.9746 | 5.3554 | 5.7332 | 6.1357 | 6.5402 | 6.9352 | 7.2811 | 8.0503 | 8.4454 | 6.1472 | 6.368 | 6.6227 | 7.0942 | 7.6193 | 8.2032 | 8.8496 | 9.7671 | 10.557 | 11.3866 | 12.1935 | 12.9883 | 13.8291 | 14.6736 | 15.4983 | 16.2146 | 17.8257 | 18.6851
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.5909 | 2.8113 | 3.1105 | 3.527 | 3.9959 | 4.5099 | 5.087 | 5.8 | 6.4767 | 7.0561 | 7.4341 | 7.7161 | 7.9876 | 8.2275 | 8.4498 | 8.6292 | 9.2597 | 9.7216 | 6.3487 | 6.8117 | 7.4426 | 8.3236 | 9.3146 | 10.4003 | 11.6086 | 13.1078 | 14.5424 | 15.7764 | 16.6048 | 17.2386 | 17.8555 | 18.3934 | 18.8874 | 19.2923 | 20.7183 | 21.8091
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.5541 | 2.7078 | 2.9139 | 3.2213 | 3.5633 | 3.9346 | 4.3764 | 4.9548 | 5.4632 | 6.0031 | 6.5393 | 7.054 | 7.5556 | 8.0139 | 8.3638 | 8.5457 | 9.1838 | 9.5447 | 6.2828 | 6.6183 | 7.0663 | 7.7316 | 8.4717 | 9.2691 | 10.223 | 11.4654 | 12.5567 | 13.715 | 14.8551 | 15.9493 | 17.0154 | 17.9852 | 18.7374 | 19.1431 | 20.5801 | 21.4095
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.5281 | 2.6631 | 2.8378 | 3.1223 | 3.4363 | 3.7885 | 4.1842 | 4.7193 | 5.206 | 5.7377 | 6.2604 | 6.77 | 7.2632 | 7.7131 | 8.0414 | 8.1966 | 9.3906 | 9.7772 | 6.213 | 6.4986 | 6.8642 | 7.4644 | 8.1289 | 8.873 | 9.7042 | 10.8271 | 11.8545 | 12.9807 | 14.0783 | 15.1465 | 16.1781 | 17.1172 | 17.8125 | 18.1523 | 21.0112 | 21.8998
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.3012 | 1.3862 | 1.4894 | 1.5955 | 1.7031 | 1.842 | 2.0599 | 2.3393 | 1.8048 | 2.0881 | 2.35 | 2.6211 | 2.9171 | 3.2688 | 3.6146 | 3.8652 | 4.6911 | 5.1961 | 3.1774 | 3.3564 | 3.5708 | 3.7907 | 4.0131 | 4.2998 | 4.7521 | 5.3446 | 3.9256 | 4.5469 | 5.111 | 5.6834 | 6.3003 | 7.0371 | 7.7615 | 8.2808 | 10.0613 | 11.2
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.3833 | 1.5722 | 1.8216 | 2.0874 | 2.3937 | 2.7472 | 3.1517 | 3.7044 | 3.4786 | 4.0287 | 4.4735 | 4.7736 | 4.9982 | 5.1449 | 5.2958 | 5.4399 | 6.2157 | 6.8744 | 3.3553 | 3.7553 | 4.2767 | 4.8312 | 5.469 | 6.2011 | 7.0312 | 8.1938 | 7.422 | 8.6075 | 9.5966 | 10.2785 | 10.7991 | 11.1358 | 11.4802 | 11.8127 | 13.6057 | 15.1907
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.3529 | 1.4963 | 1.6792 | 1.8741 | 2.0885 | 2.3538 | 2.7211 | 3.3098 | 3.0307 | 3.5779 | 4.0534 | 4.5101 | 4.926 | 5.2657 | 5.5143 | 5.6547 | 6.3882 | 6.7886 | 3.3012 | 3.6169 | 4.0136 | 4.4314 | 4.8896 | 5.4512 | 6.2573 | 7.554 | 6.6977 | 7.8988 | 8.9244 | 9.9095 | 10.806 | 11.5268 | 12.0661 | 12.3884 | 14.0788 | 15.0035
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.3271 | 1.4409 | 1.5998 | 1.7853 | 1.9728 | 2.1964 | 2.4561 | 2.8654 | 2.4833 | 3.0105 | 3.4916 | 3.9361 | 4.3549 | 4.6517 | 4.8567 | 4.9561 | 5.5631 | 6.1745 | 3.2344 | 3.4775 | 3.813 | 4.2052 | 4.5997 | 5.0657 | 5.6027 | 6.469 | 5.3666 | 6.5091 | 7.5368 | 8.4818 | 9.3679 | 9.9855 | 10.4206 | 10.6466 | 12.0548 | 13.4989
West Burton 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.6955 | 1.7879 | 1.8938 | 2.0141 | 2.1552 | 2.315 | 2.5563 | 2.8451 | 3.0783 | 3.3278 | 3.5843 | 3.8492 | 4.1553 | 4.49 | 4.7987 | 5.069 | 5.8131 | 6.1179 | 4.1535 | 4.3467 | 4.5655 | 4.8141 | 5.1055 | 5.4348 | 5.9574 | 6.5475 | 7.027 | 7.5404 | 8.0669 | 8.6079 | 9.232 | 9.9169 | 10.547 | 11.0939 | 12.6299 | 13.2805
West Burton 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.8031 | 2.0192 | 2.2827 | 2.5886 | 2.9416 | 3.3929 | 3.8604 | 4.4341 | 4.9439 | 5.3691 | 5.6134 | 5.7433 | 5.8607 | 5.97 | 6.0598 | 6.1483 | 6.6151 | 7.018 | 4.3862 | 4.8393 | 5.3838 | 6.0164 | 6.7463 | 7.7038 | 8.664 | 9.838 | 10.8827 | 11.758 | 12.2747 | 12.5592 | 12.8176 | 13.0579 | 13.2535 | 13.4463 | 14.474 | 15.3644
West Burton 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.7638 | 1.9221 | 2.0944 | 2.2914 | 2.5764 | 2.8286 | 3.1224 | 3.523 | 3.8767 | 4.2724 | 4.7043 | 5.1407 | 5.5671 | 5.9649 | 6.2169 | 6.3464 | 6.9421 | 7.3831 | 4.3161 | 4.662 | 5.0298 | 5.4504 | 6.0794 | 6.6125 | 7.2298 | 8.0606 | 8.7957 | 9.6168 | 10.5087 | 11.4093 | 12.2893 | 13.1102 | 13.6366 | 13.9198 | 15.2447 | 16.2304
West Burton 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.7298 | 1.8512 | 2.0047 | 2.1793 | 2.3913 | 2.6328 | 2.9747 | 3.3693 | 3.7103 | 4.0984 | 4.5068 | 4.9114 | 5.3052 | 5.6632 | 6.496 | 6.5916 | 7.0004 | 7.3438 | 4.2285 | 4.4849 | 4.8036 | 5.1679 | 5.6099 | 6.1125 | 6.8452 | 7.6537 | 8.3535 | 9.1511 | 9.9875 | 10.8158 | 11.6207 | 12.3525 | 14.3444 | 14.5504 | 15.4409 | 16.1924
West Burton 132kV | LINCOLN No 2 11kV S STN | Bulk Supply Point | 11 | Counterfactual | 3.073 | 3.2053 | 3.38 | 3.7763 | 4.0435 | 4.3373 | 4.6675 | 5.1383 | 5.5578 | 5.9991 | 6.4959 | 6.9885 | 7.5055 | 7.9959 | 8.4569 | 8.899 | 9.9003 | 10.2368 | 7.595 | 7.8725 | 8.2345 | 9.145 | 9.6991 | 10.3084 | 10.9931 | 11.9654 | 12.8385 | 13.7589 | 14.8114 | 15.8506 | 16.9348 | 17.9559 | 18.9068 | 19.8164 | 21.8972 | 22.614
West Burton 132kV | LINCOLN No 2 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | 3.408 | 3.7003 | 4.0831 | 4.4933 | 5.0579 | 5.6598 | 6.4485 | 7.3651 | 8.2484 | 8.9161 | 9.3474 | 9.6543 | 9.9266 | 9.4172 | 9.683 | 9.9106 | 10.5986 | 10.9954 | 8.3897 | 9.0069 | 9.8038 | 10.6564 | 11.8391 | 13.0991 | 14.7778 | 16.7134 | 18.5994 | 20.0002 | 20.9238 | 21.5958 | 22.1949 | 20.8409 | 21.4234 | 21.924 | 23.4445 | 24.3372
West Burton 132kV | LINCOLN No 2 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | 3.3612 | 3.575 | 3.8413 | 4.1333 | 4.5408 | 5.0886 | 5.6881 | 6.4 | 7.0056 | 7.6218 | 8.2697 | 8.8977 | 8.734 | 9.3056 | 9.7325 | 9.9803 | 11.5637 | 11.9919 | 8.306 | 8.7746 | 9.3457 | 9.9708 | 10.8457 | 12.0542 | 13.3694 | 14.8955 | 16.1835 | 17.4831 | 18.8416 | 20.1603 | 19.5067 | 20.7052 | 21.6138 | 22.1585 | 25.8937 | 26.8577
West Burton 132kV | LINCOLN No 2 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | 3.1127 | 3.2931 | 3.7506 | 4.0169 | 4.4137 | 4.8383 | 5.3782 | 6.0849 | 6.7767 | 7.4183 | 8.0518 | 8.668 | 9.2641 | 9.8118 | 10.2054 | 10.4188 | 11.4868 | 11.8347 | 7.6814 | 8.0658 | 9.1104 | 9.6695 | 10.5106 | 11.4095 | 12.5695 | 14.0749 | 15.5726 | 16.9277 | 18.2475 | 19.5312 | 20.7699 | 21.9089 | 22.7397 | 23.2045 | 25.6908 | 26.4583
West Burton 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.61086 | 0.67131 | 0.7443 | 0.83155 | 0.94202 | 1.0778 | 1.2286 | 1.4551 | 1.6696 | 1.9119 | 2.153 | 2.3919 | 2.6407 | 2.8894 | 3.1332 | 3.3643 | 3.7884 | 4.0424 | 1.3915 | 1.5266 | 1.6903 | 1.8877 | 2.1372 | 2.4424 | 2.7829 | 3.2905 | 3.7825 | 4.3405 | 4.8945 | 5.4383 | 5.9996 | 6.5607 | 7.1109 | 7.634 | 8.5449 | 9.1139
West Burton 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.67911 | 0.84405 | 1.0596 | 1.3354 | 1.669 | 2.0568 | 2.473 | 2.9673 | 3.4548 | 4.1279 | 4.4739 | 4.7542 | 5.0265 | 5.2747 | 5.5272 | 5.7805 | 6.2476 | 6.613 | 1.5474 | 1.924 | 2.4162 | 3.0489 | 3.8169 | 4.7093 | 5.6587 | 6.781 | 7.8961 | 9.3847 | 10.1999 | 10.8764 | 11.5367 | 12.1378 | 12.7471 | 13.3596 | 14.4137 | 15.2722
West Burton 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.66309 | 0.80314 | 0.99167 | 1.225 | 1.499 | 1.8412 | 2.2469 | 2.7088 | 3.1307 | 3.7893 | 4.1899 | 4.5916 | 4.9848 | 5.3471 | 5.6588 | 5.9217 | 6.3733 | 6.636 | 1.5187 | 1.8492 | 2.2911 | 2.842 | 3.4916 | 4.2967 | 5.2503 | 6.3282 | 7.3149 | 8.783 | 9.7027 | 10.6235 | 11.5257 | 12.3558 | 13.0846 | 13.7164 | 14.7337 | 15.3271
West Burton 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.64997 | 0.77424 | 0.94456 | 1.1666 | 1.4351 | 1.7619 | 2.1075 | 2.5238 | 2.9278 | 3.4729 | 3.8459 | 4.211 | 4.5677 | 4.8992 | 5.1767 | 5.4125 | 5.7706 | 6.1131 | 1.4847 | 1.7757 | 2.1745 | 2.6966 | 3.3304 | 4.0993 | 4.9063 | 5.8679 | 6.8065 | 8.0382 | 8.8933 | 9.7293 | 10.5452 | 11.3048 | 11.956 | 12.5263 | 13.3373 | 14.1263
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.7013 | 1.8102 | 1.9414 | 2.0829 | 2.2278 | 2.3925 | 1.9409 | 2.2543 | 2.5175 | 2.8082 | 3.0997 | 3.3895 | 3.7071 | 4.0255 | 4.3321 | 4.6424 | 5.5228 | 6.0022 | 4.0956 | 4.3239 | 4.5959 | 4.8887 | 5.1877 | 5.5268 | 4.3176 | 4.9646 | 5.5158 | 6.1281 | 6.7351 | 7.332 | 7.9809 | 8.631 | 9.2569 | 9.8896 | 11.7369 | 12.7797
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.8114 | 2.0569 | 2.3745 | 2.7197 | 3.106 | 3.5239 | 3.3822 | 4.0266 | 4.6376 | 5.1471 | 5.4417 | 5.631 | 5.7996 | 5.9365 | 6.063 | 6.191 | 6.8763 | 7.4683 | 4.3331 | 4.8502 | 5.516 | 6.2376 | 7.0403 | 7.9065 | 7.3299 | 8.6661 | 9.9433 | 11.0148 | 11.6563 | 12.0832 | 12.4712 | 12.781 | 13.0637 | 13.3536 | 14.915 | 16.2908
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.7704 | 1.9457 | 2.165 | 2.3895 | 2.6249 | 2.9136 | 2.6383 | 3.1491 | 3.5854 | 4.0662 | 4.5518 | 5.0196 | 5.4687 | 5.8743 | 6.1584 | 6.3008 | 7.0209 | 7.5316 | 4.2599 | 4.6438 | 5.118 | 5.6019 | 6.1072 | 6.7183 | 5.9013 | 6.9887 | 7.9155 | 8.9379 | 9.9587 | 10.9429 | 11.8872 | 12.7336 | 13.3362 | 13.6548 | 15.2818 | 16.4368
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.7354 | 1.8806 | 2.0682 | 2.2632 | 2.4812 | 2.7393 | 2.4079 | 2.8633 | 3.2688 | 3.7318 | 4.1987 | 4.6417 | 5.0726 | 5.4504 | 5.6939 | 5.7952 | 6.347 | 6.8675 | 4.1697 | 4.4781 | 4.8705 | 5.2774 | 5.7298 | 6.2637 | 5.3018 | 6.2427 | 7.0851 | 8.0537 | 9.0204 | 9.9359 | 10.8232 | 11.5977 | 12.1032 | 12.3248 | 13.5603 | 14.7415
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.36669 | 0.4523 | 0.55664 | 0.66201 | 0.78081 | 0.92552 | 1.0935 | 1.3751 | 1.6507 | 1.8998 | 2.152 | 2.407 | 2.6772 | 2.947 | 3.2087 | 3.4671 | 4.1003 | 4.3041 | 0.83636 | 1.0137 | 1.2277 | 1.4429 | 1.6863 | 1.9843 | 2.3324 | 2.9151 | 3.5091 | 4.0304 | 4.5554 | 5.08 | 5.6262 | 6.1709 | 6.699 | 7.2205 | 8.5289 | 8.9732
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.47514 | 0.68374 | 0.94391 | 1.2646 | 1.6558 | 2.078 | 2.5714 | 3.1693 | 3.7189 | 4.1696 | 4.392 | 4.4857 | 4.5717 | 4.6475 | 4.723 | 4.7871 | 5.1408 | 5.4518 | 1.071 | 1.5066 | 2.0441 | 2.7215 | 3.5554 | 4.4509 | 5.4854 | 6.732 | 7.8828 | 8.8301 | 9.3096 | 9.517 | 9.7083 | 9.8759 | 10.0424 | 10.186 | 10.981 | 11.6847
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.4352 | 0.57361 | 0.77098 | 0.99308 | 1.2359 | 1.5181 | 1.8487 | 2.2972 | 2.6815 | 3.0759 | 3.4697 | 3.8614 | 4.2471 | 4.606 | 4.8257 | 4.9067 | 5.327 | 5.6364 | 0.99989 | 1.3007 | 1.7345 | 2.2261 | 2.7594 | 3.3766 | 4.094 | 5.0497 | 5.8687 | 6.7005 | 7.5126 | 8.3194 | 9.1133 | 9.851 | 10.3094 | 10.49 | 11.4353 | 12.14
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.40019 | 0.51492 | 0.66153 | 0.84864 | 1.0851 | 1.3682 | 1.6764 | 2.0994 | 2.4737 | 2.8696 | 3.2649 | 3.6304 | 3.9862 | 4.3141 | 4.4968 | 4.5476 | 4.83 | 5.065 | 0.90969 | 1.151 | 1.4558 | 1.859 | 2.3751 | 2.9935 | 3.6524 | 4.5434 | 5.336 | 6.1688 | 6.9867 | 7.7307 | 8.4544 | 9.1201 | 9.4951 | 9.606 | 10.2318 | 10.7582
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.68338 | 0.76316 | 0.86057 | 0.96584 | 1.0822 | 1.2132 | 1.38 | 1.6424 | 1.8957 | 2.1822 | 2.4433 | 2.6808 | 2.9319 | 3.22 | 3.4831 | 3.7159 | 4.5446 | 5.1308 | 1.5766 | 1.7454 | 1.9484 | 2.1671 | 2.4086 | 2.6779 | 3.022 | 3.5846 | 4.1411 | 4.7792 | 5.3486 | 5.8547 | 6.3808 | 6.9866 | 7.5387 | 8.0253 | 9.8337 | 11.1569
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.75489 | 0.93643 | 1.1569 | 1.3808 | 1.645 | 1.9326 | 2.2841 | 2.7972 | 3.3255 | 3.8441 | 4.2846 | 4.5996 | 4.8467 | 5.0366 | 5.2596 | 5.4965 | 6.6902 | 7.4823 | 1.7319 | 2.1204 | 2.5826 | 3.0498 | 3.6011 | 4.1916 | 4.9108 | 6.0008 | 7.1391 | 8.2691 | 9.2544 | 9.9714 | 10.5394 | 10.966 | 11.4614 | 11.9734 | 14.6443 | 16.5418
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.73025 | 0.87269 | 1.0366 | 1.2034 | 1.369 | 1.5796 | 1.9255 | 2.4985 | 2.9895 | 3.514 | 3.9302 | 4.3544 | 4.7661 | 5.1026 | 5.3867 | 5.6314 | 6.7218 | 7.189 | 1.6879 | 2.004 | 2.3585 | 2.7169 | 3.071 | 3.5113 | 4.2788 | 5.5578 | 6.6448 | 7.8128 | 8.7094 | 9.637 | 10.5352 | 11.2548 | 11.8696 | 12.4057 | 14.8534 | 15.9141
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.70648 | 0.8198 | 0.963 | 1.13 | 1.299 | 1.4822 | 1.6936 | 2.0563 | 2.4146 | 2.8921 | 3.3331 | 3.7238 | 4.1015 | 4.3809 | 4.6067 | 4.7844 | 5.6173 | 6.3963 | 1.6277 | 1.8722 | 2.1755 | 2.5285 | 2.8843 | 3.2621 | 3.6964 | 4.4714 | 5.2453 | 6.295 | 7.2485 | 8.0879 | 8.8928 | 9.4779 | 9.9586 | 10.3529 | 12.2477 | 14.0676
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.64808 | 0.71476 | 0.79197 | 0.87712 | 0.97366 | 1.0977 | 1.2348 | 1.4723 | 1.6784 | 1.9045 | 2.1268 | 2.3455 | 2.5812 | 2.8175 | 3.0487 | 3.2707 | 3.9102 | 4.3087 | 1.5401 | 1.6797 | 1.8394 | 2.0153 | 2.214 | 2.468 | 2.7482 | 3.2415 | 3.6772 | 4.1591 | 4.6261 | 5.0796 | 5.563 | 6.0476 | 6.5212 | 6.9717 | 8.3033 | 9.1801
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.72871 | 0.88967 | 1.0895 | 1.3134 | 1.5666 | 1.8733 | 2.2444 | 2.7358 | 3.2051 | 3.6125 | 3.8272 | 3.9548 | 4.0724 | 4.1677 | 4.2689 | 4.3521 | 4.9851 | 5.4746 | 1.7143 | 2.0518 | 2.4648 | 2.9264 | 3.4469 | 4.0752 | 4.8325 | 5.8503 | 6.8311 | 7.6896 | 8.1444 | 8.4228 | 8.6806 | 8.8823 | 9.097 | 9.2685 | 10.652 | 11.7976
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.69866 | 0.80632 | 0.93091 | 1.0656 | 1.2168 | 1.4274 | 1.6803 | 2.0601 | 2.4119 | 2.7523 | 3.0724 | 3.3992 | 3.7317 | 4.0415 | 4.2701 | 4.3979 | 5.0814 | 5.4573 | 1.6607 | 1.8963 | 2.1627 | 2.4499 | 2.7703 | 3.2115 | 3.7444 | 4.55 | 5.303 | 6.0154 | 6.667 | 7.3379 | 8.0257 | 8.6643 | 9.1493 | 9.4324 | 10.9529 | 11.8059
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.6728 | 0.76126 | 0.871 | 0.99353 | 1.1335 | 1.3186 | 1.5344 | 1.871 | 2.1761 | 2.5304 | 2.854 | 3.1705 | 3.4811 | 3.7727 | 3.9602 | 4.0531 | 4.5613 | 5.0259 | 1.594 | 1.7811 | 2.0095 | 2.2641 | 2.5542 | 2.936 | 3.3788 | 4.0789 | 4.718 | 5.4685 | 6.1347 | 6.7842 | 7.4208 | 8.0206 | 8.4114 | 8.6144 | 9.7517 | 10.8161
West Burton 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.5301 | 2.5824 | 2.6283 | 2.6709 | 2.721 | 2.7767 | 2.8997 | 2.9997 | 3.0815 | 3.1727 | 3.2632 | 3.3498 | 3.4478 | 3.5446 | 3.639 | 3.7347 | 4.0076 | 4.1245 | 6.281 | 6.3906 | 6.4859 | 6.5741 | 6.6778 | 6.7927 | 7.0722 | 7.277 | 7.4455 | 7.6333 | 7.8193 | 7.9958 | 8.1946 | 8.3908 | 8.5823 | 8.776 | 9.3399 | 9.5889
West Burton 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.5678 | 2.6709 | 2.7715 | 2.8783 | 3.0027 | 3.1988 | 3.3677 | 3.5678 | 3.747 | 3.8904 | 3.965 | 3.9997 | 4.0325 | 4.062 | 4.0972 | 4.1296 | 4.3081 | 4.4507 | 6.3625 | 6.5807 | 6.7897 | 7.0108 | 7.2681 | 7.6992 | 8.0462 | 8.4559 | 8.8228 | 9.1175 | 9.2744 | 9.3506 | 9.4234 | 9.4886 | 9.565 | 9.6358 | 10.0299 | 10.3472
West Burton 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.5542 | 2.6338 | 2.7016 | 2.77 | 2.9076 | 2.9908 | 3.0884 | 3.2317 | 3.3596 | 3.496 | 3.64 | 3.7897 | 3.934 | 4.072 | 4.1628 | 4.2107 | 4.432 | 4.5952 | 6.3382 | 6.5118 | 6.6575 | 6.804 | 7.1187 | 7.2939 | 7.4988 | 7.7966 | 8.0627 | 8.3457 | 8.6423 | 8.9507 | 9.2483 | 9.5328 | 9.7229 | 9.8278 | 10.3204 | 10.6847
West Burton 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.542 | 2.6116 | 2.671 | 2.736 | 2.8104 | 2.8951 | 3.054 | 3.1892 | 3.3044 | 3.4352 | 3.5701 | 3.7044 | 3.8386 | 3.9578 | 5.1651 | 5.1994 | 5.3504 | 5.4816 | 6.3069 | 6.4554 | 6.5801 | 6.7153 | 6.8706 | 7.047 | 7.4011 | 7.6776 | 7.9133 | 8.1806 | 8.4562 | 8.7301 | 9.0037 | 9.2466 | 12.2323 | 12.3065 | 12.6368 | 12.9237
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.38829 | 0.41488 | 0.44737 | 0.48257 | 0.51826 | 0.56307 | 0.65033 | 0.77231 | 0.88867 | 1.0268 | 1.1443 | 1.2456 | 1.3482 | 1.4517 | 1.5506 | 1.6464 | 2.0231 | 2.3009 | 0.95 | 1.0062 | 1.0738 | 1.1469 | 1.2207 | 1.3131 | 1.4949 | 1.7626 | 2.0261 | 2.3428 | 2.6066 | 2.8275 | 3.0459 | 3.2665 | 3.4773 | 3.6812 | 4.5261 | 5.1748
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.41436 | 0.47779 | 0.55881 | 0.6417 | 0.74367 | 0.86071 | 1.0028 | 1.229 | 1.4647 | 1.6955 | 1.8822 | 2.0198 | 2.1468 | 2.2279 | 2.313 | 2.4534 | 2.9062 | 3.3329 | 1.0061 | 1.1412 | 1.3108 | 1.4833 | 1.6958 | 1.9384 | 2.2313 | 2.7228 | 3.2444 | 3.7611 | 4.1924 | 4.5174 | 4.8211 | 5.0124 | 5.2117 | 5.5513 | 6.6257 | 7.6705
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.40461 | 0.45271 | 0.51183 | 0.5751 | 0.6422 | 0.72925 | 0.9033 | 1.1737 | 1.3936 | 1.6373 | 1.9573 | 2.1555 | 2.3417 | 2.4804 | 2.5913 | 2.6677 | 3.0701 | 3.2576 | 0.98879 | 1.0954 | 1.2234 | 1.3591 | 1.5025 | 1.6864 | 2.0822 | 2.7018 | 3.2016 | 3.7597 | 4.5058 | 4.9508 | 5.3687 | 5.6727 | 5.9209 | 6.1003 | 7.05 | 7.4889
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.39625 | 0.43495 | 0.48604 | 0.54624 | 0.60979 | 0.68693 | 0.77892 | 0.94544 | 1.1078 | 1.3287 | 1.5208 | 1.6974 | 1.849 | 1.9646 | 2.0521 | 2.1624 | 2.5231 | 2.915 | 0.96724 | 1.0504 | 1.1584 | 1.2852 | 1.4188 | 1.5797 | 1.7706 | 2.1346 | 2.4938 | 2.9921 | 3.4173 | 3.8058 | 4.136 | 4.3835 | 4.5754 | 4.8422 | 5.7024 | 6.6487
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.61859 | 0.77607 | 0.96858 | 1.1875 | 1.4276 | 1.6821 | 1.967 | 2.3624 | 2.6827 | 3.0266 | 3.3852 | 3.7545 | 4.1649 | 4.5715 | 4.9714 | 5.3801 | 6.3488 | 6.7126 | 1.3887 | 1.7181 | 2.1174 | 2.5706 | 3.0671 | 3.5925 | 4.1798 | 4.9857 | 5.6423 | 6.3471 | 7.0813 | 7.8346 | 8.6687 | 9.4939 | 10.3054 | 11.135 | 13.1323 | 13.9101
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.7761 | 1.1188 | 1.5479 | 2.0373 | 2.5914 | 3.1726 | 3.871 | 4.6719 | 5.3917 | 5.9711 | 6.246 | 6.3812 | 6.5012 | 6.6127 | 6.7278 | 6.8273 | 7.2796 | 7.6612 | 1.7297 | 2.4493 | 3.3416 | 4.3579 | 5.5075 | 6.7108 | 8.1492 | 9.7848 | 11.2573 | 12.4467 | 13.0274 | 13.3278 | 13.5974 | 13.8474 | 14.1037 | 14.3281 | 15.3615 | 16.2366
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.71875 | 0.96015 | 1.249 | 1.5726 | 1.933 | 2.3216 | 2.7798 | 3.3609 | 3.8644 | 4.4074 | 4.9778 | 5.533 | 6.0771 | 6.5885 | 6.9126 | 7.0488 | 7.6345 | 8.0918 | 1.6277 | 2.1536 | 2.7731 | 3.4657 | 4.235 | 5.0592 | 6.0257 | 7.2307 | 8.277 | 9.4024 | 10.5812 | 11.7289 | 12.8537 | 13.9109 | 14.5923 | 14.8972 | 16.2254 | 17.274
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.66867 | 0.87415 | 1.1337 | 1.4335 | 1.7758 | 2.1445 | 2.5758 | 3.125 | 3.598 | 4.1155 | 4.6661 | 5.2034 | 5.7328 | 6.2174 | 6.5006 | 6.5947 | 6.9903 | 7.3307 | 1.4986 | 1.9339 | 2.4788 | 3.1078 | 3.8261 | 4.5974 | 5.4929 | 6.616 | 7.5848 | 8.6425 | 9.7669 | 10.8641 | 11.9444 | 12.9333 | 13.5184 | 13.7251 | 14.606 | 15.3644
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.71607 | 0.7929 | 0.87777 | 0.96497 | 1.0845 | 1.2353 | 1.3989 | 1.678 | 1.9429 | 2.2302 | 2.4884 | 2.74 | 3.0054 | 3.2704 | 3.5301 | 3.7928 | 4.6447 | 5.1073 | 1.7022 | 1.8676 | 2.0478 | 2.23 | 2.48 | 2.7945 | 3.1339 | 3.7208 | 4.2893 | 4.9085 | 5.4571 | 5.9842 | 6.5336 | 7.0825 | 7.6199 | 8.1633 | 9.9835 | 11.0071
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.81682 | 1.013 | 1.2445 | 1.5027 | 1.813 | 2.1624 | 2.5581 | 3.1001 | 3.6306 | 4.102 | 4.4007 | 4.6228 | 4.8335 | 5.0168 | 5.1928 | 5.3659 | 6.2873 | 6.8307 | 1.9276 | 2.3558 | 2.8511 | 3.4016 | 4.0592 | 4.7921 | 5.6088 | 6.7453 | 7.8693 | 8.8775 | 9.536 | 10.0379 | 10.5172 | 10.9241 | 11.3155 | 11.7035 | 13.7855 | 15.0765
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.78788 | 0.93511 | 1.1167 | 1.2746 | 1.4747 | 1.7298 | 2.067 | 2.5541 | 2.9671 | 3.428 | 3.8489 | 4.3412 | 4.739 | 5.0971 | 5.3588 | 5.5272 | 6.3572 | 6.7274 | 1.8759 | 2.2117 | 2.622 | 2.9678 | 3.4023 | 3.9499 | 4.687 | 5.7488 | 6.6444 | 7.6472 | 8.5489 | 9.6328 | 10.4845 | 11.2408 | 11.8031 | 12.179 | 14.0456 | 14.8883
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.76383 | 0.88884 | 1.0331 | 1.1932 | 1.3966 | 1.6347 | 1.8849 | 2.28 | 2.6496 | 3.0821 | 3.4667 | 3.8482 | 4.2147 | 4.5402 | 4.766 | 4.8981 | 5.613 | 6.1394 | 1.8138 | 2.0933 | 2.4096 | 2.7582 | 3.1977 | 3.7053 | 4.2265 | 5.0588 | 5.8437 | 6.7725 | 7.5848 | 8.3893 | 9.1578 | 9.8353 | 10.313 | 10.6054 | 12.232 | 13.452
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.16098 | 0.18779 | 0.21609 | 0.25206 | 0.2895 | 0.33111 | 0.37763 | 0.45245 | 0.51226 | 0.57647 | 0.64333 | 0.71627 | 0.79831 | 0.8791 | 0.95739 | 1.0372 | 1.2758 | 1.4196 | 0.37467 | 0.43192 | 0.49101 | 0.56572 | 0.64318 | 0.72904 | 0.82479 | 0.97717 | 1.0996 | 1.2308 | 1.3673 | 1.5157 | 1.6822 | 1.846 | 2.0047 | 2.1663 | 2.6547 | 2.9537
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.18776 | 0.25063 | 0.32736 | 0.41601 | 0.51134 | 0.61662 | 0.7445 | 0.901 | 1.0432 | 1.1627 | 1.2288 | 1.2684 | 1.2984 | 1.3261 | 1.3547 | 1.3775 | 1.478 | 1.5805 | 0.4324 | 0.56712 | 0.72711 | 0.91154 | 1.1088 | 1.3261 | 1.5888 | 1.9086 | 2.1996 | 2.4449 | 2.5832 | 2.668 | 2.7332 | 2.7939 | 2.8563 | 2.9073 | 3.1373 | 3.3703
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.17771 | 0.22496 | 0.27534 | 0.33239 | 0.39284 | 0.46455 | 0.54608 | 0.66 | 0.75912 | 0.86652 | 0.97973 | 1.0991 | 1.2141 | 1.3223 | 1.3969 | 1.4331 | 1.5773 | 1.7059 | 0.41435 | 0.52071 | 0.62935 | 0.75175 | 0.88066 | 1.0321 | 1.2028 | 1.4379 | 1.6431 | 1.8645 | 2.0975 | 2.3427 | 2.5792 | 2.8026 | 2.9583 | 3.0373 | 3.3609 | 3.6531
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.17033 | 0.20614 | 0.25122 | 0.30599 | 0.36386 | 0.43095 | 0.51121 | 0.62689 | 0.72744 | 0.83804 | 0.95156 | 1.0617 | 1.1692 | 1.2643 | 1.3275 | 1.3542 | 1.4493 | 1.5445 | 0.39476 | 0.47198 | 0.56628 | 0.68054 | 0.80056 | 0.93924 | 1.1043 | 1.3401 | 1.5452 | 1.7701 | 2.0006 | 2.2242 | 2.4424 | 2.6359 | 2.7655 | 2.8221 | 3.0297 | 3.238
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.6981 | 0.81337 | 0.94461 | 1.0852 | 1.2445 | 1.4255 | 1.6322 | 1.993 | 2.3061 | 2.6496 | 2.9989 | 3.336 | 3.7087 | 4.0797 | 4.4303 | 4.7867 | 5.6427 | 6.0142 | 1.6049 | 1.846 | 2.1176 | 2.4081 | 2.7364 | 3.1085 | 3.5324 | 4.2724 | 4.9216 | 5.6361 | 6.3638 | 7.0612 | 7.8295 | 8.5934 | 9.3087 | 10.0338 | 11.814 | 12.627
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.83691 | 1.1128 | 1.4561 | 1.8313 | 2.255 | 2.7382 | 3.3859 | 4.15 | 4.8389 | 5.3952 | 5.6704 | 5.8037 | 5.9192 | 6.0182 | 6.1195 | 6.2217 | 6.7183 | 7.2011 | 1.9047 | 2.4835 | 3.1961 | 3.9723 | 4.8461 | 5.8424 | 7.183 | 8.7608 | 10.1957 | 11.3572 | 11.9533 | 12.2616 | 12.5317 | 12.7611 | 12.9913 | 13.2254 | 14.3676 | 15.4912
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.78527 | 0.98177 | 1.2105 | 1.4595 | 1.7146 | 2.0583 | 2.4715 | 3.0205 | 3.4983 | 4.0082 | 4.5268 | 5.0271 | 5.5122 | 5.9534 | 6.2356 | 6.3601 | 6.9408 | 7.4254 | 1.8128 | 2.2427 | 2.7334 | 3.2667 | 3.8095 | 4.5418 | 5.4253 | 6.5865 | 7.5993 | 8.6752 | 9.7589 | 10.8039 | 11.8149 | 12.7292 | 13.3266 | 13.6095 | 14.9398 | 16.0538
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.73988 | 0.89964 | 1.1002 | 1.3067 | 1.5468 | 1.8331 | 2.1878 | 2.6922 | 3.1583 | 3.6575 | 4.1584 | 4.6383 | 5.0988 | 5.5198 | 5.7589 | 5.8438 | 6.2424 | 6.6731 | 1.696 | 2.0342 | 2.454 | 2.8851 | 3.3856 | 3.9811 | 4.7173 | 5.7603 | 6.7381 | 7.7828 | 8.8186 | 9.8084 | 10.7551 | 11.6177 | 12.1137 | 12.303 | 13.2083 | 14.1877
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.0794 | 1.1078 | 1.2062 | 1.236 | 1.2765 | 1.335 | 1.4005 | 1.5105 | 1.6185 | 1.7166 | 1.8107 | 1.9012 | 2.0013 | 2.0993 | 2.1936 | 2.288 | 2.5883 | 2.7881 | 2.5357 | 2.5946 | 2.7922 | 2.8527 | 2.9364 | 3.059 | 3.1968 | 3.4318 | 3.6708 | 3.8831 | 4.0829 | 4.2717 | 4.4783 | 4.6782 | 4.8714 | 5.0645 | 5.6956 | 6.1267
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.1008 | 1.2434 | 1.3354 | 1.4321 | 1.5469 | 1.6947 | 1.8287 | 2.0169 | 2.1858 | 2.3337 | 2.4301 | 2.498 | 2.7314 | 2.7885 | 2.8487 | 2.9005 | 3.2138 | 3.4437 | 2.5793 | 2.874 | 3.072 | 3.2773 | 3.521 | 3.8372 | 4.1087 | 4.5007 | 4.8514 | 5.1606 | 5.3681 | 5.5171 | 5.9983 | 6.1203 | 6.2491 | 6.3581 | 7.0432 | 7.5675
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.0855 | 1.2148 | 1.266 | 1.3428 | 1.4093 | 1.5227 | 1.626 | 1.7773 | 1.9038 | 2.0474 | 2.1797 | 2.3536 | 2.6657 | 2.7952 | 2.8935 | 2.9564 | 2.8436 | 3.0518 | 2.5486 | 2.8214 | 2.9326 | 3.1055 | 3.2479 | 3.496 | 3.715 | 4.0378 | 4.3056 | 4.611 | 4.8829 | 5.2614 | 5.8992 | 6.1674 | 6.3735 | 6.5089 | 6.1259 | 6.587
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.0871 | 1.1988 | 1.2671 | 1.3276 | 1.4016 | 1.511 | 1.5959 | 1.7338 | 1.85 | 1.9893 | 2.1292 | 2.2593 | 2.4791 | 2.594 | 2.6782 | 2.7206 | 2.9835 | 3.2215 | 2.5518 | 2.7804 | 2.9337 | 3.0648 | 3.2252 | 3.466 | 3.6394 | 3.9281 | 4.1703 | 4.4647 | 4.7566 | 5.027 | 5.4761 | 5.7116 | 5.8856 | 5.9733 | 6.5538 | 7.0835
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.96559 | 1.0832 | 1.2303 | 1.3989 | 1.5986 | 1.8167 | 2.0534 | 2.4325 | 2.7945 | 3.1993 | 3.5947 | 3.9484 | 4.3464 | 4.744 | 5.2587 | 5.6261 | 6.4359 | 6.6899 | 2.0346 | 2.2804 | 2.5886 | 2.9459 | 3.3699 | 3.8288 | 4.3202 | 5.0936 | 5.8408 | 6.6781 | 7.494 | 8.2173 | 9.0289 | 9.8392 | 10.8818 | 11.6272 | 13.2969 | 13.8473
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.1084 | 1.4144 | 1.8166 | 2.2578 | 2.7742 | 3.386 | 4.087 | 4.9818 | 5.6523 | 6.2041 | 6.475 | 6.5849 | 6.6759 | 6.7599 | 7.1047 | 7.1806 | 7.5175 | 7.8219 | 2.343 | 2.9932 | 3.8446 | 4.7798 | 5.8754 | 7.1793 | 8.6442 | 10.497 | 11.871 | 13.008 | 13.5841 | 13.8319 | 14.0394 | 14.2307 | 14.9426 | 15.1162 | 15.8952 | 16.5987
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.0547 | 1.2853 | 1.5733 | 1.9066 | 2.305 | 2.7893 | 3.2624 | 3.8099 | 4.2586 | 4.738 | 5.2442 | 5.721 | 6.1885 | 6.6245 | 7.0995 | 7.2009 | 7.6395 | 7.9897 | 2.2476 | 2.7581 | 3.3906 | 4.1244 | 5.0016 | 6.067 | 7.0835 | 8.2219 | 9.1535 | 10.1466 | 11.1919 | 12.1776 | 13.144 | 14.0453 | 15.0236 | 15.2541 | 16.2628 | 17.0769
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.0073 | 1.194 | 1.4553 | 1.728 | 2.0711 | 2.4977 | 2.9629 | 3.5486 | 4.0036 | 4.4929 | 4.9843 | 5.464 | 5.931 | 6.3636 | 6.7334 | 6.8046 | 7.0972 | 7.3456 | 2.1255 | 2.53 | 3.0949 | 3.6879 | 4.435 | 5.3648 | 6.3536 | 7.5658 | 8.5024 | 9.5078 | 10.511 | 11.4898 | 12.442 | 13.3239 | 14.0791 | 14.2369 | 14.8962 | 15.4586
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.65498 | 0.75093 | 0.87674 | 1.0109 | 1.1567 | 1.3327 | 1.4701 | 1.6855 | 1.8572 | 2.0431 | 2.2298 | 2.4187 | 2.6252 | 2.8308 | 3.0286 | 3.2309 | 3.7714 | 4.0228 | 1.525 | 1.73 | 1.9952 | 2.2768 | 2.59 | 2.9636 | 3.2488 | 3.6978 | 4.0579 | 4.4506 | 4.8404 | 5.2303 | 5.6526 | 6.0729 | 6.4772 | 6.89 | 8.024 | 8.577
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.74367 | 0.95289 | 1.2252 | 1.5586 | 1.9349 | 2.2877 | 2.6248 | 3.0558 | 3.4393 | 3.7659 | 4.5796 | 4.6844 | 4.7792 | 4.8543 | 4.93 | 5.0119 | 5.412 | 5.6895 | 1.7218 | 2.1775 | 2.7609 | 3.4814 | 4.3042 | 5.0548 | 5.7543 | 6.6531 | 7.4509 | 8.1363 | 9.7968 | 10.0353 | 10.254 | 10.4242 | 10.5951 | 10.7794 | 11.7174 | 12.3814
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.717 | 0.87892 | 1.1434 | 1.3769 | 1.5943 | 1.8587 | 2.1055 | 2.4529 | 2.7318 | 3.04 | 3.3499 | 3.6583 | 4.0797 | 4.3462 | 4.5214 | 4.6136 | 4.9766 | 5.1808 | 1.6743 | 2.04 | 2.6383 | 3.1509 | 3.629 | 4.2077 | 4.744 | 5.4923 | 6.0858 | 6.7428 | 7.3955 | 8.0438 | 8.9778 | 9.5326 | 9.9039 | 10.1092 | 10.9432 | 11.4193
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.69343 | 0.83705 | 1.0282 | 1.2674 | 1.5354 | 1.7929 | 2.004 | 2.3097 | 2.5638 | 2.8564 | 3.1478 | 3.429 | 3.6998 | 3.94 | 4.0864 | 4.1509 | 4.4784 | 4.7228 | 1.6136 | 1.9329 | 2.3496 | 2.876 | 3.4767 | 4.0361 | 4.4802 | 5.1217 | 5.6509 | 6.2655 | 6.8708 | 7.4525 | 8.011 | 8.5034 | 8.8078 | 8.9495 | 9.7143 | 10.2865
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.21831 | 0.24771 | 0.28021 | 0.31858 | 0.36132 | 0.41591 | 0.47671 | 0.58212 | 0.67816 | 0.77945 | 0.88178 | 0.98063 | 1.0835 | 1.2056 | 1.3096 | 1.4083 | 1.712 | 1.9096 | 0.51853 | 0.58051 | 0.64794 | 0.72729 | 0.81598 | 0.92917 | 1.0551 | 1.2765 | 1.4834 | 1.7003 | 1.9165 | 2.1223 | 2.334 | 2.5953 | 2.8122 | 3.0148 | 3.6578 | 4.0893
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.25046 | 0.31906 | 0.40566 | 0.52936 | 0.65231 | 0.78094 | 0.93639 | 1.1432 | 1.3542 | 1.6023 | 1.7167 | 1.7936 | 1.8636 | 1.9204 | 1.9797 | 2.0375 | 2.3392 | 2.5623 | 0.58796 | 0.73323 | 0.9136 | 1.1813 | 1.4422 | 1.7077 | 2.0266 | 2.4576 | 2.9027 | 3.4536 | 3.7046 | 3.8776 | 4.037 | 4.1638 | 4.2956 | 4.4252 | 5.1041 | 5.6312
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.23835 | 0.28718 | 0.36598 | 0.43537 | 0.50198 | 0.5911 | 0.72498 | 0.91298 | 1.1241 | 1.2918 | 1.4558 | 1.6124 | 1.7631 | 1.8969 | 1.996 | 2.055 | 2.346 | 2.5188 | 0.56622 | 0.67461 | 0.85242 | 1.0038 | 1.1458 | 1.3333 | 1.6237 | 2.0308 | 2.5068 | 2.8688 | 3.2177 | 3.551 | 3.8711 | 4.152 | 4.3636 | 4.4948 | 5.1477 | 5.5391
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.2289 | 0.26714 | 0.31599 | 0.39729 | 0.47607 | 0.56063 | 0.65487 | 0.80204 | 0.94314 | 1.1704 | 1.3299 | 1.4773 | 1.6177 | 1.7386 | 1.8223 | 1.8658 | 2.0861 | 2.3053 | 0.54157 | 0.62302 | 0.7253 | 0.90451 | 1.0747 | 1.2513 | 1.4452 | 1.7523 | 2.0497 | 2.5561 | 2.8911 | 3.1995 | 3.491 | 3.7407 | 3.9157 | 4.0113 | 4.5076 | 5.0095
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.69477 | 0.78838 | 0.89915 | 1.0146 | 1.1491 | 1.306 | 1.4859 | 1.78 | 2.0387 | 2.3216 | 2.6067 | 2.8721 | 3.1684 | 3.4633 | 3.7549 | 4.0503 | 4.7223 | 4.9551 | 1.5028 | 1.6974 | 1.9261 | 2.1643 | 2.4412 | 2.7635 | 3.1323 | 3.7326 | 4.2654 | 4.8493 | 5.4358 | 5.9777 | 6.58 | 7.1786 | 7.7704 | 8.3702 | 9.7586 | 10.2634
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.80753 | 1.0306 | 1.3136 | 1.616 | 1.9685 | 2.3695 | 2.8753 | 3.4751 | 3.9959 | 4.4137 | 4.6125 | 4.7022 | 4.785 | 4.8612 | 4.9372 | 5.0115 | 5.3455 | 5.6323 | 1.7463 | 2.2117 | 2.7974 | 3.4208 | 4.1462 | 4.9735 | 6.0146 | 7.2424 | 8.3089 | 9.1678 | 9.5887 | 9.7906 | 9.9787 | 10.1507 | 10.3218 | 10.4891 | 11.2489 | 11.9082
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.76509 | 0.92478 | 1.113 | 1.3253 | 1.5318 | 1.7734 | 2.0672 | 2.4862 | 2.8513 | 3.2428 | 3.6562 | 4.0492 | 4.4318 | 4.7917 | 5.0158 | 5.1091 | 5.5209 | 5.8413 | 1.6708 | 2.0175 | 2.4206 | 2.8738 | 3.3123 | 3.8215 | 4.4386 | 5.3097 | 6.0697 | 6.8829 | 7.7377 | 8.5511 | 9.3431 | 10.0872 | 10.5592 | 10.7689 | 11.7047 | 12.4411
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.72787 | 0.86001 | 1.031 | 1.199 | 1.4043 | 1.6451 | 1.9184 | 2.3089 | 2.6482 | 3.0157 | 3.4131 | 3.7986 | 4.1774 | 4.5253 | 4.7249 | 4.7891 | 5.0732 | 5.3139 | 1.5749 | 1.8533 | 2.2107 | 2.5607 | 2.989 | 3.4899 | 4.053 | 4.8525 | 5.5481 | 6.3012 | 7.1137 | 7.9011 | 8.674 | 9.3835 | 9.796 | 9.9375 | 10.5716 | 11.1139
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.43513 | 0.48497 | 0.54162 | 0.6049 | 0.67921 | 0.76784 | 0.86452 | 1.0159 | 1.1892 | 1.393 | 1.6195 | 1.7838 | 1.9551 | 2.1096 | 2.2338 | 2.3628 | 2.7011 | 2.8709 | 1.0451 | 1.1491 | 1.2666 | 1.3977 | 1.5515 | 1.7344 | 1.934 | 2.2479 | 2.6131 | 3.0451 | 3.5407 | 3.9004 | 4.2708 | 4.5981 | 4.8516 | 5.1154 | 5.827 | 6.2029
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.48704 | 0.60166 | 0.75158 | 0.91611 | 1.1024 | 1.3069 | 1.6467 | 2.0543 | 2.484 | 2.7445 | 2.8642 | 2.9246 | 2.981 | 3.0281 | 3.0797 | 3.1327 | 3.4058 | 3.6789 | 1.1576 | 1.3988 | 1.7122 | 2.0552 | 2.4435 | 2.8686 | 3.6025 | 4.4859 | 5.4435 | 6.0051 | 6.2692 | 6.4072 | 6.537 | 6.6434 | 6.7592 | 6.8788 | 7.4963 | 8.1359
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.469 | 0.56744 | 0.69277 | 0.84453 | 0.99005 | 1.2015 | 1.475 | 1.8 | 2.0588 | 2.267 | 2.4623 | 2.6512 | 2.8375 | 3.009 | 3.1268 | 3.1853 | 3.5394 | 3.7478 | 1.1256 | 1.3398 | 1.6096 | 1.9356 | 2.248 | 2.7236 | 3.3472 | 4.0734 | 4.646 | 5.0933 | 5.5035 | 5.9 | 6.2903 | 6.6471 | 6.8968 | 7.0284 | 7.8445 | 8.3166
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.45071 | 0.52813 | 0.63094 | 0.73436 | 0.87323 | 1.0401 | 1.2592 | 1.5537 | 1.8838 | 2.1323 | 2.3208 | 2.4953 | 2.6614 | 2.8137 | 2.9079 | 2.9482 | 3.1555 | 3.4071 | 1.0793 | 1.2439 | 1.4616 | 1.6796 | 1.9737 | 2.3282 | 2.8058 | 3.4515 | 4.2011 | 4.7477 | 5.143 | 5.5035 | 5.8455 | 6.1573 | 6.3535 | 6.4431 | 6.9121 | 7.4933
Willington 132kV | DERBY 11kV S STN | Bulk Supply Point | 11 | Counterfactual | 1.5116 | 1.7237 | 1.9815 | 2.2705 | 2.6111 | 2.9234 | 3.2751 | 3.8424 | 4.3032 | 4.7951 | 5.3117 | 5.8677 | 6.4904 | 7.1232 | 7.7238 | 8.3103 | 9.7734 | 10.4342 | 3.1814 | 3.6259 | 4.1598 | 4.7574 | 5.4866 | 6.1286 | 6.85 | 8.0052 | 8.9487 | 9.9558 | 11.012 | 12.1475 | 13.4159 | 14.7106 | 15.9343 | 17.1241 | 20.1348 | 21.5265
Willington 132kV | DERBY 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | 1.7201 | 2.1888 | 2.7784 | 3.4285 | 4.1118 | 4.8534 | 5.7581 | 6.8875 | 7.9179 | 8.8115 | 9.2795 | 9.5235 | 9.7288 | 9.9268 | 10.1502 | 10.3211 | 11.0968 | 11.7335 | 3.6314 | 4.6189 | 5.8426 | 7.1893 | 8.5968 | 10.1232 | 11.9765 | 14.2842 | 16.3959 | 18.2532 | 19.2414 | 19.7729 | 20.2242 | 20.6579 | 21.1413 | 21.5189 | 23.2557 | 24.6862
Willington 132kV | DERBY 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | 1.6425 | 1.9761 | 2.3702 | 2.7977 | 3.263 | 3.7985 | 4.3962 | 5.2211 | 5.9705 | 6.7314 | 7.5437 | 8.3232 | 9.0854 | 9.8009 | 10.3109 | 10.5479 | 11.5237 | 12.2871 | 3.4928 | 4.224 | 5.068 | 5.9819 | 6.9722 | 8.1053 | 9.3602 | 11.0692 | 12.6413 | 14.2174 | 15.8943 | 17.5054 | 19.0809 | 20.5602 | 21.6273 | 22.1475 | 24.3221 | 26.0389
Willington 132kV | DERBY 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | 1.578 | 1.856 | 2.2146 | 2.6148 | 3.011 | 3.4725 | 4.0391 | 4.8712 | 5.5981 | 6.4276 | 7.2276 | 8.0051 | 8.7718 | 9.4679 | 9.9169 | 10.0913 | 10.7773 | 11.3623 | 3.3258 | 3.916 | 4.6659 | 5.5016 | 6.3231 | 7.2785 | 8.4465 | 10.1514 | 11.6443 | 13.3621 | 14.9946 | 16.5805 | 18.1437 | 19.5635 | 20.4881 | 20.8628 | 22.3623 | 23.6405
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.1924 | 0.34272 | 0.42102 | 0.4999 | 0.5466 | 0.60219 | 0.66515 | 0.76141 | 0.84259 | 0.92945 | 1.0174 | 1.1114 | 1.2153 | 1.3155 | 1.4164 | 1.517 | 1.7898 | 1.9246 | 0.42791 | 0.73566 | 0.89894 | 1.063 | 1.1595 | 1.2738 | 1.4031 | 1.5993 | 1.7655 | 1.9432 | 2.1231 | 2.3148 | 2.5259 | 2.7295 | 2.9344 | 3.1386 | 3.6998 | 3.9826
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.2301 | 0.43505 | 0.57339 | 0.72139 | 0.84076 | 0.96857 | 1.1222 | 1.3153 | 1.4845 | 1.6216 | 1.6969 | 1.7422 | 1.7813 | 1.8181 | 1.8545 | 1.8859 | 2.0196 | 2.1379 | 0.50989 | 0.93778 | 1.229 | 1.5394 | 1.7856 | 2.0492 | 2.3645 | 2.759 | 3.1056 | 3.3871 | 3.5453 | 3.6432 | 3.7289 | 3.8096 | 3.8891 | 3.9585 | 4.2599 | 4.5258
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.21715 | 0.40109 | 0.50766 | 0.62107 | 0.69375 | 0.78081 | 0.87964 | 1.0238 | 1.1496 | 1.2804 | 1.4241 | 1.5623 | 1.6971 | 1.8264 | 1.9133 | 1.9615 | 2.1419 | 2.2932 | 0.48667 | 0.87561 | 1.1054 | 1.3486 | 1.5032 | 1.6868 | 1.8942 | 2.1928 | 2.4541 | 2.7254 | 3.0224 | 3.3084 | 3.5872 | 3.8549 | 4.0374 | 4.1424 | 4.5451 | 4.885
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.20684 | 0.37821 | 0.48066 | 0.5858 | 0.6548 | 0.73829 | 0.8357 | 0.97289 | 1.0933 | 1.2232 | 1.3617 | 1.4977 | 1.6313 | 1.7533 | 1.8319 | 1.8682 | 2.0012 | 2.1255 | 0.45994 | 0.81694 | 1.0342 | 1.2566 | 1.3999 | 1.5728 | 1.7733 | 2.0537 | 2.3 | 2.5649 | 2.8476 | 3.1251 | 3.3978 | 3.6469 | 3.8091 | 3.8866 | 4.1757 | 4.4441
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Counterfactual | 3.0039 | 3.1204 | 3.2509 | 3.4002 | 3.5834 | 3.7894 | 4.023 | 4.4147 | 4.7773 | 5.1851 | 5.6099 | 5.9935 | 6.4238 | 6.8211 | 7.1857 | 7.5449 | 8.4075 | 8.8082 | 7.315 | 7.5584 | 7.8285 | 8.1373 | 8.5156 | 8.9402 | 9.421 | 10.2248 | 10.9773 | 11.8259 | 12.7087 | 13.4986 | 14.3817 | 15.1933 | 15.9358 | 16.6656 | 18.4526 | 19.3165
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Electric Engagement | 3.1395 | 3.4127 | 3.7464 | 4.1596 | 4.6318 | 5.1502 | 5.8181 | 6.6405 | 7.3642 | 7.9468 | 8.2466 | 8.4114 | 8.5629 | 8.6788 | 8.7773 | 8.8659 | 9.3027 | 9.7736 | 7.6081 | 8.1808 | 8.8716 | 9.7289 | 10.7077 | 11.7826 | 13.1648 | 14.8659 | 16.364 | 17.5749 | 18.2166 | 18.5847 | 18.9259 | 19.1842 | 19.4032 | 19.6006 | 20.5893 | 21.6673
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Holistic Transition | 3.0891 | 3.275 | 3.5209 | 3.8035 | 4.1542 | 4.5446 | 4.9985 | 5.581 | 6.0711 | 6.5724 | 7.0883 | 7.5943 | 8.0937 | 8.5542 | 8.8371 | 8.9644 | 9.5817 | 10.2166 | 7.5184 | 7.925 | 8.4531 | 9.0585 | 9.8094 | 10.6418 | 11.6073 | 12.8304 | 13.856 | 14.9002 | 15.9663 | 17.0142 | 18.0501 | 19.0043 | 19.5983 | 19.8823 | 21.2875 | 22.7553
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 3.0454 | 3.1968 | 3.385 | 3.6199 | 3.9232 | 4.2946 | 4.7368 | 5.3264 | 5.8271 | 6.3433 | 6.8662 | 7.3694 | 7.8711 | 8.3066 | 8.5485 | 8.6316 | 10.1901 | 10.6529 | 7.4053 | 7.7249 | 8.1176 | 8.609 | 9.2458 | 10.0273 | 10.9533 | 12.1773 | 13.2175 | 14.2865 | 15.3627 | 16.3972 | 17.4277 | 18.3176 | 18.8157 | 18.9958 | 22.7854 | 23.8283
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.5821 | 1.6031 | 1.6267 | 1.6538 | 1.6827 | 1.7245 | 1.7691 | 1.8641 | 1.9716 | 2.1227 | 2.2575 | 2.3671 | 2.4779 | 2.5882 | 2.9237 | 3.0319 | 3.3838 | 3.5911 | 3.1994 | 3.2435 | 3.2926 | 3.3486 | 3.4084 | 3.4939 | 3.5851 | 3.7878 | 4.0216 | 4.3592 | 4.6515 | 4.886 | 5.1198 | 5.3523 | 6.0342 | 6.2616 | 7.0245 | 7.4898
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.606 | 1.6553 | 1.716 | 2.0703 | 2.1466 | 2.2606 | 2.4589 | 2.6909 | 2.9289 | 3.1332 | 3.2887 | 3.4101 | 3.528 | 3.6239 | 4.1781 | 4.2776 | 5.1405 | 5.409 | 3.2509 | 3.3553 | 3.4813 | 4.3367 | 4.4939 | 4.7292 | 5.1602 | 5.6571 | 6.173 | 6.6175 | 6.9638 | 7.2383 | 7.5062 | 7.7196 | 8.8495 | 9.0714 | 10.9022 | 11.5446
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.5972 | 1.6322 | 1.6714 | 1.7163 | 1.7872 | 1.9373 | 2.096 | 2.3152 | 2.505 | 2.702 | 2.8876 | 3.064 | 3.2325 | 3.377 | 3.8596 | 3.9488 | 4.759 | 4.9158 | 3.2352 | 3.3128 | 3.3971 | 3.493 | 3.6451 | 3.9815 | 4.3339 | 4.8221 | 5.2412 | 5.6781 | 6.0829 | 6.4675 | 6.8339 | 7.1434 | 8.1285 | 8.3269 | 10.0419 | 10.3983
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.5896 | 1.6169 | 1.6505 | 1.9747 | 2.0286 | 2.1167 | 2.2709 | 2.4408 | 2.6086 | 2.7887 | 2.9512 | 3.1058 | 3.2517 | 3.3788 | 3.705 | 3.7768 | 4.3024 | 4.565 | 3.2157 | 3.2738 | 3.344 | 4.1379 | 4.251 | 4.4357 | 4.7781 | 5.1441 | 5.5096 | 5.9054 | 6.2561 | 6.5881 | 6.8994 | 7.168 | 7.8343 | 7.9936 | 9.1305 | 9.7438
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 4.9448 | 5.0684 | 5.224 | 5.363 | 5.5262 | 5.7102 | 5.9817 | 6.3248 | 6.6406 | 6.9932 | 7.3421 | 7.655 | 8.0029 | 8.3608 | 8.7082 | 9.0624 | 9.9566 | 10.3347 | 12.2615 | 12.5199 | 12.842 | 13.1295 | 13.4659 | 13.8445 | 14.4284 | 15.1308 | 15.7847 | 16.5172 | 17.2399 | 17.8807 | 18.5894 | 19.3187 | 20.0259 | 20.7461 | 22.6026 | 23.4203
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 5.0786 | 5.3583 | 5.7248 | 6.0881 | 6.5057 | 7.0422 | 7.6746 | 8.4206 | 9.0551 | 9.5668 | 9.8236 | 9.9502 | 10.0507 | 10.1689 | 10.2939 | 10.4049 | 10.9754 | 11.4476 | 12.5505 | 13.1379 | 13.8993 | 14.6498 | 15.5106 | 16.6435 | 17.9525 | 19.4899 | 20.7963 | 21.8518 | 22.3973 | 22.679 | 22.9034 | 23.1637 | 23.4381 | 23.6826 | 24.9492 | 26.0128
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 5.0292 | 5.2424 | 5.503 | 5.771 | 6.078 | 6.3978 | 6.7767 | 7.2892 | 7.7108 | 8.1658 | 8.6458 | 9.1314 | 9.6107 | 10.0797 | 10.39 | 10.534 | 11.1907 | 11.8287 | 12.4625 | 12.928 | 13.4865 | 14.0598 | 14.7344 | 15.4137 | 16.2174 | 17.2854 | 18.1619 | 19.1053 | 20.0915 | 21.0918 | 22.0808 | 23.0496 | 23.7011 | 24.0194 | 25.48 | 26.9461
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 4.9864 | 5.1609 | 5.4004 | 5.6096 | 5.8572 | 6.158 | 6.5673 | 7.057 | 7.4763 | 7.9316 | 8.4004 | 8.8534 | 9.2947 | 9.7129 | 9.9708 | 10.0607 | 11.6658 | 12.1043 | 12.3523 | 12.7224 | 13.225 | 13.661 | 14.1768 | 14.8031 | 15.6772 | 16.6856 | 17.5512 | 18.4883 | 19.4467 | 20.3715 | 21.2688 | 22.1214 | 22.6536 | 22.8484 | 26.7245 | 27.7004
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Counterfactual | 0.21648 | 0.24828 | 0.28435 | 0.32513 | 0.37101 | 0.42488 | 0.48597 | 0.59561 | 0.69139 | 0.79922 | 0.90273 | 1.0034 | 1.1108 | 1.2177 | 1.3228 | 1.4305 | 1.743 | 1.9047 | 0.48719 | 0.55385 | 0.62862 | 0.71312 | 0.80787 | 0.91886 | 1.0444 | 1.274 | 1.4786 | 1.7108 | 1.9305 | 2.1404 | 2.3616 | 2.5816 | 2.7981 | 3.0198 | 3.6877 | 4.0535
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Electric Engagement | 0.25501 | 0.33101 | 0.42358 | 0.5277 | 0.64793 | 0.78319 | 0.94748 | 1.1687 | 1.3801 | 1.5608 | 1.667 | 1.7342 | 1.7985 | 1.8473 | 1.8961 | 1.9455 | 2.203 | 2.4386 | 0.57026 | 0.72967 | 0.92123 | 1.1363 | 1.3842 | 1.6626 | 1.9992 | 2.4601 | 2.9053 | 3.2897 | 3.5263 | 3.6828 | 3.8337 | 3.9464 | 4.0588 | 4.1731 | 4.7719 | 5.3319
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Holistic Transition | 0.24051 | 0.29196 | 0.35093 | 0.41474 | 0.48751 | 0.57479 | 0.70169 | 0.89317 | 1.0557 | 1.2371 | 1.4142 | 1.594 | 1.7685 | 1.9215 | 2.0245 | 2.0793 | 2.3489 | 2.522 | 0.54436 | 0.65698 | 0.78342 | 0.91982 | 1.0746 | 1.2586 | 1.5345 | 1.9504 | 2.3019 | 2.6957 | 3.074 | 3.4573 | 3.8285 | 4.1502 | 4.3716 | 4.4969 | 5.1187 | 5.5175
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.22836 | 0.27009 | 0.321 | 0.37791 | 0.44516 | 0.52482 | 0.61825 | 0.76999 | 0.90586 | 1.0669 | 1.226 | 1.3788 | 1.5262 | 1.6547 | 1.734 | 1.7698 | 1.9788 | 2.1912 | 0.51297 | 0.60118 | 0.7074 | 0.82602 | 0.966 | 1.1314 | 1.3239 | 1.6419 | 1.9288 | 2.2731 | 2.6086 | 2.9292 | 3.2369 | 3.5028 | 3.6701 | 3.7513 | 4.2352 | 4.7322
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.54709 | 0.64345 | 0.76042 | 0.91684 | 1.1064 | 1.3143 | 1.5459 | 1.8935 | 2.1795 | 2.4873 | 2.8577 | 3.2315 | 3.6894 | 3.9849 | 4.3079 | 4.6313 | 5.4963 | 5.9278 | 1.2334 | 1.4348 | 1.677 | 2.001 | 2.3937 | 2.8235 | 3.3005 | 4.0127 | 4.6021 | 5.2359 | 6.0016 | 6.77 | 7.7128 | 8.3101 | 8.9685 | 9.6274 | 11.417 | 12.3309
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.65448 | 0.87623 | 1.1656 | 1.5519 | 1.9778 | 2.4405 | 2.9806 | 3.6586 | 4.3006 | 4.8363 | 5.1763 | 5.4122 | 5.6195 | 5.718 | 5.8351 | 5.9444 | 6.474 | 6.9052 | 1.4666 | 1.9322 | 2.5336 | 3.3388 | 4.2243 | 5.1854 | 6.3002 | 7.7008 | 9.0354 | 10.1522 | 10.8777 | 11.392 | 11.8473 | 12.0615 | 12.316 | 12.5569 | 13.7373 | 14.7098
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.61668 | 0.784 | 1.0256 | 1.2946 | 1.5902 | 1.914 | 2.3265 | 2.861 | 3.3289 | 3.8146 | 4.3198 | 4.8019 | 5.249 | 5.6436 | 5.9173 | 6.0594 | 6.6764 | 7.1202 | 1.3994 | 1.7649 | 2.2833 | 2.8598 | 3.4926 | 4.1796 | 5.0576 | 6.1809 | 7.1668 | 8.1857 | 9.2385 | 10.2442 | 11.1728 | 11.9894 | 12.5639 | 12.8748 | 14.2442 | 15.2383
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.58308 | 0.71982 | 0.91954 | 1.1424 | 1.4237 | 1.7622 | 2.1369 | 2.6479 | 3.1031 | 3.5946 | 4.0995 | 4.5892 | 5.0562 | 5.4427 | 5.7071 | 5.8359 | 6.3509 | 6.7337 | 1.3127 | 1.6023 | 2.0216 | 2.4893 | 3.0799 | 3.7904 | 4.5714 | 5.6288 | 6.5749 | 7.5945 | 8.6375 | 9.6487 | 10.6095 | 11.3992 | 11.9457 | 12.22 | 13.3511 | 14.1989
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.27681 | 0.28424 | 0.29167 | 0.30044 | 0.31053 | 0.32652 | 0.34322 | 0.37694 | 0.40913 | 0.44592 | 0.47925 | 0.50965 | 0.54016 | 0.57081 | 0.60061 | 0.63115 | 0.76301 | 0.86914 | 0.59616 | 0.61197 | 0.62743 | 0.64559 | 0.66641 | 0.69909 | 0.73318 | 0.8055 | 0.87639 | 0.95863 | 1.0314 | 1.0962 | 1.16 | 1.2241 | 1.2864 | 1.3502 | 1.6344 | 1.8673
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.28404 | 0.30087 | 0.32111 | 0.34516 | 0.37211 | 0.41083 | 0.45749 | 0.52761 | 0.60143 | 0.6738 | 0.73463 | 0.78265 | 0.82698 | 0.86027 | 0.91334 | 0.94702 | 1.2787 | 1.3864 | 0.61176 | 0.64769 | 0.68961 | 0.73923 | 0.79471 | 0.87372 | 0.96867 | 1.1176 | 1.2764 | 1.4333 | 1.5676 | 1.6749 | 1.7748 | 1.8482 | 1.9611 | 2.0358 | 2.7384 | 2.9967
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.28143 | 0.29382 | 0.30683 | 0.32262 | 0.34002 | 0.3693 | 0.41873 | 0.49161 | 0.55459 | 0.62874 | 0.69766 | 0.76281 | 0.82282 | 0.87078 | 0.9297 | 0.95909 | 1.2658 | 1.3239 | 0.60713 | 0.63495 | 0.66291 | 0.69655 | 0.73339 | 0.79397 | 0.90333 | 1.0661 | 1.205 | 1.3693 | 1.5192 | 1.6609 | 1.7912 | 1.8934 | 2.0173 | 2.0822 | 2.7295 | 2.8607
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.27959 | 0.28924 | 0.30072 | 0.31561 | 0.33236 | 0.35842 | 0.38839 | 0.43988 | 0.49101 | 0.557 | 0.61671 | 0.6724 | 0.72308 | 0.76356 | 0.80546 | 0.82828 | 1.0249 | 1.1336 | 0.60218 | 0.62289 | 0.64678 | 0.67757 | 0.71218 | 0.76544 | 0.82651 | 0.93587 | 1.0457 | 1.1899 | 1.3181 | 1.4369 | 1.5443 | 1.6291 | 1.7166 | 1.7666 | 2.1911 | 2.4444
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.97119 | 1.1499 | 1.3526 | 1.5638 | 1.8021 | 2.0633 | 2.3564 | 2.8488 | 3.2727 | 3.753 | 4.2473 | 4.7233 | 5.2268 | 5.728 | 6.2074 | 6.6936 | 8.1708 | 8.7685 | 2.1329 | 2.5072 | 2.9292 | 3.369 | 3.865 | 4.4043 | 5.0089 | 6.0299 | 6.9194 | 7.9317 | 8.9683 | 9.9577 | 10.9971 | 12.0307 | 13.0182 | 14.0199 | 17.1378 | 18.4488
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.1319 | 1.5122 | 1.9959 | 2.5687 | 3.2071 | 3.8775 | 4.6963 | 5.7005 | 6.5347 | 7.2565 | 7.6581 | 7.9064 | 8.1695 | 8.396 | 8.6256 | 8.8599 | 10.0073 | 10.7169 | 2.4818 | 3.2879 | 4.3047 | 5.5085 | 6.8503 | 8.2487 | 9.9524 | 12.0469 | 13.7858 | 15.3021 | 16.1649 | 16.717 | 17.3068 | 17.8126 | 18.3235 | 18.8452 | 21.4104 | 23.0467
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.0766 | 1.3633 | 1.7707 | 2.1904 | 2.7138 | 3.2414 | 3.8315 | 4.5176 | 5.1464 | 5.8396 | 6.5372 | 7.2202 | 7.8945 | 8.5079 | 8.9321 | 9.1767 | 10.4047 | 11.0069 | 2.3831 | 3.0105 | 3.8902 | 4.7957 | 5.9262 | 7.054 | 8.3158 | 9.7661 | 11.1026 | 12.5786 | 14.0486 | 15.4859 | 16.9027 | 18.1856 | 19.0888 | 19.6331 | 22.3928 | 23.7626
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.02 | 1.2555 | 1.5607 | 1.8708 | 2.251 | 2.7007 | 3.1964 | 3.8731 | 4.4832 | 5.1661 | 5.8383 | 6.4862 | 7.1197 | 7.6988 | 8.0775 | 8.2886 | 9.4121 | 10.0756 | 2.2404 | 2.7444 | 3.3933 | 4.0518 | 4.8593 | 5.8084 | 6.8472 | 8.262 | 9.5438 | 10.9852 | 12.3859 | 13.7322 | 15.0463 | 16.2439 | 17.042 | 17.5066 | 20.0291 | 21.536
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.1597 | 1.1805 | 1.2033 | 1.2307 | 1.2625 | 1.3159 | 1.3715 | 1.4931 | 1.6182 | 1.7632 | 1.8897 | 1.9959 | 2.0979 | 2.2003 | 1.9848 | 2.0877 | 2.5462 | 2.9381 | 2.8741 | 2.9179 | 2.9652 | 3.022 | 3.0881 | 3.1974 | 3.3114 | 3.5784 | 3.8608 | 4.1928 | 4.4752 | 4.7062 | 4.9227 | 5.1405 | 4.5644 | 4.7827 | 5.7966 | 6.6791
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.182 | 1.2304 | 1.2924 | 1.3727 | 1.4588 | 1.2645 | 1.4085 | 1.648 | 1.9099 | 2.1668 | 2.3948 | 2.5786 | 2.7573 | 2.891 | 3.0287 | 3.1688 | 3.9986 | 4.4987 | 2.9221 | 3.0245 | 3.153 | 3.3223 | 3.5023 | 2.9614 | 3.2548 | 3.7737 | 4.3502 | 4.9211 | 5.4372 | 5.8573 | 6.2681 | 6.567 | 6.8731 | 7.1874 | 9.0753 | 10.2794
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.1742 | 1.2086 | 1.2568 | 1.3063 | 1.3581 | 1.1363 | 1.3191 | 1.5972 | 1.8288 | 2.1035 | 2.3486 | 2.7548 | 2.9706 | 3.1397 | 3.2882 | 3.4079 | 4.0335 | 4.2774 | 2.9082 | 2.9844 | 3.0905 | 3.1968 | 3.3063 | 2.7117 | 3.1251 | 3.7613 | 4.285 | 4.9102 | 5.4566 | 6.41 | 6.8894 | 7.2555 | 7.5795 | 7.8461 | 9.2518 | 9.8018
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.1675 | 1.1947 | 1.2298 | 1.2819 | 1.3377 | 1.1043 | 1.1944 | 1.3683 | 1.5448 | 1.7814 | 1.9858 | 2.1733 | 2.3473 | 2.4852 | 2.6015 | 2.6918 | 3.2871 | 3.781 | 2.8908 | 2.9487 | 3.0217 | 3.1327 | 3.2506 | 2.6308 | 2.8149 | 3.1928 | 3.5817 | 4.1137 | 4.5642 | 4.9745 | 5.3514 | 5.6447 | 5.8946 | 6.0959 | 7.4798 | 8.6419
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.35718 | 0.43379 | 0.52797 | 0.6392 | 0.77142 | 0.93259 | 1.1 | 1.3517 | 1.579 | 1.8403 | 2.1355 | 2.4114 | 2.701 | 2.9374 | 3.1559 | 3.3772 | 3.9717 | 4.2904 | 0.81677 | 0.97797 | 1.1737 | 1.4043 | 1.6784 | 2.0121 | 2.358 | 2.8774 | 3.3527 | 3.9005 | 4.5191 | 5.0927 | 5.6908 | 6.1739 | 6.6186 | 7.0685 | 8.3035 | 8.9883
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.43854 | 0.61656 | 0.84207 | 1.1124 | 1.4275 | 1.7943 | 2.2309 | 2.7672 | 3.2834 | 3.7272 | 3.9995 | 4.163 | 4.2824 | 4.372 | 4.464 | 4.5517 | 5.0064 | 5.3354 | 0.99241 | 1.3686 | 1.8378 | 2.4044 | 3.0627 | 3.826 | 4.7319 | 5.8452 | 6.9241 | 7.8544 | 8.4393 | 8.7992 | 9.0645 | 9.2615 | 9.4627 | 9.656 | 10.6622 | 11.4229
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.4083 | 0.53498 | 0.69913 | 0.87886 | 1.1134 | 1.4015 | 1.7487 | 2.1811 | 2.5484 | 2.9306 | 3.3213 | 3.6928 | 4.0209 | 4.3171 | 4.516 | 4.6156 | 5.0947 | 5.4203 | 0.93857 | 1.2179 | 1.5747 | 1.9612 | 2.4643 | 3.0808 | 3.8261 | 4.7444 | 5.522 | 6.3291 | 7.148 | 7.9258 | 8.609 | 9.2225 | 9.6407 | 9.8606 | 10.9264 | 11.6651
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.38232 | 0.4849 | 0.62125 | 0.79101 | 1.0069 | 1.2665 | 1.5547 | 1.9307 | 2.2867 | 2.6714 | 3.0526 | 3.4142 | 3.7358 | 4.0043 | 4.1704 | 4.2386 | 4.5593 | 4.8797 | 0.87137 | 1.0899 | 1.3764 | 1.7368 | 2.1948 | 2.7423 | 3.3467 | 4.1297 | 4.8772 | 5.6833 | 6.4756 | 7.2252 | 7.8866 | 8.4346 | 8.7774 | 8.9253 | 9.6351 | 10.3534
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.15853 | 0.19149 | 0.22757 | 0.27077 | 0.32282 | 0.39018 | 0.46488 | 0.58707 | 0.69216 | 0.80919 | 0.92073 | 1.0255 | 1.1373 | 1.2489 | 1.3578 | 1.4708 | 1.8377 | 2.0827 | 0.35579 | 0.42545 | 0.50039 | 0.59001 | 0.69776 | 0.83655 | 0.99028 | 1.2474 | 1.4733 | 1.7275 | 1.9655 | 2.1851 | 2.4161 | 2.6467 | 2.8716 | 3.1051 | 3.8933 | 4.4389
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.1951 | 0.27325 | 0.36439 | 0.48249 | 0.61878 | 0.76115 | 0.93201 | 1.1654 | 1.396 | 1.5983 | 1.737 | 1.8322 | 1.928 | 2.0046 | 2.0837 | 2.1655 | 2.6142 | 2.9469 | 0.43464 | 0.60048 | 0.78959 | 1.0354 | 1.319 | 1.6119 | 1.9615 | 2.4499 | 2.9382 | 3.3711 | 3.6786 | 3.896 | 4.1155 | 4.2874 | 4.4637 | 4.647 | 5.6526 | 6.4336
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.18128 | 0.23737 | 0.30898 | 0.38932 | 0.46333 | 0.56339 | 0.70786 | 0.92274 | 1.1068 | 1.3135 | 1.5134 | 1.7042 | 1.8901 | 2.0517 | 2.1731 | 2.2567 | 2.6884 | 2.9474 | 0.40995 | 0.53479 | 0.68916 | 0.86177 | 1.0198 | 1.2303 | 1.5459 | 2.0162 | 2.4168 | 2.8685 | 3.2977 | 3.7086 | 4.1079 | 4.4503 | 4.7119 | 4.8989 | 5.8677 | 6.4524
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.16965 | 0.2129 | 0.26356 | 0.3305 | 0.40638 | 0.50332 | 0.60703 | 0.76996 | 0.91884 | 1.0998 | 1.2723 | 1.4342 | 1.5923 | 1.729 | 1.8219 | 1.8758 | 2.2026 | 2.5278 | 0.37995 | 0.47241 | 0.57835 | 0.71869 | 0.87757 | 1.0794 | 1.2932 | 1.6361 | 1.952 | 2.3414 | 2.7068 | 3.0481 | 3.3791 | 3.6628 | 3.8586 | 3.9783 | 4.717 | 5.463
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.20612 | 0.24771 | 0.29502 | 0.34676 | 0.39989 | 0.4589 | 0.52615 | 0.63918 | 0.73974 | 0.85114 | 0.96139 | 1.0655 | 1.1815 | 1.2964 | 1.4085 | 1.5219 | 1.8187 | 1.9727 | 0.46878 | 0.55624 | 0.6544 | 0.76141 | 0.87089 | 0.99222 | 1.1301 | 1.3608 | 1.5681 | 1.798 | 2.0247 | 2.2367 | 2.4722 | 2.7052 | 2.9322 | 3.1618 | 3.7714 | 4.096
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.24743 | 0.34354 | 0.45672 | 0.58376 | 0.72106 | 0.88015 | 1.0929 | 1.333 | 1.5406 | 1.7121 | 1.7994 | 1.844 | 1.8792 | 1.9099 | 1.9414 | 1.9674 | 2.0898 | 2.2166 | 0.55778 | 0.761 | 0.99576 | 1.259 | 1.5419 | 1.8702 | 2.3098 | 2.8017 | 3.2265 | 3.5788 | 3.7625 | 3.8597 | 3.9379 | 4.0062 | 4.0758 | 4.1346 | 4.4167 | 4.7083
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.23175 | 0.3007 | 0.37506 | 0.4649 | 0.56018 | 0.67057 | 0.80032 | 0.96614 | 1.1093 | 1.2652 | 1.4274 | 1.5863 | 1.7398 | 1.8831 | 1.9757 | 2.015 | 2.1793 | 2.3244 | 0.5297 | 0.68151 | 0.84133 | 1.0335 | 1.2362 | 1.4697 | 1.743 | 2.0866 | 2.3835 | 2.7062 | 3.0403 | 3.3679 | 3.6841 | 3.9797 | 4.1735 | 4.2607 | 4.6339 | 4.9656
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.21901 | 0.27615 | 0.34202 | 0.41921 | 0.50539 | 0.61062 | 0.73941 | 0.90952 | 1.0513 | 1.2075 | 1.3686 | 1.5243 | 1.6746 | 1.8094 | 1.8909 | 1.9185 | 2.0266 | 2.139 | 0.49669 | 0.6185 | 0.75606 | 0.91741 | 1.0969 | 1.316 | 1.583 | 1.9314 | 2.2213 | 2.5402 | 2.8682 | 3.1848 | 3.4902 | 3.7642 | 3.9315 | 3.9911 | 4.2315 | 4.4829
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.6134 | 0.70324 | 0.80419 | 0.91572 | 1.0479 | 1.1904 | 1.346 | 1.5934 | 1.8096 | 2.0268 | 2.2407 | 2.4504 | 2.6837 | 2.9195 | 3.1473 | 3.3752 | 3.9648 | 4.2093 | 1.3176 | 1.5056 | 1.7153 | 1.9466 | 2.2201 | 2.5146 | 2.8351 | 3.3428 | 3.7912 | 4.2414 | 4.6825 | 5.1109 | 5.5853 | 6.0642 | 6.5266 | 6.9889 | 8.2119 | 8.7434
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.71054 | 0.91672 | 1.1519 | 1.4366 | 1.7623 | 2.1153 | 2.5041 | 2.9897 | 3.4317 | 3.7841 | 3.9449 | 4.0136 | 4.0723 | 4.1254 | 4.4509 | 4.5009 | 4.8019 | 5.1012 | 1.528 | 1.9629 | 2.451 | 3.0424 | 3.7184 | 4.4507 | 5.2483 | 6.2443 | 7.1542 | 7.8821 | 8.2254 | 8.3821 | 8.5183 | 8.64 | 9.3064 | 9.4217 | 10.1171 | 10.8078
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.67611 | 0.82259 | 1.0033 | 1.1939 | 1.4108 | 1.619 | 1.8678 | 2.2185 | 2.5238 | 2.8428 | 3.1792 | 3.5185 | 3.8488 | 4.1587 | 4.6196 | 4.6928 | 5.0785 | 5.3906 | 1.4666 | 1.7873 | 2.1755 | 2.5839 | 3.0477 | 3.4884 | 4.0144 | 4.7475 | 5.3866 | 6.0524 | 6.7498 | 7.4528 | 8.1367 | 8.7767 | 9.7185 | 9.8843 | 10.7655 | 11.4815
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.64295 | 0.76269 | 0.89653 | 1.0664 | 1.2654 | 1.4779 | 1.7285 | 2.0815 | 2.3674 | 2.6669 | 2.981 | 3.2873 | 3.5841 | 3.8567 | 4.1453 | 4.1913 | 4.4542 | 4.7133 | 1.3822 | 1.6372 | 1.9174 | 2.2742 | 2.6926 | 3.1374 | 3.6588 | 4.3881 | 4.9776 | 5.594 | 6.2364 | 6.8626 | 7.468 | 8.0233 | 8.6104 | 8.7125 | 9.3066 | 9.8931
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.16626 | 0.19466 | 0.22739 | 0.26238 | 0.31432 | 0.38337 | 0.45957 | 0.58203 | 0.69792 | 0.81015 | 0.91507 | 1.0091 | 1.1088 | 1.21 | 1.309 | 1.4113 | 1.7246 | 1.9191 | 0.3749 | 0.43444 | 0.50229 | 0.57474 | 0.6823 | 0.82459 | 0.98162 | 1.239 | 1.487 | 1.7298 | 1.9532 | 2.1499 | 2.3555 | 2.5645 | 2.7687 | 2.9798 | 3.6509 | 4.0843
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.19983 | 0.26724 | 0.3544 | 0.47869 | 0.62251 | 0.77832 | 0.94123 | 1.1577 | 1.3662 | 1.5506 | 1.6747 | 1.7576 | 1.8386 | 1.908 | 1.9815 | 2.0654 | 2.4628 | 2.7228 | 0.44739 | 0.58907 | 0.76995 | 1.0297 | 1.3308 | 1.654 | 1.9876 | 2.4399 | 2.8801 | 3.2734 | 3.5469 | 3.7352 | 3.9197 | 4.0737 | 4.2356 | 4.4199 | 5.3015 | 5.9148
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.18758 | 0.23762 | 0.32436 | 0.41693 | 0.4991 | 0.58842 | 0.71767 | 0.90589 | 1.0649 | 1.2445 | 1.419 | 1.5874 | 1.7517 | 1.8989 | 2.0085 | 2.0876 | 2.45 | 2.6361 | 0.4256 | 0.53529 | 0.72207 | 0.92081 | 1.0966 | 1.2833 | 1.5646 | 1.9753 | 2.32 | 2.7112 | 3.0849 | 3.4454 | 3.796 | 4.1057 | 4.34 | 4.5136 | 5.3203 | 5.7402
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.17672 | 0.21685 | 0.26992 | 0.33811 | 0.41469 | 0.51359 | 0.6236 | 0.7882 | 0.92105 | 1.0803 | 1.2326 | 1.3777 | 1.5184 | 1.6434 | 1.7304 | 1.7848 | 2.0542 | 2.3122 | 0.39766 | 0.48276 | 0.5942 | 0.7376 | 0.89861 | 1.1053 | 1.334 | 1.6813 | 1.9627 | 2.305 | 2.627 | 2.9324 | 3.2261 | 3.4848 | 3.6679 | 3.7869 | 4.3941 | 4.9872
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.98273 | 1.1591 | 1.3665 | 1.5973 | 1.9017 | 2.2437 | 2.6321 | 3.2029 | 3.6804 | 4.1758 | 4.6627 | 5.1593 | 5.7036 | 6.2693 | 6.8114 | 7.3541 | 8.5946 | 8.9963 | 2.1311 | 2.4991 | 2.9286 | 3.406 | 4.0359 | 4.7436 | 5.5463 | 6.7188 | 7.7071 | 8.7322 | 9.736 | 10.7559 | 11.8689 | 13.0335 | 14.144 | 15.2526 | 17.8249 | 18.697
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.1695 | 1.5622 | 2.0452 | 2.6975 | 3.4523 | 4.2634 | 5.2114 | 6.3486 | 7.3366 | 8.1961 | 8.5968 | 8.7946 | 8.9356 | 9.0625 | 9.1865 | 9.303 | 9.8393 | 10.331 | 2.5342 | 3.3561 | 4.3575 | 5.7172 | 7.2927 | 8.9859 | 10.9531 | 13.3039 | 15.346 | 17.152 | 18.0075 | 18.4517 | 18.7725 | 19.0603 | 19.3413 | 19.6071 | 20.8417 | 21.9748
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.0992 | 1.3677 | 1.7696 | 2.2301 | 2.7391 | 3.3055 | 3.9632 | 4.789 | 5.5749 | 6.3325 | 7.0666 | 7.7413 | 8.4011 | 9.0137 | 9.3945 | 9.5499 | 10.2328 | 10.7753 | 2.4092 | 2.9927 | 3.8557 | 4.8426 | 5.9323 | 7.1427 | 8.5422 | 10.274 | 11.948 | 13.5355 | 15.0612 | 16.4586 | 17.8248 | 19.0922 | 19.8947 | 20.2462 | 21.8088 | 23.0607
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.0385 | 1.2666 | 1.545 | 1.921 | 2.3531 | 2.8455 | 3.4068 | 4.1741 | 4.8479 | 5.6093 | 6.3289 | 7.0369 | 7.7302 | 8.3723 | 8.7647 | 8.9237 | 9.4395 | 9.8507 | 2.2523 | 2.7341 | 3.3165 | 4.1072 | 5.017 | 6.0541 | 7.2268 | 8.8152 | 10.2141 | 11.8137 | 13.295 | 14.752 | 16.1776 | 17.4981 | 18.3179 | 18.6692 | 19.8269 | 20.7569
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.8926 | 1.9793 | 2.0748 | 2.1811 | 2.2991 | 2.4331 | 2.6485 | 2.9375 | 3.2159 | 3.5293 | 3.8258 | 4.0875 | 4.3556 | 4.617 | 4.8722 | 5.1354 | 5.7895 | 6.1106 | 4.6588 | 4.8403 | 5.0379 | 5.2576 | 5.5008 | 5.7762 | 6.2445 | 6.8401 | 7.4212 | 8.0775 | 8.6955 | 9.2341 | 9.7812 | 10.3136 | 10.8327 | 11.3688 | 12.7337 | 13.4332
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.992 | 2.1951 | 2.4425 | 2.7128 | 3.0186 | 3.4355 | 3.961 | 4.5752 | 5.0861 | 5.5104 | 5.7301 | 5.8332 | 5.9226 | 5.9993 | 6.0796 | 6.1596 | 6.5812 | 6.9765 | 4.8737 | 5.3005 | 5.8129 | 6.3714 | 7.0013 | 7.8877 | 8.9795 | 10.254 | 11.3123 | 12.1974 | 12.6702 | 12.8984 | 13.0984 | 13.2665 | 13.4426 | 13.6167 | 14.5484 | 15.4395
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.9554 | 2.0987 | 2.2602 | 2.436 | 2.7025 | 3.0079 | 3.3558 | 3.7715 | 4.1195 | 4.4766 | 4.8397 | 5.1913 | 5.5435 | 5.8702 | 6.0884 | 6.195 | 6.8943 | 7.3267 | 4.8088 | 5.1231 | 5.4694 | 5.8454 | 6.4359 | 7.0875 | 7.8276 | 8.699 | 9.4275 | 10.1726 | 10.9187 | 11.6442 | 12.373 | 13.0471 | 13.5051 | 13.7407 | 15.3508 | 16.3237
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.923 | 2.0383 | 2.1813 | 2.3311 | 2.5169 | 2.7666 | 3.1567 | 3.5716 | 3.9189 | 4.2986 | 4.6857 | 5.0317 | 5.372 | 5.6727 | 5.8587 | 5.9267 | 7.1433 | 7.5389 | 4.7251 | 4.9691 | 5.2672 | 5.5793 | 5.9664 | 6.4892 | 7.3303 | 8.1916 | 8.9132 | 9.7032 | 10.5031 | 11.2105 | 11.9047 | 12.5156 | 12.8982 | 13.0432 | 15.9801 | 16.8668
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.31458 | 0.39857 | 0.49351 | 0.59577 | 0.71238 | 0.84165 | 0.98621 | 1.2184 | 1.406 | 1.6147 | 1.8373 | 2.0689 | 2.3307 | 2.607 | 2.8469 | 3.0886 | 3.6853 | 3.9275 | 0.70112 | 0.87624 | 1.0733 | 1.2851 | 1.5255 | 1.7915 | 2.0884 | 2.5615 | 2.9466 | 3.3751 | 3.838 | 4.3187 | 4.8627 | 5.4371 | 5.925 | 6.4155 | 7.649 | 8.1695
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.40757 | 0.6024 | 0.83518 | 1.0906 | 1.3848 | 1.6981 | 2.0921 | 2.5843 | 3.0508 | 3.4174 | 3.5962 | 3.6798 | 3.7587 | 3.827 | 3.8946 | 3.9587 | 4.2805 | 4.5733 | 0.90187 | 1.3111 | 1.7932 | 2.3207 | 2.9267 | 3.5707 | 4.3819 | 5.3938 | 6.3689 | 7.1344 | 7.5197 | 7.7127 | 7.8959 | 8.0502 | 8.2014 | 8.3457 | 9.0746 | 9.7386
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.37236 | 0.51194 | 0.66158 | 0.81457 | 0.99189 | 1.1991 | 1.4539 | 1.8201 | 2.1436 | 2.4784 | 2.8273 | 3.1803 | 3.5125 | 3.8313 | 4.0346 | 4.122 | 4.5309 | 4.8579 | 0.8391 | 1.1441 | 1.4648 | 1.7915 | 2.1674 | 2.6086 | 3.1522 | 3.9246 | 4.6112 | 5.3155 | 6.0435 | 6.7804 | 7.4665 | 8.1252 | 8.5526 | 8.7479 | 9.6692 | 10.4128
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.34293 | 0.45891 | 0.59563 | 0.73184 | 0.8911 | 1.0741 | 1.2955 | 1.6279 | 1.9447 | 2.2784 | 2.6093 | 2.9362 | 3.2559 | 3.5458 | 3.7137 | 3.7703 | 4.0488 | 4.3006 | 0.76267 | 1.0088 | 1.2943 | 1.578 | 1.9084 | 2.2872 | 2.7455 | 3.4311 | 4.0992 | 4.7979 | 5.4811 | 6.1554 | 6.8148 | 7.407 | 7.7538 | 7.878 | 8.496 | 9.056
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.37701 | 0.4527 | 0.55736 | 0.68459 | 0.87929 | 1.0866 | 1.3175 | 1.6333 | 1.9181 | 2.1573 | 2.4086 | 2.6663 | 2.9471 | 3.2211 | 3.487 | 3.7581 | 4.4077 | 4.6283 | 0.86827 | 1.0279 | 1.2514 | 1.5286 | 1.9507 | 2.3961 | 2.8927 | 3.5643 | 4.1782 | 4.6745 | 5.1967 | 5.7303 | 6.3094 | 6.8729 | 7.4193 | 7.9766 | 9.3271 | 9.7982
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.45628 | 0.66989 | 0.96673 | 1.3455 | 1.7942 | 2.2852 | 2.8254 | 3.4456 | 4.0382 | 4.4288 | 4.6462 | 4.7905 | 4.9297 | 5.0639 | 5.1957 | 5.3244 | 5.6247 | 5.8578 | 1.0393 | 1.5046 | 2.1527 | 2.9797 | 3.9627 | 5.0433 | 6.22 | 7.5585 | 8.8444 | 9.6588 | 10.1246 | 10.4436 | 10.7525 | 11.0497 | 11.3414 | 11.627 | 12.3071 | 12.8388
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.42659 | 0.59221 | 0.86953 | 1.1689 | 1.5059 | 1.8846 | 2.3105 | 2.8336 | 3.3013 | 3.659 | 4.0291 | 4.4012 | 4.7674 | 5.1106 | 5.3586 | 5.4673 | 5.8179 | 6.0872 | 0.98639 | 1.3626 | 1.982 | 2.6552 | 3.4166 | 4.2732 | 5.2288 | 6.381 | 7.4178 | 8.1691 | 8.9436 | 9.7224 | 10.4888 | 11.2078 | 11.7355 | 11.9766 | 12.7663 | 13.3801
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.40109 | 0.5374 | 0.73773 | 1.0231 | 1.3585 | 1.7411 | 2.1473 | 2.6464 | 3.099 | 3.4422 | 3.8056 | 4.1601 | 4.5064 | 4.8274 | 5.0461 | 5.1651 | 5.4723 | 5.6784 | 0.92058 | 1.2251 | 1.6746 | 2.3113 | 3.0631 | 3.9235 | 4.8293 | 5.9221 | 6.9201 | 7.6338 | 8.3875 | 9.1231 | 9.8403 | 10.5059 | 10.9664 | 11.2277 | 11.9076 | 12.3666
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Counterfactual | 1.1265 | 1.3071 | 1.5241 | 1.7631 | 2.0809 | 2.4486 | 2.8725 | 3.5051 | 4.0496 | 4.6131 | 5.1659 | 5.7012 | 6.2805 | 6.8462 | 7.3926 | 7.9418 | 9.3719 | 10.0213 | 2.6223 | 2.9999 | 3.4506 | 3.9464 | 4.6046 | 5.3654 | 6.2411 | 7.5488 | 8.6876 | 9.8701 | 11.0212 | 12.1246 | 13.3104 | 14.4662 | 15.5806 | 16.7014 | 19.695 | 21.1206
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.3352 | 1.7755 | 2.3279 | 3.0375 | 3.8685 | 4.6966 | 5.6654 | 6.8511 | 7.8502 | 8.6774 | 9.1165 | 9.3552 | 9.5728 | 9.7692 | 9.9642 | 10.1548 | 11.0892 | 11.8737 | 3.0738 | 4.0024 | 5.155 | 6.6352 | 8.3702 | 10.0898 | 12.0894 | 14.5418 | 16.6092 | 18.3328 | 19.2824 | 19.8257 | 20.3266 | 20.7714 | 21.212 | 21.6457 | 23.7833 | 25.6221
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.2609 | 1.5826 | 2.0462 | 2.5771 | 3.0918 | 3.6396 | 4.2924 | 5.1371 | 5.8627 | 6.6503 | 7.4556 | 8.245 | 9.0164 | 9.7221 | 10.182 | 10.4028 | 11.4299 | 12.1251 | 2.9415 | 3.6457 | 4.6455 | 5.7844 | 6.8865 | 8.0495 | 9.4446 | 11.2317 | 12.7645 | 14.4308 | 16.1175 | 17.7708 | 19.3849 | 20.8543 | 21.8309 | 22.3291 | 24.6717 | 26.2701
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.1869 | 1.44 | 1.7571 | 2.1586 | 2.6364 | 3.1941 | 3.793 | 4.6419 | 5.3475 | 6.1256 | 6.9231 | 7.7004 | 8.435 | 9.1103 | 9.5023 | 9.6675 | 10.4547 | 11.1526 | 2.7541 | 3.2936 | 3.9621 | 4.8073 | 5.8133 | 6.9855 | 8.2321 | 9.996 | 11.4642 | 13.0898 | 14.7427 | 16.3498 | 17.862 | 19.2482 | 20.0637 | 20.4279 | 22.2064 | 23.8123
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.29507 | 0.31747 | 0.59296 | 0.64196 | 0.66048 | 0.68624 | 0.71488 | 0.77104 | 0.81612 | 0.86729 | 0.92055 | 0.97058 | 1.0291 | 1.0843 | 1.1408 | 1.1949 | 1.3853 | 1.5286 | 0.70713 | 0.75717 | 1.3222 | 1.4385 | 1.4768 | 1.5299 | 1.5888 | 1.7055 | 1.8009 | 1.9101 | 2.0218 | 2.1256 | 2.2458 | 2.3594 | 2.4754 | 2.5866 | 2.987 | 3.2925
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.31973 | 0.37749 | 0.74134 | 0.90662 | 0.96086 | 1.0225 | 1.0944 | 1.1879 | 1.2767 | 1.3516 | 1.4041 | 1.443 | 1.4811 | 1.5112 | 1.5412 | 1.5686 | 1.7008 | 1.7589 | 0.76449 | 0.8971 | 1.6744 | 2.0701 | 2.1819 | 2.3089 | 2.4561 | 2.6494 | 2.8343 | 2.9915 | 3.1043 | 3.189 | 3.2727 | 3.3379 | 3.4032 | 3.4623 | 3.7549 | 3.8778
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.31526 | 0.36621 | 0.71961 | 0.86932 | 0.89933 | 0.9479 | 1.0049 | 1.0888 | 1.156 | 1.2335 | 1.3029 | 1.375 | 1.4487 | 1.5124 | 1.5666 | 1.5276 | 1.6929 | 1.806 | 0.75647 | 0.87684 | 1.6344 | 2 | 2.0641 | 2.1662 | 2.2877 | 2.466 | 2.6088 | 2.7734 | 2.9179 | 3.0688 | 3.2241 | 3.3575 | 3.472 | 3.3621 | 3.731 | 3.9833
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.31162 | 0.3568 | 0.7059 | 0.85291 | 0.88666 | 0.93414 | 0.98647 | 1.0697 | 1.1381 | 1.2205 | 1.2983 | 1.3751 | 1.4505 | 1.5184 | 1.5725 | 1.6266 | 1.7811 | 1.9064 | 0.74703 | 0.85286 | 1.5994 | 1.9573 | 2.0271 | 2.1248 | 2.2323 | 2.4051 | 2.5473 | 2.7195 | 2.8809 | 3.0397 | 3.1956 | 3.3351 | 3.4468 | 3.5696 | 3.9092 | 4.1923
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Counterfactual | 0.17532 | 0.21518 | 0.2602 | 0.31115 | 0.36612 | 0.43232 | 0.50054 | 0.61352 | 0.71863 | 0.83782 | 0.96213 | 1.0743 | 1.1975 | 1.3164 | 1.4273 | 1.5383 | 1.8388 | 1.9811 | 0.39224 | 0.47594 | 0.57003 | 0.67625 | 0.79007 | 0.92633 | 1.0662 | 1.2972 | 1.5145 | 1.7615 | 2.0226 | 2.2562 | 2.511 | 2.7549 | 2.9798 | 3.205 | 3.826 | 4.1303
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Electric Engagement | 0.21853 | 0.32018 | 0.42711 | 0.55024 | 0.68931 | 0.85131 | 1.0791 | 1.3475 | 1.607 | 1.7821 | 1.8708 | 1.9151 | 1.9548 | 1.9999 | 2.0413 | 2.0775 | 2.2964 | 2.4533 | 0.48536 | 0.70343 | 0.92479 | 1.1794 | 1.4664 | 1.8001 | 2.2798 | 2.8393 | 3.3861 | 3.7469 | 3.9341 | 4.0314 | 4.1194 | 4.2167 | 4.3066 | 4.3863 | 4.8685 | 5.2249
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Holistic Transition | 0.20231 | 0.27598 | 0.34652 | 0.42336 | 0.52732 | 0.66841 | 0.821 | 1.0142 | 1.1765 | 1.3358 | 1.5074 | 1.6773 | 1.8433 | 2.008 | 2.1117 | 2.1574 | 2.4055 | 2.5726 | 0.45646 | 0.62112 | 0.77223 | 0.93644 | 1.1586 | 1.468 | 1.7986 | 2.2077 | 2.5486 | 2.88 | 3.2349 | 3.586 | 3.9289 | 4.268 | 4.4848 | 4.5857 | 5.1342 | 5.5123
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.18868 | 0.25186 | 0.31025 | 0.37903 | 0.46938 | 0.57512 | 0.71367 | 0.89859 | 1.075 | 1.2285 | 1.3843 | 1.5353 | 1.6829 | 1.8229 | 1.9037 | 1.9362 | 2.1008 | 2.2495 | 0.42116 | 0.55939 | 0.68115 | 0.82469 | 1.0141 | 1.2347 | 1.5296 | 1.9178 | 2.2943 | 2.6125 | 2.9305 | 3.2385 | 3.5392 | 3.824 | 3.9904 | 4.0603 | 4.4216 | 4.7505
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.31042 | 0.37328 | 0.53437 | 0.61746 | 0.73002 | 0.86085 | 1.0112 | 1.2709 | 1.5085 | 1.776 | 2.0973 | 2.3983 | 2.7295 | 3.0336 | 3.2829 | 3.5017 | 4.0524 | 4.309 | 0.71401 | 0.84492 | 1.172 | 1.3434 | 1.5756 | 1.8454 | 2.1551 | 2.6924 | 3.1898 | 3.7525 | 4.4494 | 5.1016 | 5.8172 | 6.4698 | 6.9895 | 7.4363 | 8.5906 | 9.154
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.38838 | 0.63003 | 0.82279 | 1.0669 | 1.3486 | 1.6595 | 2.1045 | 2.6811 | 3.3263 | 3.8275 | 4.0859 | 4.2274 | 4.3596 | 4.488 | 4.5762 | 4.6519 | 5.0082 | 5.3273 | 0.88254 | 1.3792 | 1.7776 | 2.2837 | 2.8681 | 3.5132 | 4.4524 | 5.6806 | 7.107 | 8.2079 | 8.7814 | 9.11 | 9.419 | 9.7145 | 9.9133 | 10.0856 | 10.9035 | 11.6471
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.35933 | 0.55237 | 0.70202 | 0.8748 | 1.076 | 1.3791 | 1.7743 | 2.2833 | 2.7603 | 3.1472 | 3.5094 | 3.8546 | 4.1917 | 4.4806 | 4.6695 | 4.7582 | 5.162 | 5.4568 | 0.83095 | 1.2352 | 1.5561 | 1.9259 | 2.3561 | 3.0198 | 3.9 | 5.0319 | 6.1013 | 6.9402 | 7.7139 | 8.4526 | 9.1737 | 9.7771 | 10.18 | 10.3803 | 11.3024 | 11.9778
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.33363 | 0.50875 | 0.61873 | 0.76108 | 0.93282 | 1.1399 | 1.4366 | 1.8584 | 2.3694 | 2.8564 | 3.228 | 3.5854 | 3.918 | 4.2241 | 4.3915 | 4.4578 | 4.761 | 5.0438 | 0.76463 | 1.1239 | 1.3532 | 1.6513 | 2.0116 | 2.4465 | 3.0799 | 3.9856 | 5.1307 | 6.2136 | 7.0027 | 7.7592 | 8.4607 | 9.105 | 9.4559 | 9.6033 | 10.2913 | 10.9407