## Introduction
Data Dictionary
Column Heading | Description
Associated GSP | Name of the upstream Grid Supply Point (GSP) which supplies the substation. Note that some GSPs which run in parallel are reported as groups.
Substation | Name of the substation for which the generation and demand headroom figures have been calculated.
Supply Level | Identifier for whether the substation is a Primary or a Bulk Supply Point. The definition is supplied in the 'NDP 2026 Introduction & Methodology Report'.
Voltage Level (kV) | Voltage of the lower voltage side of the transformation at the substation.
Scenario | Identifier for one of the four Distribution Future Energy Scenarios (DFES) the headroom figures refer to. Holistic Transition was chosen as the best view scenario for the NDP 2026.
Units | The units used to define the headroom available at each substation under each scenario and all of the years reported on (see below).
2024 | Defines the year snapshot for the headroom calculation, where the year refers to the end of the fiscal year.
2025
2026
2027
2028
2029
2030
2031
2032
2033
2034
2035
2036
2037
2038
2039
2040
2045
2050
South Wales
Network Headroom Report 2026
May 2026
v1.0
How to use this workbook
The 'Demand Headroom' and 'Generation Headroom' sheets contain data as described by the data dictionary below. Cells highlighted in red indicate zero headroom, which is defined as the point at which adding demand or generation at a given substation would cause a thermal overload to occur on an related asset in the network. The impact of some high-certainty medium-term reinforcement schemes on the network has been included from the year 2030. This may be observed as a step change increase in the available headroom from the year 2030.
The 'Fault Level Contribution' sheet contains the total make and break contribution (kA) from the demand and generation expected to connect at each primary substation for each year and scenario under the DFES forecasts. The existing maximum prospective fault levels under normal system running conditions and the make and break switchgear ratings at bussing points can be taken from the LTDS Table 4.
In the context of the NHR, zero headroom does not necessarily mean a prospective customer would not be able to connect. This data should not be used to make connections decisions as it is intended to provide a view of the capacity of the network against the DFES scenarios rather than a view of the contractually available capacity. Prospective customers should follow the regular connections application process to gain an accurate assessment of the headroom available for their connection.
Summary
This Network Headroom Report (NHR) workbook provides a view of the capacity to connect additional demand and generation to NGED's South Wales network, in line with the load growth forecasted across the four Distribution Future Energy Scenarios (DFES) out to 2050. The DFES 2024 publication was used as the basis for this NHR to align with the forecasts used for the Network Development Reports.
The NHR forms one part of the wider Network Development Plan (NDP), and it is recommended to view this report alongside the NDP Introduction & Methodology Report and the Network Development Reports which are presented as an interactive map on the Network Opportunity and Development Map (NODM).

## Demand Headroom
Associated GSP | Substation | Supply Level | Voltage Level (kV) | Scenario | Units | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050
Cardiff East / Aberthaw | Ashgrove | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Ashgrove | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Ashgrove | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Ashgrove | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Barry Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 56.1 | 55.6 | 55.3 | 55 | 54.6 | 54.2 | 45.8 | 45 | 43.8 | 43 | 42.1 | 40.9 | 39.2 | 37.3 | 35.5 | 33.9 | 32.2 | 0 | 0
Cardiff East / Aberthaw | Barry Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 56.1 | 55.3 | 54.7 | 53.6 | 52.5 | 51.5 | 41.9 | 39.4 | 36.6 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Barry Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 56.1 | 55.3 | 54.8 | 54.3 | 53.7 | 53.1 | 44 | 42.1 | 39.7 | 37.8 | 35.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Barry Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 56.1 | 55.3 | 54.7 | 54 | 53.2 | 52.4 | 43.2 | 41.3 | 39.1 | 37 | 34.9 | 32.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Barry Grid Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.4 | 10.2 | 10 | 9.8 | 9.6 | 9.4 | 8.7 | 8.3 | 7.8 | 7.4 | 7 | 6.5 | 5.7 | 4.8 | 4 | 3.2 | 2.4 | 0 | 0
Cardiff East / Aberthaw | Barry Grid Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.4 | 10 | 9.6 | 9 | 8.4 | 7.9 | 6.9 | 5.7 | 4.3 | 3 | 2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Barry Grid Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.4 | 10 | 9.6 | 9.3 | 9 | 8.6 | 7.9 | 7 | 5.9 | 4.9 | 3.9 | 2.7 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Barry Grid Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.4 | 10 | 9.6 | 9.2 | 8.8 | 8.4 | 7.5 | 6.6 | 5.6 | 4.8 | 3.8 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Birchgrove | Primary Substation | 11 | Counterfactual | Headroom (MW) | 25.1 | 24.7 | 24.6 | 24.4 | 24.1 | 23.8 | 4.2 | 3.9 | 3.3 | 2.9 | 2.5 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Birchgrove | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 25.1 | 24.5 | 24 | 23.3 | 22.5 | 21.8 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Birchgrove | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 25.1 | 24.5 | 24.1 | 23.7 | 23.3 | 22.9 | 3.2 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Birchgrove | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 25.1 | 24.5 | 24.1 | 23.6 | 23.1 | 22.7 | 2.9 | 1.9 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Boverton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.2 | 8 | 7.9 | 7.8 | 7.6 | 7.4 | 2.4 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Boverton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.2 | 7.9 | 7.7 | 7.4 | 7 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Boverton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.2 | 7.9 | 7.7 | 7.5 | 7.3 | 7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Boverton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.2 | 7.9 | 7.7 | 7.5 | 7.1 | 6.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Broad St.Barry | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.9 | 4.7 | 4.7 | 4.6 | 4.4 | 4.2 | 4.1 | 3.7 | 3.1 | 2.6 | 2.2 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Broad St.Barry | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.9 | 4.6 | 4.4 | 3.9 | 3.4 | 3 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Broad St.Barry | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.9 | 4.6 | 4.5 | 4.3 | 4 | 3.7 | 3.3 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Broad St.Barry | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.9 | 4.6 | 4.4 | 4.1 | 3.8 | 3.4 | 2.9 | 2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Canton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 6.6 | 4.3 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Canton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Canton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Canton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff Central Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 43.4 | 41.2 | 37.8 | 35.4 | 32.5 | 28.6 | 23.5 | 17.2 | 11.6 | 6.7 | 1.5 | 0 | 0
Cardiff East / Aberthaw | Cardiff Central Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 30.5 | 21.6 | 11.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff Central Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 27.4 | 18.6 | 10.8 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff Central Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 36.1 | 30.1 | 22.9 | 15.3 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff East Grid Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 7.1 | 6.7 | 6.5 | 6.2 | 5.8 | 5.2 | 5.8 | 5.1 | 4.2 | 3.7 | 3 | 2.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff East Grid Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 7.1 | 6.4 | 5.7 | 4.6 | 3.5 | 2.4 | 2.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff East Grid Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 7.1 | 6.4 | 5.8 | 5 | 4.3 | 3.6 | 3.4 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff East Grid Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 7.1 | 6.4 | 5.8 | 5.2 | 4.1 | 3.1 | 3.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff North Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 40.3 | 38.7 | 36.5 | 35.1 | 33.5 | 31.1 | 27.9 | 24.6 | 21.3 | 18.4 | 15.2 | 0 | 0
Cardiff East / Aberthaw | Cardiff North Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 30.2 | 24.3 | 18.2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff North Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 26.7 | 21.8 | 17.4 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff North Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 32.3 | 28.6 | 24.3 | 20 | 15.7 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff South Grid | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 22.2 | 17.6 | 17.5 | 17.4 | 17.2 | 13.2 | 10.1 | 8.9 | 8.1 | 7.7 | 7.5 | 7 | 6.6 | 6.1 | 5.7 | 5.3 | 4.8 | 0 | 0
Cardiff East / Aberthaw | Cardiff South Grid | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 22.2 | 17.4 | 16.9 | 16.5 | 11 | 9.3 | 7.1 | 5.6 | 4.3 | 3.3 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff South Grid | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 22.2 | 17.4 | 16.9 | 11.6 | 9.7 | 8 | 6.1 | 5 | 3.8 | 3.1 | 2.7 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff South Grid | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 22.2 | 17.4 | 17.1 | 16.9 | 11.9 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff West Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 25.5 | 23.2 | 19.9 | 17.7 | 15.2 | 11.9 | 7.4 | 2.6 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff West Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 14.8 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff West Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 18.4 | 13.5 | 7.4 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cardiff West Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 17.4 | 12.3 | 6.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Court Road Barry | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5 | 4.8 | 4.7 | 4.6 | 4.5 | 4.3 | 4.2 | 3.9 | 3.4 | 3 | 2.6 | 2.1 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Court Road Barry | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5 | 4.7 | 4.5 | 4 | 3.5 | 3 | 2.6 | 1.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Court Road Barry | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5 | 4.7 | 4.6 | 4.4 | 4.1 | 3.8 | 3.4 | 2.6 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Court Road Barry | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5 | 4.7 | 4.4 | 4.2 | 3.8 | 3.4 | 3.1 | 2.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cowbridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.2 | 5 | 4.8 | 4.6 | 4.3 | 4.1 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cowbridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.2 | 5 | 4.8 | 4.4 | 4 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cowbridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.2 | 5 | 4.8 | 4.6 | 4.3 | 4.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cowbridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.2 | 5 | 4.7 | 4.4 | 4 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Crwys Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 2.1 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Crwys Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Crwys Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Crwys Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cyncoed | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 4.7 | 4 | 3.6 | 3.1 | 2.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cyncoed | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cyncoed | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cyncoed | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 2.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | East Aberthaw | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 29.6 | 29.5 | 29.6 | 29.7 | 29.8 | 30 | 46.6 | 46 | 45.3 | 44.8 | 44.3 | 43.3 | 42 | 40.6 | 39.3 | 31.3 | 16.9 | 0 | 0
Cardiff East / Aberthaw | East Aberthaw | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 29.6 | 29.5 | 29.7 | 29.8 | 29.9 | 30 | 44.3 | 42.7 | 41 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | East Aberthaw | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 29.6 | 29.5 | 29.6 | 29.8 | 29.9 | 30 | 45.5 | 44.4 | 42.9 | 40.1 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | East Aberthaw | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 29.6 | 29.5 | 29.6 | 29.7 | 29.8 | 30 | 44.7 | 43.5 | 42.1 | 40.3 | 38.2 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | East Aberthaw Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.5 | 4.3 | 4.4 | 4.3 | 4.3 | 4.3 | 4.2 | 4 | 3.8 | 3.7 | 3.6 | 3.3 | 2.9 | 2.5 | 2.1 | 1.5 | 0.8 | 0 | 0
Cardiff East / Aberthaw | East Aberthaw Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.4 | 4.2 | 4.2 | 4 | 3.8 | 3.6 | 3.4 | 3 | 2.5 | 1.9 | 1.6 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | East Aberthaw Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.4 | 4.2 | 4.2 | 4.1 | 4.1 | 4 | 3.8 | 3.5 | 3.1 | 2.4 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | East Aberthaw Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.4 | 4.2 | 4.2 | 4.1 | 4 | 3.9 | 3.6 | 3.3 | 2.9 | 2.2 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Ely | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 3.5 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Ely | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Ely | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Ely | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Fairwater | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 3.4 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Fairwater | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Fairwater | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Fairwater | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Grangetown Grid Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 20.9 | 20.7 | 20.4 | 20.1 | 19.9 | 19.4 | 18.7 | 18.4 | 18 | 17.7 | 17.4 | 16.9 | 16.4 | 15.8 | 15.3 | 14.9 | 14.4 | 0 | 0
Cardiff East / Aberthaw | Grangetown Grid Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 20.9 | 20.5 | 20 | 19.4 | 18.6 | 18 | 16.9 | 15.9 | 14.7 | 13.5 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Grangetown Grid Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 20.9 | 20.5 | 20 | 19.3 | 19 | 18.4 | 17.1 | 16.4 | 15.6 | 15 | 14.1 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Grangetown Grid Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 20.9 | 20.4 | 20 | 19.5 | 18.8 | 18.2 | 17.1 | 16.4 | 15.6 | 14.4 | 13.4 | 12.2 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Heath | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.3 | 0 | 0 | 0 | 0 | 0 | 6 | 5.7 | 5.2 | 4.9 | 4.6 | 4.1 | 3.3 | 2.5 | 1.8 | 1.1 | 0 | 0 | 0
Cardiff East / Aberthaw | Heath | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.3 | 0 | 0 | 0 | 0 | 0 | 4 | 2.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Heath | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.3 | 0 | 0 | 0 | 0 | 0 | 4.6 | 3.7 | 2.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Heath | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.3 | 0 | 0 | 0 | 0 | 0 | 4.7 | 3.9 | 3 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Heath Hospital Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.3 | 0 | 0 | 0 | 0 | 0 | 5.9 | 5.7 | 5.4 | 5.2 | 5 | 4.7 | 4.4 | 4.2 | 3.9 | 3.6 | 3.4 | 0 | 0
Cardiff East / Aberthaw | Heath Hospital Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.3 | 0 | 0 | 0 | 0 | 0 | 4.2 | 3.4 | 2.6 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Heath Hospital Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.3 | 0 | 0 | 0 | 0 | 0 | 3.3 | 2.7 | 2.2 | 1.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Heath Hospital Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.3 | 0 | 0 | 0 | 0 | 0 | 4.3 | 3.9 | 3.4 | 2.9 | 2.5 | 1.9 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Highmead | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 3.1 | 2.5 | 2.2 | 1.9 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Highmead | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Highmead | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Highmead | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Llandough | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Llandough | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Llandough | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Llandough | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Llanishen | Primary Substation | 11 | Counterfactual | Headroom (MW) | 24.9 | 24.6 | 24.4 | 24.2 | 23.9 | 23.7 | 4.2 | 3.8 | 3.2 | 2.9 | 2.4 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Llanishen | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 24.9 | 24.3 | 23.9 | 23.1 | 22.4 | 21.6 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Llanishen | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 24.9 | 24.3 | 23.9 | 23.5 | 23.2 | 22.7 | 3.1 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Llanishen | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 24.9 | 24.3 | 23.9 | 23.5 | 23 | 22.5 | 2.8 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Northcote St. | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 2 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Northcote St. | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Northcote St. | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Northcote St. | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Park Lane SWAE | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 4.2 | 4.1 | 4.1 | 4 | 3.8 | 3.6 | 3.3 | 3 | 2.7 | 2.5 | 1.2 | 0
Cardiff East / Aberthaw | Park Lane SWAE | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 2.4 | 1.7 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Park Lane SWAE | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 2.2 | 2 | 1.7 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Park Lane SWAE | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 2.9 | 2.6 | 2.2 | 1.7 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Penarth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Penarth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Penarth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Penarth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Rover Way Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 25.1 | 25.1 | 25.2 | 25.3 | 25.4 | 24.9 | 23.8 | 23.7 | 23.4 | 23.3 | 23.2 | 22.9 | 22.6 | 22.5 | 22.5 | 22.5 | 22.5 | 0 | 0
Cardiff East / Aberthaw | Rover Way Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 25.1 | 25 | 25.1 | 25.2 | 24.6 | 24.4 | 13.9 | 13.5 | 11.4 | 11.2 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Rover Way Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 25.1 | 25 | 25.2 | 24.8 | 24.7 | 24.5 | 13.8 | 13.6 | 11.6 | 11.5 | 11.2 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Rover Way Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 25.1 | 25 | 25.2 | 25.3 | 24.7 | 24.3 | 23.2 | 23 | 22.7 | 22.2 | 21.8 | 21.4 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Sanatorium | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 1.3 | 0.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Sanatorium | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Sanatorium | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Sanatorium | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Sandon St. | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.2 | 1.1 | 1 | 1.1 | 1.1 | 1 | 10.7 | 10.6 | 10.5 | 10.4 | 10.2 | 10 | 9.9 | 9.7 | 9.6 | 9.4 | 9.3 | 8.6 | 7.8
Cardiff East / Aberthaw | Sandon St. | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 9.4 | 9 | 8.7 | 8.3 | 7.9 | 7.4 | 6.9 | 6.5 | 6.1 | 5.7 | 5.4 | 4.1 | 3.5
Cardiff East / Aberthaw | Sandon St. | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 9.8 | 9.7 | 9.6 | 9.4 | 9.2 | 8.7 | 8.3 | 8 | 7.6 | 7.3 | 7 | 5.3 | 4.2
Cardiff East / Aberthaw | Sandon St. | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.2 | 0.7 | 0.6 | 0.6 | 0 | 0 | 10.1 | 9.9 | 9.6 | 9.3 | 9 | 8.5 | 8.2 | 7.8 | 7.6 | 7.3 | 7.2 | 6.7 | 6
Cardiff East / Aberthaw | Ship Hill Barry | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.7 | 8.6 | 8.5 | 8.5 | 8.4 | 8.3 | 4 | 3.6 | 3 | 2.6 | 2.2 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Ship Hill Barry | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.7 | 8.5 | 8.4 | 8.1 | 7.8 | 7.5 | 2.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Ship Hill Barry | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.7 | 8.5 | 8.5 | 8.4 | 8.2 | 8 | 3.2 | 2.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Ship Hill Barry | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.7 | 8.5 | 8.4 | 8.2 | 8 | 7.8 | 2.9 | 2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | St Mellons | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.7 | 8.5 | 8.1 | 7.9 | 7.7 | 7.1 | 6.1 | 5.1 | 4 | 3.1 | 2.1 | 0 | 0
Cardiff East / Aberthaw | St Mellons | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 7.4 | 6.7 | 5.2 | 3.9 | 2.9 | 1.8 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | St Mellons | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.3 | 7.8 | 7.1 | 6.3 | 5.2 | 3.9 | 2.6 | 1.2 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | St Mellons | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 7.9 | 7.5 | 6.3 | 5.1 | 3.8 | 2.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Sully Grid Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 23.7 | 23.5 | 23.5 | 23.5 | 23.3 | 23.1 | 22.8 | 22.7 | 22.5 | 22.3 | 22.2 | 21.9 | 21.4 | 20.8 | 20.4 | 20 | 19.5 | 0 | 0
Cardiff East / Aberthaw | Sully Grid Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 23.7 | 23.4 | 23.3 | 23.2 | 22.9 | 22.6 | 22.1 | 21.6 | 21.1 | 20.6 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Sully Grid Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 23.7 | 23.4 | 23.4 | 23.3 | 23.1 | 22.9 | 22.4 | 21.8 | 21.1 | 20.6 | 20 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Sully Grid Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 23.7 | 23.4 | 23.3 | 23.2 | 22.8 | 22.4 | 21.9 | 21.4 | 20.9 | 20.1 | 19.3 | 18.5 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Taff Bank | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 13.4 | 13.1 | 12.5 | 11.8 | 11 | 10.1 | 9.2 | 8.1 | 7 | 6.1 | 5.2 | 3.1 | 1.7
Cardiff East / Aberthaw | Taff Bank | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 10.6 | 9.6 | 8.1 | 5.9 | 2.9 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Taff Bank | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.6 | 7.9 | 5.2 | 2.7 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Taff Bank | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 12.5 | 11.6 | 10.6 | 9.3 | 8.1 | 6.9 | 5.7 | 4.5 | 3.9 | 3.4 | 2.9 | 0.8 | 0
Cardiff East / Aberthaw | Trowbridge Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 22 | 21.8 | 21.6 | 21.3 | 21 | 20.4 | 19.9 | 19.5 | 18.7 | 18 | 17.2 | 16.2 | 15 | 13.5 | 12 | 10.7 | 9.5 | 0 | 0
Cardiff East / Aberthaw | Trowbridge Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 22 | 21.6 | 21 | 20.3 | 19.3 | 18.6 | 17.9 | 16.2 | 14.3 | 12.2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Trowbridge Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 22 | 21.5 | 21.1 | 20.2 | 19.8 | 19.3 | 18.2 | 16.7 | 15 | 13.4 | 11.5 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Trowbridge Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 22 | 21.5 | 21.1 | 20.6 | 19.6 | 19 | 18.1 | 16.9 | 15.4 | 13.7 | 12 | 10.2 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Wood Street | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 16.6 | 16.7 | 16.8 | 16.9 | 17.1 | 17 | 16.9 | 16.8 | 16.6 | 16.5 | 16.4 | 15.8 | 15
Cardiff East / Aberthaw | Wood Street | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 15.6 | 15.5 | 15 | 14.7 | 14.5 | 14 | 13.6 | 13.2 | 13 | 12.7 | 12.5 | 11.5 | 11
Cardiff East / Aberthaw | Wood Street | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16.2 | 16.3 | 16.3 | 16.2 | 15.9 | 15.6 | 15.4 | 15.2 | 15 | 14.9 | 13.4 | 12.2
Cardiff East / Aberthaw | Wood Street | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 16.1 | 16.2 | 16.1 | 15.9 | 15.6 | 15.2 | 14.9 | 14.6 | 14.4 | 14.2 | 14.1 | 13.7 | 12.8
Margam (Grange) | Caerau Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.9 | 12.7 | 12.6 | 12.4 | 12.2 | 12 | 10.6 | 9.1 | 7.6 | 6.2 | 4.8 | 3.3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Caerau Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.9 | 12.6 | 12.3 | 11.8 | 10.3 | 8 | 5.1 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Caerau Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.9 | 12.6 | 12.4 | 12.2 | 10.6 | 8.9 | 6.2 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Caerau Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.9 | 12.6 | 12.3 | 11.7 | 10.8 | 8.7 | 5.8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Llynfi | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.8 | 14.7 | 14.5 | 14.4 | 14.1 | 13.9 | 13.6 | 13.3 | 12.9 | 12.6 | 11 | 8.8 | 6.1 | 3.3 | 1.6 | 0 | 0 | 0 | 0
Margam (Grange) | Llynfi | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.8 | 14.6 | 14.3 | 13.9 | 4.4 | 3.9 | 3.5 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Llynfi | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.8 | 14.6 | 14.4 | 5.1 | 4.9 | 4.6 | 4.2 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Llynfi | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.8 | 14.6 | 5.3 | 5 | 4.6 | 4.3 | 3.9 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Ogmore Vale | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.2 | 8.2 | 8.1 | 8 | 7.9 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 6.8 | 6.5 | 6.2 | 3.3 | 1.6 | 0 | 0 | 0 | 0
Margam (Grange) | Ogmore Vale | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.2 | 8.1 | 8 | 7.8 | 7.5 | 7.2 | 5.2 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Ogmore Vale | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.2 | 8.1 | 8 | 8 | 7.8 | 7.7 | 6.3 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Ogmore Vale | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.2 | 8.1 | 8 | 7.8 | 7.6 | 7.3 | 5.8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Brawdy | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.6 | 2.2 | 1.9 | 1.6 | 1.2 | 0.5 | 8.4 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Brawdy | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.6 | 2.2 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Brawdy | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.6 | 2.2 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Brawdy | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.6 | 2.1 | 1.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Broadfield | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.8 | 1.5 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Broadfield | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.8 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Broadfield | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.8 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Broadfield | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.8 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Fishguard | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.5 | 2.1 | 1.9 | 1.5 | 1.1 | 0 | 5.6 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Fishguard | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.5 | 2.1 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Fishguard | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.5 | 2.1 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Fishguard | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.5 | 2.1 | 1.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Golden Hill Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 52 | 51.9 | 51.8 | 51.6 | 51.5 | 50.2 | 44.6 | 42.1 | 32.3 | 23.5 | 14.5 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Golden Hill Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 52 | 51.8 | 51.6 | 51.3 | 18.8 | 0 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Golden Hill Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 52 | 51.8 | 51.7 | 40 | 20.2 | 1.2 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Golden Hill Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 52 | 51.8 | 49.1 | 44.9 | 23.5 | 4 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Golden Hill Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.6 | 9.3 | 9 | 8.7 | 8.4 | 7.5 | 5.6 | 4.6 | 2.9 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Golden Hill Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.6 | 9.2 | 8.8 | 8.1 | 6.7 | 5.3 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Golden Hill Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.6 | 9.2 | 8.8 | 7.8 | 6.9 | 5.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Golden Hill Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.6 | 9.2 | 8.7 | 8.2 | 6.9 | 5.6 | 3.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Haverfordwest Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 31.5 | 29.6 | 27.6 | 25.2 | 22.2 | 16.1 | 10.9 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Haverfordwest Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 31.5 | 29.2 | 26.1 | 21.2 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Haverfordwest Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 31.5 | 29.2 | 26.4 | 19.1 | 3.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Haverfordwest Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 31.5 | 29.1 | 26 | 22.4 | 7.2 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Haverfordwest Power Stn | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.9 | 11.7 | 11.6 | 11.5 | 11.3 | 10.1 | 7.7 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Haverfordwest Power Stn | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.9 | 11.6 | 11.4 | 11 | 3.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Haverfordwest Power Stn | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.9 | 11.7 | 11.4 | 10 | 3.7 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Haverfordwest Power Stn | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.9 | 11.6 | 11.4 | 11.1 | 6.9 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Merlins Bridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 3.8 | 3.5 | 3.1 | 2.7 | 2.3 | 2 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Merlins Bridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 3.8 | 3.3 | 2.7 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Merlins Bridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 3.8 | 3.4 | 3 | 2.5 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Merlins Bridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 3.7 | 3.3 | 2.8 | 2.1 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Milford Haven | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 3.6 | 3.5 | 3.4 | 3.3 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Milford Haven | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 3.6 | 3.4 | 3.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Milford Haven | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 3.6 | 3.4 | 3.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Milford Haven | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 3.6 | 3.4 | 3.2 | 2.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Milford Haven Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 5.9 | 5.7 | 5.3 | 4.9 | 4.4 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Milford Haven Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 5.9 | 5.6 | 5 | 4.2 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Milford Haven Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 5.9 | 5.6 | 5.1 | 3.5 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Milford Haven Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.6 | 5 | 4.4 | 3.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Nevern | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.4 | 2.1 | 1.8 | 1.5 | 1.1 | 0 | 4.4 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Nevern | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.5 | 2 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Nevern | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.5 | 2.1 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Nevern | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.5 | 2 | 1.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Neyland | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.2 | 3.1 | 3 | 2.9 | 2.8 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Neyland | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.2 | 3.1 | 2.9 | 2.7 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Neyland | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.2 | 3.1 | 3 | 2.8 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Neyland | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.2 | 3.1 | 3 | 2.8 | 2.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Penblewin | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.8 | 2.6 | 2.5 | 2.3 | 2.1 | 1.6 | 1.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Penblewin | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.8 | 2.6 | 2.5 | 2.1 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Penblewin | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.8 | 2.7 | 2.5 | 1.9 | 1.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Penblewin | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.8 | 2.6 | 2.4 | 2.2 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Davids | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.5 | 2.1 | 1.9 | 1.5 | 1.2 | 0.5 | 5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Davids | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.5 | 2.1 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Davids | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.5 | 2.1 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Davids | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.5 | 2.1 | 1.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Florence | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.8 | 1.5 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Florence | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.8 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Florence | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.8 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Florence | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.8 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Twynells | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.4 | 5.4 | 5.3 | 5.3 | 5.2 | 3.6 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Twynells | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.4 | 5.4 | 5.3 | 5.2 | 3.1 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Twynells | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.4 | 5.4 | 5.3 | 3.3 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Twynells | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.4 | 5.4 | 5.3 | 5.3 | 3.2 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Steynton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6 | 5.7 | 5.3 | 4.9 | 4.4 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Steynton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6 | 5.6 | 5 | 4.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Steynton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6 | 5.6 | 5.1 | 3.6 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Steynton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6 | 5.6 | 5 | 4.4 | 2.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Tenby | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.7 | 1.5 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Tenby | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.7 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Tenby | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.7 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Tenby | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.7 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Bridgend Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 17.1 | 16.5 | 16.2 | 15.8 | 15.3 | 14.5 | 13.2 | 12.2 | 10.6 | 9.6 | 8.4 | 6.8 | 4.3 | 1.7 | 0 | 0 | 0 | 0 | 0
Pyle | Bridgend Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 17.1 | 16.1 | 15.3 | 13.8 | 12.3 | 10.8 | 8.7 | 5.4 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Bridgend Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 17.1 | 16 | 15.3 | 14.5 | 13.6 | 12.6 | 10.3 | 7.5 | 3.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Bridgend Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 17.1 | 16 | 15.2 | 14.2 | 12.7 | 11.2 | 8.9 | 6.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Bridgend Trading Estate | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.3 | 11.2 | 11.2 | 11.1 | 11 | 10.8 | 10.3 | 10.1 | 9.8 | 9.6 | 9.3 | 8.9 | 8.4 | 7.8 | 7.3 | 6.9 | 6.2 | 0 | 0
Pyle | Bridgend Trading Estate | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.3 | 11.1 | 10.9 | 10.7 | 10.3 | 10 | 9.4 | 8.7 | 7.9 | 7.2 | 6.4 | 5.6 | 4.5 | 3 | 0 | 0 | 0 | 0 | 0
Pyle | Bridgend Trading Estate | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.3 | 11.1 | 11 | 10.8 | 10.6 | 10.4 | 9.5 | 8.8 | 8 | 7.3 | 6.5 | 5.6 | 4 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Bridgend Trading Estate | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 11.1 | 10.9 | 10.7 | 10.3 | 9.9 | 9.2 | 8.6 | 7.9 | 6.8 | 5.9 | 4.9 | 4.2 | 3.1 | 1.2 | 0 | 0 | 0 | 0
Pyle | Litchard | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.3 | 6.1 | 6 | 5.8 | 5.6 | 5.3 | 4.6 | 4.2 | 3.7 | 3.3 | 2.8 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Litchard | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.3 | 5.9 | 5.6 | 5.1 | 4.5 | 4 | 3.1 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Litchard | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.3 | 5.9 | 5.6 | 5.3 | 5 | 4.6 | 3.4 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Litchard | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.3 | 5.9 | 5.6 | 5.2 | 4.6 | 3.9 | 2.8 | 1.9 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Llangewydd | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.7 | 5.6 | 5.4 | 5.2 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Llangewydd | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.6 | 5.3 | 4.7 | 4.2 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Llangewydd | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.5 | 5.2 | 5 | 4.6 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Llangewydd | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.6 | 5.3 | 4.9 | 4.5 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Nottage | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.2 | 7.9 | 7.7 | 7.4 | 6.9 | 6.5 | 7.9 | 7.6 | 7.1 | 6.8 | 6.5 | 6 | 5.4 | 4.7 | 4 | 3.3 | 2.7 | 0 | 0
Pyle | Nottage | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.2 | 7.6 | 7.1 | 6.2 | 5.1 | 4.2 | 6.5 | 5.5 | 4.5 | 3.5 | 2.6 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Nottage | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.2 | 7.6 | 7.1 | 6.6 | 6 | 5.4 | 7.3 | 6.6 | 5.7 | 4.9 | 4.1 | 3.1 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Nottage | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.2 | 7.6 | 7.1 | 6.5 | 5.8 | 5 | 7 | 6.3 | 5.5 | 4.7 | 4 | 3 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0
Pyle | Pyle 132/33 | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 50 | 49.6 | 49.4 | 49.2 | 48.8 | 48.3 | 38 | 37.4 | 36.5 | 35.9 | 35.2 | 34.2 | 32.8 | 31.2 | 29.7 | 28.4 | 26.9 | 17.8 | 7.4
Pyle | Pyle 132/33 | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 50 | 49.4 | 48.8 | 47.8 | 46.8 | 45.9 | 35.2 | 33 | 30.9 | 28.7 | 26.8 | 24.9 | 22.2 | 20.2 | 18.3 | 16.5 | 14.2 | 0 | 0
Pyle | Pyle 132/33 | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 50 | 49.3 | 48.8 | 48.4 | 47.8 | 47.1 | 36.5 | 34.9 | 33 | 31.3 | 29.4 | 27.1 | 24.2 | 20.4 | 16.1 | 10.6 | 7.2 | 0 | 0
Pyle | Pyle 132/33 | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 50 | 49.3 | 48.9 | 48.3 | 47.4 | 46.6 | 35.8 | 34.4 | 32.6 | 30.7 | 28.8 | 26.8 | 24.8 | 22.5 | 20 | 17 | 13.9 | 4.3 | 1.5
Pyle | Pyle Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.7 | 9.5 | 9.4 | 9.3 | 9.1 | 8.9 | 8.4 | 8.1 | 7.6 | 7.3 | 7 | 6.4 | 5.7 | 4.9 | 4.1 | 3.5 | 2.7 | 0 | 0
Pyle | Pyle Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.7 | 9.3 | 9 | 8.5 | 8 | 7.6 | 6.9 | 5.8 | 4.8 | 3.7 | 2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Pyle Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.7 | 9.3 | 9 | 8.8 | 8.5 | 8.2 | 7.3 | 6.5 | 5.6 | 4.7 | 3.8 | 2.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Pyle Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.7 | 9.3 | 9.1 | 8.8 | 8.3 | 7.9 | 7.1 | 6.4 | 5.5 | 4.3 | 3.3 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Schwyll | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.1 | 3 | 3 | 3 | 3 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Schwyll | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.1 | 3 | 2.9 | 2.8 | 2.7 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Schwyll | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.1 | 3 | 2.9 | 2.9 | 2.9 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Schwyll | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.1 | 3 | 2.9 | 2.9 | 2.8 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Waterton Industrial Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 24.9 | 23 | 23 | 23 | 23 | 22.8 | 22.1 | 21.8 | 21.5 | 21.3 | 21 | 20.6 | 20 | 19.3 | 18.8 | 18.3 | 17.6 | 0 | 0
Pyle | Waterton Industrial Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 24.9 | 23 | 22.9 | 22.7 | 22.5 | 22.3 | 21.6 | 20.9 | 20.4 | 19.8 | 19.2 | 16.1 | 11 | 5.6 | 0 | 0 | 0 | 0 | 0
Pyle | Waterton Industrial Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 24.9 | 23 | 22.9 | 22.9 | 22.8 | 22.6 | 21.4 | 20.8 | 20 | 19.4 | 18.5 | 17.1 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Waterton Industrial Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 24.9 | 23 | 22.9 | 22.8 | 22.3 | 21.8 | 20.8 | 20.3 | 19.6 | 18.2 | 17.1 | 14.8 | 11 | 5.6 | 0 | 0 | 0 | 0 | 0
Rassau | Abergavenny | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 38.6 | 37 | 36.3 | 35.4 | 34.2 | 32.1 | 62.4 | 59.3 | 54.7 | 51.6 | 48 | 42.6 | 35.3 | 26.7 | 19.1 | 12.5 | 4.3 | 0 | 0
Rassau | Abergavenny | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 38.6 | 36.6 | 35 | 31.9 | 28.2 | 25 | 52.2 | 43.3 | 32.9 | 22.7 | 13.6 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abergavenny | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 38.6 | 36.6 | 35.4 | 34 | 32.5 | 30.7 | 57 | 49.7 | 40.1 | 32.3 | 21.9 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abergavenny | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 38.6 | 36.5 | 34.9 | 33 | 28.9 | 24.9 | 51.2 | 44.4 | 34.7 | 21.1 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abergavenny Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 16.6 | 16.3 | 16 | 15.8 | 15.5 | 15.2 | 15 | 14.5 | 13.7 | 13.1 | 12.5 | 11.7 | 10.6 | 9.3 | 8.1 | 7 | 4.4 | 0 | 0
Rassau | Abergavenny Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 16.6 | 16.2 | 15.6 | 14.8 | 14.1 | 13.3 | 12.8 | 11.1 | 9.3 | 7.6 | 6.2 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abergavenny Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 16.6 | 16.2 | 15.7 | 15.4 | 15.1 | 14.7 | 14.1 | 12.9 | 11.2 | 9.7 | 8.1 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abergavenny Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 16.6 | 16.1 | 15.6 | 15.1 | 14.5 | 13.9 | 13.2 | 12 | 10.6 | 8.9 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abersychan | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6 | 5.9 | 5.7 | 5.6 | 5.4 | 5.2 | 5.2 | 4.9 | 4.4 | 4.1 | 3.6 | 3.1 | 2.4 | 1.6 | 0.9 | 0 | 0 | 0 | 0
Rassau | Abersychan | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6 | 5.8 | 5.5 | 5 | 4.5 | 4 | 3.8 | 2.8 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abersychan | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6 | 5.8 | 5.6 | 5.4 | 5.2 | 4.9 | 4.8 | 4 | 3.1 | 2.4 | 1.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abersychan | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6 | 5.7 | 5.5 | 5.2 | 4.8 | 4.4 | 4.1 | 3.4 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abertillery | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.3 | 7.1 | 7.1 | 7 | 6.9 | 6.7 | 6.7 | 6.5 | 6.1 | 5.8 | 5.6 | 5.2 | 4.7 | 4.1 | 3.5 | 3.1 | 2.5 | 0 | 0
Rassau | Abertillery | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.3 | 7.1 | 6.9 | 6.5 | 6.2 | 5.8 | 5.6 | 4.9 | 4 | 3.2 | 2.6 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abertillery | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.3 | 7.1 | 7 | 6.9 | 6.7 | 6.6 | 6.5 | 6 | 5.3 | 4.7 | 4.1 | 3.3 | 2.4 | 1.5 | 0.6 | 0 | 0 | 0 | 0
Rassau | Abertillery | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.3 | 7 | 6.8 | 6.6 | 6.4 | 6.1 | 5.9 | 5.3 | 4.6 | 3.9 | 3.1 | 2.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Blaenavon | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.6 | 7.5 | 7.5 | 7.5 | 7.5 | 7.3 | 7.3 | 7.3 | 7.1 | 7 | 6.9 | 6.7 | 6.4 | 6.1 | 5.8 | 5.5 | 5.2 | 3.1 | 0
Rassau | Blaenavon | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.6 | 7.5 | 7.4 | 7.3 | 7 | 6.8 | 6.9 | 6.5 | 6.1 | 5.8 | 5.5 | 5.1 | 4.6 | 4.1 | 3.4 | 2.7 | 0 | 0 | 0
Rassau | Blaenavon | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.6 | 7.5 | 7.4 | 7.3 | 7.2 | 7.2 | 7.1 | 6.8 | 6.4 | 6.1 | 5.7 | 5.3 | 4.7 | 4 | 3.2 | 2.6 | 0 | 0 | 0
Rassau | Blaenavon | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.6 | 7.4 | 7.4 | 7.3 | 7 | 6.9 | 6.8 | 6.6 | 6.2 | 5.7 | 5.2 | 4.7 | 4.3 | 3.7 | 2.6 | 0 | 0 | 0 | 0
Rassau | Brecon | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.5 | 4.3 | 4.2 | 4 | 3.8 | 3.3 | 3.9 | 3.4 | 2.8 | 2.4 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Brecon | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.5 | 4.2 | 4 | 3.5 | 1.8 | 0 | 2.7 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Brecon | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.5 | 4.2 | 4.1 | 3.9 | 3.7 | 3 | 3.3 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Brecon | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.5 | 4.2 | 4 | 3.7 | 1.8 | 0 | 2.4 | 1.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Brynmawr | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.4 | 5.2 | 5.1 | 5 | 4.9 | 4.7 | 4.9 | 4.7 | 4.2 | 3.9 | 3.5 | 3.1 | 2.4 | 1.6 | 0.9 | 0 | 0 | 0 | 0
Rassau | Brynmawr | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.4 | 5.1 | 4.9 | 4.5 | 4.1 | 3.7 | 3.7 | 2.8 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Brynmawr | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.4 | 5.1 | 5 | 4.8 | 4.6 | 4.4 | 4.3 | 3.5 | 2.6 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Brynmawr | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.4 | 5.1 | 4.9 | 4.6 | 4.3 | 3.9 | 3.9 | 3.2 | 2.4 | 1.4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Builth Wells | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.8 | 5.6 | 5.6 | 5.3 | 4.6 | 3.5 | 5 | 4.8 | 4.5 | 4.2 | 4 | 3.6 | 3.1 | 2.5 | 2.1 | 1.7 | 1.2 | 0 | 0
Rassau | Builth Wells | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.8 | 5.6 | 5.3 | 3.7 | 1.9 | 0 | 4.5 | 4 | 3.4 | 2.8 | 2.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Builth Wells | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.8 | 5.6 | 5.5 | 4.7 | 4 | 3.1 | 4.7 | 4.1 | 3.4 | 2.8 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Builth Wells | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.8 | 5.6 | 5.2 | 4.2 | 1.9 | 0 | 4.1 | 3.6 | 3 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Crickhowell | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.5 | 6.7 | 6.2 | 5.7 | 5 | 3.9 | 8.3 | 8.1 | 7.9 | 7.8 | 7.6 | 7.4 | 7.1 | 6.7 | 6.4 | 6.2 | 5.8 | 0 | 0
Rassau | Crickhowell | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.5 | 6.5 | 5.7 | 4.1 | 2.1 | 0 | 7.9 | 7.5 | 7.1 | 6.7 | 6.2 | 5.8 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Crickhowell | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.5 | 6.5 | 5.9 | 5.1 | 4.3 | 3.5 | 8.1 | 7.7 | 7.2 | 6.8 | 6.3 | 5.7 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Crickhowell | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.5 | 6.4 | 5.6 | 4.6 | 2.2 | 0 | 7.8 | 7.5 | 7.1 | 6.4 | 5.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Crumlin | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 47 | 46 | 45.7 | 45.3 | 44.7 | 43.6 | 43.3 | 41.7 | 39.2 | 37.7 | 35.9 | 33.1 | 29.1 | 24.5 | 17.8 | 11.4 | 2.2 | 0 | 0
Rassau | Crumlin | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 47 | 45.4 | 44.3 | 42.1 | 39.5 | 37.1 | 35.8 | 30.5 | 24.9 | 16.1 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Crumlin | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 47 | 45.5 | 44.7 | 43.7 | 42.5 | 41.3 | 40 | 36.2 | 31.3 | 25.9 | 15.8 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Crumlin | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 47 | 45.3 | 44.2 | 42.8 | 40.6 | 38.2 | 36.5 | 32.6 | 27.8 | 20.6 | 11.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Crumlin Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 16.9 | 16.8 | 16.8 | 16.8 | 16.8 | 16.6 | 16.1 | 15.8 | 15.5 | 15.3 | 15.1 | 14.6 | 13.8 | 13 | 12.3 | 11.4 | 2.2 | 0 | 0
Rassau | Crumlin Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 16.9 | 16.6 | 16.5 | 16.2 | 15.7 | 15.2 | 14.7 | 13.9 | 13 | 12.1 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Crumlin Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 16.9 | 16.7 | 16.6 | 16.4 | 16.1 | 15.9 | 15.4 | 14.8 | 14 | 13.2 | 12.2 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Crumlin Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 16.9 | 16.6 | 16.5 | 16.4 | 15.9 | 15.3 | 14.7 | 14 | 13.2 | 12.1 | 11.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Cwmfelinfach | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.3 | 7.1 | 7 | 6.8 | 6.6 | 6.3 | 6.6 | 6.2 | 5.6 | 5.1 | 4.7 | 4 | 3 | 1.9 | 0.8 | 0 | 0 | 0 | 0
Rassau | Cwmfelinfach | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.3 | 6.9 | 6.6 | 5.9 | 5.3 | 4.6 | 4.6 | 3.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Cwmfelinfach | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.3 | 6.9 | 6.6 | 6.4 | 6 | 5.7 | 5.7 | 4.7 | 3.3 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Cwmfelinfach | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.3 | 6.9 | 6.5 | 6.1 | 5.5 | 4.9 | 4.8 | 3.8 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Ebbw Vale Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 60.7 | 59.1 | 58.7 | 58.1 | 57.1 | 55.6 | 55.2 | 52.6 | 48.6 | 45.9 | 42.9 | 38.4 | 31.9 | 24.8 | 18 | 11.6 | 2.2 | 0 | 0
Rassau | Ebbw Vale Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 60.7 | 58.2 | 56.5 | 53.1 | 49.3 | 45.6 | 43.7 | 34.7 | 25.5 | 16.3 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Ebbw Vale Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 60.7 | 58.3 | 57.1 | 55.7 | 53.9 | 51.7 | 49.1 | 42.2 | 34 | 26.2 | 16 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Ebbw Vale Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 60.7 | 58.1 | 56.3 | 54.1 | 50.8 | 47.3 | 45 | 38.4 | 30.3 | 20.8 | 11.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Ebbw Vale Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 27.1 | 27 | 26.9 | 26.8 | 26.6 | 26.5 | 26.3 | 25.9 | 25.3 | 25.1 | 24.8 | 24.4 | 23.9 | 23.3 | 17.9 | 11.5 | 2.2 | 0 | 0
Rassau | Ebbw Vale Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 27.1 | 26.9 | 26.7 | 26.4 | 26 | 25.7 | 25.3 | 24.3 | 23.3 | 16.2 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Ebbw Vale Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 27.1 | 26.9 | 26.8 | 26.7 | 26.5 | 26.1 | 25.7 | 24.8 | 24 | 23.4 | 15.9 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Ebbw Vale Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 27.1 | 26.9 | 26.7 | 26.5 | 26.2 | 25.8 | 25.7 | 24.9 | 24 | 20.7 | 11.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Glasbury | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.1 | 6 | 5.9 | 5.6 | 4.9 | 3.7 | 6.1 | 5.9 | 5.6 | 5.3 | 5.1 | 4.7 | 4.3 | 3.8 | 3.3 | 2.9 | 2.3 | 0 | 0
Rassau | Glasbury | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.1 | 6 | 5.6 | 4 | 2 | 0 | 5.5 | 4.9 | 4.2 | 3.5 | 2.9 | 2.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Glasbury | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.1 | 6 | 5.8 | 5 | 4.2 | 3.3 | 5.7 | 5.1 | 4.4 | 3.9 | 3.2 | 2.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Glasbury | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.1 | 6 | 5.5 | 4.5 | 2 | 0 | 5.4 | 4.9 | 4.2 | 3.2 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Llandrindod Wells | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.5 | 2.3 | 2.1 | 1.9 | 1.7 | 1.2 | 4.3 | 4 | 3.6 | 3.2 | 2.9 | 2.4 | 1.9 | 1.2 | 0.6 | 0 | 0 | 0 | 0
Rassau | Llandrindod Wells | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.5 | 2.2 | 1.9 | 1.4 | 0.7 | 0 | 3.5 | 2.6 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Llandrindod Wells | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.5 | 2.2 | 2 | 1.6 | 1.4 | 1 | 3.8 | 3 | 2.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Llandrindod Wells | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.5 | 2.2 | 1.9 | 1.5 | 0.7 | 0 | 3.2 | 2.6 | 1.8 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Monmouth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.8 | 8.5 | 8.5 | 8.4 | 8.2 | 8 | 8 | 7.6 | 7.1 | 6.7 | 6.3 | 5.3 | 3.8 | 2.1 | 0 | 0 | 0 | 0 | 0
Rassau | Monmouth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.8 | 8.5 | 8.3 | 7.9 | 7.4 | 7 | 6.7 | 5.7 | 3.4 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Monmouth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.8 | 8.5 | 8.3 | 8.2 | 7.9 | 7.6 | 7.2 | 6.6 | 5.5 | 4.5 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Monmouth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.8 | 8.4 | 8.3 | 8 | 7.6 | 7.2 | 6.7 | 6 | 4.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Panteg 132/66 | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 17.6 | 17 | 16.8 | 16.6 | 16.1 | 15.4 | 32.7 | 32.3 | 31.3 | 30.6 | 29.7 | 28.4 | 24.8 | 20.7 | 16.9 | 12.7 | 4.4 | 0 | 0
Rassau | Panteg 132/66 | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 17.6 | 16.8 | 16.2 | 14.9 | 13.4 | 12 | 30.3 | 28.2 | 23.2 | 18.4 | 13.8 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Panteg 132/66 | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 17.6 | 16.8 | 16.4 | 15.8 | 15.2 | 14.4 | 31.8 | 30.1 | 27.6 | 24.3 | 19.7 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Panteg 132/66 | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 17.6 | 16.7 | 16.1 | 15.4 | 13.9 | 12.5 | 30.6 | 28.9 | 24.6 | 18.5 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Pengam Grid | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 8.1 | 7.7 | 7.6 | 7.4 | 7.2 | 6.8 | 6.2 | 5.6 | 4.6 | 3.9 | 3.1 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Pengam Grid | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 8.1 | 7.5 | 7.1 | 6.1 | 5.2 | 4.3 | 3.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Pengam Grid | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 8.1 | 7.5 | 7.2 | 6.8 | 6.4 | 5.9 | 4.9 | 3.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Pengam Grid | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 8.1 | 7.5 | 7 | 6.5 | 5.6 | 4.7 | 3.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Pontllanffraith | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.3 | 6.1 | 6 | 5.8 | 5.7 | 5.4 | 5.7 | 5.3 | 4.8 | 4.5 | 4.2 | 3.7 | 2.9 | 1.8 | 0.8 | 0 | 0 | 0 | 0
Rassau | Pontllanffraith | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.3 | 6 | 5.7 | 5.2 | 4.7 | 4.2 | 4.2 | 3.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Pontllanffraith | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.3 | 6 | 5.7 | 5.5 | 5.2 | 4.9 | 4.9 | 4.1 | 3.1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Pontllanffraith | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.3 | 6 | 5.7 | 5.3 | 4.9 | 4.5 | 4.4 | 3.6 | 2.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Rassau West Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 17.4 | 17.2 | 17.3 | 17.4 | 17.5 | 17.5 | 17.5 | 17.5 | 17.2 | 17 | 16.8 | 16.3 | 15.6 | 14.9 | 14 | 11.5 | 2.2 | 0 | 0
Rassau | Rassau West Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 17.4 | 17.1 | 17.1 | 17 | 16.9 | 16.8 | 16.7 | 15.9 | 15.2 | 14.4 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Rassau West Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 17.4 | 17.1 | 17.1 | 17.2 | 17.2 | 17.2 | 16.8 | 16.2 | 15.5 | 14.5 | 13.4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Rassau West Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 17.4 | 17.1 | 17.1 | 17 | 16.9 | 16.8 | 16.7 | 16.1 | 15.4 | 14.3 | 11.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Rhayader | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.1 | 1.9 | 1.7 | 1.6 | 1.4 | 1 | 3.7 | 3.6 | 3.4 | 3.3 | 3.2 | 3 | 2.8 | 2.5 | 2.3 | 2.1 | 1.8 | 0 | 0
Rassau | Rhayader | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.1 | 1.8 | 1.6 | 1.1 | 0.6 | 0 | 3.4 | 3.2 | 2.8 | 2.5 | 2.1 | 1.7 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0
Rassau | Rhayader | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.1 | 1.8 | 1.6 | 1.3 | 1.1 | 0.8 | 3.4 | 3.1 | 2.7 | 2.4 | 2 | 1.5 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0
Rassau | Rhayader | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.1 | 1.8 | 1.5 | 1.2 | 0.5 | 0 | 3.2 | 2.9 | 2.5 | 1.9 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Tredegar | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 7.1 | 7 | 7 | 6.8 | 6.7 | 6.8 | 6.6 | 6.2 | 6 | 5.7 | 5.3 | 4.8 | 4.3 | 3.9 | 3.4 | 3 | 0 | 0
Rassau | Tredegar | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 7 | 6.9 | 6.6 | 6.3 | 6 | 5.9 | 5.1 | 4.2 | 3.4 | 2.7 | 2.1 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0
Rassau | Tredegar | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 7 | 6.9 | 6.7 | 6.5 | 6.2 | 5.9 | 5.2 | 4.5 | 3.9 | 3.3 | 2.6 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0
Rassau | Tredegar | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 7 | 6.8 | 6.6 | 6.3 | 6 | 5.9 | 5.4 | 4.7 | 4 | 3.4 | 2.7 | 2.1 | 1.3 | 0.7 | 0 | 0 | 0 | 0
Rassau | Usk | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.1 | 10.8 | 10.7 | 10.7 | 10.5 | 10.2 | 10 | 9.5 | 8.7 | 8.1 | 7.5 | 6.2 | 4.3 | 2.1 | 0 | 0 | 0 | 0 | 0
Rassau | Usk | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.1 | 10.7 | 10.5 | 9.9 | 9.4 | 8.8 | 8.1 | 6.5 | 3.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Usk | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.1 | 10.7 | 10.5 | 10.4 | 10.1 | 9.7 | 8.8 | 7.6 | 5.9 | 4.4 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Usk | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.1 | 10.7 | 10.4 | 10.2 | 9.6 | 9 | 8.1 | 6.8 | 4.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberaeron | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 2.7 | 2.7 | 2.6 | 2.4 | 2.2 | 3.4 | 3.1 | 2.6 | 2.2 | 1.8 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberaeron | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 2.7 | 2.6 | 2.2 | 1.9 | 1.5 | 2.4 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberaeron | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 2.7 | 2.7 | 2.5 | 2.4 | 2 | 3 | 2.5 | 1.8 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberaeron | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 2.7 | 2.6 | 2.4 | 2.1 | 1.8 | 2.7 | 2.1 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Abercrave | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.5 | 5.3 | 5.5 | 5.5 | 5.4 | 5.3 | 4.5 | 4.4 | 4.2 | 4 | 3.8 | 3.6 | 3.2 | 2.8 | 2.6 | 0.6 | 0 | 0 | 0
Swansea North | Abercrave | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.5 | 5.3 | 5.5 | 5.3 | 5.1 | 5.1 | 4.1 | 3.7 | 3.4 | 3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Abercrave | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.5 | 5.3 | 5.5 | 5.5 | 5.4 | 5.5 | 4.5 | 4.2 | 4 | 3.9 | 3.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Abercrave | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.5 | 5.3 | 5.5 | 5.5 | 5.3 | 5.2 | 4.2 | 4 | 3.7 | 3.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberdare | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.6 | 3.2 | 2.9 | 2.5 | 2 | 1.8 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberdare | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3.4 | 2.8 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberdare | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.4 | 2.8 | 2.4 | 1.9 | 1.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberdare | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.4 | 2.6 | 1.9 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberpergwm | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.2 | 9.7 | 10.1 | 10 | 9.9 | 9.7 | 8.4 | 8.2 | 7.8 | 7.6 | 7.2 | 6.7 | 6 | 5.3 | 4.9 | 4.6 | 0 | 0 | 0
Swansea North | Aberpergwm | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.2 | 9.7 | 10 | 9.7 | 9.3 | 9.3 | 7.7 | 7 | 6.3 | 5.6 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberpergwm | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.2 | 9.7 | 10.1 | 10 | 9.8 | 9.9 | 8.4 | 8 | 7.4 | 7.2 | 6.7 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberpergwm | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.2 | 9.7 | 10.1 | 10 | 9.6 | 9.5 | 7.8 | 7.4 | 7 | 6.1 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ammanford Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 40.5 | 39.5 | 39.1 | 37.1 | 36.4 | 35.5 | 36.6 | 35.3 | 32.8 | 31 | 29 | 26.5 | 23 | 19 | 15.1 | 11.6 | 7.8 | 0 | 0
Swansea North | Ammanford Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 40.5 | 39.3 | 37.1 | 35.4 | 33.7 | 32 | 32.5 | 28.3 | 23.5 | 18.3 | 13.9 | 9.3 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ammanford Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 40.5 | 39.3 | 37.2 | 36.5 | 35.6 | 34.6 | 34.2 | 30.8 | 25.7 | 21.4 | 16.6 | 11 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ammanford Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 40.5 | 39.3 | 37 | 36 | 34.4 | 32.9 | 33 | 29.7 | 25.2 | 20 | 15 | 9.7 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Bishopston | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.5 | 1.3 | 1.2 | 1.1 | 0.9 | 0.6 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Bishopston | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.5 | 1.2 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Bishopston | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.5 | 1.2 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Bishopston | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.5 | 1.2 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Blaenporth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.1 | 3 | 2.9 | 2.9 | 2.8 | 2.4 | 2.9 | 2.7 | 2.3 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Blaenporth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.1 | 3 | 2.9 | 2.5 | 1.8 | 1.1 | 2.5 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Blaenporth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.1 | 3 | 2.9 | 2.9 | 2.6 | 2.2 | 2.4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Blaenporth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.1 | 3 | 2.9 | 2.7 | 2 | 1.3 | 2.6 | 2.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Bridell | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 3.5 | 3.2 | 2.9 | 2.6 | 2.2 | 3 | 2.8 | 2.5 | 2.2 | 2 | 1.6 | 1.3 | 0.9 | 0.5 | 0 | 0 | 0 | 0
Swansea North | Bridell | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 3.4 | 3 | 2.4 | 1.7 | 1 | 2.6 | 2.1 | 1.6 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Bridell | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 3.4 | 3.1 | 2.7 | 2.4 | 2 | 2.8 | 2.4 | 1.9 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Bridell | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 3.4 | 3 | 2.6 | 1.9 | 1.2 | 2.6 | 2.2 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Briton Ferry Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 43.7 | 36.5 | 34.8 | 34.3 | 33.5 | 32 | 28.7 | 27.2 | 25 | 23.6 | 21.9 | 19.5 | 16.2 | 12.7 | 9.5 | 6.7 | 3.3 | 0 | 0
Swansea North | Briton Ferry Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 43.7 | 34.6 | 32.9 | 30.4 | 27.3 | 24.7 | 20.6 | 15.6 | 8.9 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Briton Ferry Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 43.7 | 34.6 | 33.1 | 31.2 | 29.7 | 28 | 24 | 20.2 | 14.5 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Briton Ferry Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 43.7 | 34.6 | 33.2 | 31.8 | 29.2 | 27 | 22.6 | 19.1 | 14.4 | 9.9 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Britton Ferry Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.7 | 3.3 | 3.1 | 3 | 2.9 | 2.6 | 1.7 | 1.4 | 1 | 0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Britton Ferry Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.7 | 3.2 | 2.8 | 2.6 | 2 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Britton Ferry Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.7 | 3.2 | 2.8 | 2.3 | 2 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Britton Ferry Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.7 | 3.2 | 2.9 | 2.7 | 2.2 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Cardigan | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.5 | 3.2 | 2.9 | 2.6 | 2.2 | 6.8 | 6.6 | 6 | 5.5 | 4.9 | 4.3 | 3.5 | 2.7 | 1.9 | 1.1 | 0 | 0 | 0
Swansea North | Cardigan | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3.5 | 3.1 | 2.4 | 1.7 | 1 | 5.9 | 4.9 | 3.7 | 2.6 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Cardigan | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.5 | 3.1 | 2.8 | 2.4 | 2 | 6.3 | 5.3 | 4.1 | 3.1 | 2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Cardigan | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.4 | 3 | 2.6 | 1.9 | 1.2 | 5.9 | 5.1 | 3.9 | 2.4 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Carmarthen Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 16.5 | 13.5 | 13 | 12.4 | 11.6 | 10.6 | 4 | 3.9 | 3.8 | 3.7 | 3.6 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Carmarthen Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 16.5 | 13.2 | 12.2 | 10.6 | 8.9 | 7.2 | 3.8 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Carmarthen Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 16.5 | 13.2 | 12.3 | 11.4 | 10.5 | 9.4 | 3.9 | 3.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Carmarthen Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 16.5 | 13.2 | 12.1 | 10.9 | 9 | 7.1 | 3.8 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Clase | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.6 | 10.8 | 10.7 | 10.5 | 10.2 | 9.9 | 12.5 | 12.6 | 12.6 | 12.6 | 11.8 | 10.3 | 7.6 | 4.7 | 2.1 | 0 | 0 | 0 | 0
Swansea North | Clase | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.6 | 10.7 | 10.3 | 9.7 | 7 | 3.9 | 12 | 9.2 | 5.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Clase | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.6 | 10.7 | 10.3 | 9.9 | 8.7 | 6.4 | 12.5 | 11.2 | 8.6 | 6.5 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Clase | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.6 | 10.7 | 10.4 | 10 | 9.3 | 7 | 12.6 | 11.7 | 9 | 5.7 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Commercial St Neath | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.7 | 7.4 | 7.3 | 7.1 | 6.8 | 6.5 | 6.1 | 5.6 | 5 | 4.6 | 4.1 | 3.4 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0
Swansea North | Commercial St Neath | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.7 | 7.3 | 6.9 | 6.2 | 5.5 | 4.7 | 3.9 | 2.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Commercial St Neath | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.7 | 7.3 | 6.9 | 6.6 | 6.3 | 5.9 | 5.3 | 4.2 | 2.8 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Commercial St Neath | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.7 | 7.2 | 6.9 | 6.4 | 5.9 | 5.3 | 4.6 | 3.6 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Cross Hands | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.9 | 6.8 | 6.8 | 5.4 | 5.2 | 4.9 | 4.9 | 4.5 | 3.6 | 2.9 | 2.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Cross Hands | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.9 | 6.8 | 5.5 | 5 | 4.5 | 4.1 | 3.9 | 2.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Cross Hands | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.9 | 6.8 | 5.4 | 5.3 | 5.1 | 4.8 | 4.2 | 3.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Cross Hands | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.9 | 6.8 | 5.4 | 5.1 | 4.7 | 4.3 | 4.1 | 3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Cwmffrwd | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.4 | 7.3 | 7.2 | 7.2 | 7.1 | 7 | 7 | 6.9 | 6.7 | 6.5 | 6.3 | 5.9 | 5.5 | 5.1 | 4.7 | 4.3 | 3.8 | 2.2 | 0
Swansea North | Cwmffrwd | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.4 | 7.2 | 7.1 | 7 | 6.8 | 6.6 | 6.6 | 6.1 | 5.7 | 5.1 | 4.4 | 3.8 | 3 | 2.4 | 2 | 1.6 | 1.2 | 0 | 0
Swansea North | Cwmffrwd | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.4 | 7.2 | 7.1 | 7 | 6.9 | 6.8 | 6.6 | 6.2 | 5.5 | 4.9 | 4.3 | 3.6 | 2.8 | 2.1 | 1.4 | 0.6 | 0 | 0 | 0
Swansea North | Cwmffrwd | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.4 | 7.2 | 7.1 | 7 | 6.8 | 6.6 | 6.5 | 6.2 | 5.8 | 5.2 | 4.6 | 3.9 | 3.3 | 2.5 | 0 | 0 | 0 | 0 | 0
Swansea North | Garngoch | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.4 | 0 | 0 | 0 | 0 | 0 | 5.3 | 5.4 | 5.4 | 5.4 | 5.4 | 5.1 | 4.5 | 3.7 | 1.7 | 0 | 0 | 0 | 0
Swansea North | Garngoch | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.4 | 0 | 0 | 0 | 0 | 0 | 5 | 4.7 | 3.9 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Garngoch | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.4 | 0 | 0 | 0 | 0 | 0 | 4.6 | 4.5 | 4.3 | 4.5 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Garngoch | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.4 | 0 | 0 | 0 | 0 | 0 | 5.3 | 5.3 | 4.8 | 4.2 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Gethin Street Swansea | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.3 | 12.2 | 12.2 | 12.1 | 12 | 11.9 | 11.7 | 11.6 | 11.3 | 11 | 10.7 | 10.3 | 9.9 | 9.5 | 9 | 8.6 | 8.2 | 7 | 5.7
Swansea North | Gethin Street Swansea | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.3 | 12.1 | 12 | 11.4 | 11.1 | 10.9 | 10.5 | 9.6 | 8.6 | 7.6 | 6.7 | 5.4 | 4.3 | 3.3 | 2.7 | 2 | 1.3 | 0 | 0
Swansea North | Gethin Street Swansea | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.3 | 12.1 | 12 | 11.9 | 11.7 | 11.6 | 11.1 | 10.4 | 9.6 | 8.9 | 8.3 | 7.2 | 6.2 | 5.4 | 4.7 | 3.9 | 3.2 | 0 | 0
Swansea North | Gethin Street Swansea | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.3 | 12.1 | 12 | 11.7 | 11.5 | 11.3 | 11 | 10.5 | 9.8 | 9 | 8.2 | 7.4 | 6.7 | 6.1 | 5.7 | 5.3 | 5.1 | 4.4 | 3.5
Swansea North | Gwaun Cae Gurwen | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.9 | 1.7 | 1.6 | 1.5 | 1.4 | 1.2 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Gwaun Cae Gurwen | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.9 | 1.7 | 1.5 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Gwaun Cae Gurwen | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.9 | 1.7 | 1.6 | 1.4 | 1.3 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Gwaun Cae Gurwen | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.9 | 1.7 | 1.5 | 1.3 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Hendy | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 6.5 | 6.4 | 6.3 | 6.1 | 6 | 6 | 5.8 | 5.5 | 5.2 | 5 | 4.6 | 4.1 | 3.6 | 2.9 | 2.2 | 1.7 | 0 | 0
Swansea North | Hendy | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 6.4 | 6.2 | 5.9 | 5.5 | 5.2 | 5 | 4.3 | 3.5 | 2.8 | 2.2 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Hendy | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 6.4 | 6.3 | 6.1 | 5.9 | 5.7 | 5.6 | 5.1 | 4.4 | 3.5 | 2.7 | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Hendy | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 6.4 | 6.2 | 6 | 5.7 | 5.5 | 5.4 | 4.8 | 4.2 | 3.4 | 2.7 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Hirwaun Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 53.5 | 40.8 | 38.4 | 37.7 | 36.9 | 35.9 | 34.3 | 32.9 | 31.3 | 30.4 | 29.3 | 27.6 | 25.2 | 22.2 | 19.1 | 9.9 | 0 | 0 | 0
Swansea North | Hirwaun Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 53.5 | 40.6 | 37.7 | 35.6 | 33.4 | 29.8 | 29.7 | 26.6 | 23.2 | 19.9 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Hirwaun Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 53.5 | 40.6 | 37.8 | 36.8 | 36 | 33.2 | 32 | 29.7 | 26.4 | 23.4 | 20.9 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Hirwaun Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 53.5 | 40.5 | 37.3 | 35.7 | 33.6 | 30.2 | 29.6 | 27.1 | 23.4 | 19.7 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Hirwaun Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.4 | 7.3 | 5.5 | 5.3 | 5.2 | 5 | 4.2 | 3.5 | 3.1 | 2.9 | 2.6 | 2.2 | 1.7 | 1.3 | 0.9 | 0.5 | 0 | 0 | 0
Swansea North | Hirwaun Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.4 | 7.3 | 5.4 | 5.1 | 4.9 | 3.2 | 3.2 | 2.5 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Hirwaun Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.4 | 7.3 | 5.3 | 5.1 | 5 | 3.2 | 2.8 | 2.1 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Hirwaun Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.4 | 7.3 | 5.2 | 4.9 | 4.6 | 2.9 | 2.8 | 2.3 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Jersey Marine | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.8 | 9.7 | 9.4 | 9.3 | 9.2 | 9 | 9.5 | 9.3 | 8.9 | 8.7 | 8.5 | 8.1 | 7.5 | 6.9 | 6.3 | 5.8 | 5.1 | 1.5 | 0
Swansea North | Jersey Marine | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.8 | 9.5 | 9.1 | 8.7 | 8.2 | 7.8 | 8.2 | 7.4 | 6.5 | 5.6 | 4.9 | 4.2 | 3.1 | 2.3 | 1.5 | 0.6 | 0 | 0 | 0
Swansea North | Jersey Marine | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.8 | 9.5 | 9.2 | 8.8 | 8.7 | 8.5 | 8.9 | 8.3 | 7.6 | 7 | 6.2 | 5.3 | 4.2 | 3.2 | 2.2 | 1.3 | 0 | 0 | 0
Swansea North | Jersey Marine | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.8 | 9.5 | 9.1 | 8.9 | 8.4 | 8.1 | 8.5 | 8 | 7.3 | 6.6 | 5.8 | 4.9 | 4 | 3.1 | 2.3 | 1.5 | 0.7 | 0 | 0
Swansea North | Kidwelly | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 2.6 | 2.4 | 2.1 | 1.7 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Kidwelly | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 2.4 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Kidwelly | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 2.4 | 2 | 1.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Kidwelly | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 2.4 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lampeter Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 2.9 | 2.6 | 2.5 | 2.2 | 1.9 | 1.5 | 9 | 8.8 | 8.6 | 8.3 | 7.5 | 4.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lampeter Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 2.9 | 2.6 | 2.3 | 1.8 | 1.3 | 0.7 | 8.6 | 8.1 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lampeter Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 2.9 | 2.6 | 2.4 | 2.1 | 1.7 | 1.2 | 8.6 | 8.2 | 4.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lampeter Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 2.9 | 2.6 | 2.3 | 1.8 | 1.2 | 0.5 | 8.4 | 8 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lampeter Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.9 | 2.6 | 2.4 | 2.2 | 1.9 | 1.5 | 3.8 | 3.6 | 3.2 | 3 | 2.7 | 2.3 | 1.9 | 1.5 | 1.1 | 0.7 | 0 | 0 | 0
Swansea North | Lampeter Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.9 | 2.6 | 2.3 | 1.8 | 1.3 | 0.7 | 3.3 | 2.7 | 2.1 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lampeter Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.9 | 2.6 | 2.3 | 2 | 1.7 | 1.2 | 3.4 | 2.9 | 2.2 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lampeter Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.9 | 2.6 | 2.2 | 1.8 | 1.2 | 0.5 | 3.1 | 2.6 | 2.1 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lime Street Gorseinon | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.4 | 0 | 0 | 0 | 0 | 0 | 7 | 6.3 | 5.3 | 4.6 | 3.9 | 3.3 | 2.4 | 1.6 | 0.8 | 0 | 0 | 0 | 0
Swansea North | Lime Street Gorseinon | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.4 | 0 | 0 | 0 | 0 | 0 | 4.6 | 3.1 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lime Street Gorseinon | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.4 | 0 | 0 | 0 | 0 | 0 | 6 | 4.7 | 3.3 | 2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lime Street Gorseinon | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.4 | 0 | 0 | 0 | 0 | 0 | 5.5 | 4.2 | 2.9 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanarth Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 3.1 | 2.8 | 2.7 | 2.6 | 2.5 | 2.3 | 3.4 | 3.1 | 2.6 | 2.2 | 1.8 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanarth Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 3.1 | 2.8 | 2.7 | 2.3 | 1.9 | 1.5 | 2.4 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanarth Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 3.1 | 2.8 | 2.7 | 2.6 | 2.4 | 2.1 | 3 | 2.5 | 1.8 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanarth Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 3.1 | 2.8 | 2.7 | 2.5 | 2.2 | 1.9 | 2.7 | 2.1 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanarth Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.1 | 2.8 | 2.7 | 2.6 | 2.5 | 2.3 | 3.4 | 3.1 | 2.6 | 2.2 | 1.8 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanarth Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.1 | 2.8 | 2.7 | 2.3 | 1.9 | 1.5 | 2.4 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanarth Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.1 | 2.8 | 2.7 | 2.6 | 2.4 | 2.1 | 3 | 2.5 | 1.8 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanarth Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.1 | 2.8 | 2.6 | 2.5 | 2.2 | 1.9 | 2.7 | 2.1 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llandarcy | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13 | 12.8 | 12.6 | 12.3 | 11.9 | 11.3 | 10.4 | 9.9 | 9.2 | 8.8 | 8.3 | 7.6 | 6.8 | 5.9 | 5 | 4.1 | 3.2 | 0 | 0
Swansea North | Llandarcy | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13 | 12.8 | 12.4 | 11.8 | 10.9 | 10.3 | 9.3 | 8.2 | 7.1 | 5.9 | 5 | 4 | 2.7 | 1.6 | 0.5 | 0 | 0 | 0 | 0
Swansea North | Llandarcy | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13 | 12.8 | 12.4 | 11.8 | 11.5 | 11.1 | 10 | 9.1 | 7.9 | 7 | 5.9 | 4.8 | 3.5 | 2.2 | 0.9 | 0 | 0 | 0 | 0
Swansea North | Llandarcy | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13 | 12.8 | 12.4 | 11.7 | 10.8 | 10.2 | 9.1 | 8.3 | 7.1 | 5.9 | 4.7 | 3.6 | 2.4 | 1.1 | 0 | 0 | 0 | 0 | 0
Swansea North | Llandeilo | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 3.6 | 3.6 | 3.6 | 3.5 | 3.2 | 4.8 | 4.6 | 4.4 | 4.3 | 4.1 | 3.9 | 3.6 | 3.2 | 2.9 | 2.6 | 2.1 | 0 | 0
Swansea North | Llandeilo | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 3.6 | 3.5 | 3.1 | 2.6 | 2.2 | 4.3 | 3.9 | 3.4 | 3 | 2.6 | 2 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0
Swansea North | Llandeilo | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 3.6 | 3.6 | 3.4 | 3.2 | 2.9 | 4.4 | 4 | 3.5 | 3.1 | 2.6 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llandeilo | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 3.6 | 3.5 | 3.3 | 2.7 | 2 | 4.3 | 4 | 3.5 | 2.8 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llandovery | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.6 | 4.5 | 4.5 | 4.5 | 4.4 | 4.3 | 4.3 | 4.2 | 4 | 3.9 | 3.8 | 3.6 | 3.4 | 3.1 | 2.9 | 2.8 | 2.5 | 0 | 0
Swansea North | Llandovery | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.6 | 4.5 | 4.4 | 4.3 | 4.2 | 3.8 | 4 | 3.7 | 3.4 | 3 | 2.6 | 2.3 | 1.8 | 1.5 | 1.2 | 0 | 0 | 0 | 0
Swansea North | Llandovery | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.6 | 4.5 | 4.5 | 4.4 | 4.4 | 4.3 | 4 | 3.7 | 3.3 | 3 | 2.6 | 2.2 | 1.8 | 1.4 | 1.1 | 0 | 0 | 0 | 0
Swansea North | Llandovery | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.6 | 4.5 | 4.4 | 4.4 | 4.2 | 3.7 | 3.9 | 3.6 | 3.2 | 2.6 | 2.1 | 1.7 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanelli Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 19.4 | 19.2 | 19 | 18.9 | 18.6 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanelli Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 19.4 | 19 | 18.6 | 17.9 | 17.1 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanelli Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 19.4 | 19 | 18.7 | 18.4 | 18 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanelli Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 19.4 | 19 | 18.6 | 18.1 | 17.5 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanfihangel Ystrad | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.2 | 2.9 | 2.9 | 2.8 | 2.6 | 2.4 | 3.4 | 3.1 | 2.6 | 2.2 | 1.8 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanfihangel Ystrad | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.2 | 3 | 2.8 | 2.4 | 2 | 1.6 | 2.4 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanfihangel Ystrad | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.2 | 3 | 2.9 | 2.7 | 2.6 | 2.2 | 3 | 2.5 | 1.8 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanfihangel Ystrad | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.2 | 2.9 | 2.8 | 2.6 | 2.3 | 2 | 2.7 | 2.1 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanfyrnach | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.2 | 2.9 | 2.8 | 2.7 | 2.6 | 2.3 | 4 | 3.9 | 3.8 | 3.7 | 3.6 | 3.5 | 3.2 | 2.9 | 2.6 | 2.3 | 2 | 0 | 0
Swansea North | Llanfyrnach | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.2 | 2.9 | 2.7 | 2.3 | 1.9 | 1.4 | 3.8 | 3.5 | 3.1 | 2.8 | 2.4 | 2 | 1.6 | 1.2 | 0.9 | 0.6 | 0 | 0 | 0
Swansea North | Llanfyrnach | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.2 | 2.9 | 2.7 | 2.6 | 2.4 | 2.2 | 3.9 | 3.7 | 3.4 | 3.1 | 2.7 | 2.2 | 1.8 | 1.4 | 1 | 0 | 0 | 0 | 0
Swansea North | Llanfyrnach | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.2 | 2.9 | 2.7 | 2.5 | 1.9 | 1.3 | 3.8 | 3.5 | 3.1 | 2.6 | 2.1 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llangadog | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.6 | 3.5 | 3.5 | 3.4 | 3.2 | 4.4 | 4.3 | 4.2 | 4.1 | 4 | 3.9 | 3.7 | 3.5 | 3.3 | 3.2 | 3 | 0 | 0
Swansea North | Llangadog | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.5 | 3.5 | 3 | 2.6 | 2.1 | 4.2 | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 2.9 | 2.6 | 1.5 | 0 | 0 | 0 | 0
Swansea North | Llangadog | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.5 | 3.5 | 3.4 | 3.2 | 2.9 | 4.2 | 4 | 3.8 | 3.6 | 3.4 | 3.1 | 2.9 | 2.5 | 1 | 0 | 0 | 0 | 0
Swansea North | Llangadog | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.5 | 3.5 | 3.2 | 2.6 | 2 | 4.1 | 3.9 | 3.7 | 3.3 | 2.9 | 2.6 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanllwni | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.2 | 2.8 | 2.6 | 2.4 | 2.1 | 1.7 | 2.9 | 2.8 | 2.7 | 2.6 | 2.5 | 2.3 | 2.1 | 1.8 | 1.6 | 1.4 | 1.2 | 0 | 0
Swansea North | Llanllwni | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.2 | 2.8 | 2.5 | 1.9 | 1.4 | 0.8 | 2.7 | 2.5 | 2.2 | 2 | 1.7 | 1.5 | 1.1 | 0.9 | 0.6 | 0 | 0 | 0 | 0
Swansea North | Llanllwni | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.2 | 2.8 | 2.5 | 2.2 | 1.8 | 1.3 | 2.9 | 2.7 | 2.5 | 2.2 | 1.9 | 1.6 | 1.3 | 1 | 0.8 | 0.5 | 0 | 0 | 0
Swansea North | Llanllwni | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.2 | 2.8 | 2.4 | 2 | 1.3 | 0.6 | 2.7 | 2.5 | 2.3 | 2 | 1.7 | 1.4 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanrhidian | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.5 | 1.3 | 1.2 | 1.1 | 0.9 | 0.6 | 1.8 | 1.6 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanrhidian | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.5 | 1.3 | 1.1 | 0.7 | 0 | 0 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanrhidian | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.5 | 1.3 | 1.1 | 0.8 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanrhidian | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.5 | 1.2 | 1.1 | 0.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Maerdy | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.3 | 7.2 | 7.3 | 7.3 | 7.3 | 7.1 | 6.8 | 6.5 | 6.1 | 5.8 | 5.5 | 5 | 4.4 | 3.6 | 2.5 | 1.5 | 0 | 0 | 0
Swansea North | Maerdy | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.3 | 7.2 | 7.2 | 6.8 | 6.4 | 6 | 5.5 | 4.6 | 3.7 | 2.8 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Maerdy | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.3 | 7.2 | 7.2 | 7.2 | 7.1 | 6.9 | 6.5 | 5.9 | 5 | 3.8 | 3.1 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Maerdy | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.3 | 7.2 | 7.2 | 6.9 | 6.5 | 6.2 | 5.7 | 4.9 | 3.7 | 2.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Maesarddafen | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.8 | 4.7 | 4.6 | 4.6 | 4.5 | 4.4 | 4.3 | 4.1 | 3.8 | 3.6 | 3.3 | 2.9 | 2.3 | 1.7 | 1.3 | 0.9 | 0 | 0 | 0
Swansea North | Maesarddafen | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.8 | 4.6 | 4.5 | 4.3 | 4 | 3.7 | 3.5 | 2.9 | 2.3 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Maesarddafen | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.8 | 4.6 | 4.5 | 4.4 | 4.3 | 4.2 | 3.9 | 3.5 | 2.8 | 2.1 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Maesarddafen | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.8 | 4.6 | 4.5 | 4.3 | 4 | 3.7 | 3.5 | 3.1 | 2.5 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Meinciau | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 2.6 | 2.4 | 2.1 | 1.7 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Meinciau | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 2.4 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Meinciau | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 2.4 | 2 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Meinciau | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 2.4 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Morriston Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 15.5 | 15.2 | 15.1 | 14.9 | 14.7 | 14.4 | 13.8 | 13.4 | 12.8 | 12.4 | 11.9 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Morriston Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 15.5 | 15 | 14.6 | 13.9 | 13.3 | 12.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Morriston Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 15.5 | 15 | 14.7 | 14.4 | 14.2 | 13.8 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Morriston Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 15.5 | 15 | 14.6 | 14.2 | 13.6 | 13 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Nantgaredig | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.4 | 3.4 | 3.4 | 3.3 | 3 | 4.3 | 4.2 | 4.1 | 4 | 3.9 | 3.8 | 3.6 | 3.4 | 3.1 | 2.7 | 2.2 | 0 | 0
Swansea North | Nantgaredig | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3.4 | 3.3 | 2.9 | 2.5 | 2 | 4 | 3.9 | 3.7 | 3.3 | 2.7 | 2.1 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0
Swansea North | Nantgaredig | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.4 | 3.3 | 3.2 | 3 | 2.8 | 4.1 | 3.9 | 3.7 | 3.5 | 2.9 | 2.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Nantgaredig | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.3 | 3.3 | 3.1 | 2.5 | 1.9 | 4 | 3.8 | 3.6 | 2.9 | 2.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | New Lodge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 2.6 | 2.4 | 2.1 | 1.7 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | New Lodge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 2.5 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | New Lodge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 2.4 | 2 | 1.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | New Lodge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 2.4 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Newcastle Emlyn South | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.5 | 5.4 | 5.1 | 4.9 | 4.5 | 5.5 | 5.1 | 4.4 | 3.7 | 2.8 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Newcastle Emlyn South | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.5 | 5.2 | 4.6 | 3.7 | 2.8 | 4.5 | 3.4 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Newcastle Emlyn South | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.5 | 5.3 | 5.1 | 4.8 | 4.3 | 4.9 | 3.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Newcastle Emlyn South | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.5 | 5.2 | 4.8 | 4.1 | 3.2 | 4.7 | 3.8 | 2.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pantyffynon | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.7 | 3.6 | 3.4 | 3.1 | 2.9 | 2.8 | 2.3 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pantyffynon | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.6 | 3.3 | 2.7 | 2.1 | 1.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pantyffynon | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.6 | 3.3 | 3.1 | 2.8 | 2.5 | 2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pantyffynon | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.6 | 3.3 | 3 | 2.4 | 1.9 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pendine | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.1 | 2.9 | 2.8 | 2.7 | 2.5 | 2.3 | 4.7 | 4.7 | 4.7 | 4.6 | 4.6 | 4.6 | 4.5 | 4.4 | 4.2 | 4.2 | 4.1 | 3.7 | 3.4
Swansea North | Pendine | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.1 | 2.8 | 2.6 | 2.2 | 1.8 | 1.4 | 4.6 | 4.5 | 4.4 | 4.4 | 4.3 | 4.2 | 4 | 3.9 | 3.8 | 3.7 | 3.7 | 3.4 | 3.2
Swansea North | Pendine | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.1 | 2.8 | 2.7 | 2.5 | 2.4 | 2.2 | 4.7 | 4.6 | 4.5 | 4.4 | 4.3 | 4.2 | 4.1 | 4 | 3.9 | 3.7 | 3.7 | 3.3 | 0
Swansea North | Pendine | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.1 | 2.8 | 2.6 | 2.4 | 1.9 | 1.3 | 4.6 | 4.5 | 4.4 | 4.3 | 4.2 | 4.1 | 3.9 | 3.8 | 3.7 | 3.5 | 3.4 | 3.1 | 0
Swansea North | Pont Ar Annell | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.8 | 5.7 | 5.6 | 5.4 | 5.3 | 5 | 5.6 | 5.5 | 5.4 | 5.3 | 5.3 | 5.2 | 5.1 | 4.9 | 4.8 | 4.7 | 4.4 | 0 | 0
Swansea North | Pont Ar Annell | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.8 | 5.6 | 5.4 | 5 | 4.5 | 4.1 | 5.5 | 5.3 | 5.2 | 5 | 4.9 | 4.8 | 3.9 | 3 | 1.8 | 0.6 | 0 | 0 | 0
Swansea North | Pont Ar Annell | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.8 | 5.6 | 5.4 | 5.3 | 5.1 | 4.9 | 5.5 | 5.3 | 5.2 | 5 | 4.9 | 4.5 | 3.7 | 2.5 | 1.1 | 0 | 0 | 0 | 0
Swansea North | Pont Ar Annell | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.8 | 5.6 | 5.4 | 5.2 | 4.6 | 4 | 5.3 | 5.2 | 5.1 | 4.7 | 4.2 | 3.2 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pontardawe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.1 | 6.7 | 6.6 | 6.3 | 6 | 5.6 | 5 | 4.4 | 3.6 | 3.1 | 2.4 | 1.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pontardawe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.1 | 6.6 | 6.2 | 5.5 | 4.7 | 3.9 | 2.9 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pontardawe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.1 | 6.6 | 6.3 | 6 | 5.5 | 5.1 | 4.2 | 3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pontardawe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.1 | 6.6 | 6.2 | 5.7 | 5 | 4.3 | 3.4 | 2.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pontyates | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 2.6 | 2.4 | 2.1 | 1.7 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pontyates | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 2.4 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pontyates | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 2.4 | 1.9 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pontyates | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 2.4 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ravenhill | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.3 | 6 | 5.7 | 5.4 | 4.9 | 4.4 | 3.4 | 2.7 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ravenhill | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.3 | 5.7 | 4.9 | 3.5 | 2.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ravenhill | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.3 | 5.7 | 5 | 4.1 | 3.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ravenhill | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.3 | 5.8 | 5.2 | 4.6 | 3.8 | 3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Rhos Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 20 | 18.8 | 18.2 | 17.4 | 16.5 | 15.2 | 16.6 | 15.2 | 12.7 | 10.6 | 8.1 | 5.2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Rhos Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 20 | 18.8 | 17.7 | 15.8 | 13.7 | 11.8 | 12.9 | 8.9 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Rhos Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 20 | 18.7 | 17.9 | 16.9 | 15.8 | 14.4 | 14.3 | 10.4 | 5.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Rhos Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 20 | 18.7 | 17.6 | 16.2 | 14.1 | 12 | 12.7 | 9.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Rhos Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 7.1 | 7 | 6.9 | 6.7 | 6.6 | 6.6 | 6.4 | 6 | 5.6 | 5.3 | 4.9 | 4.4 | 3.8 | 3.3 | 2.9 | 2.4 | 0 | 0
Swansea North | Rhos Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 7 | 6.9 | 6.6 | 6.3 | 6 | 6 | 5.4 | 4.7 | 4 | 3.4 | 2.9 | 2.1 | 1.4 | 1 | 0 | 0 | 0 | 0
Swansea North | Rhos Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 7 | 6.9 | 6.8 | 6.6 | 6.4 | 6.3 | 5.7 | 4.9 | 4.3 | 3.7 | 2.9 | 2.2 | 1.5 | 0.8 | 0 | 0 | 0 | 0
Swansea North | Rhos Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 7 | 6.9 | 6.7 | 6.4 | 6.1 | 6 | 5.5 | 4.8 | 4.1 | 3.2 | 2.4 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0
Swansea North | Sketty Park | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.7 | 6.3 | 5.8 | 5.2 | 4.5 | 3.8 | 2.7 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Sketty Park | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.7 | 5.7 | 4.5 | 3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Sketty Park | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.7 | 5.7 | 4.5 | 3.3 | 2.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Sketty Park | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.7 | 5.7 | 4.7 | 3.6 | 2.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | St Clears | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.2 | 3 | 2.9 | 2.8 | 2.6 | 2.4 | 6.9 | 6.7 | 6.5 | 6.4 | 6.2 | 6 | 5.5 | 4.9 | 4.3 | 3.9 | 3.3 | 0 | 0
Swansea North | St Clears | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.2 | 3 | 2.7 | 2.3 | 1.9 | 1.5 | 6.4 | 6 | 5.3 | 4.7 | 4 | 3.4 | 2.5 | 1.8 | 1.2 | 0.6 | 0 | 0 | 0
Swansea North | St Clears | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.2 | 2.9 | 2.8 | 2.6 | 2.5 | 2.2 | 6.6 | 6.3 | 5.8 | 5.2 | 4.4 | 3.5 | 2.7 | 1.8 | 1.1 | 0 | 0 | 0 | 0
Swansea North | St Clears | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.2 | 2.9 | 2.7 | 2.5 | 2 | 1.4 | 6.3 | 6 | 5.3 | 4.4 | 3.4 | 2.5 | 1.6 | 0.5 | 0 | 0 | 0 | 0 | 0
Swansea North | Strand Swansea | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.8 | 5.6 | 5.3 | 5.1 | 4.8 | 4.3 | 4 | 3.5 | 3.2 | 2.8 | 2.3 | 1.8 | 1.2 | 0.6 | 0 | 0 | 0 | 0
Swansea North | Strand Swansea | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.5 | 5.1 | 4.3 | 3.7 | 3.1 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Strand Swansea | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.6 | 5.3 | 4.9 | 4.5 | 4.2 | 3.6 | 2.8 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Strand Swansea | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.5 | 5.2 | 4.7 | 4.2 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Swansea North Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 13 | 13.3 | 13.4 | 13.5 | 13.7 | 13.8 | 14.5 | 13.7 | 12.5 | 11.6 | 10.6 | 9.3 | 7.6 | 5.7 | 4 | 2.4 | 0.6 | 0 | 0
Swansea North | Swansea North Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 13 | 13.4 | 13.5 | 13.4 | 9.4 | 5.2 | 10.8 | 8.3 | 5.5 | 2.9 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Swansea North Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 13 | 13.4 | 13.5 | 13.7 | 11.6 | 8.6 | 12.1 | 10.1 | 8 | 6.2 | 4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Swansea North Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 13 | 13.4 | 13.5 | 13.6 | 12.4 | 9.4 | 12.3 | 10.5 | 8.2 | 6 | 3.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Swansea North Local | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.3 | 11.3 | 11.3 | 11.4 | 11.4 | 11.4 | 11.4 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
Swansea North | Swansea North Local | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.3 | 11.3 | 11.3 | 11.4 | 11.4 | 11.4 | 11.4 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
Swansea North | Swansea North Local | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.3 | 11.3 | 11.3 | 11.4 | 11.4 | 11.4 | 11.4 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
Swansea North | Swansea North Local | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 11.3 | 11.3 | 11.4 | 11.4 | 11.4 | 11.4 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
Swansea North | Swansea Trading Estate | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.7 | 8.4 | 8.4 | 8.3 | 8.1 | 7.8 | 7.2 | 6.8 | 6.1 | 5.6 | 5 | 4.2 | 3.2 | 2.1 | 1.2 | 0.5 | 0 | 0 | 0
Swansea North | Swansea Trading Estate | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.7 | 8.3 | 8.2 | 7.7 | 7.2 | 6.7 | 5.7 | 4.4 | 3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Swansea Trading Estate | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.7 | 8.3 | 8.2 | 8 | 7.6 | 6.9 | 5.7 | 4.8 | 3.7 | 3.1 | 2.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Swansea Trading Estate | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.7 | 8.3 | 8.1 | 7.9 | 7.2 | 6.5 | 5.5 | 4.5 | 3.4 | 2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Swansea Waterfront | Primary Substation | 11 | Counterfactual | Headroom (MW) | 27.4 | 27.4 | 27.3 | 27.3 | 27.3 | 27.2 | 26.5 | 26.5 | 26.3 | 26.1 | 25.9 | 25.7 | 25.4 | 25.1 | 24.8 | 24.6 | 24.4 | 23.1 | 22.4
Swansea North | Swansea Waterfront | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 27.4 | 27.3 | 26.9 | 26.8 | 26.6 | 26.4 | 16.1 | 15.7 | 15.1 | 10.9 | 10.4 | 9.8 | 9 | 8.4 | 7.9 | 7.5 | 7 | 5 | 4.1
Swansea North | Swansea Waterfront | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 27.4 | 27.3 | 27 | 26.9 | 26.9 | 26.8 | 16.4 | 16.1 | 15.8 | 11.9 | 11.5 | 11 | 10.3 | 9.8 | 9.2 | 8.7 | 8.2 | 6 | 4.9
Swansea North | Swansea Waterfront | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 27.4 | 27.3 | 27.2 | 27.1 | 27 | 26.9 | 26.1 | 25.8 | 25.4 | 25 | 24.6 | 24.1 | 23.8 | 23.3 | 23 | 22.8 | 22.5 | 21.8 | 21.4
Swansea North | Swansea West Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 47.7 | 46.5 | 45.3 | 43.9 | 42.2 | 40.3 | 37.9 | 35.5 | 32 | 29.5 | 26.9 | 23.3 | 18.9 | 14.1 | 9.6 | 5.6 | 1.3 | 0 | 0
Swansea North | Swansea West Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 47.7 | 45.2 | 42.3 | 37.8 | 33.5 | 29.2 | 24.1 | 16 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Swansea West Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 47.7 | 45.2 | 42.6 | 39.6 | 36.6 | 33 | 28.7 | 22.9 | 16.4 | 10.7 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Swansea West Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 47.7 | 45.2 | 43 | 40.3 | 37.1 | 33.8 | 29.6 | 24.5 | 18.3 | 12.1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Tir John Power Station | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 34.4 | 33 | 32 | 30.7 | 29.3 | 27.2 | 20.9 | 18.5 | 14.5 | 11.6 | 8.5 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Tir John Power Station | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 34.4 | 31.9 | 29.4 | 25.3 | 21.1 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Tir John Power Station | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 34.4 | 31.9 | 29.8 | 27.5 | 25.6 | 23.6 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Tir John Power Station | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 34.4 | 31.8 | 29.6 | 26.9 | 23.1 | 19.8 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Tir John Primary | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 10.9 | 10.9 | 11 | 11 | 11 | 11 | 11.1 | 11.1 | 11.1 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2
Swansea North | Tir John Primary | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 10.9 | 10.9 | 11 | 11 | 11 | 11 | 11.1 | 11.1 | 11.1 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2
Swansea North | Tir John Primary | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 10.9 | 10.9 | 11 | 11 | 11 | 11 | 11.1 | 11.1 | 11.1 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.1
Swansea North | Tir John Primary | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 10.9 | 10.9 | 11 | 11 | 11 | 11 | 11.1 | 11.1 | 11.1 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.1
Swansea North | Travellers Rest Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.6 | 3.4 | 3.2 | 3 | 2.6 | 2.1 | 1.7 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Travellers Rest Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3.5 | 3.2 | 2.7 | 2.1 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Travellers Rest Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.5 | 3.3 | 3 | 2.8 | 2.5 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Travellers Rest Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.5 | 3.2 | 2.9 | 2.3 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Tregaron | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.8 | 2.5 | 2.4 | 2.1 | 1.9 | 1.5 | 5.9 | 5.6 | 5.3 | 5 | 4.7 | 4.3 | 3.9 | 3.4 | 3 | 2.4 | 1.9 | 0 | 0
Swansea North | Tregaron | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.8 | 2.5 | 2.2 | 1.7 | 1.2 | 0.7 | 5.3 | 4.7 | 4.1 | 3.5 | 3 | 2.4 | 1.8 | 1.1 | 0.6 | 0 | 0 | 0 | 0
Swansea North | Tregaron | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.8 | 2.5 | 2.2 | 2 | 1.6 | 1.1 | 5.5 | 5 | 4.5 | 4.1 | 3.7 | 3.1 | 2.5 | 1.9 | 1.4 | 0.8 | 0 | 0 | 0
Swansea North | Tregaron | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.8 | 2.5 | 2.2 | 1.7 | 1.2 | 0.5 | 5.2 | 4.7 | 4.1 | 3.5 | 2.9 | 2.2 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0
Swansea North | Trevaughan | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.7 | 5.2 | 4.9 | 4.5 | 4.1 | 3.6 | 6.9 | 6.5 | 5.8 | 5.3 | 4.7 | 4 | 3 | 2 | 0.9 | 0 | 0 | 0 | 0
Swansea North | Trevaughan | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.7 | 5.1 | 4.5 | 3.8 | 3 | 2.2 | 5.6 | 4.3 | 3 | 1.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Trevaughan | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.7 | 5.1 | 4.5 | 4 | 3.4 | 2.8 | 5.9 | 4.8 | 3.3 | 2.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Trevaughan | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.7 | 5.1 | 4.5 | 3.7 | 2.9 | 2.1 | 5.4 | 4.3 | 3.1 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Trostre Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 24 | 23.6 | 23.5 | 23.2 | 22.7 | 22.1 | 20.6 | 18.2 | 14.2 | 11.4 | 8.4 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Trostre Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 24 | 23.5 | 22.9 | 21.7 | 20.5 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Trostre Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 24 | 23.4 | 23 | 22.4 | 21.7 | 20.8 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Trostre Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 24 | 23.4 | 22.9 | 21.9 | 20.7 | 19.4 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Tumble | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.2 | 4 | 3.8 | 3.6 | 3.4 | 3.1 | 2.9 | 2.6 | 2.2 | 1.9 | 1.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Tumble | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.2 | 3.9 | 3.7 | 3.3 | 2.9 | 2.4 | 2.1 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Tumble | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.2 | 3.9 | 3.8 | 3.6 | 3.3 | 3.1 | 2.8 | 2.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Tumble | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.2 | 3.9 | 3.7 | 3.4 | 3.1 | 2.7 | 2.4 | 2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Uplands Swansea | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.7 | 9.2 | 8.6 | 7.8 | 7 | 6.1 | 5.2 | 4.2 | 2.7 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Uplands Swansea | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.7 | 8.6 | 7.3 | 5.1 | 3.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Uplands Swansea | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.7 | 8.6 | 7.3 | 5.9 | 4.7 | 3.4 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Uplands Swansea | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.7 | 8.6 | 7.5 | 6.1 | 4.8 | 3.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Upper Bank | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 2.9 | 2.8 | 2.6 | 2.4 | 2.2 | 1.7 | 1.5 | 1 | 0.8 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Upper Bank | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 2.7 | 2.3 | 1.7 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Upper Bank | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 2.7 | 2.3 | 1.9 | 1.6 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Upper Bank | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 2.7 | 2.4 | 2.1 | 1.7 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Victoria Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Victoria Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Victoria Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Victoria Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Wern | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.4 | 13.3 | 13.2 | 13.2 | 13.1 | 13 | 12.9 | 12.7 | 12.6 | 12.5 | 12.4 | 12.2 | 11.8 | 11.5 | 11.2 | 10.9 | 10.6 | 8.6 | 7.2
Swansea North | Wern | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.4 | 13.2 | 13.1 | 12.8 | 12.6 | 12.3 | 12.2 | 11.8 | 11.3 | 10.8 | 10.4 | 9.9 | 9.3 | 8.8 | 8.4 | 7.9 | 7.5 | 5.5 | 4.2
Swansea North | Wern | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.4 | 13.2 | 13.1 | 12.9 | 12.9 | 12.7 | 12.6 | 12.2 | 11.8 | 11.4 | 11 | 10.5 | 9.9 | 9.3 | 8.7 | 8.1 | 7.5 | 5.2 | 3.8
Swansea North | Wern | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.4 | 13.2 | 13.1 | 12.9 | 12.7 | 12.5 | 12.3 | 12 | 11.6 | 11.2 | 10.8 | 10.3 | 9.8 | 9.3 | 8.8 | 8.3 | 7.8 | 6.3 | 5.7
Swansea North | West Cross | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.2 | 2.9 | 2.5 | 2.1 | 1.7 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | West Cross | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.2 | 2.6 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | West Cross | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.2 | 2.6 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | West Cross | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.2 | 2.5 | 1.9 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Westfa | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.1 | 2.7 | 2.5 | 2.2 | 1.8 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Westfa | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.1 | 2.5 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Westfa | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.1 | 2.5 | 2 | 1.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Westfa | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.1 | 2.5 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Whitland | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.2 | 2.9 | 2.8 | 2.7 | 2.6 | 2.3 | 4.3 | 4.2 | 4 | 3.9 | 3.7 | 3.5 | 3.3 | 3 | 2.8 | 2.7 | 2.4 | 1.2 | 0
Swansea North | Whitland | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.2 | 2.9 | 2.7 | 2.3 | 1.9 | 1.4 | 4.1 | 3.8 | 3.5 | 3.2 | 2.9 | 2.6 | 2.2 | 1.9 | 1.6 | 1.4 | 1.1 | 0 | 0
Swansea North | Whitland | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.2 | 2.9 | 2.7 | 2.6 | 2.4 | 2.2 | 4 | 3.7 | 3.3 | 3.1 | 2.7 | 2.4 | 2 | 1.7 | 1.4 | 1 | 0.7 | 0 | 0
Swansea North | Whitland | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.2 | 2.9 | 2.7 | 2.5 | 1.9 | 1.3 | 3.9 | 3.6 | 3.3 | 2.8 | 2.4 | 2 | 1.8 | 1.3 | 1.1 | 0.7 | 0 | 0 | 0
Swansea North | Ynys Street | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10.7 | 10.1 | 9.7 | 9.3 | 8.7 | 7.9 | 7.2 | 6.5 | 5.9 | 5.3 | 1.4 | 0
Swansea North | Ynys Street | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.3 | 8.2 | 6.9 | 5.7 | 4.7 | 3.8 | 2.6 | 1.7 | 0.9 | 0 | 0 | 0 | 0
Swansea North | Ynys Street | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 10.2 | 9.5 | 8.5 | 7.8 | 7 | 6 | 5 | 3.9 | 2.8 | 1.7 | 0.8 | 0 | 0
Swansea North | Ynys Street | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 9 | 7.9 | 6.9 | 5.9 | 4.9 | 4 | 2.9 | 2.1 | 1.1 | 0 | 0 | 0
Swansea North | Ynysfeio | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 6.4 | 6.4 | 6.2 | 6.1 | 5.9 | 5.7 | 5.5 | 5.1 | 4.8 | 4.5 | 4.1 | 3.5 | 2.8 | 1.8 | 1 | 0 | 0 | 0
Swansea North | Ynysfeio | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 6.4 | 6.2 | 5.7 | 5.3 | 4.9 | 4.5 | 3.7 | 2.9 | 2.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ynysfeio | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 6.4 | 6.2 | 6 | 5.9 | 5.7 | 5.5 | 4.9 | 4 | 2.9 | 2.3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ynysfeio | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 6.3 | 6.1 | 5.8 | 5.4 | 5.1 | 4.7 | 4 | 2.9 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ystradgynlais Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 25 | 20.3 | 19.8 | 19.3 | 18.6 | 17.7 | 17.2 | 16 | 14.3 | 13.2 | 11.8 | 10.1 | 7.7 | 5 | 2.6 | 0.6 | 0 | 0 | 0
Swansea North | Ystradgynlais Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 25 | 20.1 | 19.1 | 17.5 | 15.7 | 14 | 13.1 | 10 | 6.6 | 3.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ystradgynlais Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 25 | 20.1 | 19.3 | 18.5 | 17.7 | 16.6 | 15.9 | 13.5 | 10.4 | 8 | 5.2 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ystradgynlais Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 25 | 20 | 19 | 18 | 16.4 | 14.8 | 13.8 | 11.5 | 8.7 | 5.2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Abertysswg | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.5 | 1.1 | 0.9 | 0.7 | 0 | 0 | 2.8 | 2.6 | 2.3 | 2.1 | 1.8 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Abertysswg | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Abertysswg | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 2.4 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Abertysswg | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 1.9 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Caerphilly | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5 | 4.8 | 4.7 | 4.4 | 4.2 | 4 | 3.7 | 3.4 | 2.9 | 2.6 | 2.2 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Caerphilly | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5 | 4.7 | 4.4 | 3.7 | 3.2 | 2.7 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Caerphilly | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5 | 4.7 | 4.5 | 4.1 | 3.8 | 3.5 | 2.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Caerphilly | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5 | 4.7 | 4.4 | 3.9 | 3.4 | 2.9 | 2.3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Creigiau | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.2 | 3.7 | 3.7 | 2.6 | 2.6 | 2.2 | 1.7 | 1.3 | 0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Creigiau | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.2 | 3.7 | 2.5 | 2.3 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Creigiau | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.2 | 3.7 | 2.5 | 1.9 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Creigiau | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.2 | 3.7 | 2.5 | 2.4 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Dowlais Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 24 | 21 | 19 | 18.1 | 16.8 | 14.9 | 12.4 | 10 | 6.1 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Dowlais Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 24 | 20.1 | 16.9 | 13 | 8.8 | 4.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Dowlais Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 24 | 20.3 | 17.6 | 15.6 | 13.6 | 11.5 | 7.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Dowlais Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 24 | 19.9 | 16.6 | 14 | 10.4 | 6.8 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Energlyn 33kv | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.6 | 5.6 | 5.6 | 5.6 | 5.7 | 5.7 | 5.5 | 5.1 | 4.8 | 4.5 | 4.1 | 0 | 0
Upper Boat 132 & 33 | Energlyn 33kv | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.6 | 5.5 | 5.1 | 4.7 | 4.3 | 3.9 | 3.3 | 2.8 | 2.1 | 1.2 | 0 | 0 | 0
Upper Boat 132 & 33 | Energlyn 33kv | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.6 | 5.6 | 5.4 | 5 | 4.4 | 3.7 | 2.8 | 2 | 1.2 | 0.7 | 0 | 0 | 0
Upper Boat 132 & 33 | Energlyn 33kv | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.6 | 5.6 | 5.4 | 5 | 4.5 | 4.1 | 3.5 | 2.8 | 2.2 | 1.5 | 0.9 | 0 | 0
Upper Boat 132 & 33 | Energlyn Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 24.9 | 24.7 | 24.5 | 24.3 | 24 | 23.7 | 23.4 | 23 | 22.4 | 22 | 21.5 | 20.9 | 20 | 19.1 | 18.2 | 17.4 | 16.3 | 9.7 | 6.2
Upper Boat 132 & 33 | Energlyn Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 24.9 | 24.5 | 24.1 | 23.5 | 22.9 | 22.3 | 21.6 | 20.3 | 18.9 | 17.6 | 16.4 | 15.3 | 13.7 | 12.3 | 10.7 | 9 | 7.5 | 0 | 0
Upper Boat 132 & 33 | Energlyn Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 24.9 | 24.5 | 24.2 | 23.8 | 23.5 | 23 | 22.5 | 21.5 | 20.3 | 19.2 | 17.7 | 16 | 14.2 | 12.7 | 11.2 | 9.7 | 8.2 | 0 | 0
Upper Boat 132 & 33 | Energlyn Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 24.9 | 24.5 | 24.1 | 23.7 | 23.1 | 22.5 | 21.9 | 21 | 19.8 | 18.6 | 17.2 | 15.7 | 14.1 | 12.5 | 11.2 | 9.9 | 8.7 | 4.7 | 0
Upper Boat 132 & 33 | Gas Yard | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Gas Yard | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Gas Yard | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Gas Yard | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Ironbridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.6 | 4 | 4 | 2.9 | 2.8 | 2.2 | 2 | 1.4 | 0.8 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Ironbridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.6 | 3.9 | 2.6 | 2.3 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Ironbridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.6 | 3.9 | 2.7 | 1.9 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Ironbridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.6 | 3.9 | 2.6 | 2.5 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Lady Windsor | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.8 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Lady Windsor | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.8 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Lady Windsor | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.8 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Lady Windsor | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.8 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Merthyr East Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 16.1 | 14.3 | 14.1 | 14 | 13.8 | 13.5 | 12.2 | 9.9 | 6 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Merthyr East Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 16.1 | 14.1 | 13.7 | 12.9 | 8.8 | 4.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Merthyr East Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 16.1 | 14.1 | 13.8 | 13.5 | 13.2 | 11.4 | 7.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Merthyr East Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 16.1 | 14 | 13.6 | 13.2 | 10.3 | 6.7 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Middle Fan | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Middle Fan | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Middle Fan | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Middle Fan | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mill St Tonyrefail | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mill St Tonyrefail | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mill St Tonyrefail | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mill St Tonyrefail | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Morlanga | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.8 | 3.9 | 3.9 | 2.8 | 2.8 | 2.2 | 2 | 1.4 | 0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Morlanga | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.8 | 3.8 | 2.6 | 2.3 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Morlanga | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.8 | 3.8 | 2.6 | 1.9 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Morlanga | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.8 | 3.8 | 2.6 | 2.5 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mountain Ash | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 5.2 | 3.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mountain Ash | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 5.2 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mountain Ash | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 5.2 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mountain Ash | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 5.2 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mountain Ash | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mountain Ash | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mountain Ash | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mountain Ash | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Nantgarw Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 24.2 | 24.1 | 24.1 | 24 | 24 | 23.9 | 23.9 | 23.7 | 23.4 | 23.3 | 23 | 22.6 | 22 | 21.2 | 20.6 | 20 | 19.3 | 15.6 | 12.3
Upper Boat 132 & 33 | Nantgarw Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 24.2 | 24 | 23.9 | 23.6 | 23.3 | 23.1 | 22.9 | 22.1 | 21.3 | 20.6 | 19.8 | 19 | 18 | 17 | 16.1 | 15.1 | 14.3 | 0 | 0
Upper Boat 132 & 33 | Nantgarw Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 24.2 | 24 | 23.9 | 23.7 | 23.6 | 23.4 | 22.8 | 22.1 | 21.2 | 20.5 | 19.6 | 18.6 | 17.6 | 16.6 | 15.6 | 14.4 | 13.5 | 0 | 0
Upper Boat 132 & 33 | Nantgarw Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 24.2 | 24 | 23.9 | 23.7 | 23.3 | 22.9 | 22.6 | 22 | 21.1 | 19.9 | 18.8 | 17.8 | 17 | 15.8 | 15.1 | 13.9 | 13.1 | 9.5 | 0
Upper Boat 132 & 33 | Nantwen | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.5 | 1.1 | 0.9 | 0.7 | 0 | 0 | 8.7 | 8.6 | 8.1 | 7.6 | 7.1 | 6.5 | 5.5 | 4.5 | 3.5 | 2.5 | 1.4 | 0 | 0
Upper Boat 132 & 33 | Nantwen | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 7.2 | 5.9 | 4.5 | 3.1 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Nantwen | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 7.9 | 6.9 | 5.7 | 4.5 | 2.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Nantwen | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 7.6 | 6.7 | 5.5 | 4.3 | 2.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Nelson | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.5 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Nelson | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.5 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Nelson | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Nelson | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Pencoed Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 19.4 | 19.2 | 19.1 | 19 | 18.8 | 18.7 | 18.4 | 18.2 | 17.8 | 17.5 | 17 | 16.3 | 15.1 | 14.1 | 13.3 | 12.7 | 12.1 | 7.6 | 3.7
Upper Boat 132 & 33 | Pencoed Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 19.4 | 19.1 | 18.8 | 18.5 | 18.3 | 18 | 17.5 | 16.8 | 15.9 | 15 | 14.1 | 12.8 | 10.7 | 9.4 | 8.3 | 7.2 | 6.5 | 0 | 0
Upper Boat 132 & 33 | Pencoed Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 19.4 | 19.1 | 18.8 | 18.6 | 18.5 | 18.2 | 17.8 | 17 | 16 | 15 | 13.9 | 12.6 | 11 | 9.1 | 7.2 | 5.8 | 4.9 | 0 | 0
Upper Boat 132 & 33 | Pencoed Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 19.4 | 19.1 | 18.7 | 18.3 | 18 | 17.6 | 17 | 16.2 | 15.2 | 14.3 | 13.4 | 12.2 | 11.4 | 10.6 | 9.4 | 7.9 | 6.6 | 3.4 | 0
Upper Boat 132 & 33 | Pentrebach | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.5 | 1.1 | 0.9 | 0.7 | 0 | 0 | 4 | 3.8 | 3.5 | 3.2 | 2.9 | 2.5 | 1.9 | 1.2 | 0.6 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Pentrebach | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 2.9 | 2.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Pentrebach | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 3 | 2.3 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Pentrebach | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 3 | 2.4 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Pontyclun 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 24.1 | 20.3 | 19.5 | 19.4 | 19.3 | 19.1 | 18.6 | 18.3 | 17.3 | 17.1 | 16.8 | 15.7 | 15 | 14.3 | 13 | 12.5 | 11.8 | 7.3 | 4.1
Upper Boat 132 & 33 | Pontyclun 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 24.1 | 20.1 | 19.1 | 18.7 | 18.2 | 17.8 | 17.1 | 16.2 | 14.5 | 13.5 | 12.7 | 11.1 | 9.9 | 8.7 | 7.1 | 6.1 | 5.1 | 0 | 0
Upper Boat 132 & 33 | Pontyclun 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 24.1 | 20.1 | 19.1 | 18.9 | 18.6 | 18.4 | 17.6 | 16.8 | 15 | 14.2 | 13.3 | 11.4 | 10.3 | 9.2 | 7.5 | 6.3 | 5.3 | 0 | 0
Upper Boat 132 & 33 | Pontyclun 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 24.1 | 20.1 | 19.2 | 18.9 | 18.4 | 18 | 17.2 | 16.5 | 15 | 13.9 | 12.9 | 11.1 | 10.2 | 9.1 | 7.7 | 6.6 | 5.8 | 1.8 | 0
Upper Boat 132 & 33 | Swansea Road Merthyr | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.5 | 1.1 | 0.9 | 0.7 | 0 | 0 | 3.9 | 3.7 | 3.4 | 3.2 | 2.9 | 2.5 | 1.9 | 1.2 | 0.6 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Swansea Road Merthyr | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 2.9 | 2.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Swansea Road Merthyr | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 2.9 | 2.3 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Swansea Road Merthyr | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 3 | 2.4 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Talbot Green Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 19.5 | 19.4 | 18.7 | 18.4 | 18.4 | 18.4 | 18.2 | 18 | 17.8 | 17.8 | 17.6 | 17.3 | 16.7 | 16.1 | 15.5 | 15 | 14.2 | 11.7 | 9.3
Upper Boat 132 & 33 | Talbot Green Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 19.5 | 18.7 | 18.3 | 17.7 | 17.4 | 17.2 | 16.9 | 16.2 | 15.4 | 14.7 | 14 | 12.9 | 11.7 | 10.5 | 9.9 | 9.3 | 8.4 | 0 | 0
Upper Boat 132 & 33 | Talbot Green Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 19.5 | 18.7 | 18.3 | 18 | 17.6 | 17.5 | 17.1 | 16.4 | 15.6 | 15 | 14.3 | 13.4 | 12.5 | 11.3 | 10.7 | 9.9 | 9.1 | 0 | 0
Upper Boat 132 & 33 | Talbot Green Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 19.5 | 18.7 | 18.4 | 17.9 | 17.8 | 17.6 | 17.2 | 16.7 | 16.1 | 15.4 | 14.7 | 14 | 13.2 | 12.1 | 11.5 | 10.8 | 10.2 | 8.2 | 0
Upper Boat 132 & 33 | Tonypandy | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Tonypandy | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Tonypandy | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Tonypandy | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Trethomas | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.9 | 6.9 | 6.8 | 6.8 | 6.8 | 6.7 | 6.6 | 6.5 | 6 | 5.6 | 5 | 4.2 | 3.1 | 1.7 | 0.5 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Trethomas | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.9 | 6.8 | 6.7 | 6.6 | 6.3 | 5.6 | 5.1 | 3.4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Trethomas | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.9 | 6.8 | 6.8 | 6.7 | 6.6 | 6.5 | 5.9 | 4.5 | 2.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Trethomas | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.9 | 6.8 | 6.7 | 6.6 | 6.5 | 5.8 | 5.3 | 4.1 | 2.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Upper Boat Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 4.1 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Upper Boat Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 4.1 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Upper Boat Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 4.1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Upper Boat Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 4.1 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Upper Boat Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 18.9 | 18.7 | 18.4 | 18.1 | 17.7 | 17.3 | 16.6 | 15.9 | 15 | 14.3 | 13.4 | 12.3 | 10.6 | 9.1 | 7.9 | 6.7 | 5.6 | 0 | 0
Upper Boat 132 & 33 | Upper Boat Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 18.9 | 18.4 | 17.9 | 17 | 16.2 | 15.4 | 14.5 | 12.7 | 10.7 | 8.7 | 6.9 | 4.8 | 2 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Upper Boat Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 18.9 | 18.4 | 17.9 | 17.3 | 16.7 | 16.1 | 15.1 | 13.7 | 11.9 | 10.1 | 8.2 | 6 | 3.6 | 1.5 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Upper Boat Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 18.9 | 18.4 | 17.7 | 16.9 | 16 | 15.2 | 13.9 | 12.5 | 10.7 | 8.8 | 6.9 | 4.9 | 3.3 | 1.5 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Wattstown | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.3 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Wattstown | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Wattstown | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Wattstown | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Caldicot | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.5 | 10.2 | 10 | 9.8 | 9.6 | 9.3 | 7.8 | 7.5 | 7.1 | 6.8 | 6.4 | 6 | 5.4 | 4.7 | 4 | 3.5 | 2.8 | 0 | 0
Uskmouth | Caldicot | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.5 | 10.1 | 9.7 | 9.3 | 8.8 | 8.2 | 6.6 | 5.7 | 4.8 | 3.9 | 3.1 | 2.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Caldicot | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.5 | 10.1 | 9.8 | 9.5 | 9.2 | 9 | 7.3 | 6.5 | 5.6 | 4.9 | 3.9 | 3 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0
Uskmouth | Caldicot | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.5 | 10.1 | 9.7 | 9.4 | 8.9 | 8.4 | 6.8 | 6.2 | 5.3 | 4.3 | 3.4 | 2.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Chepstow | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.4 | 3 | 2.6 | 2.3 | 1.9 | 1.6 | 2.4 | 1.9 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Chepstow | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.4 | 2.9 | 2.3 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Chepstow | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.4 | 2.9 | 2.4 | 2 | 1.5 | 1.1 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Chepstow | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.4 | 2.9 | 2.3 | 1.7 | 1.1 | 0.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Cwmbran Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 8.9 | 1.6 | 0 | 0 | 0 | 0 | 12.3 | 11.8 | 11.2 | 10.8 | 10.3 | 9.7 | 8.7 | 7.6 | 6.6 | 5.9 | 4.8 | 0 | 0
Uskmouth | Cwmbran Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 8.9 | 0 | 0 | 0 | 0 | 0 | 10.5 | 9 | 7.3 | 5.8 | 4.3 | 2.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Cwmbran Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 8.9 | 0 | 0 | 0 | 0 | 0 | 11.1 | 10 | 8.7 | 7.8 | 6.4 | 4.9 | 3.1 | 1 | 0 | 0 | 0 | 0 | 0
Uskmouth | Cwmbran Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 8.9 | 0 | 0 | 0 | 0 | 0 | 10 | 8.9 | 7.6 | 5.8 | 4.3 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Llantarnam Bsp | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 18.5 | 17.7 | 17.2 | 16.5 | 15.7 | 14.5 | 13.2 | 11.9 | 10.7 | 9.5 | 0 | 0
Uskmouth | Llantarnam Bsp | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 16.4 | 14.7 | 12.8 | 11 | 9.6 | 8.1 | 6.2 | 2.8 | 0 | 0 | 0 | 0 | 0
Uskmouth | Llantarnam Bsp | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 18.3 | 17 | 15.5 | 14.1 | 12.6 | 10.8 | 8.8 | 6.4 | 0 | 0 | 0 | 0 | 0
Uskmouth | Llantarnam Bsp | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 17.4 | 16.2 | 14.8 | 13.2 | 11.7 | 10 | 8.2 | 6.3 | 0 | 0 | 0 | 0 | 0
Uskmouth | Llantarnam Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 14.6 | 14 | 13.2 | 12.6 | 12 | 11 | 9.5 | 7.8 | 6.4 | 5.1 | 3.5 | 0 | 0
Uskmouth | Llantarnam Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 11.5 | 9.3 | 7.1 | 4.9 | 3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Llantarnam Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 12.7 | 11.2 | 9.4 | 7.9 | 6 | 3.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Llantarnam Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 12.1 | 10.7 | 8.9 | 6.9 | 5 | 2.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Magor Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 23.3 | 17.7 | 17.4 | 17 | 16.6 | 16.1 | 15.5 | 15 | 14.4 | 14 | 13.6 | 18.1 | 17 | 15.9 | 15 | 14.1 | 13.2 | 9.3 | 6.1
Uskmouth | Magor Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 23.3 | 17.6 | 17.2 | 16.6 | 16 | 15.4 | 14.8 | 13.9 | 17.4 | 13.6 | 10.3 | 6.6 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Magor Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 23.3 | 17.6 | 17.2 | 16.6 | 16.1 | 15.6 | 14.7 | 13.6 | 12.4 | 16.7 | 13.5 | 9.5 | 5.5 | 1.7 | 0 | 0 | 0 | 0 | 0
Uskmouth | Magor Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 23.3 | 17.6 | 17.1 | 16.5 | 15.9 | 15.3 | 14.5 | 13.7 | 17.6 | 15.1 | 11.2 | 6.9 | 3 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Newhouse Primary S/S | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.4 | 3 | 2.6 | 2.3 | 1.9 | 1.6 | 2.4 | 2 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Newhouse Primary S/S | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.4 | 2.9 | 2.3 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Newhouse Primary S/S | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.4 | 2.9 | 2.4 | 2 | 1.5 | 1.1 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Newhouse Primary S/S | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.4 | 2.9 | 2.3 | 1.8 | 1.1 | 0.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Newport East Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 16.5 | 15.5 | 14 | 13 | 12 | 10.7 | 8.8 | 6.8 | 4.9 | 3.3 | 1.4 | 0 | 0
Uskmouth | Newport East Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 12.2 | 9 | 5.8 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Newport East Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 14.7 | 12.7 | 10 | 7.8 | 5.3 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Newport East Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 13.1 | 10.9 | 8.3 | 5.5 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Newport South Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 13.5 | 13 | 12.6 | 12.2 | 11.8 | 11 | 10.5 | 10.6 | 10.8 | 11 | 11.1 | 7.3 | 6.8
Uskmouth | Newport South Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 12.5 | 11.7 | 11 | 10.3 | 9.6 | 8.6 | 8.3 | 7.7 | 6 | 3.9 | 2.8 | 1.4 | 0
Uskmouth | Newport South Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 12.7 | 12.4 | 12 | 11.7 | 11.3 | 11.2 | 10.9 | 9.6 | 7.8 | 7.1 | 7.3 | 4.9 | 0
Uskmouth | Newport South Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 12.2 | 11.7 | 11.1 | 10.1 | 9.3 | 8.3 | 8.4 | 8.2 | 7.8 | 6 | 4.2 | 3.7 | 2.3
Uskmouth | Newport West Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.9 | 9.6 | 9.3 | 9.1 | 8.9 | 8.4 | 7.8 | 7.2 | 6.6 | 6.1 | 5.3 | 0 | 0
Uskmouth | Newport West Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.3 | 6.4 | 5.5 | 2.5 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Newport West Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.6 | 7.1 | 6.4 | 3.8 | 3.2 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Newport West Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 7.9 | 7.2 | 6.1 | 5.4 | 2.6 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0
Uskmouth | Panteg Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 10.2 | 9.9 | 9.4 | 9.3 | 9.1 | 8.8 | 12.7 | 12.3 | 11.7 | 11.4 | 10.9 | 10.2 | 9.1 | 8 | 6.9 | 6 | 4.9 | 0 | 0
Uskmouth | Panteg Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 10.2 | 9.2 | 8.8 | 8.2 | 7.6 | 6.9 | 10.5 | 9.2 | 7.8 | 6.3 | 5.1 | 3.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Panteg Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 10.2 | 9.2 | 8.9 | 8.6 | 8.3 | 7.9 | 11.5 | 10.5 | 9.3 | 8.3 | 6.9 | 5.1 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Panteg Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 10.2 | 9.2 | 8.9 | 8.4 | 7.8 | 7.2 | 10.6 | 9.7 | 8.4 | 7 | 5.7 | 4.1 | 2.7 | 0.9 | 0 | 0 | 0 | 0 | 0
Uskmouth | Pontypool North Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15 | 10.5 | 10.6 | 10.6 | 10.6 | 10.5 | 10.2 | 10.1 | 10 | 9.9 | 9.8 | 9.6 | 9.3 | 8.9 | 8.6 | 8.3 | 7.9 | 5.1 | 3.1
Uskmouth | Pontypool North Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15 | 10.5 | 10.5 | 10.5 | 10.4 | 10.3 | 9.9 | 9.6 | 9.3 | 8.9 | 8.5 | 8.1 | 7.5 | 6.9 | 6.3 | 5.6 | 5.1 | 2.5 | 1.5
Uskmouth | Pontypool North Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 9.7 | 9.4 | 9 | 8.7 | 8.2 | 7.7 | 7 | 6.1 | 5.2 | 4.5 | 4 | 1.4 | 0
Uskmouth | Pontypool North Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15 | 10.5 | 10.5 | 10.5 | 10.3 | 10.1 | 9.6 | 9.3 | 8.9 | 8.1 | 7.5 | 6.9 | 6.5 | 5.7 | 5.3 | 4.4 | 3.8 | 1.4 | 0
Uskmouth | Ringland Newport | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7 | 6.7 | 6.1 | 4.5 | 4 | 3.3 | 3 | 2.5 | 1.8 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Ringland Newport | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7 | 6.5 | 4.4 | 3.5 | 2.5 | 1.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Ringland Newport | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7 | 6.5 | 4.4 | 3.7 | 3.1 | 2.6 | 2.4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Ringland Newport | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7 | 6.5 | 4.6 | 3.9 | 3 | 2.1 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Rogerstone | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.8 | 19.5 | 19.4 | 19.2 | 18.9 | 18.6 | 18.5 | 18 | 17.2 | 16.6 | 16 | 15.2 | 14 | 12.7 | 11.4 | 10.3 | 9 | 1.2 | 0
Uskmouth | Rogerstone | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.8 | 19.4 | 19 | 18.2 | 17.3 | 16.5 | 15.9 | 14.2 | 12.3 | 10.5 | 9.1 | 7.7 | 5.7 | 4.2 | 2.7 | 1.1 | 0 | 0 | 0
Uskmouth | Rogerstone | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.8 | 19.4 | 19.1 | 18.8 | 18.4 | 18 | 17.8 | 16.5 | 15 | 13.6 | 12.1 | 10.4 | 8.4 | 6.4 | 4.5 | 2.7 | 0.9 | 0 | 0
Uskmouth | Rogerstone | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.8 | 19.3 | 19 | 18.5 | 17.9 | 17.3 | 16.9 | 15.7 | 14.3 | 12.7 | 11.2 | 9.5 | 7.7 | 5.8 | 4.2 | 2.5 | 0.9 | 0 | 0
Uskmouth | St Arvans | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.9 | 2.8 | 2.5 | 2.2 | 1.9 | 1.6 | 2.4 | 1.9 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | St Arvans | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.9 | 2.8 | 2.3 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | St Arvans | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.9 | 2.8 | 2.3 | 1.9 | 1.5 | 1.1 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | St Arvans | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.9 | 2.8 | 2.2 | 1.7 | 1.1 | 0.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Sudbrook Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 28.8 | 28.1 | 27.4 | 26.9 | 26.3 | 25.7 | 25.4 | 24.5 | 23.3 | 22.6 | 21.7 | 20.4 | 18.5 | 16.5 | 14.6 | 12.9 | 11 | 0 | 0
Uskmouth | Sudbrook Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 28.8 | 27.9 | 26.9 | 25.6 | 24.1 | 22.8 | 19.5 | 16.2 | 16.9 | 13.6 | 10.3 | 6.6 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Sudbrook Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 28.8 | 27.9 | 27 | 26.3 | 25.5 | 24.9 | 21.6 | 18.5 | 14.9 | 17.1 | 13.5 | 9.5 | 5.5 | 1.7 | 0 | 0 | 0 | 0 | 0
Uskmouth | Sudbrook Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 28.8 | 27.9 | 26.8 | 26 | 24.7 | 23.6 | 20 | 17.4 | 18.6 | 15.1 | 11.2 | 6.9 | 3 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Sudbrook Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.8 | 10.6 | 10.3 | 10.1 | 9.9 | 9.6 | 9.5 | 9.1 | 8.7 | 8.4 | 8 | 7.4 | 6.7 | 5.8 | 5 | 4.4 | 3.5 | 0 | 0
Uskmouth | Sudbrook Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.8 | 10.5 | 10.1 | 9.6 | 9 | 8.4 | 8.1 | 7.1 | 6.1 | 5.1 | 4.1 | 3.1 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0
Uskmouth | Sudbrook Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.8 | 10.5 | 10.1 | 9.8 | 9.5 | 9.3 | 8.8 | 8 | 6.9 | 6 | 4.9 | 3.7 | 2.4 | 1.2 | 0 | 0 | 0 | 0 | 0
Uskmouth | Sudbrook Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.8 | 10.4 | 10 | 9.7 | 9.2 | 8.6 | 8.2 | 7.4 | 6.5 | 5.2 | 4 | 2.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0

## Generation Headroom
Associated GSP | Substation | Supply Level | Voltage Level (kV) | Scenario | Units | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050
Cardiff East / Aberthaw | Ashgrove | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.4 | 12.4 | 12.3 | 12.3 | 12.2 | 12.1 | 11.9 | 11.8 | 11.8 | 11.7 | 11.6 | 11.6 | 11.5 | 11.5 | 11.5 | 11.5 | 11.4 | 11.4 | 11.1
Cardiff East / Aberthaw | Ashgrove | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.4 | 12.3 | 12.1 | 12 | 11.9 | 11.8 | 11.5 | 11.4 | 11.3 | 11.2 | 11.1 | 11 | 10.9 | 10.7 | 10.6 | 10.5 | 10.4 | 9.6 | 8.8
Cardiff East / Aberthaw | Ashgrove | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.4 | 12.2 | 11.9 | 11.7 | 11.5 | 11.3 | 11 | 10.8 | 10.6 | 10.5 | 10.3 | 9.8 | 9.7 | 9.6 | 9.6 | 9.5 | 9.3 | 8.3 | 7.3
Cardiff East / Aberthaw | Ashgrove | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.4 | 12.4 | 12.2 | 12.2 | 12.1 | 12 | 11.8 | 11.7 | 11.6 | 11.5 | 11.4 | 11.4 | 11.4 | 11.3 | 11.3 | 11.3 | 11.3 | 11 | 10.7
Cardiff East / Aberthaw | Barry Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 42.9 | 42.6 | 42.3 | 41.6 | 41.4 | 41.1 | 14.9 | 14.5 | 14.1 | 13.6 | 13.1 | 12.7 | 12.5 | 12.3 | 12.1 | 11.9 | 11.7 | 10.6 | 8.7
Cardiff East / Aberthaw | Barry Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 42.9 | 42.2 | 41.2 | 40.7 | 40.2 | 39.6 | 13.1 | 12.3 | 11.6 | 10.7 | 9.8 | 8.9 | 8.1 | 7.2 | 6.4 | 3.5 | 2.6 | 0 | 1.7
Cardiff East / Aberthaw | Barry Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 42.9 | 41.5 | 40.8 | 40.2 | 39.4 | 38.5 | 11.7 | 10.7 | 9.6 | 8.7 | 3.5 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Barry Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 42.9 | 42.5 | 41.6 | 41.3 | 41 | 40.5 | 14.2 | 13.7 | 13.2 | 12.8 | 12.2 | 11.8 | 11.5 | 11.2 | 10.9 | 8.4 | 1 | 0 | 3
Cardiff East / Aberthaw | Barry Grid Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.1 | 18 | 17.8 | 17.7 | 17.6 | 17.4 | 17.3 | 17 | 16.7 | 16.4 | 16 | 15.7 | 15.6 | 15.5 | 15.3 | 15.2 | 15.1 | 14.2 | 13
Cardiff East / Aberthaw | Barry Grid Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.1 | 17.7 | 17.5 | 17.2 | 17 | 16.7 | 16.3 | 15.8 | 15.2 | 14.6 | 14 | 13.3 | 12.7 | 12 | 11.4 | 10.8 | 10.2 | 6.7 | 4.4
Cardiff East / Aberthaw | Barry Grid Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.1 | 17.6 | 17.3 | 17 | 16.6 | 16.2 | 15.6 | 15 | 14.3 | 13.7 | 12.9 | 12.3 | 11.7 | 11.2 | 10.7 | 10.2 | 9.6 | 6.5 | 4.6
Cardiff East / Aberthaw | Barry Grid Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.1 | 17.9 | 17.7 | 17.6 | 17.4 | 17.2 | 16.9 | 16.6 | 16.3 | 16 | 15.5 | 15.2 | 14.9 | 14.7 | 14.4 | 14.2 | 14 | 12.2 | 10.1
Cardiff East / Aberthaw | Birchgrove | Primary Substation | 11 | Counterfactual | Headroom (MW) | 35.3 | 35.2 | 35.1 | 35 | 34.8 | 34.7 | 18.9 | 18.7 | 18.5 | 18.3 | 18.1 | 18 | 17.9 | 17.9 | 17.9 | 17.8 | 17.8 | 17.5 | 16.9
Cardiff East / Aberthaw | Birchgrove | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 35.3 | 35 | 34.7 | 34.4 | 34.2 | 34 | 18 | 17.7 | 17.5 | 17.2 | 16.8 | 16.5 | 16.3 | 15.8 | 15.4 | 15 | 14.6 | 12.9 | 11.2
Cardiff East / Aberthaw | Birchgrove | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 35.3 | 34.8 | 34.3 | 33.9 | 33.5 | 33.1 | 17 | 16.6 | 16.2 | 15.7 | 15.2 | 14.7 | 14.4 | 14 | 13.8 | 13.5 | 13.1 | 10.8 | 8.9
Cardiff East / Aberthaw | Birchgrove | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 35.3 | 35.1 | 35 | 34.8 | 34.6 | 34.4 | 18.6 | 18.4 | 18.3 | 18.1 | 17.9 | 17.8 | 17.7 | 17.6 | 17.6 | 17.5 | 17.5 | 16.7 | 15.7
Cardiff East / Aberthaw | Boverton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.4 | 10.3 | 10.2 | 10.1 | 10 | 9.9 | 9.6 | 9.3 | 9 | 8.7 | 8.4 | 8.1 | 8 | 7.9 | 7.7 | 7.6 | 7.5 | 6.6 | 5.7
Cardiff East / Aberthaw | Boverton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.4 | 10.2 | 10 | 9.8 | 9.5 | 9.2 | 8.6 | 8 | 7.4 | 6.7 | 5.9 | 5.1 | 4.4 | 3.7 | 3.1 | 1.6 | 0.9 | 0 | 0
Cardiff East / Aberthaw | Boverton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.4 | 10.1 | 9.8 | 9.6 | 9.2 | 8.9 | 8.2 | 7.6 | 6.9 | 6.2 | 3.9 | 3.2 | 2.5 | 1.6 | 1.1 | 0.5 | 0 | 0 | 0
Cardiff East / Aberthaw | Boverton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.4 | 10.3 | 10.1 | 10 | 9.8 | 9.6 | 9.2 | 8.8 | 8.5 | 8.1 | 7.6 | 7.2 | 6.9 | 6.6 | 6.4 | 5.5 | 5.3 | 3.5 | 1.7
Cardiff East / Aberthaw | Broad St.Barry | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.2 | 12.1 | 12 | 11.8 | 11.7 | 11.6 | 6.1 | 6 | 5.9 | 5.8 | 5.6 | 5.6 | 5.5 | 5.4 | 5.4 | 5.3 | 5.3 | 5 | 4.4
Cardiff East / Aberthaw | Broad St.Barry | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.2 | 11.9 | 11.6 | 11.4 | 11.2 | 11 | 5.4 | 5.2 | 5 | 4.8 | 4.6 | 4.4 | 4.2 | 4 | 3.8 | 3.6 | 3.3 | 1.9 | 6.1
Cardiff East / Aberthaw | Broad St.Barry | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.2 | 11.8 | 11.4 | 11 | 10.7 | 10.3 | 4.7 | 4.3 | 4 | 3.8 | 3.5 | 3.4 | 3.1 | 2.9 | 2.6 | 2.3 | 2 | 0 | 4.3
Cardiff East / Aberthaw | Broad St.Barry | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.2 | 12 | 11.9 | 11.7 | 11.6 | 11.4 | 5.9 | 5.7 | 5.5 | 5.4 | 5.3 | 5.3 | 5.2 | 5.2 | 5.1 | 5 | 4.8 | 3.9 | 8.5
Cardiff East / Aberthaw | Canton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.4 | 14.4 | 14.4 | 14.4 | 14.3 | 14.3 | 14 | 13.9 | 13.8 | 13.8 | 13.7 | 13.7 | 13.7 | 13.6 | 13.6 | 13.6 | 13.6 | 13.5 | 13.3
Cardiff East / Aberthaw | Canton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.4 | 14.4 | 14.2 | 14.1 | 14 | 13.9 | 13.5 | 13.4 | 13.3 | 13.2 | 13.1 | 13.1 | 13 | 12.8 | 12.7 | 12.6 | 12.4 | 11.9 | 11.2
Cardiff East / Aberthaw | Canton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.4 | 14.4 | 14 | 13.8 | 13.6 | 13.4 | 13 | 12.8 | 12.6 | 12.5 | 12.3 | 12.1 | 12 | 11.9 | 11.8 | 11.7 | 11.5 | 10.6 | 9.6
Cardiff East / Aberthaw | Canton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.4 | 14.4 | 14.4 | 14.3 | 14.2 | 14.1 | 13.8 | 13.7 | 13.6 | 13.5 | 13.5 | 13.5 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.2 | 12.8
Cardiff East / Aberthaw | Cardiff Central Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 20.6 | 20.7 | 20.7 | 20.8 | 20.8 | 20.9 | 32.6 | 32.6 | 32.7 | 32.8 | 32.8 | 32.8 | 32.8 | 32.8 | 32.8 | 32.8 | 32.8 | 32.8 | 32.8
Cardiff East / Aberthaw | Cardiff Central Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 20.6 | 20.8 | 20.9 | 21.1 | 21.4 | 21.1 | 32.6 | 32.6 | 32.7 | 32.8 | 32.8 | 32.8 | 32.8 | 32.8 | 32.9 | 33 | 33.1 | 33.5 | 33.9
Cardiff East / Aberthaw | Cardiff Central Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 20.6 | 20.8 | 21.2 | 21.5 | 21.1 | 20.9 | 32.6 | 32.6 | 32.7 | 32.9 | 33.1 | 33.2 | 33.3 | 33.4 | 33.5 | 33.6 | 33.7 | 34.3 | 34.9
Cardiff East / Aberthaw | Cardiff Central Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 20.6 | 20.7 | 20.8 | 20.9 | 21 | 21.2 | 32.6 | 32.6 | 32.7 | 32.8 | 32.8 | 32.8 | 32.8 | 32.8 | 32.8 | 32.8 | 32.8 | 32.8 | 32.8
Cardiff East / Aberthaw | Cardiff East Grid Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 27.2 | 27.2 | 27.1 | 26.8 | 26.6 | 26.4 | 25.9 | 25.6 | 25.4 | 25.2 | 25 | 24.9 | 24.9 | 24.8 | 24.8 | 24.8 | 24.7 | 24.5 | 23.9
Cardiff East / Aberthaw | Cardiff East Grid Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 27.2 | 27 | 26.4 | 26 | 25.6 | 25.2 | 24.6 | 24.3 | 24.1 | 23.8 | 23.5 | 23.3 | 23.1 | 22.6 | 22.2 | 21.8 | 21.4 | 19.8 | 17.7
Cardiff East / Aberthaw | Cardiff East Grid Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 27.2 | 26.7 | 25.8 | 25.2 | 24.6 | 24 | 23.1 | 22.6 | 22.2 | 21.7 | 21.1 | 20.6 | 20.1 | 19.8 | 19.5 | 19.2 | 18.7 | 15.9 | 13.1
Cardiff East / Aberthaw | Cardiff East Grid Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 27.2 | 27.2 | 26.9 | 26.6 | 26.3 | 26 | 25.4 | 25.1 | 25 | 24.8 | 24.6 | 24.5 | 24.5 | 24.4 | 24.4 | 24.3 | 24.3 | 23.5 | 22.5
Cardiff East / Aberthaw | Cardiff North Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 20.2 | 20.6 | 20.6 | 20.6 | 20.6 | 20.5 | 86.1 | 85.7 | 85.4 | 85.1 | 84.7 | 84.5 | 84.3 | 84.2 | 84.1 | 84 | 83.9 | 83.5 | 83
Cardiff East / Aberthaw | Cardiff North Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 20.2 | 20.6 | 20.5 | 20.4 | 20.4 | 20.4 | 83.8 | 83.3 | 83.1 | 82.9 | 82.8 | 78.7 | 78.6 | 77.6 | 77.5 | 77.2 | 76.7 | 73.9 | 70.2
Cardiff East / Aberthaw | Cardiff North Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 20.2 | 20.5 | 20.4 | 20.4 | 20.3 | 20.2 | 82.8 | 78.5 | 77.6 | 77.4 | 76.7 | 75.9 | 75.3 | 74.7 | 74.2 | 73.6 | 72.7 | 67.4 | 62.7
Cardiff East / Aberthaw | Cardiff North Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 20.2 | 20.6 | 20.6 | 20.5 | 20.5 | 20.5 | 85.4 | 85 | 84.6 | 84.2 | 83.8 | 83.6 | 83.5 | 83.3 | 83.2 | 83.1 | 83 | 78.6 | 77.5
Cardiff East / Aberthaw | Cardiff South Grid | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 36.3 | 36.4 | 36.3 | 36.3 | 36.2 | 36.8 | 36.7 | 36.6 | 36.5 | 36.3 | 36.2 | 36.2 | 36.1 | 36 | 36 | 35.9 | 35.8 | 35.5 | 35.4
Cardiff East / Aberthaw | Cardiff South Grid | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 36.3 | 36.4 | 36.3 | 36.3 | 35.7 | 34.8 | 34.7 | 34.2 | 33.4 | 32.7 | 31.8 | 31.2 | 30.9 | 30.8 | 30.7 | 30.6 | 30.6 | 30.2 | 29.8
Cardiff East / Aberthaw | Cardiff South Grid | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 36.3 | 36.4 | 36.3 | 36.3 | 35.3 | 34.2 | 34.4 | 33.3 | 32.3 | 31.3 | 31 | 30.9 | 30.8 | 30.7 | 30.7 | 30.6 | 30.5 | 29.9 | 29.4
Cardiff East / Aberthaw | Cardiff South Grid | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 36.3 | 36.4 | 36.3 | 36.3 | 36 | 35.1 | 34.8 | 34.4 | 33.7 | 33.3 | 33 | 32.7 | 32.5 | 32.3 | 32.1 | 31.9 | 31.7 | 30.9 | 30.6
Cardiff East / Aberthaw | Cardiff West Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 50.9 | 50.4 | 50 | 49.6 | 49.1 | 48.6 | 71.9 | 71.2 | 70.5 | 69.7 | 68.9 | 68.4 | 68 | 67.7 | 67.5 | 67.3 | 67.2 | 66.2 | 64
Cardiff East / Aberthaw | Cardiff West Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 50.9 | 49.5 | 48.3 | 47.4 | 46.3 | 45.1 | 68.9 | 67.6 | 66.3 | 64.9 | 63.5 | 62.3 | 61.2 | 59.7 | 58.3 | 56.7 | 55.2 | 47.8 | 41
Cardiff East / Aberthaw | Cardiff West Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 50.9 | 48.8 | 47 | 45.1 | 43.2 | 41.2 | 65 | 63.2 | 61.3 | 59.6 | 57.1 | 55.4 | 53.9 | 52.5 | 51.2 | 49.9 | 48.3 | 38.8 | 30.9
Cardiff East / Aberthaw | Cardiff West Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 50.9 | 50.1 | 49.5 | 48.9 | 48.1 | 47.1 | 70.3 | 69.2 | 68.3 | 67.4 | 66.6 | 66.2 | 65.8 | 65.5 | 65.2 | 64.8 | 55.9 | 52.9 | 48.9
Cardiff East / Aberthaw | Court Road Barry | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.1 | 12.1 | 11.9 | 11.8 | 11.7 | 11.6 | 6.3 | 6.2 | 6.1 | 6 | 5.9 | 5.9 | 5.8 | 5.7 | 5.7 | 5.6 | 5.6 | 5.3 | 4.8
Cardiff East / Aberthaw | Court Road Barry | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.1 | 11.9 | 11.5 | 11.3 | 11.1 | 10.9 | 5.7 | 5.5 | 5.3 | 5.2 | 5 | 4.8 | 4.6 | 4.4 | 4.3 | 4.1 | 3.9 | 2.6 | 7
Cardiff East / Aberthaw | Court Road Barry | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.1 | 11.8 | 11.3 | 11 | 10.7 | 10.3 | 5.1 | 4.8 | 4.5 | 4.3 | 4 | 3.9 | 3.7 | 3.5 | 3.2 | 3 | 2.7 | 1.1 | 5.2
Cardiff East / Aberthaw | Court Road Barry | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.1 | 12 | 11.8 | 11.7 | 11.5 | 11.4 | 6.1 | 6 | 5.8 | 5.7 | 5.6 | 5.6 | 5.5 | 5.5 | 5.4 | 5.3 | 5.2 | 4.3 | 9
Cardiff East / Aberthaw | Cowbridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.9 | 10.9 | 10.8 | 10.7 | 10.6 | 10.5 | 10.1 | 9.7 | 9.1 | 8.6 | 7.8 | 7.3 | 7 | 6.8 | 6.6 | 6.4 | 6.1 | 4.6 | 2.8
Cardiff East / Aberthaw | Cowbridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.9 | 10.8 | 10.6 | 10.5 | 10 | 9.6 | 8.8 | 7.8 | 6.7 | 5.6 | 4.3 | 3 | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cowbridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.9 | 10.7 | 10.5 | 10.4 | 9.7 | 9.2 | 8.3 | 7.3 | 6.2 | 5.1 | 3.7 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Cowbridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.9 | 10.8 | 10.7 | 10.5 | 10.1 | 9.9 | 9.5 | 9 | 8.5 | 7.9 | 7.1 | 6.4 | 5.9 | 5.5 | 5.1 | 4.8 | 4.3 | 1.4 | 0
Cardiff East / Aberthaw | Crwys Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15 | 15 | 15 | 15 | 14.9 | 14.9 | 14.3 | 14.3 | 14.3 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14
Cardiff East / Aberthaw | Crwys Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15 | 15 | 15 | 15 | 14.9 | 14.8 | 14.2 | 14.1 | 14 | 13.9 | 13.8 | 13.7 | 13.7 | 13.5 | 13.4 | 13.3 | 13.1 | 12.6 | 11.9
Cardiff East / Aberthaw | Crwys Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15 | 15 | 14.9 | 14.7 | 14.5 | 14.3 | 13.6 | 13.4 | 13.3 | 13.1 | 12.9 | 12.7 | 12.6 | 12.5 | 12.4 | 12.3 | 12.1 | 11.2 | 10.3
Cardiff East / Aberthaw | Crwys Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15 | 15 | 15 | 15 | 14.9 | 14.9 | 14.3 | 14.3 | 14.3 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.1 | 13.9 | 13.6
Cardiff East / Aberthaw | Cyncoed | Primary Substation | 11 | Counterfactual | Headroom (MW) | 21.8 | 21.7 | 21.5 | 21.4 | 21.2 | 21 | 20.4 | 20.2 | 20 | 19.8 | 19.6 | 19.5 | 19.4 | 19.4 | 19.4 | 19.3 | 19.3 | 19.2 | 18.8
Cardiff East / Aberthaw | Cyncoed | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 21.8 | 21.4 | 21 | 20.8 | 20.5 | 20.3 | 19.6 | 19.4 | 19.1 | 18.8 | 18.7 | 17.4 | 17.4 | 17.2 | 17 | 16.8 | 16.5 | 15.5 | 14.2
Cardiff East / Aberthaw | Cyncoed | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 21.8 | 21.1 | 20.6 | 20.2 | 19.7 | 19.3 | 17.5 | 17.3 | 17 | 16.8 | 16.4 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 14.9 | 13 | 11.2
Cardiff East / Aberthaw | Cyncoed | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 21.8 | 21.6 | 21.4 | 21.2 | 20.9 | 20.7 | 20 | 19.6 | 19.4 | 19.3 | 19.1 | 19 | 19 | 19 | 19 | 19 | 18.9 | 17.5 | 17.2
Cardiff East / Aberthaw | East Aberthaw | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 29.6 | 29.6 | 29.6 | 29.4 | 29.4 | 29.3 | 72.5 | 71.4 | 70.1 | 68.8 | 67.3 | 66.2 | 65.5 | 65 | 64.5 | 63.9 | 63.2 | 59.3 | 55.3
Cardiff East / Aberthaw | East Aberthaw | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 29.6 | 29.6 | 29.4 | 29.3 | 29.3 | 29.2 | 69.4 | 67 | 64.5 | 61.8 | 58.9 | 55.9 | 53.2 | 50.2 | 47.5 | 44.1 | 40.8 | 26.1 | 18.4
Cardiff East / Aberthaw | East Aberthaw | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 29.6 | 29.4 | 29.4 | 29.3 | 29.2 | 29.1 | 68.1 | 65.8 | 63.1 | 60 | 55 | 51.1 | 47.3 | 44.6 | 42.7 | 40.8 | 38.8 | 27.5 | 22.7
Cardiff East / Aberthaw | East Aberthaw | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 29.6 | 29.6 | 29.4 | 29.3 | 29.3 | 29.2 | 71.2 | 69.9 | 68.7 | 67 | 64.8 | 63.2 | 61.7 | 60.4 | 59.6 | 58.1 | 56.7 | 49.3 | 41.8
Cardiff East / Aberthaw | East Aberthaw Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.9 | 11.1 | 11.1 | 7.4 | 7.3 | 7.2 | 6.9 | 6.5 | 6.2 | 5.8 | 5.3 | 4.9 | 4.7 | 4.6 | 4.4 | 4.2 | 3.9 | 2.3 | 1.1
Cardiff East / Aberthaw | East Aberthaw Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.9 | 11 | 7.4 | 7.2 | 7 | 6.7 | 6 | 5.3 | 4.6 | 3.8 | 2.9 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | East Aberthaw Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.9 | 7.4 | 7.3 | 7.1 | 6.8 | 6.4 | 5.7 | 5 | 4.2 | 3 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | East Aberthaw Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.9 | 11.1 | 7.5 | 7.4 | 7.2 | 7 | 6.6 | 6.2 | 5.9 | 5.2 | 4.4 | 3.8 | 3.1 | 2.6 | 2.3 | 2.1 | 1.8 | 0 | 0
Cardiff East / Aberthaw | Ely | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.4 | 17.3 | 17.2 | 17.2 | 17.1 | 17.1 | 17 | 17 | 16.9 | 16.9 | 16.9 | 16.8 | 16.8 | 16.8 | 16.7 | 16.7 | 16.7 | 16.7 | 15.7
Cardiff East / Aberthaw | Ely | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.4 | 17.2 | 17.1 | 17 | 16.9 | 16.8 | 16.7 | 16.7 | 15.7 | 15.7 | 15.6 | 15.5 | 15.4 | 15.3 | 15.2 | 15.1 | 15 | 13.6 | 11.4
Cardiff East / Aberthaw | Ely | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.4 | 17.1 | 16.9 | 16.8 | 16.7 | 15.6 | 15.5 | 15.4 | 15.2 | 15 | 14.9 | 14.7 | 14.3 | 13.9 | 13.5 | 13.1 | 12.6 | 9.6 | 6.8
Cardiff East / Aberthaw | Ely | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.4 | 17.3 | 17.2 | 17.1 | 17 | 16.9 | 16.8 | 16.7 | 16.7 | 16.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.6 | 15.6 | 15.4 | 15.2
Cardiff East / Aberthaw | Fairwater | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.8 | 11.7 | 11.6 | 11.5 | 11.5 | 11.4 | 11.3 | 11.2 | 11.1 | 10.9 | 10.8 | 10.7 | 10.6 | 10.6 | 10.6 | 10.5 | 10.5 | 10.5 | 9.7
Cardiff East / Aberthaw | Fairwater | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.8 | 11.5 | 11.3 | 11.2 | 11.1 | 11 | 10.8 | 10.6 | 10.5 | 9.7 | 9.5 | 9.3 | 9.2 | 8.9 | 8.7 | 8.5 | 8.3 | 7.5 | 6.5
Cardiff East / Aberthaw | Fairwater | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.8 | 11.4 | 11.1 | 10.9 | 10.6 | 10.4 | 9.6 | 9.3 | 8.9 | 8.7 | 8.4 | 8.1 | 7.9 | 7.7 | 7.6 | 7.5 | 7.2 | 5.9 | 4.7
Cardiff East / Aberthaw | Fairwater | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.8 | 11.7 | 11.5 | 11.4 | 11.3 | 11.1 | 11 | 10.7 | 10.6 | 10.5 | 9.8 | 9.8 | 9.8 | 9.7 | 9.7 | 9.7 | 9.7 | 9.4 | 8.8
Cardiff East / Aberthaw | Grangetown Grid Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 23.7 | 23.7 | 23.5 | 23.3 | 23.2 | 23 | 22.7 | 22.6 | 22.4 | 22.2 | 22 | 21.9 | 21.9 | 21.8 | 21.7 | 21.7 | 21.6 | 21.3 | 20.6
Cardiff East / Aberthaw | Grangetown Grid Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 23.7 | 23.5 | 23.1 | 22.9 | 22.5 | 22.2 | 21.7 | 21.4 | 21 | 20.6 | 20.3 | 20 | 19.8 | 19.6 | 21.2 | 20.9 | 20.7 | 18.9 | 17.7
Cardiff East / Aberthaw | Grangetown Grid Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 23.7 | 23.4 | 22.8 | 22.3 | 21.9 | 21.3 | 20.5 | 20 | 19.5 | 19.2 | 18.9 | 18.6 | 18.2 | 17.7 | 24.3 | 23.9 | 23.6 | 22.1 | 20.6
Cardiff East / Aberthaw | Grangetown Grid Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 23.7 | 23.6 | 23.3 | 23.1 | 22.8 | 22.5 | 22 | 21.8 | 21.6 | 21.4 | 21.2 | 21.1 | 21 | 20.9 | 22.6 | 22.5 | 22.4 | 21.4 | 20.5
Cardiff East / Aberthaw | Heath | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20 | 20 | 19.9 | 19.9 | 19.8 | 19.7 | 19.2 | 19.1 | 19 | 18.9 | 18.8 | 18.8 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.6 | 18.2
Cardiff East / Aberthaw | Heath | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20 | 20 | 19.7 | 19.5 | 19.4 | 19.2 | 18.7 | 18.6 | 18.4 | 18.3 | 18.2 | 18.1 | 18 | 17.8 | 17.5 | 17.3 | 17.1 | 16.3 | 15.2
Cardiff East / Aberthaw | Heath | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20 | 19.8 | 19.4 | 19.1 | 18.8 | 18.5 | 17.9 | 17.7 | 17.4 | 17.2 | 16.8 | 16.6 | 16.4 | 16.2 | 16.1 | 15.9 | 15.7 | 14.2 | 12.7
Cardiff East / Aberthaw | Heath | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20 | 20 | 19.9 | 19.8 | 19.7 | 19.6 | 19.1 | 19 | 18.9 | 18.8 | 18.7 | 18.7 | 18.7 | 18.7 | 18.6 | 18.6 | 18.6 | 18.2 | 17.7
Cardiff East / Aberthaw | Heath Hospital Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.9 | 11.9 | 11.9 | 11.9 | 11.8 | 11.8 | 11.6 | 11.6 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
Cardiff East / Aberthaw | Heath Hospital Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.9 | 11.9 | 11.9 | 11.9 | 11.8 | 11.8 | 11.6 | 11.6 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.4 | 11.3
Cardiff East / Aberthaw | Heath Hospital Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.9 | 11.9 | 11.9 | 11.9 | 11.8 | 11.8 | 11.6 | 11.6 | 11.5 | 11.5 | 11.5 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.3 | 11.2 | 11
Cardiff East / Aberthaw | Heath Hospital Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.9 | 11.9 | 11.9 | 11.9 | 11.8 | 11.8 | 11.6 | 11.6 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
Cardiff East / Aberthaw | Highmead | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.3 | 20.2 | 20 | 19.9 | 19.7 | 19.6 | 19.5 | 19.2 | 19.1 | 18.8 | 18.6 | 18.4 | 18.4 | 18.3 | 18.3 | 18.2 | 18.2 | 17.8 | 17.2
Cardiff East / Aberthaw | Highmead | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.3 | 20 | 19.6 | 19.4 | 19.2 | 18.9 | 18.7 | 18.3 | 18 | 17.7 | 17.3 | 17 | 16.7 | 15.8 | 15.6 | 15.1 | 14.7 | 12.9 | 11.2
Cardiff East / Aberthaw | Highmead | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.3 | 19.8 | 19.3 | 19 | 18.5 | 18.1 | 17.7 | 17.2 | 16.8 | 16.5 | 15.3 | 14.9 | 14.5 | 14.2 | 13.9 | 13.6 | 13.2 | 10.8 | 9
Cardiff East / Aberthaw | Highmead | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.3 | 20.1 | 19.9 | 19.8 | 19.6 | 19.4 | 19.2 | 19 | 18.8 | 18.5 | 18.3 | 18.2 | 18.1 | 18 | 17.9 | 17.7 | 17.6 | 16.8 | 15.5
Cardiff East / Aberthaw | Llandough | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 5.8 | 5.5 | 5.2 | 4.9 | 4.6 | 4.2 | 3.9 | 3.7 | 3.6 | 3.4 | 3.3 | 3.2 | 2.7 | 1.6
Cardiff East / Aberthaw | Llandough | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 6.3 | 5.9 | 5.6 | 5.2 | 4.8 | 4.2 | 3.6 | 3 | 2.3 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Llandough | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 6.1 | 5.6 | 5.1 | 4.5 | 3.9 | 3.1 | 2.3 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Llandough | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.5 | 6.2 | 5.9 | 5.7 | 5.3 | 4.9 | 4.4 | 3.9 | 3.6 | 3.1 | 2.9 | 2.7 | 2.4 | 2.2 | 2 | 0 | 0 | 0
Cardiff East / Aberthaw | Llanishen | Primary Substation | 11 | Counterfactual | Headroom (MW) | 35.4 | 35.4 | 35.3 | 35.2 | 35 | 34.9 | 18.9 | 18.7 | 18.5 | 18.3 | 18.1 | 18 | 17.9 | 17.9 | 17.9 | 17.8 | 17.8 | 17.5 | 16.9
Cardiff East / Aberthaw | Llanishen | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 35.4 | 35.2 | 34.8 | 34.6 | 34.4 | 34.1 | 18.1 | 17.8 | 17.5 | 17.2 | 16.8 | 16.5 | 16.3 | 15.8 | 15.5 | 15.1 | 14.7 | 12.9 | 11.3
Cardiff East / Aberthaw | Llanishen | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 35.4 | 34.9 | 34.5 | 34.1 | 33.7 | 33.3 | 17 | 16.6 | 16.2 | 15.8 | 15.2 | 14.7 | 14.4 | 14.1 | 13.8 | 13.5 | 13.1 | 10.8 | 8.9
Cardiff East / Aberthaw | Llanishen | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 35.4 | 35.3 | 35.2 | 35 | 34.8 | 34.6 | 18.6 | 18.5 | 18.3 | 18.1 | 17.9 | 17.8 | 17.7 | 17.6 | 17.6 | 17.6 | 17.5 | 16.7 | 15.7
Cardiff East / Aberthaw | Northcote St. | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.2 | 19.2 | 19.2 | 19.1 | 19.1 | 19 | 18.1 | 18 | 18 | 17.9 | 17.9 | 17.9 | 17.9 | 17.9 | 17.9 | 17.9 | 17.8 | 17.7 | 17.4
Cardiff East / Aberthaw | Northcote St. | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.2 | 19.2 | 19.2 | 19.1 | 19 | 18.8 | 17.7 | 17.6 | 17.4 | 17.3 | 17.1 | 17 | 16.9 | 16.7 | 16.4 | 16.2 | 15.9 | 15 | 13.9
Cardiff East / Aberthaw | Northcote St. | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.2 | 19.2 | 19 | 18.7 | 18.3 | 18 | 16.8 | 16.5 | 16.2 | 16 | 15.6 | 15.3 | 15.1 | 14.9 | 14.7 | 14.5 | 14.3 | 12.6 | 11
Cardiff East / Aberthaw | Northcote St. | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.2 | 19.2 | 19.2 | 19.1 | 19.1 | 19 | 18.1 | 18 | 18 | 17.9 | 17.8 | 17.8 | 17.8 | 17.7 | 17.7 | 17.7 | 17.7 | 17.3 | 16.8
Cardiff East / Aberthaw | Park Lane SWAE | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.8 | 19.8 | 19.8 | 19.7 | 19.7 | 19.6 | 19 | 19 | 18.9 | 18.9 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8
Cardiff East / Aberthaw | Park Lane SWAE | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.8 | 19.8 | 19.8 | 19.7 | 19.7 | 19.6 | 19 | 19 | 18.9 | 18.9 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.7
Cardiff East / Aberthaw | Park Lane SWAE | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.8 | 19.8 | 19.8 | 19.7 | 19.7 | 19.6 | 19 | 19 | 18.9 | 18.9 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.5 | 18.2
Cardiff East / Aberthaw | Park Lane SWAE | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.8 | 19.8 | 19.8 | 19.7 | 19.7 | 19.6 | 19 | 19 | 18.9 | 18.9 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8
Cardiff East / Aberthaw | Penarth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.1 | 5 | 4.9 | 4.7 | 4.6 | 4.4 | 4.4 | 4.2 | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 3.1 | 3 | 3 | 2.9 | 2.6 | 1.6
Cardiff East / Aberthaw | Penarth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.1 | 4.8 | 4.5 | 4.2 | 4 | 3.7 | 3.5 | 3.1 | 2.6 | 2.2 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Penarth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.1 | 4.6 | 4.2 | 3.9 | 3.5 | 3 | 2.7 | 2.1 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff East / Aberthaw | Penarth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.1 | 4.9 | 4.7 | 4.5 | 4.3 | 4 | 3.9 | 3.5 | 3.2 | 2.9 | 2.7 | 2.5 | 2.3 | 2.2 | 2.1 | 1.9 | 0 | 0 | 0
Cardiff East / Aberthaw | Rover Way Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 21.3 | 21.3 | 21.3 | 21.2 | 21.2 | 21.2 | 20.6 | 20.6 | 20.5 | 20.4 | 20.2 | 20 | 19.9 | 19.9 | 19.9 | 19.9 | 19.9 | 19.8 | 19.7
Cardiff East / Aberthaw | Rover Way Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 21.3 | 21.3 | 21.3 | 21.2 | 21.3 | 21.1 | 20.1 | 19.7 | 19.3 | 19 | 18.6 | 18.4 | 18.3 | 18.3 | 18.3 | 18.2 | 18.2 | 18 | 17.9
Cardiff East / Aberthaw | Rover Way Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 21.3 | 21.3 | 21.3 | 21.3 | 21.2 | 20.9 | 28.8 | 28.4 | 28.1 | 27.7 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 26.5 | 17.9 | 17.7 | 17.5
Cardiff East / Aberthaw | Rover Way Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 21.3 | 21.3 | 21.3 | 21.2 | 21.3 | 21.1 | 20.2 | 19.8 | 19.4 | 19.1 | 18.7 | 14 | 14 | 14 | 13.9 | 13.9 | 13.9 | 13.8 | 13.7
Cardiff East / Aberthaw | Sanatorium | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.3 | 11.3 | 11.3 | 11.2 | 11.1 | 11.1 | 10.7 | 10.6 | 10.5 | 10.4 | 10.4 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.2 | 10
Cardiff East / Aberthaw | Sanatorium | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.3 | 11.3 | 11 | 10.9 | 10.8 | 10.6 | 10.2 | 10.1 | 9.9 | 9.8 | 9.7 | 9.6 | 9.5 | 9.4 | 9.3 | 9.1 | 9 | 8.4 | 7.8
Cardiff East / Aberthaw | Sanatorium | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.3 | 11.2 | 10.8 | 10.6 | 10.3 | 10.1 | 9.6 | 9.3 | 9.1 | 9 | 8.8 | 8.6 | 8.5 | 8.4 | 8.3 | 8.2 | 8 | 7.1 | 6.2
Cardiff East / Aberthaw | Sanatorium | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 11.3 | 11.2 | 11.1 | 11 | 10.8 | 10.4 | 10.2 | 10.2 | 10.1 | 10.1 | 10 | 10 | 10 | 10 | 10 | 10 | 9.8 | 9.4
Cardiff East / Aberthaw | Sandon St. | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.5 | 19.5 | 19.5 | 19.5 | 19.4 | 19.4 | 18.7 | 18.6 | 18.6 | 18.6 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.4
Cardiff East / Aberthaw | Sandon St. | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.5 | 19.5 | 19.5 | 19.5 | 19.4 | 19.3 | 18.6 | 18.5 | 18.4 | 18.3 | 18.2 | 18.1 | 18.1 | 18 | 17.9 | 17.8 | 17.8 | 17.5 | 17.1
Cardiff East / Aberthaw | Sandon St. | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.5 | 19.5 | 19.5 | 19.5 | 19.2 | 19.1 | 18.2 | 18.1 | 18 | 17.8 | 17.7 | 17.6 | 17.5 | 17.5 | 17.4 | 17.4 | 17.3 | 16.8 | 16.4
Cardiff East / Aberthaw | Sandon St. | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.5 | 19.5 | 19.5 | 19.5 | 19.4 | 19.4 | 18.7 | 18.6 | 18.6 | 18.5 | 18.4 | 18.3 | 18.3 | 18.3 | 18.2 | 18.2 | 18.2 | 18.1 | 17.9
Cardiff East / Aberthaw | Ship Hill Barry | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.3 | 11.3 | 11.2 | 11.1 | 11.1 | 11 | 6.1 | 6 | 5.9 | 5.8 | 5.6 | 5.6 | 5.5 | 5.4 | 5.4 | 5.3 | 5.3 | 5 | 4.4
Cardiff East / Aberthaw | Ship Hill Barry | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.3 | 11.1 | 11 | 10.9 | 10.8 | 10.6 | 5.4 | 5.2 | 5 | 4.8 | 4.6 | 4.4 | 4.2 | 4 | 3.8 | 3.6 | 3.3 | 1.9 | 6.1
Cardiff East / Aberthaw | Ship Hill Barry | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.3 | 11.1 | 10.9 | 10.7 | 10.5 | 10.3 | 4.7 | 4.3 | 4 | 3.8 | 3.5 | 3.4 | 3.1 | 2.9 | 2.6 | 2.3 | 2 | 0 | 4.2
Cardiff East / Aberthaw | Ship Hill Barry | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 11.2 | 11.1 | 11.1 | 11 | 10.9 | 5.9 | 5.7 | 5.5 | 5.4 | 5.3 | 5.3 | 5.2 | 5.2 | 5.1 | 5 | 4.8 | 3.9 | 8.5
Cardiff East / Aberthaw | St Mellons | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.4 | 14.3 | 14.3 | 14.2 | 14.2 | 14.1 | 13.9 | 13.7 | 13.6 | 13.4 | 13.2 | 13.1 | 13.1 | 13.1 | 13 | 13 | 13 | 12.7 | 12.3
Cardiff East / Aberthaw | St Mellons | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.4 | 14.3 | 14.2 | 14.1 | 14 | 13.8 | 13.6 | 13.4 | 13.1 | 12.9 | 12.6 | 12.3 | 12.1 | 11.7 | 11.5 | 11.2 | 10.9 | 8.9 | 7.7
Cardiff East / Aberthaw | St Mellons | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.4 | 14.3 | 14.1 | 14 | 13.8 | 13.6 | 13.3 | 13 | 12.7 | 12.4 | 11.9 | 11.6 | 11.4 | 9.9 | 9.8 | 9.7 | 9.4 | 8 | 7.3
Cardiff East / Aberthaw | St Mellons | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.4 | 14.3 | 14.2 | 14.1 | 14 | 13.9 | 13.7 | 13.6 | 13.5 | 13.3 | 13.1 | 12.9 | 12.8 | 12.7 | 12.7 | 12.7 | 12.6 | 11.3 | 10.2
Cardiff East / Aberthaw | Sully Grid Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 25.4 | 25.4 | 25.3 | 25.2 | 25.1 | 25 | 24.7 | 24.6 | 24.5 | 24.4 | 24.3 | 24.2 | 24.2 | 24.1 | 24.1 | 24 | 24 | 23.8 | 23.4
Cardiff East / Aberthaw | Sully Grid Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 25.4 | 25.3 | 25.1 | 25 | 24.8 | 24.5 | 24.1 | 23.9 | 23.8 | 23.6 | 23.4 | 23.2 | 23.1 | 22.9 | 22.8 | 22.6 | 22.5 | 20.8 | 19.9
Cardiff East / Aberthaw | Sully Grid Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 25.4 | 25.2 | 25 | 24.8 | 24.5 | 24.2 | 23.8 | 23.6 | 23.4 | 23.2 | 23 | 22.8 | 21.2 | 21 | 20.9 | 20.7 | 20.5 | 19.4 | 18.5
Cardiff East / Aberthaw | Sully Grid Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 25.4 | 25.3 | 25.2 | 25.1 | 24.9 | 24.7 | 24.4 | 24.3 | 24.2 | 24 | 23.9 | 23.9 | 23.8 | 23.8 | 23.7 | 23.6 | 23.5 | 22.2 | 21.5
Cardiff East / Aberthaw | Taff Bank | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.5 | 16.5 | 16.4 | 16.4 | 16.3 | 16.2 | 15.8 | 15.7 | 15.7 | 15.6 | 15.5 | 15.4 | 15.2 | 15.1 | 15 | 14.8 | 14.7 | 14 | 13.4
Cardiff East / Aberthaw | Taff Bank | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.5 | 16.4 | 16.2 | 15.8 | 15.3 | 14.5 | 14.3 | 13.9 | 13.2 | 12.1 | 10.1 | 8.7 | 7.9 | 7.8 | 7.8 | 7.7 | 7.6 | 7.4 | 7
Cardiff East / Aberthaw | Taff Bank | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.5 | 16.4 | 15.8 | 15.2 | 14.3 | 13.8 | 13.1 | 12 | 10.1 | 7.5 | 7.1 | 6.9 | 6.8 | 6.8 | 6.7 | 6.7 | 6.6 | 6.7 | 6.2
Cardiff East / Aberthaw | Taff Bank | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.5 | 16.5 | 16.3 | 16.2 | 15.8 | 15.6 | 15.3 | 14.8 | 14.3 | 13.8 | 13.2 | 12.8 | 12.5 | 12.1 | 11.8 | 11.6 | 11.3 | 10.2 | 9.4
Cardiff East / Aberthaw | Trowbridge Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 18.1 | 18 | 17.8 | 17.7 | 17.6 | 17.4 | 17.2 | 17 | 16.9 | 21.9 | 21.6 | 21.3 | 21.1 | 20.8 | 20.5 | 20.2 | 20 | 19.7 | 19.2
Cardiff East / Aberthaw | Trowbridge Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 18.1 | 17.8 | 17.5 | 17.2 | 16.8 | 16.6 | 16.3 | 15.9 | 15.3 | 19.8 | 18.9 | 18.1 | 15.8 | 14.9 | 14.7 | 14.4 | 14.1 | 12.8 | 10.5
Cardiff East / Aberthaw | Trowbridge Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 18.1 | 17.6 | 17.2 | 16.7 | 16.2 | 15.8 | 15.2 | 14.4 | 13.5 | 17.7 | 16.4 | 15.3 | 12.9 | 12.6 | 12.3 | 12 | 11.7 | 8.1 | 6.6
Cardiff East / Aberthaw | Trowbridge Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 18.1 | 17.9 | 17.7 | 17.5 | 17.2 | 16.9 | 16.7 | 16.3 | 15.8 | 20.4 | 19.7 | 19.2 | 17.8 | 16.9 | 16.7 | 16.6 | 16.5 | 15.8 | 14.1
Cardiff East / Aberthaw | Wood Street | Primary Substation | 11 | Counterfactual | Headroom (MW) | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 31.7 | 31.6 | 31.6 | 31.5 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4
Cardiff East / Aberthaw | Wood Street | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 29.4 | 29.6 | 29.7 | 29.7 | 29.8 | 29.8 | 31.7 | 31.6 | 31.6 | 31.5 | 31.4 | 31.4 | 31.4 | 31.4 | 31.3 | 31.2 | 31.1 | 30.6 | 30.1
Cardiff East / Aberthaw | Wood Street | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 29.4 | 29.7 | 29.9 | 30 | 30.1 | 30.1 | 31.7 | 31.6 | 31.5 | 31.3 | 31.1 | 30.9 | 30.8 | 30.7 | 30.6 | 30.5 | 30.4 | 29.6 | 28.9
Cardiff East / Aberthaw | Wood Street | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 29.4 | 29.5 | 29.5 | 29.5 | 29.6 | 29.6 | 31.7 | 31.6 | 31.6 | 31.5 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4
Margam (Grange) | Caerau Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.8 | 13.6 | 13.2 | 12.9 | 12.6 | 12.2 | 11.4 | 7.7 | 6.4 | 4.9 | 3.2 | 1.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Caerau Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.8 | 13.1 | 12.5 | 11.9 | 11.1 | 9.4 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Caerau Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.8 | 12.8 | 11.9 | 11.2 | 9.4 | 7.3 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Caerau Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.8 | 13.4 | 13 | 12.6 | 12.1 | 10.6 | 8.6 | 4.1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Llynfi | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.8 | 13.6 | 13.3 | 13 | 12.6 | 12.2 | 11.3 | 7.7 | 6.4 | 4.9 | 3.2 | 1.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Llynfi | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.8 | 13.2 | 12.5 | 12 | 11.2 | 9.5 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Llynfi | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.8 | 12.9 | 12 | 11.3 | 9.5 | 7.3 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Llynfi | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.8 | 13.5 | 13 | 12.6 | 12.1 | 10.6 | 8.6 | 4.1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Ogmore Vale | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.2 | 11.2 | 11.1 | 11.1 | 11 | 10.9 | 10.8 | 7.8 | 6.4 | 5 | 3.2 | 1.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Ogmore Vale | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.2 | 11.1 | 11 | 10.9 | 10.7 | 9.5 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Ogmore Vale | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.2 | 11 | 10.9 | 10.7 | 9.5 | 7.4 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Margam (Grange) | Ogmore Vale | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.2 | 11.2 | 11.1 | 11 | 10.9 | 10.7 | 8.7 | 4.1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Brawdy | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.3 | 3.2 | 2.9 | 2.7 | 2.6 | 2.4 | 8.9 | 8.9 | 8.9 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.7 | 8.7 | 8.7 | 8.7 | 6.8
Pembroke | Brawdy | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.3 | 2.9 | 2.3 | 1.9 | 1.5 | 1 | 8.7 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Brawdy | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.3 | 2.7 | 1.8 | 1.2 | 0.6 | 0 | 8.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Brawdy | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.3 | 3.1 | 2.7 | 2.5 | 2.2 | 1.9 | 8.8 | 8.8 | 8.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Broadfield | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 3.9 | 3.6 | 3.3 | 3.1 | 2.8 | 6.2 | 5.4 | 4.5 | 3.6 | 2.4 | 1.6 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0
Pembroke | Broadfield | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 3.6 | 2.9 | 2.4 | 1.7 | 0.9 | 3.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Broadfield | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 3.4 | 2.5 | 1.8 | 0.8 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Broadfield | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 3.9 | 3.4 | 3 | 2.6 | 2 | 5.2 | 4.3 | 3.5 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Fishguard | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.3 | 3.1 | 2.9 | 2.7 | 2.5 | 2.4 | 3.1 | 3.1 | 3 | 2.9 | 2.6 | 2.4 | 2.1 | 2.8 | 2.4 | 2 | 1.7 | 1.5 | 1.6
Pembroke | Fishguard | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.3 | 2.9 | 2.3 | 1.9 | 1.5 | 1 | 2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Fishguard | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.3 | 2.7 | 1.8 | 1.2 | 0.6 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Fishguard | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.3 | 3.1 | 2.7 | 2.5 | 2.2 | 1.9 | 2.7 | 2.3 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Golden Hill Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 37.4 | 35.3 | 33.8 | 31.7 | 30.4 | 29.2 | 29.7 | 26.4 | 23 | 18.9 | 13.4 | 9.2 | 6.1 | 4.7 | 2.2 | 0 | 0 | 0 | 0
Pembroke | Golden Hill Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 37.4 | 33 | 28.9 | 26.5 | 20.7 | 14.1 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Golden Hill Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 37.4 | 31.7 | 26.8 | 22.2 | 15.5 | 8.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Golden Hill Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 37.4 | 34.8 | 31.7 | 29.8 | 25.3 | 20 | 17.5 | 9.8 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Golden Hill Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.9 | 10.7 | 10.6 | 10.5 | 10.3 | 10.1 | 8.1 | 7.7 | 7.5 | 7.3 | 7 | 6.7 | 6.5 | 6.3 | 6 | 5.7 | 5.5 | 4.6 | 3.6
Pembroke | Golden Hill Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.9 | 10.5 | 10.1 | 9.9 | 9.1 | 8.1 | 5.6 | 4.2 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Golden Hill Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.9 | 10.3 | 9.8 | 9 | 8.1 | 7 | 4.3 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Golden Hill Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.9 | 10.7 | 10.4 | 10.2 | 9.5 | 8.7 | 6.2 | 5.2 | 4.6 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Haverfordwest Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 31.8 | 30 | 28.8 | 27 | 25.9 | 24.9 | 30.1 | 26.7 | 23.3 | 19.1 | 13.6 | 9.3 | 6.2 | 4.8 | 2.2 | 0 | 0 | 0 | 0
Pembroke | Haverfordwest Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 31.8 | 28.1 | 24.6 | 22.5 | 17.6 | 11.9 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Haverfordwest Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 31.8 | 26.9 | 22.8 | 18.9 | 13.2 | 7.2 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Haverfordwest Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 31.8 | 29.6 | 26.9 | 25.3 | 21.5 | 17 | 17.7 | 9.9 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Haverfordwest Power Stn | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.8 | 10.7 | 10.6 | 10.5 | 10.4 | 10.4 | 10.3 | 9.9 | 9.5 | 8.8 | 7.8 | 7 | 6.3 | 5.7 | 5.1 | 4.4 | 3.9 | 2.6 | 1
Pembroke | Haverfordwest Power Stn | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.8 | 10.6 | 10.4 | 10.2 | 9.5 | 8.7 | 7.4 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Haverfordwest Power Stn | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.8 | 10.5 | 10.2 | 9.9 | 9.1 | 8.2 | 6.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Haverfordwest Power Stn | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.8 | 10.7 | 10.5 | 10.4 | 9.9 | 9.2 | 8.2 | 6.8 | 5.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Merlins Bridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.7 | 9.6 | 9.5 | 9.3 | 9.2 | 9 | 8.7 | 8.4 | 8 | 7.6 | 7 | 6.6 | 6.4 | 6.2 | 6 | 5.7 | 5.6 | 4.5 | 3.2
Pembroke | Merlins Bridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.7 | 9.4 | 9.2 | 8.9 | 8.5 | 8 | 6.3 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Merlins Bridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.7 | 9.3 | 8.9 | 8.5 | 8 | 7.4 | 6.3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Merlins Bridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.7 | 9.5 | 9.3 | 9.1 | 8.8 | 8.4 | 8 | 7.4 | 6.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Milford Haven | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 4 | 4 | 3.9 | 3.9 | 3.9 | 3.7 | 3.6 | 3.6 | 3.5 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3 | 2.4 | 2.4 | 1.6 | 0
Pembroke | Milford Haven | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 4 | 3.9 | 3.8 | 3.7 | 3.6 | 2.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Milford Haven | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 3.9 | 3.8 | 3.6 | 3.5 | 3.4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Milford Haven | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 4 | 3.9 | 3.9 | 3.7 | 3.7 | 3.3 | 2.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Milford Haven Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 10.6 | 10.6 | 10.4 | 10.4 | 10.2 | 10 | 7.3 | 6.8 | 6.4 | 5.8 | 5.1 | 4.5 | 4.1 | 3.9 | 2.2 | 0 | 0 | 0 | 0
Pembroke | Milford Haven Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 10.6 | 10.4 | 10.2 | 9.9 | 8.9 | 7.7 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Milford Haven Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 10.6 | 10.3 | 9.7 | 8.8 | 7.7 | 6.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Milford Haven Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 10.6 | 10.5 | 10.3 | 10.1 | 9.2 | 8.1 | 4.3 | 2.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Nevern | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.3 | 3.2 | 2.9 | 2.7 | 2.6 | 2.4 | 3.2 | 3.1 | 3 | 2.9 | 2.6 | 2.4 | 2.1 | 2.8 | 2.4 | 2 | 1.7 | 1.5 | 1.6
Pembroke | Nevern | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.3 | 2.9 | 2.3 | 1.9 | 1.5 | 1 | 2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Nevern | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.3 | 2.7 | 1.8 | 1.2 | 0.6 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Nevern | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.3 | 3.1 | 2.7 | 2.5 | 2.2 | 1.9 | 2.7 | 2.3 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Neyland | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.1 | 5.1 | 5 | 4.9 | 4.9 | 4.8 | 4.6 | 4.4 | 4.3 | 4 | 3.7 | 3.5 | 3.3 | 3.1 | 3 | 2.5 | 2.5 | 1.6 | 0
Pembroke | Neyland | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.1 | 5 | 4.9 | 4.7 | 4.5 | 4.4 | 3.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Neyland | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.1 | 4.9 | 4.7 | 4.5 | 4.3 | 4.1 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Neyland | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.1 | 5 | 4.9 | 4.9 | 4.7 | 4.6 | 4.3 | 2.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Penblewin | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.3 | 2.3 | 2.2 | 1.3 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Penblewin | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.3 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Penblewin | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.3 | 1.4 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Penblewin | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.3 | 2.3 | 1.3 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Davids | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.3 | 3.1 | 2.9 | 2.7 | 2.5 | 2.4 | 5.7 | 5.7 | 5.7 | 5.7 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Pembroke | St Davids | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.3 | 2.9 | 2.3 | 1.9 | 1.5 | 1 | 4.5 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Davids | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.3 | 2.7 | 1.8 | 1.2 | 0.6 | 0 | 4.5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Davids | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.3 | 3.1 | 2.7 | 2.5 | 2.2 | 1.9 | 5.7 | 4.5 | 4.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Florence | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 3.9 | 3.6 | 3.3 | 3.1 | 2.8 | 5.5 | 4.8 | 4 | 3.1 | 2.1 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Florence | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 3.6 | 2.9 | 2.4 | 1.7 | 0.9 | 3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Florence | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 3.4 | 2.4 | 1.8 | 0.8 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Florence | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 3.8 | 3.3 | 3 | 2.5 | 2 | 4.7 | 3.9 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Twynells | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.7 | 1.7 | 1.7 | 1.6 | 1.6 | 2 | 3.5 | 3.4 | 3.3 | 3 | 2.7 | 2.4 | 2.3 | 2.2 | 2.1 | 2 | 1.8 | 1 | 0
Pembroke | St Twynells | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.7 | 1.7 | 1.6 | 1.6 | 1.3 | 0.9 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Twynells | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.7 | 1.6 | 1.6 | 1.7 | 1.4 | 0.9 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | St Twynells | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.7 | 1.7 | 1.6 | 1.6 | 1.4 | 1 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Steynton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.6 | 8.6 | 8.5 | 8.5 | 8.4 | 8.2 | 6 | 5.6 | 5.4 | 5 | 4.6 | 4.2 | 3.9 | 3.7 | 3.6 | 2.4 | 2.4 | 1.6 | 0
Pembroke | Steynton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.6 | 8.5 | 8.4 | 8.2 | 7.4 | 6.4 | 2.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Steynton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.6 | 8.4 | 8 | 7.3 | 6.3 | 5.1 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Steynton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.6 | 8.6 | 8.4 | 8.3 | 7.5 | 6.5 | 3.4 | 2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Tenby | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 3.9 | 3.6 | 3.3 | 3.1 | 2.8 | 5.4 | 5.4 | 4.5 | 3.6 | 2.4 | 1.5 | 0.9 | 0.5 | 0 | 0 | 0 | 0 | 0
Pembroke | Tenby | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 3.6 | 2.9 | 2.4 | 1.7 | 0.9 | 3.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Tenby | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 3.4 | 2.5 | 1.8 | 0.8 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pembroke | Tenby | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 3.8 | 3.4 | 3 | 2.6 | 2 | 5.2 | 4.3 | 3.5 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Bridgend Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 38 | 37.7 | 37.3 | 37 | 36.7 | 36.3 | 35.4 | 34.6 | 33.8 | 32.9 | 31.9 | 31.2 | 30.7 | 30.4 | 30 | 29.7 | 29.1 | 23.2 | 19.1
Pyle | Bridgend Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 38 | 37.3 | 36.6 | 36 | 35.2 | 34.3 | 32.5 | 31 | 29.5 | 27.9 | 26 | 24.2 | 22.7 | 20.1 | 15.9 | 11.3 | 9 | 0 | 0
Pyle | Bridgend Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 38 | 37 | 35.9 | 35 | 33.8 | 32.4 | 30.3 | 28.5 | 26.6 | 24.6 | 22.6 | 20.9 | 12.2 | 6.7 | 1.1 | 0 | 0 | 0 | 0
Pyle | Bridgend Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 38 | 37.5 | 37.1 | 36.7 | 36.2 | 35.5 | 34.3 | 33.3 | 32.5 | 31.5 | 30.2 | 29.4 | 28.8 | 28.2 | 25.8 | 21.9 | 17.9 | 9.4 | 4.2
Pyle | Bridgend Trading Estate | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.1 | 19.1 | 19.1 | 19 | 19 | 18.9 | 18.5 | 18.4 | 18.3 | 18.2 | 18.1 | 18 | 18 | 17.9 | 17.9 | 17.8 | 17.6 | 14.6 | 14.3
Pyle | Bridgend Trading Estate | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.1 | 19.1 | 19.1 | 18.9 | 18.7 | 18.5 | 18 | 17.8 | 17.7 | 17.5 | 17.3 | 17.2 | 17 | 16.3 | 14.3 | 11.9 | 11.1 | 10.4 | 9.6
Pyle | Bridgend Trading Estate | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.1 | 19.1 | 18.9 | 18.6 | 18.4 | 18.1 | 17.5 | 17.2 | 17 | 16.7 | 16.5 | 16.3 | 15.4 | 13.3 | 10.7 | 9.9 | 9.8 | 8.7 | 7.7
Pyle | Bridgend Trading Estate | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.1 | 19.1 | 19.1 | 19 | 19 | 18.8 | 18.3 | 18.1 | 18 | 17.9 | 17.8 | 17.7 | 17.6 | 17.6 | 16.6 | 14.4 | 12.1 | 11.7 | 11.2
Pyle | Litchard | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.7 | 19.5 | 19.3 | 19.2 | 19 | 18.8 | 18.6 | 18.3 | 18 | 17.6 | 17.3 | 17 | 16.9 | 16.7 | 16.6 | 16.5 | 16.3 | 14.7 | 13.8
Pyle | Litchard | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.7 | 19.3 | 18.9 | 18.7 | 18.4 | 18 | 17.5 | 17 | 16.5 | 16 | 15.4 | 14.8 | 14.3 | 13.5 | 12.2 | 11 | 10.5 | 7.9 | 5.8
Pyle | Litchard | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.7 | 19.2 | 18.6 | 18.3 | 17.8 | 17.3 | 16.6 | 16 | 15.3 | 14.7 | 14 | 13.5 | 12.6 | 11.3 | 10.1 | 9.7 | 9.3 | 6.4 | 4.5
Pyle | Litchard | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.7 | 19.5 | 19.2 | 19 | 18.8 | 18.5 | 18.1 | 17.8 | 17.5 | 17.1 | 16.7 | 16.4 | 16.1 | 15.9 | 15.4 | 14.5 | 13.8 | 12.4 | 10.6
Pyle | Llangewydd | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.1 | 9.9 | 9.7 | 9.5 | 9.3 | 10.1 | 11.5 | 11.2 | 11 | 9.6 | 9.3 | 9 | 8.8 | 8.6 | 8.5 | 8.3 | 8.1 | 6.8 | 3.9
Pyle | Llangewydd | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.1 | 9.6 | 9.1 | 8.7 | 8.3 | 8.9 | 9.6 | 9 | 8.3 | 7.3 | 6.3 | 5.2 | 4.3 | 3.2 | 2.3 | 1.4 | 0 | 0 | 0
Pyle | Llangewydd | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.1 | 9.3 | 8.7 | 8.1 | 7.4 | 7.7 | 9 | 8.2 | 7.2 | 6.2 | 5 | 4.1 | 2.8 | 0.8 | 0 | 0 | 0 | 0 | 0
Pyle | Llangewydd | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.1 | 9.8 | 9.5 | 9.3 | 8.9 | 9.6 | 11.1 | 10.9 | 9.6 | 9.3 | 8.7 | 8.3 | 7.9 | 7.6 | 6.8 | 5.9 | 5 | 0.9 | 0
Pyle | Nottage | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Nottage | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Nottage | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Nottage | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Pyle 132/33 | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 24.3 | 24.1 | 23.8 | 9.7 | 9.4 | 10.2 | 30.4 | 29.8 | 29.1 | 28.4 | 27.4 | 26.8 | 26.3 | 25.9 | 25.5 | 25.1 | 24.8 | 20.8 | 16
Pyle | Pyle 132/33 | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 24.3 | 23.8 | 23.2 | 22.8 | 22.2 | 22.7 | 42.5 | 41.3 | 39.9 | 55.4 | 53.7 | 52 | 50.4 | 48.6 | 47.2 | 45.7 | 44.2 | 26.5 | 21.7
Pyle | Pyle 132/33 | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 24.3 | 23.5 | 22.8 | 22.2 | 21.3 | 21.5 | 41 | 39.5 | 37.9 | 53.1 | 51.1 | 49.5 | 47 | 41.4 | 38.9 | 36.1 | 32.7 | 23.7 | 20
Pyle | Pyle 132/33 | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 24.3 | 24 | 23.7 | 23.4 | 23 | 23.5 | 38.3 | 37.5 | 36.8 | 52.9 | 51.6 | 50.8 | 49.9 | 49.2 | 48.1 | 46.8 | 44.7 | 34.6 | 30.4
Pyle | Pyle Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.8 | 14.7 | 14.6 | 9.7 | 9.4 | 10.2 | 13.6 | 13.3 | 13 | 12.5 | 12 | 11.6 | 11.3 | 11.1 | 10.8 | 10.6 | 10.3 | 8.8 | 5.8
Pyle | Pyle Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.8 | 14.6 | 14.4 | 14.2 | 13.9 | 13.6 | 12.7 | 12 | 11.2 | 10.3 | 9.3 | 8.2 | 7.2 | 6 | 5.1 | 4.2 | 3.3 | 0 | 0
Pyle | Pyle Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.8 | 14.5 | 14.2 | 13.9 | 13.5 | 13 | 12 | 11.1 | 10.2 | 9.1 | 7.8 | 6.8 | 5.7 | 2.7 | 1.4 | 0 | 0 | 0 | 0
Pyle | Pyle Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.8 | 14.7 | 14.6 | 14.4 | 14.2 | 14 | 13.3 | 12.9 | 12.5 | 11.9 | 11.2 | 10.6 | 10 | 9.4 | 8.9 | 8.1 | 6.6 | 1.3 | 0
Pyle | Schwyll | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.2 | 6.2 | 6.1 | 6.1 | 6 | 6 | 5.8 | 5.6 | 5.3 | 5 | 4.6 | 4.4 | 4.2 | 4.1 | 3.9 | 3.8 | 3.7 | 2.8 | 1.1
Pyle | Schwyll | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.2 | 6.1 | 6 | 5.9 | 5.8 | 5.6 | 5.1 | 4.6 | 4 | 3.3 | 2.5 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Schwyll | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.2 | 6.1 | 6 | 5.9 | 5.7 | 5.5 | 5 | 4.4 | 3.8 | 3.1 | 2.3 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Pyle | Schwyll | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.2 | 6.2 | 6.1 | 6 | 6 | 5.8 | 5.6 | 5.3 | 5.1 | 4.8 | 4.3 | 4 | 3.7 | 3.5 | 3 | 2.5 | 2 | 0 | 0
Pyle | Waterton Industrial Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 27.9 | 26 | 25.9 | 25.9 | 25.8 | 25.7 | 25.2 | 25.1 | 25 | 24.8 | 24.7 | 24.6 | 24.5 | 24.4 | 24.4 | 24.3 | 24.2 | 22.7 | 22.2
Pyle | Waterton Industrial Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 27.9 | 26 | 25.8 | 25.7 | 25.5 | 25.3 | 19.5 | 19.2 | 18.9 | 18.6 | 18.2 | 17.9 | 17.6 | 17.1 | 16 | 14.6 | 14.3 | 12.2 | 11
Pyle | Waterton Industrial Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 27.9 | 25.9 | 25.6 | 25.4 | 25.2 | 24.9 | 24.3 | 24 | 23.6 | 23.2 | 22.8 | 22.6 | 21.2 | 19.3 | 17.9 | 17.6 | 17.4 | 15.8 | 14.7
Pyle | Waterton Industrial Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 27.9 | 26 | 25.9 | 25.8 | 25.7 | 25.6 | 25.1 | 24.9 | 24.8 | 24.6 | 24.4 | 24.3 | 24.2 | 24.1 | 23.6 | 22.6 | 21.7 | 20.2 | 19.3
Rassau | Abergavenny | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 41.7 | 40.5 | 39.1 | 38 | 36.5 | 34.1 | 36.2 | 31.1 | 24.6 | 17.5 | 8.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abergavenny | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 41.7 | 39.4 | 36.2 | 33.1 | 27.6 | 21 | 21.9 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abergavenny | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 41.7 | 38.8 | 34.5 | 32 | 24.7 | 15.9 | 17.8 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abergavenny | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 41.7 | 40.2 | 38.2 | 36.5 | 33.7 | 28.9 | 31.5 | 26.2 | 20.5 | 13.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abergavenny Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.1 | 28.8 | 28.5 | 28.3 | 28.1 | 27.7 | 27.2 | 26.3 | 25.3 | 24.2 | 22.8 | 21.9 | 21.4 | 21 | 17.6 | 13.9 | 10.1 | 0 | 0
Rassau | Abergavenny Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.1 | 28.5 | 27.9 | 27.4 | 26.8 | 25.9 | 24.7 | 23.3 | 21.7 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abergavenny Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.1 | 28.3 | 27.5 | 27 | 26 | 24.9 | 23.4 | 21.8 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abergavenny Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.1 | 28.7 | 28.3 | 28 | 27.6 | 27 | 26.3 | 25.4 | 24.6 | 23.5 | 21.8 | 18.1 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abersychan | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11 | 10.9 | 10.8 | 10.7 | 10.6 | 10.5 | 10.3 | 10 | 9.7 | 9.4 | 9 | 8.7 | 8.5 | 8.4 | 8.3 | 8.2 | 8.1 | 5.8 | 0
Rassau | Abersychan | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11 | 10.8 | 10.5 | 10.3 | 10 | 9.8 | 9.3 | 8.8 | 8.2 | 7.6 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abersychan | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11 | 10.7 | 10.3 | 10 | 9.7 | 9.3 | 8.7 | 8.1 | 7.5 | 6.8 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Abersychan | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11 | 10.9 | 10.7 | 10.6 | 10.5 | 10.3 | 10 | 9.7 | 9.4 | 9 | 8.5 | 8.2 | 7.9 | 7.7 | 7.5 | 7.3 | 7.1 | 0 | 0
Rassau | Abertillery | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.7 | 10.6 | 10.5 | 10.4 | 10.4 | 10.3 | 9.9 | 9.8 | 9.6 | 9.3 | 9 | 8.8 | 8.7 | 8.6 | 8.5 | 8.4 | 8.3 | 7.5 | 6.7
Rassau | Abertillery | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.7 | 10.5 | 10.3 | 9.8 | 9.8 | 9.6 | 9.3 | 8.8 | 8.4 | 7.9 | 7.3 | 6.8 | 6.3 | 5.7 | 5.2 | 4.7 | 4.2 | 1.1 | 0
Rassau | Abertillery | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.7 | 10.4 | 9.8 | 9.8 | 9.5 | 9.2 | 8.7 | 8.2 | 7.6 | 7 | 6.3 | 5.7 | 5 | 4.5 | 4.2 | 3.8 | 3.4 | 0 | 0
Rassau | Abertillery | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.7 | 10.6 | 10.4 | 10.3 | 10.2 | 9.8 | 9.8 | 9.5 | 9.3 | 9 | 8.6 | 8.3 | 8 | 7.8 | 7.7 | 7.5 | 7.4 | 5.8 | 4.2
Rassau | Blaenavon | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.2 | 11.2 | 11.1 | 11.1 | 11 | 11 | 10.9 | 10.9 | 10.8 | 10.8 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.6 | 0 | 0
Rassau | Blaenavon | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.2 | 11.1 | 11 | 10.9 | 10.8 | 10.7 | 10.6 | 10.6 | 10.5 | 10.5 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Blaenavon | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.2 | 11.1 | 10.9 | 10.8 | 10.7 | 10.6 | 10.5 | 10.5 | 9.8 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Blaenavon | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.2 | 11.1 | 11.1 | 11 | 10.9 | 10.8 | 10.8 | 10.8 | 10.7 | 10.7 | 10.6 | 10.6 | 10.6 | 10.6 | 10.5 | 9.7 | 9 | 0 | 0
Rassau | Brecon | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.3 | 9.8 | 8.8 | 8.1 | 7.1 | 5.3 | 9 | 6.9 | 4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Brecon | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.3 | 9.2 | 7 | 4.7 | 0 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Brecon | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.3 | 8.9 | 6 | 4.4 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Brecon | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.3 | 9.6 | 8.3 | 7 | 5.1 | 1.4 | 7 | 4.8 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Brynmawr | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Brynmawr | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Brynmawr | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Brynmawr | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Builth Wells | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.2 | 9.1 | 8.9 | 8.2 | 7.1 | 5.3 | 6.7 | 5 | 3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Builth Wells | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.2 | 9 | 7 | 4.8 | 0 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Builth Wells | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.2 | 8.9 | 6 | 4.4 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Builth Wells | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.2 | 9.1 | 8.3 | 7.1 | 5.1 | 1.4 | 5.3 | 3.6 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Crickhowell | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.1 | 10.1 | 10 | 10 | 9.4 | 7.6 | 8.4 | 6.4 | 3.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Crickhowell | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.1 | 10 | 9.3 | 7 | 2.6 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Crickhowell | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.1 | 10 | 8.2 | 6.5 | 0.8 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Crickhowell | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.1 | 10.1 | 10 | 9.3 | 7.3 | 3.6 | 6.5 | 4.4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Crumlin | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 42.1 | 41.7 | 41.2 | 40.8 | 40.3 | 39.8 | 37.9 | 36.5 | 30.3 | 28.3 | 25.8 | 24.1 | 23.1 | 22.2 | 21.5 | 20.8 | 21.9 | 44.2 | 39.8
Rassau | Crumlin | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 42.1 | 39.1 | 37.6 | 32.8 | 31.3 | 29.3 | 27.3 | 23.8 | 20.3 | 16.4 | 12.3 | 8.4 | 38.5 | 34.6 | 29.7 | 22.3 | 16.3 | 0 | 0
Rassau | Crumlin | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 42.1 | 40.6 | 39.1 | 38 | 33 | 30.7 | 22.1 | 17.9 | 13.6 | 8.8 | 2.2 | 0 | 19.1 | 11.3 | 8.2 | 3.1 | 1.6 | 0 | 0
Rassau | Crumlin | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 42.1 | 41.5 | 40.8 | 40.3 | 39.6 | 38.6 | 35.9 | 34.3 | 27.2 | 24.6 | 21 | 18.3 | 46.2 | 33.2 | 32.1 | 29.7 | 26.6 | 15 | 5
Rassau | Crumlin Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 19.9 | 19.9 | 19.7 | 19.6 | 19.5 | 19.3 | 18.5 | 18.1 | 17.8 | 17.5 | 17.1 | 16.8 | 16.6 | 16.5 | 16.4 | 16.3 | 16.1 | 14.4 | 13.3
Rassau | Crumlin Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 19.9 | 19.7 | 19.4 | 19.2 | 18.8 | 18.4 | 17.3 | 16.7 | 16.2 | 15.6 | 12.3 | 8.3 | 13.7 | 12.9 | 11.8 | 8.2 | 7.1 | 0 | 0
Rassau | Crumlin Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 19.9 | 19.6 | 19.2 | 18.9 | 18.4 | 17.8 | 16.7 | 16.2 | 13.6 | 8.8 | 2.2 | 0 | 12.4 | 8.3 | 7.3 | 3.1 | 1.6 | 0 | 0
Rassau | Crumlin Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 19.9 | 19.8 | 19.6 | 19.5 | 19.2 | 18.8 | 17.9 | 17.6 | 17.3 | 16.9 | 16.4 | 16.1 | 15.8 | 15.4 | 14.9 | 13.1 | 12.1 | 8.6 | 5
Rassau | Cwmfelinfach | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.7 | 7.7 | 7.6 | 7.6 | 7.6 | 7.5 | 7.2 | 7.1 | 6.9 | 6.8 | 6.5 | 6.4 | 6.3 | 6.2 | 6.2 | 6.1 | 6 | 5.5 | 4.7
Rassau | Cwmfelinfach | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.7 | 7.6 | 7.6 | 7.5 | 7.4 | 7.3 | 6.9 | 6.6 | 6.3 | 6 | 5.7 | 5.4 | 5 | 4.4 | 3.6 | 2.7 | 0 | 0 | 0
Rassau | Cwmfelinfach | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.7 | 7.6 | 7.5 | 7.5 | 7.3 | 7.2 | 6.7 | 6.5 | 6.1 | 5.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Cwmfelinfach | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.7 | 7.6 | 7.6 | 7.6 | 7.5 | 7.4 | 7.1 | 7 | 6.8 | 6.7 | 6.3 | 6.1 | 5.9 | 5.7 | 5.6 | 5.5 | 2.7 | 1 | 0
Rassau | Ebbw Vale Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 30.6 | 30.5 | 30.2 | 30.1 | 29.9 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2 | 8.9
Rassau | Ebbw Vale Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 30.6 | 30.2 | 29.7 | 29.4 | 29.1 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7 | 6.7 | 6 | 5.3 | 4.1 | 0 | 0
Rassau | Ebbw Vale Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 30.6 | 30 | 29.5 | 29 | 28.4 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 5.5 | 4.9 | 3 | 1.6 | 0 | 0
Rassau | Ebbw Vale Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 30.6 | 30.4 | 30.1 | 29.9 | 29.6 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Ebbw Vale Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 25.6 | 25.6 | 25.5 | 25.4 | 25.3 | 25.2 | 18.1 | 17.8 | 10.5 | 10.2 | 9.9 | 9.8 | 9.6 | 9.6 | 9.5 | 9.4 | 11.6 | 11 | 10.3
Rassau | Ebbw Vale Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 25.6 | 18.1 | 17.9 | 10.4 | 10.2 | 10 | 10.1 | 9.5 | 8.9 | 8.5 | 8 | 6.8 | 7.1 | 6.7 | 6.3 | 5.9 | 7.8 | 0 | 0
Rassau | Ebbw Vale Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 25.6 | 25.4 | 25 | 24.8 | 17.2 | 16.7 | 9.3 | 8.6 | 8.1 | 7.2 | 2.2 | 0 | 6 | 5.7 | 5.4 | 3.1 | 1.6 | 0 | 0
Rassau | Ebbw Vale Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 25.6 | 25.5 | 25.4 | 25.3 | 25.1 | 24.9 | 17.8 | 17.4 | 9.8 | 9.4 | 9 | 8.8 | 8.5 | 8.3 | 8.2 | 8.1 | 10.3 | 4.1 | 0
Rassau | Glasbury | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8 | 7.9 | 7.8 | 7.7 | 6.9 | 5.1 | 6.8 | 6 | 5 | 4 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Glasbury | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8 | 7.8 | 6.8 | 4.6 | 0 | 0 | 4.5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Glasbury | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8 | 7.8 | 5.8 | 4.3 | 0 | 0 | 3.9 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Glasbury | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8 | 7.9 | 7.7 | 6.8 | 4.9 | 1.3 | 6.1 | 5.3 | 4.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Llandrindod Wells | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.5 | 1.3 | 0.6 | 0 | 0 | 0 | 4 | 2.8 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Llandrindod Wells | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Llandrindod Wells | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Llandrindod Wells | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.5 | 1.2 | 0 | 0 | 0 | 0 | 2.9 | 1.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Monmouth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11 | 10.5 | 10.3 | 10.1 | 9.8 | 9.5 | 7.2 | 6.4 | 5.3 | 4.2 | 2.7 | 1.7 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0
Rassau | Monmouth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11 | 10.3 | 9.8 | 9.5 | 8.9 | 8.3 | 5 | 3.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Monmouth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11 | 10.2 | 9.6 | 9.2 | 8.4 | 7.4 | 3.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Monmouth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11 | 10.5 | 10.1 | 9.9 | 9.5 | 9 | 6.3 | 5.2 | 4.3 | 3.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Panteg 132/66 | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 28.8 | 28.8 | 28.9 | 29.1 | 29 | 28.4 | 28 | 28.2 | 28.3 | 28.1 | 26.6 | 22.7 | 19.8 | 17.7 | 15.7 | 13.6 | 10 | 0 | 0
Rassau | Panteg 132/66 | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 28.8 | 29 | 28.8 | 28.1 | 26.8 | 21.4 | 28.1 | 26.9 | 20 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Panteg 132/66 | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 28.8 | 29.1 | 28.3 | 27.3 | 25.1 | 16.2 | 27.1 | 25.3 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Panteg 132/66 | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 28.8 | 28.8 | 29.1 | 29 | 28.3 | 27.2 | 28.2 | 28.1 | 27.8 | 27 | 22.2 | 15.8 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Pengam Grid | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.5 | 29.3 | 29 | 28.8 | 28.6 | 28.4 | 28.1 | 27.8 | 27.4 | 26.9 | 25.6 | 23.9 | 22.9 | 22.1 | 21.3 | 20.7 | 21.8 | 23 | 21.5
Rassau | Pengam Grid | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.5 | 28.9 | 28.3 | 28 | 27.6 | 27.2 | 26.7 | 23.7 | 20.1 | 16.3 | 12.2 | 8.3 | 22.4 | 21.5 | 20 | 18.6 | 16.1 | 0 | 0
Rassau | Pengam Grid | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.5 | 28.7 | 27.9 | 27.4 | 26.7 | 26.1 | 21.9 | 17.8 | 13.5 | 8.8 | 2.2 | 0 | 17 | 11.2 | 8.2 | 3.1 | 1.6 | 0 | 0
Rassau | Pengam Grid | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.5 | 29.2 | 28.8 | 28.6 | 28.3 | 28 | 27.6 | 27.2 | 26.8 | 24.5 | 20.8 | 18.2 | 22.9 | 21.9 | 21.6 | 21.4 | 21.1 | 16 | 4.9
Rassau | Pontllanffraith | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.3 | 10.1 | 10 | 9.8 | 9.7 | 9.5 | 9.3 | 9 | 8.7 | 8.4 | 8 | 7.7 | 7.6 | 7.5 | 7.4 | 7.3 | 7.1 | 5.7 | 4.7
Rassau | Pontllanffraith | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.3 | 9.9 | 9.6 | 9.3 | 9.1 | 8.7 | 8.3 | 7.8 | 7.4 | 6.8 | 6.2 | 5.6 | 5.1 | 4.4 | 3.6 | 2.7 | 0 | 0 | 0
Rassau | Pontllanffraith | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.3 | 9.8 | 9.3 | 9 | 8.6 | 8.1 | 7.5 | 6.9 | 6.3 | 5.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Pontllanffraith | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.3 | 10.1 | 9.9 | 9.7 | 9.5 | 9.3 | 9 | 8.7 | 8.4 | 8.1 | 7.4 | 6.9 | 6.4 | 5.9 | 5.7 | 5.6 | 2.8 | 1 | 0
Rassau | Rassau West Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 30.5 | 30 | 29.9 | 29.8 | 29.8 | 29.7 | 29.9 | 29.8 | 29.8 | 29.7 | 24.2 | 24.2 | 24 | 23.9 | 23.8 | 23.4 | 21.9 | 21.1 | 20.5
Rassau | Rassau West Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 30.5 | 29.6 | 29.4 | 29.3 | 29.2 | 29.1 | 29.7 | 24.3 | 24 | 23.3 | 22.5 | 21.6 | 20.8 | 16.7 | 16.1 | 15.5 | 15 | 0 | 0
Rassau | Rassau West Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 30.5 | 29.9 | 29.7 | 29.5 | 29.1 | 29 | 24.3 | 23.9 | 23.2 | 22.2 | 16.7 | 4.9 | 15.8 | 15.2 | 14.9 | 11.3 | 9.5 | 0 | 0
Rassau | Rassau West Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 30.5 | 30 | 29.9 | 29.8 | 29.7 | 29.5 | 29.8 | 29.7 | 24.2 | 23.8 | 23.1 | 22.5 | 21.6 | 20.7 | 17.8 | 17.7 | 17.6 | 16.3 | 13.3
Rassau | Rhayader | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Rhayader | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Rhayader | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Rhayader | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Tredegar | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Tredegar | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Tredegar | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Tredegar | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1 | 0.9 | 0.8 | 0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Usk | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.8 | 8.7 | 8.6 | 8.5 | 8.4 | 8.2 | 6.7 | 6.3 | 5.5 | 4.3 | 2.8 | 1.8 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0
Rassau | Usk | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.8 | 8.7 | 8.4 | 8.2 | 7.9 | 7.5 | 5.2 | 3.5 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Usk | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.8 | 8.6 | 8.3 | 8.1 | 7.6 | 7.1 | 3.8 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rassau | Usk | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.8 | 8.7 | 8.5 | 8.4 | 8.2 | 7.9 | 6.3 | 5.5 | 4.5 | 3.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberaeron | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7 | 6.9 | 6.8 | 6.8 | 6.7 | 6.6 | 6.4 | 5.1 | 3.5 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberaeron | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7 | 6.8 | 6.7 | 6.4 | 5.8 | 4.9 | 3.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberaeron | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7 | 6.8 | 6.6 | 6.6 | 5.2 | 3.9 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberaeron | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7 | 6.8 | 6.8 | 6.7 | 6.7 | 6.3 | 5.5 | 4.1 | 2.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Abercrave | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.8 | 7.4 | 7.3 | 7.2 | 7.7 | 7.6 | 3.7 | 3.4 | 3 | 2.5 | 2 | 0.9 | 1.4 | 1.3 | 0 | 0 | 0 | 0 | 0
Swansea North | Abercrave | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.8 | 7.6 | 7.4 | 7.9 | 7.5 | 7.3 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Abercrave | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.8 | 7.3 | 7.6 | 7.4 | 7 | 6.6 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Abercrave | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.8 | 7.4 | 7.2 | 7.8 | 7.6 | 7.4 | 3 | 2.6 | 2 | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberdare | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.6 | 15.3 | 15.1 | 14.9 | 14.7 | 14.4 | 10.7 | 11.4 | 10.5 | 8.9 | 6.9 | 3.2 | 5 | 4.5 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberdare | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.6 | 15.1 | 14.5 | 14 | 13.5 | 12.8 | 5.8 | 3.3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberdare | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.6 | 14.9 | 14.2 | 13.7 | 12.9 | 12 | 5.6 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberdare | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.6 | 15.3 | 14.9 | 14.6 | 14.2 | 13.7 | 10.2 | 9.1 | 7.2 | 5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberpergwm | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.3 | 12.6 | 12.5 | 12.4 | 13 | 12.9 | 7.7 | 7.3 | 6.4 | 5.4 | 4.2 | 1.9 | 3.1 | 2.8 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberpergwm | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.3 | 13 | 12.8 | 12.8 | 12.6 | 12.3 | 3.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberpergwm | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.3 | 12.5 | 12.8 | 12.6 | 12.3 | 11.7 | 3.4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Aberpergwm | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.3 | 12.6 | 12.4 | 13 | 12.8 | 12.6 | 6.4 | 5.6 | 4.4 | 3.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ammanford Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 40.9 | 39.9 | 39.4 | 38.9 | 38.4 | 37.5 | 39.1 | 37.3 | 34.7 | 31.6 | 27.8 | 25 | 23.4 | 22.2 | 20.8 | 19.5 | 18.8 | 10.9 | 1.4
Swansea North | Ammanford Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 40.9 | 39.2 | 38 | 37.1 | 35.7 | 34 | 33.3 | 28.2 | 22.7 | 16.6 | 10.2 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ammanford Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 40.9 | 38.7 | 37 | 35.9 | 33.7 | 31.2 | 28.2 | 22.4 | 15.1 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ammanford Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 40.9 | 39.7 | 39 | 38.2 | 37.4 | 36.1 | 37 | 34.1 | 30.8 | 27.1 | 21.9 | 18.3 | 15.7 | 12.9 | 11 | 7.1 | 3.1 | 0 | 0
Swansea North | Bishopston | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Bishopston | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1 | 0.8 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Bishopston | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Bishopston | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1 | 0.9 | 0.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Blaenporth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.5 | 0.8 | 0.6 | 0.5 | 0 | 0 | 3.5 | 3.4 | 3.3 | 2.9 | 1.9 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Blaenporth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 3.2 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Blaenporth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.5 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Blaenporth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 3.3 | 3 | 2.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Bridell | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.6 | 0.9 | 0.7 | 0.5 | 0 | 0 | 2.6 | 2.6 | 2.6 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.4
Swansea North | Bridell | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 2.4 | 2.3 | 2.2 | 2.2 | 2.1 | 2 | 2 | 1.6 | 1.5 | 1.5 | 0 | 0 | 0
Swansea North | Bridell | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.6 | 0 | 0 | 0 | 0 | 0 | 2.1 | 2 | 1.2 | 1.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Bridell | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.6 | 0.8 | 0.5 | 0 | 0 | 0 | 2.5 | 2.4 | 2.4 | 2.4 | 2.3 | 2.3 | 2.3 | 1.9 | 1.9 | 1.9 | 1.8 | 1.6 | 1.4
Swansea North | Briton Ferry Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 49.5 | 49.5 | 48.4 | 48.5 | 48.6 | 48.6 | 46 | 46 | 45.9 | 45.8 | 45.6 | 45.6 | 45.5 | 45.4 | 46.4 | 46.4 | 46.3 | 47.1 | 44.9
Swansea North | Briton Ferry Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 49.5 | 49.5 | 49.6 | 49.6 | 49.7 | 49.7 | 46.4 | 46.2 | 46 | 45.8 | 45.6 | 45.1 | 43.2 | 41.1 | 39.4 | 37.6 | 35.1 | 21.7 | 13.6
Swansea North | Briton Ferry Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 49.5 | 49.5 | 49.6 | 49.7 | 49.7 | 49.8 | 46.1 | 45.8 | 45.6 | 45.3 | 42.4 | 39 | 33.7 | 31.9 | 30.5 | 29 | 27.5 | 17 | 11
Swansea North | Briton Ferry Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 49.5 | 49.5 | 49.6 | 49.6 | 49.7 | 49.8 | 46.8 | 46.6 | 46.5 | 46.4 | 46.3 | 46.2 | 46.1 | 46 | 45 | 36.6 | 37.3 | 29.9 | 23.6
Swansea North | Britton Ferry Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.4 | 18.4 | 18.4 | 18.3 | 18.3 | 18.3 | 17.9 | 17.7 | 17.5 | 17.4 | 17.2 | 17.1 | 17.1 | 17.1 | 17 | 17 | 17 | 16.9 | 16.7
Swansea North | Britton Ferry Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.4 | 18.4 | 18.4 | 18.3 | 17.9 | 17.6 | 17 | 16.7 | 15.8 | 15.6 | 15.4 | 15.3 | 15.1 | 15 | 14.9 | 14.8 | 14.8 | 14.2 | 13.7
Swansea North | Britton Ferry Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.4 | 18.4 | 18.3 | 18 | 17.7 | 17.4 | 16.7 | 15.7 | 15.5 | 15.3 | 15.1 | 15 | 14.9 | 14.8 | 14.7 | 14.7 | 14.6 | 14 | 13.6
Swansea North | Britton Ferry Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.4 | 18.4 | 18.4 | 18.4 | 18 | 17.7 | 17.1 | 16.8 | 16.6 | 15.7 | 15.6 | 15.6 | 15.5 | 15.5 | 15.5 | 15.4 | 15.4 | 15.1 | 14.8
Swansea North | Cardigan | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.6 | 0.9 | 0.7 | 0.5 | 0 | 0 | 4.7 | 4.6 | 4.6 | 4.5 | 4.4 | 4.4 | 4.3 | 4.3 | 4.3 | 4.2 | 4.2 | 4.1 | 3.9
Swansea North | Cardigan | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 4 | 3.8 | 3.5 | 3.2 | 2.9 | 2.8 | 2.5 | 2 | 1.8 | 1.7 | 0 | 0 | 0
Swansea North | Cardigan | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.6 | 0 | 0 | 0 | 0 | 0 | 3.4 | 3 | 2 | 1.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Cardigan | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.6 | 0.8 | 0.5 | 0 | 0 | 0 | 4.5 | 4.3 | 4.2 | 4 | 3.8 | 3.8 | 3.7 | 3.3 | 3.3 | 3.3 | 2.1 | 1.8 | 1.4
Swansea North | Carmarthen Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 22.8 | 21.6 | 20.9 | 20.4 | 19.7 | 18.5 | 2.5 | 2.5 | 2.4 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Carmarthen Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 22.8 | 21 | 19.6 | 18.4 | 16.2 | 13.5 | 2.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Carmarthen Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 22.8 | 20.6 | 18.6 | 17.5 | 14.1 | 10 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Carmarthen Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 22.8 | 21.4 | 20.5 | 19.7 | 18.5 | 16.4 | 2.4 | 2.4 | 2.4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Clase | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.1 | 11.2 | 11.3 | 11.3 | 11.3 | 11.4 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.4 | 10.4 | 9.8 | 9.8
Swansea North | Clase | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.1 | 11.3 | 11.4 | 11.5 | 11.6 | 11.7 | 10.7 | 10.7 | 10.6 | 10.5 | 10.5 | 10.4 | 10.4 | 10.3 | 10.2 | 12.3 | 11.8 | 10.9 | 8.5
Swansea North | Clase | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.1 | 11.3 | 11.5 | 11.6 | 11.7 | 11.9 | 10.7 | 10.6 | 10.6 | 10.5 | 10.3 | 10.2 | 9.9 | 9.6 | 9.3 | 11.7 | 11.6 | 10.7 | 8.1
Swansea North | Clase | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.1 | 11.2 | 11.3 | 11.4 | 11.5 | 11.6 | 10.7 | 10.6 | 10.5 | 10.5 | 10.4 | 10.3 | 10.2 | 10.1 | 9.9 | 12.2 | 12.1 | 11.8 | 11.8
Swansea North | Commercial St Neath | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.4 | 19.2 | 19 | 18.9 | 18.7 | 18.5 | 18.2 | 17.8 | 17.4 | 16.9 | 16.3 | 15.9 | 15.7 | 15.5 | 15.4 | 15.3 | 15.1 | 13.8 | 12.3
Swansea North | Commercial St Neath | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.4 | 18.9 | 18.6 | 18.3 | 17.9 | 17.5 | 16.9 | 16.3 | 15.6 | 14.8 | 14 | 13.2 | 12.4 | 11.5 | 10.8 | 10 | 9.3 | 5.6 | 2.5
Swansea North | Commercial St Neath | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.4 | 18.8 | 18.3 | 17.9 | 17.3 | 16.7 | 15.9 | 15.2 | 14.3 | 13.3 | 12.1 | 11.3 | 10.5 | 9.8 | 9.2 | 8.7 | 8.1 | 4.7 | 2.7
Swansea North | Commercial St Neath | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.4 | 19.1 | 18.9 | 18.7 | 18.5 | 18.2 | 17.8 | 17.4 | 17.1 | 16.6 | 15.8 | 15.3 | 14.8 | 14.4 | 14.2 | 14.1 | 13.8 | 11.8 | 9.2
Swansea North | Cross Hands | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.7 | 9.7 | 9.7 | 9.7 | 9.6 | 9.6 | 9.5 | 9.4 | 9.2 | 8.9 | 8.1 | 7.5 | 7.1 | 6.7 | 6.3 | 5.9 | 5.6 | 4.1 | 2.1
Swansea North | Cross Hands | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.7 | 9.7 | 9.6 | 9.6 | 9.5 | 9.4 | 9.3 | 8 | 6.5 | 4.7 | 3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Cross Hands | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.7 | 9.7 | 9.6 | 9.5 | 9.4 | 9.2 | 7.9 | 6.3 | 4 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Cross Hands | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.7 | 9.7 | 9.7 | 9.6 | 9.6 | 9.5 | 9.3 | 8.8 | 8 | 7.1 | 5.8 | 5 | 4.2 | 3.5 | 3.1 | 0.6 | 0 | 0 | 0
Swansea North | Cwmffrwd | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.2 | 10.2 | 10.2 | 10.1 | 10 | 9.9 | 9.7 | 9.5 | 9.3 | 9 | 8.6 | 8.2 | 8 | 7.9 | 7.7 | 7.5 | 7.4 | 6.6 | 0
Swansea North | Cwmffrwd | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.2 | 10.2 | 10 | 9.9 | 9.7 | 9.5 | 9.2 | 8.7 | 8.1 | 7.3 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Cwmffrwd | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.2 | 10.1 | 9.9 | 9.8 | 9.5 | 9.2 | 8.7 | 8.1 | 7.2 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Cwmffrwd | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.2 | 10.2 | 10.1 | 10 | 9.9 | 9.8 | 9.5 | 9.2 | 8.9 | 8.4 | 7.8 | 7.3 | 6.9 | 6.6 | 6.3 | 6 | 5.5 | 0 | 0
Swansea North | Garngoch | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.9 | 13.5 | 13.2 | 13 | 12.7 | 12.3 | 16.6 | 16.6 | 16.5 | 16.5 | 16.4 | 16.4 | 16.3 | 16.2 | 16.2 | 16.1 | 16.1 | 16.2 | 15.4
Swansea North | Garngoch | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.9 | 13.1 | 12.5 | 11.9 | 11.1 | 10 | 16.4 | 16.2 | 14.6 | 14.6 | 14.6 | 14.6 | 14.6 | 14.6 | 14.5 | 14.4 | 14.3 | 10.4 | 6.7
Swansea North | Garngoch | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.9 | 12.9 | 12 | 11.2 | 10 | 8.8 | 16.2 | 16.1 | 14.6 | 14.6 | 14.6 | 14.7 | 14.6 | 13.9 | 13.1 | 14.2 | 13.5 | 9.2 | 6.3
Swansea North | Garngoch | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.9 | 13.4 | 13 | 12.5 | 12 | 11.3 | 16.6 | 16.4 | 16.3 | 16.2 | 16.1 | 16.1 | 15.4 | 15.4 | 15.3 | 15.2 | 15.1 | 14.7 | 14.1
Swansea North | Gethin Street Swansea | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19 | 19 | 19 | 19 | 18.9 | 18.9 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.2 | 18.1 | 18.1 | 18 | 18 | 18 | 17.9 | 17.6
Swansea North | Gethin Street Swansea | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19 | 19 | 19 | 19 | 18.9 | 18.9 | 18.1 | 18 | 17.8 | 17.5 | 17.2 | 17 | 16.8 | 16.7 | 16.6 | 16.5 | 16.4 | 15.6 | 15
Swansea North | Gethin Street Swansea | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19 | 19 | 19 | 19 | 18.9 | 18.7 | 17.8 | 17.5 | 17.2 | 16.8 | 16.6 | 16.4 | 16.3 | 15.8 | 15.8 | 15.7 | 15.6 | 14.9 | 14.1
Swansea North | Gethin Street Swansea | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19 | 19 | 19 | 19 | 18.9 | 18.9 | 18.1 | 18.1 | 18.1 | 17.9 | 17.7 | 17.6 | 17.5 | 17.4 | 17.3 | 17.3 | 17.3 | 16.9 | 16.5
Swansea North | Gwaun Cae Gurwen | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.8 | 2.8 | 2.7 | 2.6 | 2.6 | 2.5 | 2.2 | 2 | 1.8 | 1.5 | 1.2 | 0.7 | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0
Swansea North | Gwaun Cae Gurwen | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.8 | 2.7 | 2.5 | 2.4 | 2.2 | 2 | 1.6 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Gwaun Cae Gurwen | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.8 | 2.6 | 2.4 | 2.2 | 1.9 | 1.6 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Gwaun Cae Gurwen | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.8 | 2.7 | 2.6 | 2.6 | 2.5 | 2.3 | 2 | 1.8 | 1.6 | 1.4 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Hendy | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.9 | 9.8 | 9.8 | 9.7 | 9.6 | 9.5 | 9.3 | 9.1 | 8.8 | 8.5 | 8.2 | 7.9 | 7.8 | 7.7 | 7.5 | 7.3 | 7.2 | 6.1 | 4.8
Swansea North | Hendy | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.9 | 9.7 | 9.5 | 9.4 | 9.2 | 8.8 | 8.6 | 8.2 | 7.7 | 7.3 | 6.7 | 6.2 | 5.8 | 5 | 4.5 | 3.8 | 2.7 | 0.5 | 0
Swansea North | Hendy | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.9 | 9.6 | 9.4 | 9.2 | 8.8 | 8.4 | 8 | 7.5 | 6.9 | 6 | 5.2 | 4.5 | 3.7 | 2.8 | 2.2 | 1.8 | 1.5 | 0 | 0
Swansea North | Hendy | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.9 | 9.8 | 9.7 | 9.6 | 9.4 | 9.3 | 9.1 | 8.8 | 8.5 | 8.1 | 7.6 | 7.2 | 6.8 | 6.4 | 6.1 | 5.9 | 5.6 | 3.6 | 2
Swansea North | Hirwaun Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 29.9 | 29.6 | 29.2 | 28.9 | 28.7 | 28.3 | 10.4 | 11 | 10.2 | 8.6 | 6.7 | 3.1 | 4.9 | 4.4 | 0 | 0 | 0 | 0 | 0
Swansea North | Hirwaun Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 29.9 | 29.1 | 28.3 | 27.8 | 27.3 | 26.7 | 5.6 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Hirwaun Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 29.9 | 28.8 | 27.7 | 27 | 26.1 | 25.2 | 5.5 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Hirwaun Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 29.9 | 29.5 | 29 | 28.8 | 28.4 | 28 | 9.8 | 8.9 | 7 | 4.9 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Hirwaun Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.7 | 4.7 | 4.7 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Hirwaun Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.7 | 2.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Hirwaun Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.7 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Hirwaun Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.7 | 4.7 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Jersey Marine | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 16.9 | 16.9 | 16.9 | 16.8 | 16.8 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.4 | 15.5
Swansea North | Jersey Marine | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.1 | 16.8 | 16.7 | 16.7 | 16.6 | 16.4 | 15.9 | 15.5 | 14.9 | 14.5 | 14.1 | 13.7 | 11.6 | 9.8
Swansea North | Jersey Marine | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.1 | 16.8 | 16.7 | 16.6 | 16.1 | 15.4 | 14.9 | 14.4 | 14 | 13.7 | 13.4 | 13.1 | 11.2 | 10.1
Swansea North | Jersey Marine | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 16.9 | 16.8 | 16.8 | 16.7 | 16.6 | 16.6 | 16.5 | 16.5 | 16.5 | 16.4 | 16.3 | 15.1 | 13.6
Swansea North | Kidwelly | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.7 | 5.7 | 5.6 | 5.6 | 5.5 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Kidwelly | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.7 | 5.6 | 5.5 | 5.4 | 5.2 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Kidwelly | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.7 | 5.6 | 5.4 | 5.3 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Kidwelly | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.7 | 5.7 | 5.6 | 5.5 | 5.4 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lampeter Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 2.4 | 2.3 | 2.1 | 1.9 | 1.6 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lampeter Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lampeter Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lampeter Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 2.4 | 2.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lampeter Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.4 | 2.3 | 2.1 | 1.9 | 1.6 | 0 | 4.3 | 3.6 | 2.8 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lampeter Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.4 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lampeter Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.4 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lampeter Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.4 | 2.3 | 2 | 0 | 0 | 0 | 3.6 | 2.9 | 2.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Lime Street Gorseinon | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.9 | 13.6 | 13.3 | 13 | 12.7 | 12.4 | 13 | 12.7 | 12.4 | 12 | 11.5 | 11.2 | 11 | 10.9 | 10.8 | 10.7 | 10.6 | 9.6 | 8.3
Swansea North | Lime Street Gorseinon | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.9 | 13.1 | 12.5 | 11.9 | 11.1 | 10 | 11.3 | 10.6 | 10.2 | 9.6 | 8.9 | 8.2 | 7.6 | 6.8 | 6.1 | 5.2 | 4.6 | 1 | 0
Swansea North | Lime Street Gorseinon | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.9 | 12.9 | 12 | 11.2 | 10 | 8.8 | 10.5 | 9.7 | 9.1 | 8.4 | 7.4 | 7 | 6.4 | 5.7 | 5.2 | 4.6 | 3.9 | 0 | 0
Swansea North | Lime Street Gorseinon | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.9 | 13.4 | 13 | 12.6 | 12 | 11.3 | 12.1 | 11.7 | 11.3 | 10.9 | 10.4 | 10 | 9.6 | 9.2 | 9.1 | 8.8 | 8.7 | 6.7 | 4.5
Swansea North | Llanarth Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 7.8 | 7.3 | 7.2 | 7 | 6.8 | 6.9 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanarth Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 7.8 | 7 | 6.8 | 6.4 | 5.8 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanarth Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 7.8 | 7.5 | 7.1 | 6.9 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanarth Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 7.8 | 7.3 | 7.1 | 7.3 | 7 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanarth Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.8 | 7.3 | 7.2 | 7 | 6.8 | 6.9 | 6.5 | 5.2 | 3.6 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanarth Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.8 | 7 | 6.8 | 6.4 | 5.8 | 5 | 3.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanarth Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.8 | 7.5 | 7.1 | 6.9 | 5.2 | 3.9 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanarth Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.8 | 7.3 | 7.1 | 7.3 | 7 | 6.3 | 5.5 | 4.1 | 2.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llandarcy | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.3 | 1.6 | 1.4 | 1.3 | 1.1 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4 | 9.3
Swansea North | Llandarcy | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.3 | 1.4 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1 | 8.6 | 8.1 | 7.7 | 7.3 | 4.9 | 1.1
Swansea North | Llandarcy | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.3 | 1.3 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9 | 8.4 | 7.9 | 7.5 | 7.1 | 6.7 | 1.3 | 0
Swansea North | Llandarcy | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.3 | 1.5 | 1.3 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4 | 10.1 | 9.9 | 9.6 | 9.3 | 7.5 | 4.1
Swansea North | Llandeilo | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.2 | 6.2 | 5.9 | 5.7 | 5.4 | 4.6 | 2.9 | 2.8 | 2.8 | 2.7 | 2.6 | 2.5 | 2.4 | 2 | 1.3 | 0.6 | 0 | 0 | 0
Swansea North | Llandeilo | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.2 | 5.8 | 5 | 4.4 | 3.4 | 2.2 | 2.7 | 2.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llandeilo | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.2 | 5.7 | 4.5 | 3.9 | 2.4 | 0.6 | 2.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llandeilo | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.2 | 6.1 | 5.7 | 5.1 | 4.6 | 3.7 | 2.8 | 2.8 | 2.7 | 2.6 | 2.4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llandovery | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.7 | 5.7 | 5.5 | 5.5 | 5.4 | 4.8 | 2.7 | 2.7 | 2.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llandovery | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.7 | 5.3 | 5.1 | 4.7 | 3.6 | 2.3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llandovery | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.7 | 5.3 | 4.8 | 4.2 | 2.5 | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llandovery | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.7 | 5.6 | 5.5 | 5.1 | 4.8 | 3.9 | 2.7 | 2.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanelli Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 30.3 | 30.2 | 29.9 | 29.8 | 29.6 | 29.4 | 29.4 | 29.1 | 28.8 | 28.4 | 28.1 | 27.8 | 27.8 | 27.7 | 27.4 | 26.6 | 26.5 | 26 | 24.6
Swansea North | Llanelli Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 30.3 | 29.8 | 29.4 | 29.1 | 28.8 | 28.4 | 28.1 | 27.6 | 26.6 | 26.2 | 25.6 | 25 | 23.8 | 23.2 | 22.6 | 22.1 | 21.5 | 7.6 | 0
Swansea North | Llanelli Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 30.3 | 29.6 | 29 | 28.5 | 27.9 | 27.4 | 26.5 | 25.9 | 25 | 24.1 | 23.2 | 22.5 | 21.7 | 20.8 | 20.1 | 19.3 | 18.8 | 0 | 0
Swansea North | Llanelli Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 30.3 | 30.1 | 29.8 | 29.6 | 29.3 | 29 | 29 | 28.6 | 28.2 | 27.8 | 27.5 | 26.5 | 26.3 | 26.2 | 25.9 | 25.7 | 25.4 | 23.5 | 21.4
Swansea North | Llanfihangel Ystrad | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7 | 6.9 | 6.8 | 6.7 | 6.6 | 6.4 | 5.2 | 3.9 | 2.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanfihangel Ystrad | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7 | 6.9 | 6.8 | 6.4 | 5.8 | 5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanfihangel Ystrad | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7 | 6.8 | 6.7 | 6.6 | 5.2 | 3.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanfihangel Ystrad | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7 | 6.9 | 6.8 | 6.7 | 6.5 | 6.1 | 4.2 | 2.9 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanfyrnach | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.2 | 1.4 | 1.2 | 1 | 0.7 | 0 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanfyrnach | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.2 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanfyrnach | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanfyrnach | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.2 | 1.4 | 1 | 0.7 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llangadog | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.8 | 5.6 | 5.5 | 5.3 | 4.7 | 4 | 3.2 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llangadog | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.4 | 4.9 | 4.5 | 3.5 | 2.3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llangadog | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.4 | 4.6 | 4.1 | 2.5 | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llangadog | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.8 | 5.5 | 5 | 4.7 | 3.8 | 3.3 | 2.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanllwni | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.3 | 2.2 | 2 | 1.8 | 1.5 | 0 | 2.6 | 1.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanllwni | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.3 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanllwni | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanllwni | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.3 | 2.1 | 1.9 | 0 | 0 | 0 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanrhidian | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanrhidian | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanrhidian | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Llanrhidian | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Maerdy | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.9 | 4.8 | 4.7 | 4.6 | 3.2 | 4.3 | 4.3 | 0 | 0 | 0 | 0 | 0
Swansea North | Maerdy | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 3.3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Maerdy | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Maerdy | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 4.9 | 4.5 | 4.2 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Maesarddafen | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.6 | 11.5 | 11.4 | 11.3 | 11.3 | 11.2 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.8 | 6.7
Swansea North | Maesarddafen | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.6 | 11.4 | 11.2 | 11.1 | 11 | 10.8 | 13.8 | 13.8 | 6.9 | 6.9 | 6.8 | 6.8 | 6.6 | 6.5 | 6.5 | 6.4 | 6.3 | 5.5 | 4.8
Swansea North | Maesarddafen | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.6 | 11.3 | 11 | 10.9 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Maesarddafen | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.6 | 11.5 | 11.4 | 11.3 | 11.1 | 11 | 13.8 | 13.8 | 13.8 | 6.9 | 6.9 | 6.9 | 6.8 | 6.8 | 6.8 | 6.8 | 6.7 | 6.4 | 6.1
Swansea North | Meinciau | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.4 | 5.4 | 5.4 | 5.4 | 5.3 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Meinciau | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.4 | 5.4 | 5.3 | 5.3 | 4.9 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Meinciau | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.4 | 5.4 | 5.3 | 5.2 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Meinciau | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.4 | 5.4 | 5.4 | 5.3 | 5.3 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Morriston Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.5 | 29.3 | 29.2 | 29.1 | 28.9 | 28.8 | 28.7 | 28.5 | 28.2 | 28 | 27.7 | 27.5 | 27.5 | 27.4 | 26.3 | 26.3 | 26.2 | 25.3 | 23.8
Swansea North | Morriston Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.5 | 29.1 | 28.9 | 28.7 | 28.5 | 28.3 | 28 | 27.6 | 26.3 | 25.7 | 24.7 | 23.7 | 22.8 | 21.8 | 21 | 20.3 | 19.5 | 0 | 0
Swansea North | Morriston Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.5 | 29 | 28.7 | 28.5 | 28.2 | 27.8 | 27.6 | 26.2 | 25.5 | 24.4 | 23.3 | 22.4 | 21.7 | 20.8 | 20.2 | 19.5 | 18.7 | 0 | 0
Swansea North | Morriston Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.5 | 29.2 | 29.1 | 28.9 | 28.8 | 28.6 | 28.5 | 28.2 | 28 | 27.7 | 27.5 | 26.3 | 26 | 25.7 | 25.6 | 25.4 | 25.1 | 22.8 | 17.8
Swansea North | Nantgaredig | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.2 | 4.5 | 4.2 | 3.8 | 3.4 | 2.9 | 2.6 | 2.3 | 2.1 | 1.7 | 1.3 | 1.3 | 0 | 0
Swansea North | Nantgaredig | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 5.3 | 5.3 | 5.2 | 5.1 | 5 | 3.7 | 2.9 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Nantgaredig | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 5.3 | 5.2 | 5.2 | 5 | 4.8 | 3.3 | 2.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Nantgaredig | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 5.3 | 5.3 | 5.3 | 5.2 | 5.1 | 4.3 | 4 | 3.6 | 3.2 | 2.6 | 1.9 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0
Swansea North | New Lodge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 5.2 | 5 | 4.9 | 4.7 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | New Lodge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 5 | 4.6 | 4.3 | 3.7 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | New Lodge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 4.8 | 4.3 | 3.9 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | New Lodge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 5.1 | 4.9 | 4.6 | 4.2 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Newcastle Emlyn South | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.5 | 5.7 | 5.5 | 5.2 | 5 | 4.7 | 4.4 | 4 | 3.5 | 2.8 | 1.9 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Newcastle Emlyn South | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.5 | 5.3 | 4.7 | 4.3 | 3.7 | 3.1 | 3.2 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Newcastle Emlyn South | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.5 | 5.1 | 4.2 | 3.6 | 2.5 | 1.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Newcastle Emlyn South | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.5 | 5.7 | 5.3 | 5 | 4.6 | 4.1 | 4 | 3.3 | 2.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pantyffynon | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.5 | 5.7 | 5.5 | 5.4 | 5.2 | 4.9 | 4.6 | 4 | 3.3 | 2.5 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pantyffynon | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.5 | 5.5 | 5.1 | 4.8 | 4.3 | 3.7 | 2.9 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pantyffynon | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.5 | 5.2 | 4.7 | 4.3 | 3.5 | 2.7 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pantyffynon | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.5 | 5.6 | 5.4 | 5.2 | 4.9 | 4.5 | 3.9 | 3 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pendine | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.3 | 1.5 | 1.2 | 1 | 0.7 | 0 | 1.5 | 1.4 | 1.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pendine | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.3 | 1.3 | 0.8 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pendine | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pendine | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.3 | 1.4 | 1.1 | 0.8 | 0 | 0 | 1.4 | 1.3 | 1.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pont Ar Annell | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5 | 5 | 4.9 | 4.9 | 4.9 | 4.8 | 3.4 | 3.3 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pont Ar Annell | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5 | 5 | 4.8 | 4.7 | 3.6 | 2.3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pont Ar Annell | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5 | 4.9 | 4.7 | 4.2 | 2.5 | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pont Ar Annell | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5 | 5 | 4.9 | 4.8 | 4.8 | 4 | 3.3 | 2.6 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pontardawe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.6 | 13.4 | 13.2 | 13.1 | 12.9 | 12.6 | 10.9 | 10.3 | 9.6 | 8.9 | 7.9 | 11.8 | 11.5 | 11.3 | 11.1 | 10.8 | 10.6 | 8.8 | 6.5
Swansea North | Pontardawe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.6 | 13.1 | 12.7 | 12.4 | 11.9 | 11.4 | 9.1 | 8.1 | 6.9 | 5.6 | 4.2 | 7.4 | 6.2 | 4.9 | 3.9 | 3 | 1.5 | 0 | 0
Swansea North | Pontardawe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.6 | 13 | 12.4 | 12 | 11.2 | 10.3 | 7.8 | 6.6 | 5.1 | 3.7 | 2.1 | 5.6 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pontardawe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.6 | 13.3 | 13.1 | 12.8 | 12.5 | 12.1 | 10.2 | 9.5 | 8.9 | 8.2 | 7.1 | 11 | 10.4 | 9.9 | 9.6 | 9.2 | 8.8 | 4 | 0
Swansea North | Pontyates | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.6 | 5.5 | 5.5 | 5.5 | 5.4 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pontyates | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.6 | 5.5 | 5.4 | 5.3 | 4.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pontyates | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.6 | 5.4 | 5.3 | 4.8 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Pontyates | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.6 | 5.5 | 5.5 | 5.4 | 5.2 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ravenhill | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.3 | 14.1 | 14 | 13.8 | 13.6 | 13.5 | 13.3 | 13 | 12.9 | 12.6 | 12.4 | 12.2 | 12.1 | 12 | 11.9 | 11.8 | 11.6 | 11 | 9.9
Swansea North | Ravenhill | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.3 | 13.7 | 13.1 | 12.2 | 11.8 | 11.1 | 10.3 | 9.5 | 9.3 | 9 | 8.8 | 8.5 | 8.2 | 7.8 | 7.5 | 7.2 | 6.9 | 4.9 | 3.1
Swansea North | Ravenhill | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.3 | 13.5 | 12.8 | 11.9 | 11.2 | 10.4 | 9.4 | 8.5 | 8.2 | 7.8 | 7.4 | 7.1 | 6.8 | 6.5 | 6.2 | 5.9 | 5.5 | 3.2 | 1.2
Swansea North | Ravenhill | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.3 | 14 | 13.8 | 13.5 | 13.3 | 13 | 12.7 | 12.4 | 12.1 | 11.8 | 11.5 | 11.3 | 11.1 | 10.9 | 10.7 | 10.6 | 10.4 | 8.9 | 7.1
Swansea North | Rhos Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 12.5 | 12 | 11.4 | 10.9 | 10.2 | 6.2 | 5.7 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Rhos Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 12.5 | 8.8 | 7.5 | 6.1 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Rhos Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 12.5 | 8.4 | 6.6 | 5.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Rhos Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 12.5 | 11.9 | 11.1 | 7.5 | 6.2 | 3.6 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Rhos Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.8 | 8.8 | 8.6 | 8.5 | 8.3 | 8 | 7.1 | 5.8 | 4.1 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Rhos Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.8 | 8.7 | 8.4 | 8 | 7.3 | 6.3 | 4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Rhos Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.8 | 8.6 | 8.2 | 8 | 6.8 | 5.3 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Rhos Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.8 | 8.7 | 8.6 | 8.4 | 8 | 7.3 | 6.1 | 4.6 | 3.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Sketty Park | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14 | 13.9 | 13.8 | 13.7 | 13.6 | 13.5 | 13.6 | 13.5 | 13.4 | 13.3 | 13.3 | 13.3 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.7 | 11.3
Swansea North | Sketty Park | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14 | 13.8 | 13.6 | 13.4 | 13.3 | 13.2 | 13.3 | 13.3 | 11.9 | 11.8 | 11.6 | 11.4 | 11.2 | 10.9 | 10.7 | 10.5 | 10.3 | 8.7 | 7.3
Swansea North | Sketty Park | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14 | 13.7 | 13.5 | 13.3 | 13.1 | 13 | 11.9 | 11.8 | 11.6 | 11.3 | 11 | 10.8 | 10.6 | 10.4 | 10.2 | 10 | 9.7 | 8 | 6.7
Swansea North | Sketty Park | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14 | 13.9 | 13.8 | 13.6 | 13.5 | 13.4 | 13.5 | 13.4 | 13.3 | 13.3 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.8 | 11.8 | 11.2 | 10.2
Swansea North | St Clears | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.1 | 1.3 | 1.1 | 0.9 | 0.6 | 0 | 3.1 | 2.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | St Clears | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.1 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | St Clears | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | St Clears | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.1 | 1.3 | 1 | 0.7 | 0 | 0 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Strand Swansea | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.3 | 18.3 | 18.2 | 18.2 | 18.1 | 18.1 | 17.3 | 17.3 | 17.2 | 17.1 | 16.9 | 16.9 | 16.8 | 16.8 | 16.8 | 16.7 | 16.7 | 16.5 | 16.1
Swansea North | Strand Swansea | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.3 | 18.3 | 18.2 | 18 | 17.9 | 17.7 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15.1 | 14.6 | 13.7 | 12.6
Swansea North | Strand Swansea | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.3 | 18.3 | 18 | 17.7 | 17.4 | 17.1 | 16 | 15.8 | 15.5 | 15.2 | 14.9 | 14.5 | 14.5 | 14.3 | 14.2 | 14 | 13.8 | 12.3 | 10.9
Swansea North | Strand Swansea | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.3 | 18.3 | 18.2 | 18.2 | 18.1 | 18 | 17.2 | 17 | 16.9 | 16.7 | 16.6 | 16.6 | 16.5 | 16.5 | 16.5 | 16.5 | 16.4 | 15.9 | 15.1
Swansea North | Swansea North Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 11.1 | 11.2 | 11.2 | 11.3 | 11.3 | 11.4 | 44.7 | 44.2 | 43.7 | 43.1 | 42.4 | 41.9 | 41.5 | 41.2 | 42.3 | 42.1 | 41.9 | 40.2 | 38.6
Swansea North | Swansea North Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 11.1 | 11.3 | 11.4 | 11.4 | 11.6 | 11.7 | 43.4 | 42.2 | 41.1 | 40 | 39 | 38 | 37.1 | 36.1 | 35.2 | 34.9 | 32.8 | 27.7 | 21.4
Swansea North | Swansea North Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 11.1 | 11.3 | 11.4 | 11.5 | 11.7 | 11.9 | 42 | 40.6 | 39.4 | 38.2 | 33.9 | 30.8 | 29.4 | 26.7 | 25.9 | 27.5 | 26.4 | 18.5 | 14.9
Swansea North | Swansea North Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 11.1 | 11.2 | 11.3 | 11.4 | 11.4 | 11.5 | 44.8 | 44 | 43.3 | 42.5 | 41.6 | 40.9 | 40.3 | 39.6 | 37.9 | 38.3 | 37.3 | 35.3 | 30.6
Swansea North | Swansea North Local | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.6 | 10.6 | 10.6 | 10.6 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
Swansea North | Swansea North Local | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.6 | 10.6 | 10.6 | 10.6 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.4 | 10.4
Swansea North | Swansea North Local | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.6 | 10.6 | 10.6 | 10.6 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
Swansea North | Swansea North Local | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.6 | 10.6 | 10.6 | 10.6 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
Swansea North | Swansea Trading Estate | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Swansea Trading Estate | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Swansea Trading Estate | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8 | 9.8
Swansea North | Swansea Trading Estate | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Swansea Waterfront | Primary Substation | 11 | Counterfactual | Headroom (MW) | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.5 | 28.2 | 28.1 | 28 | 27.9 | 27.7 | 27.6 | 27.5 | 27.4 | 27.3 | 27.3 | 27.2 | 27 | 26.7
Swansea North | Swansea Waterfront | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 28.6 | 28.6 | 28.6 | 28.6 | 28.5 | 28.4 | 28 | 27.7 | 27.4 | 27 | 26.6 | 26.4 | 26.2 | 25.9 | 25.8 | 25.7 | 25.6 | 24.4 | 23.7
Swansea North | Swansea Waterfront | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 28.6 | 28.6 | 28.6 | 28.5 | 28.4 | 28.2 | 27.5 | 27.2 | 26.7 | 26.4 | 26 | 25.8 | 25.6 | 25.5 | 25.4 | 25.3 | 25.2 | 24 | 23.4
Swansea North | Swansea Waterfront | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.5 | 28.1 | 27.9 | 27.6 | 27.3 | 27 | 26.8 | 26.7 | 26.5 | 26.5 | 26.4 | 26.4 | 25.8 | 25.3
Swansea North | Swansea West Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 68.5 | 68.1 | 50.2 | 49.7 | 49.1 | 48.4 | 47.1 | 46.2 | 45.5 | 44.5 | 43.5 | 42.9 | 42.4 | 42.1 | 60 | 59.7 | 59.4 | 57.4 | 53.8
Swansea North | Swansea West Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 68.5 | 67.1 | 65.5 | 64.1 | 62.8 | 61.4 | 59 | 57.1 | 55.8 | 54.2 | 52.6 | 51.7 | 50.3 | 48.7 | 47.1 | 45.4 | 43.9 | 0 | 0
Swansea North | Swansea West Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 68.5 | 66.6 | 64.4 | 62.5 | 60.5 | 58.1 | 55.1 | 52.6 | 50.7 | 48.8 | 46.7 | 45.9 | 44.5 | 41.8 | 40.6 | 37.8 | 28.9 | 0 | 0
Swansea North | Swansea West Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 68.5 | 67.9 | 67.1 | 66.3 | 65.4 | 64.4 | 62.8 | 61.6 | 60.7 | 59.6 | 58.4 | 58.4 | 57.8 | 57.3 | 56.9 | 56.4 | 55.9 | 50.3 | 17.6
Swansea North | Tir John Power Station | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 70 | 69.2 | 66.5 | 66.1 | 65.7 | 65.3 | 61.8 | 61.2 | 60.5 | 59.6 | 58.6 | 58.1 | 57.6 | 57.2 | 57.2 | 56.9 | 58.5 | 74.2 | 71.7
Swansea North | Tir John Power Station | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 70 | 67.2 | 65.1 | 64.3 | 63.2 | 62.1 | 59 | 57.7 | 56.3 | 54.4 | 52.6 | 51.1 | 69.3 | 67.8 | 66.5 | 65.3 | 59.6 | 29.5 | 8.3
Swansea North | Tir John Power Station | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 70 | 65.7 | 64.5 | 63.2 | 61.7 | 60.1 | 56.6 | 54.5 | 52.5 | 50.4 | 42.7 | 50 | 44 | 38.7 | 34.1 | 29.7 | 25.4 | 0 | 0
Swansea North | Tir John Power Station | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 70 | 67.4 | 65.6 | 64.9 | 64.2 | 63.4 | 60.1 | 59.1 | 58.2 | 57 | 55.7 | 54.9 | 73.7 | 72.9 | 71.9 | 71.4 | 70.8 | 66.6 | 52.5
Swansea North | Tir John Primary | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 9.8 | 9.8 | 8.1 | 8.1 | 8.1 | 8.1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Swansea North | Tir John Primary | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 9.8 | 8.1 | 8.1 | 8.1 | 8.1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7.9 | 7.9
Swansea North | Tir John Primary | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 9.8 | 8.1 | 8.1 | 8.1 | 8.1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7.9 | 7.9 | 7.9
Swansea North | Tir John Primary | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 9.8 | 8.1 | 8.1 | 8.1 | 8.1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7.9
Swansea North | Travellers Rest Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.5 | 11.4 | 11.2 | 11.1 | 11 | 10.8 | 10.6 | 9.9 | 9.4 | 8.8 | 8 | 7.5 | 7.1 | 6.9 | 6.7 | 6.5 | 6.3 | 4.7 | 2.9
Swansea North | Travellers Rest Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.5 | 11.2 | 10.9 | 10.6 | 10.3 | 9.6 | 9 | 8.2 | 7.2 | 6.2 | 5 | 3.8 | 2.7 | 1.5 | 0.8 | 0 | 0 | 0 | 0
Swansea North | Travellers Rest Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.5 | 11.1 | 10.6 | 10.3 | 9.6 | 9 | 8.2 | 7.2 | 6 | 4.8 | 3.4 | 2.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Travellers Rest Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.5 | 11.3 | 11.1 | 11 | 10.7 | 10.3 | 9.8 | 9.4 | 8.9 | 8.2 | 7.2 | 6.6 | 6 | 5.5 | 5.2 | 5 | 4.7 | 2 | 0
Swansea North | Tregaron | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 3.2 | 2.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Tregaron | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Tregaron | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Tregaron | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Trevaughan | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.1 | 17.8 | 17.6 | 17.4 | 17.2 | 16.9 | 15.4 | 14.6 | 13.6 | 12.5 | 11.1 | 10.1 | 9.5 | 9 | 8.4 | 7.8 | 7.3 | 4.5 | 1.4
Swansea North | Trevaughan | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.1 | 17.6 | 17.1 | 16.8 | 16.2 | 15.5 | 13.2 | 11.3 | 9.4 | 7.2 | 5 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Trevaughan | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.1 | 17.4 | 16.8 | 16.4 | 15.4 | 14.3 | 11.5 | 9.4 | 6.8 | 4.3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Trevaughan | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.1 | 17.7 | 17.4 | 17.1 | 16.8 | 16.1 | 14.4 | 13.2 | 11.9 | 10.6 | 8.8 | 7.5 | 6.4 | 5.4 | 4.8 | 4.1 | 3.2 | 0 | 0
Swansea North | Trostre Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 41.6 | 41.3 | 40.8 | 40.4 | 39.3 | 37.1 | 49.2 | 48.1 | 46.6 | 45 | 43 | 41.5 | 40.6 | 39.9 | 38.8 | 38.1 | 37.5 | 33.1 | 27.9
Swansea North | Trostre Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 41.6 | 40.7 | 38.7 | 35.9 | 31.6 | 26.4 | 45.8 | 43 | 39.8 | 36.3 | 32.7 | 29 | 25 | 21.3 | 16.4 | 13.6 | 7.6 | 0 | 0
Swansea North | Trostre Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 41.6 | 40.3 | 36.2 | 33.1 | 26.2 | 0 | 25.4 | 21.8 | 17 | 8.5 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Trostre Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 41.6 | 41.1 | 40.6 | 38.5 | 35.7 | 30.9 | 47.4 | 45.5 | 43.9 | 41.9 | 39.3 | 33.5 | 31.8 | 30.4 | 28 | 26.8 | 22.7 | 13.6 | 3.1
Swansea North | Tumble | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11 | 10.9 | 10.8 | 10.7 | 10.6 | 10.5 | 10 | 9.6 | 9.3 | 8.8 | 8.2 | 7.6 | 7.2 | 6.8 | 6.3 | 6 | 5.7 | 4.1 | 2.1
Swansea North | Tumble | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11 | 10.8 | 10.6 | 10.4 | 10 | 9.7 | 8.9 | 8.1 | 6.5 | 4.8 | 3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Tumble | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11 | 10.7 | 10.4 | 10.1 | 9.6 | 9.1 | 8 | 6.4 | 4.1 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Tumble | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11 | 10.9 | 10.8 | 10.6 | 10.4 | 10.1 | 9.6 | 9.4 | 8.2 | 7.2 | 5.9 | 5.1 | 4.3 | 3.6 | 3.1 | 0.7 | 0 | 0 | 0
Swansea North | Uplands Swansea | Primary Substation | 11 | Counterfactual | Headroom (MW) | 19.2 | 19.2 | 19.1 | 19.1 | 19 | 18.9 | 18.3 | 18.2 | 18.1 | 17.9 | 17.8 | 17.8 | 17.7 | 17.7 | 17.7 | 17.7 | 17.6 | 17.3 | 16.5
Swansea North | Uplands Swansea | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 19.2 | 19.1 | 18.7 | 18.4 | 18.3 | 18.1 | 17.5 | 17.3 | 17.2 | 17 | 16.8 | 16.5 | 16.3 | 15.8 | 15.4 | 14.9 | 14.4 | 12.8 | 11.3
Swansea North | Uplands Swansea | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 19.2 | 19 | 18.4 | 18 | 17.7 | 17.3 | 16.6 | 16.3 | 15.8 | 15.5 | 14.9 | 14.4 | 14 | 13.8 | 13.5 | 13.2 | 12.9 | 11 | 9.1
Swansea North | Uplands Swansea | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 19.2 | 19.2 | 19.1 | 18.9 | 18.7 | 18.6 | 17.9 | 17.8 | 17.7 | 17.5 | 17.4 | 17.4 | 17.3 | 17.3 | 17.2 | 17.1 | 17 | 15.8 | 14.8
Swansea North | Upper Bank | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.7 | 15.7 | 15.7 | 15.6 | 15.5 | 15.4 | 15.1 | 15 | 14.8 | 14.6 | 14.5 | 14.4 | 14.3 | 14.3 | 14.2 | 14.2 | 14.2 | 13.7 | 13.3
Swansea North | Upper Bank | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.7 | 15.7 | 15.5 | 15.3 | 15 | 14.8 | 14.4 | 14.2 | 14.1 | 13.8 | 13.6 | 13.4 | 13.2 | 13 | 12.7 | 11.8 | 11.7 | 10.9 | 10
Swansea North | Upper Bank | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.7 | 15.6 | 15.3 | 15 | 14.6 | 14.4 | 13.9 | 13.7 | 13.4 | 13.1 | 12.7 | 11.8 | 11.7 | 11.7 | 11.6 | 11.4 | 11.3 | 10.2 | 9.1
Swansea North | Upper Bank | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.7 | 15.7 | 15.7 | 15.5 | 15.4 | 15.2 | 14.8 | 14.6 | 14.5 | 14.3 | 14.1 | 14 | 13.8 | 13.7 | 13.5 | 13.4 | 13.3 | 12.7 | 11.7
Swansea North | Victoria Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Victoria Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Victoria Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Victoria Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Wern | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.9 | 17.9 | 17.9 | 17.8 | 17.8 | 17.8 | 17.5 | 17.3 | 17.2 | 17 | 16.8 | 16.7 | 16.7 | 16.6 | 16.6 | 16.5 | 16.5 | 16.2 | 15.7
Swansea North | Wern | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.9 | 17.9 | 17.8 | 17.7 | 17.5 | 17.3 | 16.9 | 16.7 | 16.5 | 16.2 | 15.9 | 15.6 | 15.5 | 15.2 | 15.1 | 14.9 | 14.7 | 13.5 | 12.5
Swansea North | Wern | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.9 | 17.9 | 17.7 | 17.5 | 17.3 | 17.1 | 16.6 | 16.4 | 16 | 15.8 | 15.5 | 15.3 | 15.2 | 15 | 14.8 | 14.6 | 14.4 | 13.2 | 12.5
Swansea North | Wern | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.9 | 17.9 | 17.9 | 17.8 | 17.7 | 17.6 | 17.2 | 17.1 | 16.9 | 16.8 | 16.6 | 16.5 | 16.4 | 16.3 | 16.2 | 16 | 16 | 15.6 | 14.9
Swansea North | West Cross | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11 | 10.9 | 10.8 | 10.7 | 10.6 | 10.5 | 10.4 | 10.3 | 10.2 | 10.1 | 10 | 10 | 9.9 | 9.9 | 9.9 | 9.8 | 9.8 | 9.6 | 9.2
Swansea North | West Cross | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11 | 10.7 | 10.4 | 10.3 | 10.1 | 9.9 | 9.8 | 9.7 | 9.6 | 9.4 | 9.3 | 9.2 | 8.8 | 8.6 | 8.4 | 8.2 | 8.1 | 6.8 | 5.7
Swansea North | West Cross | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11 | 10.6 | 10.2 | 10 | 9.7 | 9.5 | 9.3 | 9.2 | 8.7 | 8.5 | 8.3 | 8.1 | 8 | 7.8 | 7.6 | 7.4 | 7.1 | 5.7 | 4.3
Swansea North | West Cross | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11 | 10.8 | 10.7 | 10.6 | 10.4 | 10.3 | 10.2 | 10.1 | 10 | 9.9 | 9.8 | 9.8 | 9.7 | 9.7 | 9.7 | 9.7 | 9.6 | 9.2 | 8.3
Swansea North | Westfa | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 6.7 | 6.5 | 6.4 | 6.2 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Westfa | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 6.5 | 6.1 | 5.8 | 5.2 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Westfa | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 6.4 | 5.8 | 5.4 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Westfa | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.7 | 6.4 | 6.1 | 5.7 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Whitland | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.2 | 1.4 | 1.2 | 1 | 0.7 | 0 | 4.1 | 3.5 | 2.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Whitland | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.2 | 1.2 | 0.7 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Whitland | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.2 | 1.1 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Whitland | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.2 | 1.4 | 1 | 0.7 | 0 | 0 | 3.7 | 2.9 | 2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ynys Street | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 8.7 | 8.4 | 8.1 | 7.7 | 7.4 | 7.2 | 7.1 | 7 | 6.9 | 6.8 | 4.9 | 4
Swansea North | Ynys Street | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 7.9 | 7.4 | 6.8 | 6.2 | 5.6 | 5 | 4.4 | 3.9 | 3.4 | 3 | 2.5 | 0 | 0
Swansea North | Ynys Street | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 7.1 | 6.5 | 5.8 | 5.2 | 4.5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ynys Street | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.3 | 8 | 7.7 | 7.3 | 6.9 | 6.6 | 6.4 | 6.2 | 6.1 | 5.9 | 5.8 | 1.4 | 0
Swansea North | Ynysfeio | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.2 | 1.1 | 1 | 0.9 | 0.8 | 0.7 | 9.4 | 9.2 | 9 | 8.7 | 6.9 | 3.2 | 5 | 4.5 | 0 | 0 | 0 | 0 | 0
Swansea North | Ynysfeio | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.2 | 0.9 | 0.6 | 0 | 0 | 0 | 5.8 | 3.3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ynysfeio | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 5.6 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ynysfeio | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.2 | 1 | 0.9 | 0.8 | 0.7 | 0.5 | 9.2 | 9 | 7.2 | 5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ystradgynlais Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 32.5 | 32.1 | 31.3 | 30.9 | 30.1 | 29.5 | 29.6 | 28.3 | 26.8 | 25.1 | 22.9 | 26 | 25.2 | 24.6 | 23.9 | 23.3 | 22.7 | 18.4 | 13
Swansea North | Ystradgynlais Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 32.5 | 31.4 | 30.3 | 29.2 | 28 | 26.6 | 25.8 | 23.2 | 20.5 | 17.4 | 14.1 | 15.3 | 12.4 | 9.1 | 5.4 | 2.6 | 0 | 0 | 0
Swansea North | Ystradgynlais Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 32.5 | 31.2 | 29.5 | 28.5 | 26.6 | 24.5 | 23.3 | 20.4 | 17.1 | 13.7 | 9.7 | 10.6 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0
Swansea North | Ystradgynlais Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 32.5 | 32 | 31.3 | 30.4 | 29.6 | 28.4 | 28.1 | 26.7 | 25.4 | 23.6 | 20.9 | 23.6 | 22.3 | 21 | 20 | 19.1 | 18 | 7.5 | 0
Upper Boat 132 & 33 | Abertysswg | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.5 | 11.4 | 11.3 | 11.2 | 11 | 10.8 | 10.9 | 10.6 | 10.3 | 9.9 | 9.5 | 9.2 | 9.1 | 9 | 8.8 | 8.7 | 8.5 | 7.1 | 6.1
Upper Boat 132 & 33 | Abertysswg | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.5 | 11.2 | 10.8 | 10.5 | 10.2 | 9.7 | 5.3 | 4.7 | 4.2 | 3.5 | 2.8 | 2.1 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Abertysswg | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.5 | 11.1 | 10.5 | 10.3 | 9.7 | 9 | 9.3 | 8.7 | 8.1 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Abertysswg | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.5 | 11.3 | 11 | 10.9 | 10.7 | 10.4 | 10.5 | 10.3 | 9.8 | 9.5 | 9 | 8.6 | 8.2 | 7.6 | 7.2 | 6.8 | 6.6 | 4.9 | 2.8
Upper Boat 132 & 33 | Caerphilly | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17 | 17 | 16.8 | 16.7 | 16.6 | 16.4 | 16.2 | 16.1 | 15.9 | 15.7 | 15.5 | 15.4 | 15.3 | 15.2 | 15.2 | 15.1 | 15 | 14.1 | 13.3
Upper Boat 132 & 33 | Caerphilly | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17 | 16.8 | 16.5 | 16.1 | 15.9 | 15.7 | 15.4 | 15.1 | 14.8 | 14.5 | 14.2 | 14 | 13.4 | 13.1 | 12.5 | 11.9 | 11.3 | 9.8 | 7.6
Upper Boat 132 & 33 | Caerphilly | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17 | 16.7 | 16.2 | 15.8 | 15.5 | 15.1 | 14.7 | 14.4 | 14 | 13.3 | 12.7 | 11.9 | 11.4 | 11.2 | 11 | 10.7 | 10.4 | 8.7 | 6.7
Upper Boat 132 & 33 | Caerphilly | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17 | 16.9 | 16.7 | 16.5 | 16.3 | 16.1 | 15.9 | 15.7 | 15.5 | 15.3 | 15 | 14.7 | 14.3 | 13.4 | 13.4 | 13.3 | 13.3 | 12.6 | 11.7
Upper Boat 132 & 33 | Creigiau | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.8 | 11.6 | 11.6 | 11.5 | 11.5 | 11.3 | 11.2 | 11 | 10.7 | 10.5 | 9.8 | 9.7 | 9.5 | 9.3 | 9.1 | 8.8 | 8.7 | 8 | 6.9
Upper Boat 132 & 33 | Creigiau | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.8 | 11.6 | 11.5 | 11.4 | 11.1 | 10.8 | 10.4 | 9.6 | 9 | 8.3 | 7.6 | 6.6 | 5.9 | 5.5 | 5 | 4.4 | 3.7 | 0 | 0
Upper Boat 132 & 33 | Creigiau | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.8 | 11.5 | 11.4 | 11.2 | 10.8 | 9.8 | 9.3 | 8.6 | 7.7 | 6.9 | 6 | 5.6 | 5.1 | 4 | 2 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Creigiau | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.8 | 11.6 | 11.5 | 11.5 | 11.2 | 10.9 | 10.5 | 9.8 | 9.5 | 9.1 | 8.6 | 8.2 | 7.8 | 7.5 | 7.3 | 7.1 | 6.9 | 5.2 | 1.2
Upper Boat 132 & 33 | Dowlais Grid | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 29.1 | 28.8 | 28.4 | 27.9 | 27.5 | 26.9 | 26.9 | 26.3 | 25.6 | 24.8 | 23.7 | 21.6 | 27.1 | 26.1 | 24.8 | 23.4 | 18.7 | 10.2 | 2.8
Upper Boat 132 & 33 | Dowlais Grid | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 29.1 | 28.2 | 27 | 26.1 | 25 | 23.7 | 17.6 | 14.7 | 11.5 | 6.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Dowlais Grid | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 29.1 | 27.9 | 26.2 | 25.3 | 23.6 | 21.5 | 20.7 | 15.9 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Dowlais Grid | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 29.1 | 28.6 | 27.8 | 27.2 | 26.6 | 25.6 | 22.2 | 19.7 | 17.1 | 13.8 | 8.5 | 4.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Energlyn 33kv | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6 | 6
Upper Boat 132 & 33 | Energlyn 33kv | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6 | 5.9 | 5.7 | 4.6 | 3.6
Upper Boat 132 & 33 | Energlyn 33kv | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6 | 5.9 | 5.8 | 5.8 | 5.7 | 5.5 | 5.4 | 4.4 | 3.7
Upper Boat 132 & 33 | Energlyn 33kv | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6 | 6 | 5.9 | 5.8 | 5.7
Upper Boat 132 & 33 | Energlyn Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 28.9 | 28.8 | 28.7 | 28.5 | 28.4 | 21.2 | 20.9 | 20.6 | 20.3 | 20 | 19.6 | 19.3 | 19.2 | 19.1 | 18.9 | 18.8 | 18.6 | 17.1 | 16
Upper Boat 132 & 33 | Energlyn Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 28.9 | 28.6 | 28.3 | 28.1 | 27.9 | 20.4 | 20 | 19.5 | 18.9 | 18.4 | 17.7 | 17.1 | 16.6 | 15.8 | 15 | 14.1 | 13.4 | 10.1 | 7.8
Upper Boat 132 & 33 | Energlyn Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 28.9 | 28.5 | 28.1 | 27.8 | 27.5 | 19.9 | 19.3 | 18.7 | 18 | 17.3 | 16.2 | 15.3 | 14.6 | 14.1 | 13.6 | 13.2 | 12.7 | 9.7 | 8
Upper Boat 132 & 33 | Energlyn Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 28.9 | 28.8 | 28.6 | 28.4 | 28.3 | 20.9 | 20.6 | 20.3 | 20 | 19.7 | 19.1 | 18.6 | 18.1 | 17.6 | 17.4 | 17.2 | 17.1 | 15.5 | 13.6
Upper Boat 132 & 33 | Gas Yard | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.4 | 5.8 | 4.9 | 4.1 | 3.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Gas Yard | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.4 | 4.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Gas Yard | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Gas Yard | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.4 | 5.5 | 3.1 | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Ironbridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.8 | 11.8 | 11.8 | 11.7 | 11.7 | 11.6 | 11.5 | 11.4 | 11.3 | 11.2 | 11.1 | 11.1 | 11 | 11 | 11 | 11 | 11 | 10.8 | 9.5
Upper Boat 132 & 33 | Ironbridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.8 | 11.8 | 11.6 | 11.5 | 11.3 | 11.2 | 11 | 10.9 | 10.7 | 10.6 | 10.4 | 10.3 | 9.1 | 8 | 7.2 | 6.4 | 5.5 | 0 | 0
Upper Boat 132 & 33 | Ironbridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.8 | 11.7 | 11.5 | 11.3 | 11.2 | 11 | 10.8 | 10.6 | 10.4 | 10.3 | 9.7 | 8.7 | 7.1 | 4 | 2 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Ironbridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.8 | 11.8 | 11.7 | 11.6 | 11.5 | 11.4 | 11.3 | 11.2 | 11.1 | 11 | 10.9 | 10.8 | 10.8 | 10.8 | 10.7 | 10.4 | 10.2 | 5.6 | 1.2
Upper Boat 132 & 33 | Lady Windsor | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 6.5 | 5.5 | 4.6 | 3.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Lady Windsor | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Lady Windsor | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Lady Windsor | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 6.2 | 3.5 | 2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Merthyr East Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 30.9 | 30.2 | 30 | 29.8 | 29.6 | 29.4 | 29 | 28.6 | 28.2 | 26.8 | 23.7 | 21.5 | 26.2 | 25.8 | 24.7 | 23.4 | 18.6 | 10.2 | 2.8
Upper Boat 132 & 33 | Merthyr East Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 30.9 | 30 | 29.5 | 29.2 | 28.8 | 28 | 19.8 | 15.9 | 11.7 | 6.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Merthyr East Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 30.9 | 29.9 | 29.2 | 28.8 | 28.2 | 25.5 | 20.6 | 15.8 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Merthyr East Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 30.9 | 30.2 | 29.9 | 29.6 | 29.4 | 29.1 | 22.1 | 19.7 | 17 | 13.8 | 8.5 | 4.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Middle Fan | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.5 | 5 | 4.2 | 3.5 | 2.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Middle Fan | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.5 | 3.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Middle Fan | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.5 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Middle Fan | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.5 | 4.7 | 2.6 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mill St Tonyrefail | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.5 | 2.9 | 2.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mill St Tonyrefail | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 2.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mill St Tonyrefail | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mill St Tonyrefail | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.3 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Morlanga | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.9 | 3.9 | 3.8 | 3.8 | 3.8 | 3.7 | 3.5 | 3.3 | 3 | 2.7 | 2.3 | 2.1 | 1.9 | 1.8 | 1.7 | 1.6 | 1.5 | 0.8 | 0
Upper Boat 132 & 33 | Morlanga | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.9 | 3.8 | 3.8 | 3.7 | 3.5 | 3.2 | 2.7 | 2.2 | 1.7 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Morlanga | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.9 | 3.8 | 3.8 | 3.6 | 3.3 | 2.9 | 2.4 | 2 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Morlanga | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.9 | 3.9 | 3.8 | 3.8 | 3.6 | 3.3 | 3 | 2.7 | 2.4 | 2.2 | 1.7 | 1.4 | 1.1 | 0.9 | 0.8 | 0.6 | 0 | 0 | 0
Upper Boat 132 & 33 | Mountain Ash | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 7.8 | 7 | 6 | 5 | 3.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mountain Ash | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 7.8 | 5.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mountain Ash | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 7.8 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mountain Ash | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 7.8 | 6.6 | 3.7 | 2.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mountain Ash | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.1 | 5 | 4.8 | 4.7 | 3.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mountain Ash | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.1 | 4.8 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mountain Ash | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.1 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Mountain Ash | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.1 | 4.9 | 3.7 | 2.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Nantgarw Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 30.1 | 30.1 | 30 | 30 | 29.9 | 29.9 | 29.4 | 29.3 | 29 | 28.8 | 28.6 | 28.4 | 28.3 | 28.3 | 28.2 | 28.1 | 28.1 | 27.5 | 26.8
Upper Boat 132 & 33 | Nantgarw Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 30.1 | 30.1 | 30 | 29.8 | 29.6 | 29.4 | 28.8 | 28.5 | 28.2 | 27.8 | 27.4 | 27.1 | 26.7 | 26.3 | 26 | 25.6 | 25.3 | 23.7 | 22.4
Upper Boat 132 & 33 | Nantgarw Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 30.1 | 30.1 | 29.9 | 29.6 | 29.4 | 29.1 | 28.4 | 28 | 27.6 | 27.2 | 26.7 | 26.4 | 26.1 | 25.7 | 25.4 | 25.2 | 24.9 | 23.3 | 22.4
Upper Boat 132 & 33 | Nantgarw Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 30.1 | 30.1 | 30 | 30 | 29.9 | 29.7 | 29.2 | 29 | 28.9 | 28.6 | 28.3 | 28.2 | 28 | 27.9 | 27.8 | 27.7 | 27.5 | 26.6 | 25.6
Upper Boat 132 & 33 | Nantwen | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.4 | 6.3 | 6.3 | 6.3 | 6.3 | 6.2 | 2.6 | 2.5 | 2.3 | 2.2 | 1.9 | 1.8 | 5.6 | 5.5 | 5.5 | 5.4 | 5.3 | 4.4 | 3.6
Upper Boat 132 & 33 | Nantwen | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.4 | 6.3 | 6.2 | 6.2 | 6.1 | 6 | 2.3 | 2 | 1.7 | 1.4 | 1 | 0.6 | 3.6 | 2.8 | 1.6 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Nantwen | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.4 | 6.2 | 6.2 | 6.1 | 6 | 5.9 | 2.2 | 2 | 1.7 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Nantwen | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.4 | 6.3 | 6.3 | 6.2 | 6.2 | 6.1 | 2.6 | 2.4 | 2.3 | 2.2 | 1.9 | 1.6 | 5.1 | 4.7 | 4.6 | 4.4 | 2.5 | 0 | 0
Upper Boat 132 & 33 | Nelson | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7 | 6.3 | 5.3 | 4.5 | 3.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Nelson | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7 | 4.8 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Nelson | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Nelson | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7 | 5.9 | 3.3 | 1.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Pencoed Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 31.1 | 30.8 | 30.7 | 30.6 | 30.4 | 30.2 | 29.9 | 29.5 | 29 | 28.5 | 27.8 | 27.3 | 25.3 | 25.2 | 25.1 | 24.9 | 24.8 | 23.6 | 21.9
Upper Boat 132 & 33 | Pencoed Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 31.1 | 30.7 | 30.5 | 30.3 | 30 | 29.6 | 29 | 28.2 | 27.4 | 25.2 | 24.5 | 23.5 | 21.9 | 20.6 | 19.8 | 18.9 | 18.3 | 13.2 | 10.6
Upper Boat 132 & 33 | Pencoed Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 31.1 | 30.6 | 30.3 | 30 | 29.6 | 29 | 28.1 | 27.3 | 25 | 24.1 | 22.7 | 21.6 | 20.3 | 18.9 | 17.6 | 16.7 | 16.2 | 13 | 11.4
Upper Boat 132 & 33 | Pencoed Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 31.1 | 30.8 | 30.6 | 30.3 | 30 | 29.6 | 29.1 | 28.4 | 27.7 | 25.3 | 24.9 | 24.4 | 24 | 23.8 | 23.2 | 22.5 | 21.8 | 19.3 | 17
Upper Boat 132 & 33 | Pentrebach | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.3 | 9.2 | 9.1 | 9 | 8.8 | 8.6 | 7 | 6.6 | 6.2 | 5.8 | 5.3 | 4.9 | 8.3 | 8.1 | 7.9 | 7.7 | 7.5 | 5.8 | 4.1
Upper Boat 132 & 33 | Pentrebach | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.3 | 9.1 | 8.7 | 8.4 | 8 | 7.5 | 6 | 5.3 | 4.5 | 3.6 | 2.5 | 1.3 | 3.9 | 2.8 | 1.6 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Pentrebach | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.3 | 9 | 8.5 | 8.1 | 7.5 | 6.7 | 5.2 | 4.4 | 3.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Pentrebach | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.3 | 9.2 | 9 | 8.8 | 8.6 | 8.2 | 6.6 | 6.2 | 5.8 | 5.2 | 4.4 | 3.7 | 6.5 | 5.7 | 5.3 | 5.1 | 3 | 0 | 0
Upper Boat 132 & 33 | Pontyclun 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 4.5 | 4.2 | 4.3 | 4.2 | 4.1 | 3.9 | 3.3 | 3.1 | 3 | 2.8 | 2.5 | 2.4 | 2.4 | 2.3 | 2.3 | 2.2 | 2.2 | 1.8 | 1.2
Upper Boat 132 & 33 | Pontyclun 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 4.5 | 4 | 3.9 | 3.7 | 3.5 | 3.3 | 2.5 | 2.2 | 1.8 | 1.5 | 1.1 | 0.8 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Pontyclun 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 4.5 | 3.9 | 3.7 | 3.4 | 3.1 | 2.8 | 1.9 | 1.6 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Pontyclun 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 4.5 | 4.1 | 4.1 | 3.9 | 3.8 | 3.6 | 2.9 | 2.7 | 2.4 | 2.2 | 1.9 | 1.6 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Swansea Road Merthyr | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.3 | 9.2 | 9.1 | 8.9 | 8.8 | 8.6 | 8.3 | 7.8 | 7.3 | 6.7 | 6 | 5.5 | 8.8 | 8.5 | 8.3 | 8 | 7.7 | 5.8 | 4.1
Upper Boat 132 & 33 | Swansea Road Merthyr | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.3 | 9.1 | 8.7 | 8.4 | 8 | 7.5 | 6.9 | 6 | 4.9 | 3.7 | 2.5 | 1.3 | 3.9 | 2.8 | 1.6 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Swansea Road Merthyr | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.3 | 9 | 8.5 | 8.1 | 7.5 | 6.7 | 6 | 4.9 | 3.6 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Swansea Road Merthyr | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.3 | 9.2 | 9 | 8.8 | 8.5 | 8.2 | 7.8 | 7.2 | 6.7 | 5.9 | 4.7 | 3.7 | 6.5 | 5.7 | 5.3 | 5.1 | 3 | 0 | 0
Upper Boat 132 & 33 | Talbot Green Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 28.1 | 26 | 26 | 26 | 26 | 21.2 | 21 | 20.9 | 20.7 | 20.5 | 20.3 | 20.2 | 20 | 19.9 | 19.9 | 19.8 | 19.6 | 19.3 | 18.9
Upper Boat 132 & 33 | Talbot Green Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 28.1 | 26 | 21.2 | 20.9 | 20.8 | 20.6 | 20.5 | 20.1 | 19.8 | 19.5 | 19.2 | 19 | 18.6 | 18.1 | 17.9 | 17.8 | 17.4 | 16.5 | 14.1
Upper Boat 132 & 33 | Talbot Green Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 28.1 | 21.4 | 21.1 | 20.7 | 20.6 | 20.3 | 20.1 | 19.6 | 19.3 | 18.9 | 18.5 | 18.3 | 17.9 | 17.5 | 17.4 | 17.2 | 16.9 | 16 | 13.9
Upper Boat 132 & 33 | Talbot Green Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 28.1 | 26 | 21.3 | 21.1 | 21 | 20.9 | 20.7 | 20.4 | 20.2 | 20 | 19.7 | 19.6 | 19.3 | 19 | 18.9 | 18.9 | 18.6 | 18.1 | 16.7
Upper Boat 132 & 33 | Tonypandy | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.9 | 1.8 | 1.5 | 1.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Tonypandy | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.9 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Tonypandy | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.9 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Tonypandy | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.9 | 1.7 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Trethomas | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.4 | 9.6 | 9.5 | 9.5 | 9.4 | 9.4 | 9.2 | 9.1 | 9 | 8.9 | 8.7 | 8.6 | 8.5 | 8.5 | 8.4 | 8.4 | 8.3 | 7.3 | 6.8
Upper Boat 132 & 33 | Trethomas | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.4 | 9.5 | 9.4 | 9.3 | 9.2 | 9 | 8.9 | 8.7 | 8.5 | 8.2 | 7.9 | 7.7 | 7.4 | 7.1 | 6.7 | 6.2 | 5.3 | 4 | 3
Upper Boat 132 & 33 | Trethomas | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.4 | 9.5 | 9.3 | 9.2 | 9 | 8.8 | 8.6 | 8.3 | 8 | 7.7 | 7.2 | 6.8 | 6.2 | 5.7 | 5.3 | 5.1 | 4.9 | 3.7 | 3
Upper Boat 132 & 33 | Trethomas | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.4 | 9.6 | 9.5 | 9.4 | 9.4 | 9.2 | 9.1 | 9 | 8.9 | 8.7 | 8.5 | 8.4 | 8.2 | 7.9 | 7.7 | 7.5 | 7.3 | 6.1 | 5.3
Upper Boat 132 & 33 | Upper Boat Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 6.2 | 5.6 | 4.7 | 4 | 3.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Upper Boat Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 6.2 | 4.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Upper Boat Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 6.2 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Upper Boat Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 6.2 | 5.3 | 3 | 1.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Upper Boat Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 28.1 | 28 | 27.9 | 27.7 | 27.6 | 27.5 | 26.6 | 26.4 | 26.1 | 25.7 | 25.2 | 24.7 | 24.3 | 24 | 23.8 | 23.6 | 23.5 | 22.6 | 21.5
Upper Boat 132 & 33 | Upper Boat Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 28.1 | 27.8 | 27.5 | 27.5 | 26.4 | 26.2 | 25.8 | 25.2 | 24.6 | 23.8 | 22.9 | 21.8 | 20.6 | 19.3 | 18.7 | 18.1 | 17.6 | 14.2 | 11.9
Upper Boat 132 & 33 | Upper Boat Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 28.1 | 27.7 | 26.5 | 26.4 | 25.9 | 25.4 | 24.8 | 24 | 22.9 | 21.8 | 20.5 | 19.5 | 17.4 | 16.7 | 16.2 | 15.8 | 15.4 | 12.8 | 11.2
Upper Boat 132 & 33 | Upper Boat Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 28.1 | 27.9 | 27.7 | 27.5 | 26.5 | 26.4 | 26.1 | 25.6 | 25 | 24.3 | 23.4 | 22.8 | 22.5 | 22.2 | 22.1 | 21.8 | 21.6 | 19.5 | 17.7
Upper Boat 132 & 33 | Wattstown | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.7 | 4.2 | 3.6 | 3 | 2.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Wattstown | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.7 | 3.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Wattstown | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.7 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Boat 132 & 33 | Wattstown | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.7 | 4 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Caldicot | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.2 | 14.1 | 14 | 13.9 | 13.7 | 13.6 | 9 | 8.8 | 8.5 | 8.3 | 8 | 7.8 | 7.6 | 7.5 | 7.4 | 7.3 | 7.2 | 6.5 | 5.6
Uskmouth | Caldicot | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.2 | 14 | 13.7 | 13.4 | 13.1 | 12.7 | 8.1 | 7.7 | 7.4 | 7 | 6.5 | 6 | 5.6 | 5.1 | 4.7 | 4.3 | 3.9 | 1.6 | 0
Uskmouth | Caldicot | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.2 | 13.9 | 13.5 | 13.2 | 12.7 | 12.2 | 7.7 | 7.2 | 6.7 | 6.2 | 5.5 | 5 | 4.6 | 4.2 | 3.8 | 3.5 | 3.1 | 1 | 0
Uskmouth | Caldicot | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.2 | 14.1 | 13.8 | 13.7 | 13.4 | 13.2 | 8.6 | 8.4 | 8.2 | 7.9 | 7.5 | 7.2 | 6.9 | 6.7 | 6.5 | 6.4 | 6.3 | 4.9 | 3.4
Uskmouth | Chepstow | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.5 | 3.4 | 3.3 | 3.3 | 3.2 | 3.1 | 2.8 | 2.6 | 2.4 | 2.3 | 2.1 | 1.9 | 1.8 | 1.8 | 1.7 | 1.6 | 1.6 | 1 | 0
Uskmouth | Chepstow | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.5 | 3.2 | 3 | 2.8 | 2.6 | 2.4 | 1.9 | 1.6 | 1.3 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Chepstow | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.5 | 3.1 | 2.8 | 2.5 | 2.2 | 1.9 | 1.4 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Chepstow | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.5 | 3.4 | 3.2 | 3.1 | 3 | 2.8 | 2.4 | 2.2 | 2.1 | 1.9 | 1.6 | 1.4 | 1.3 | 1.1 | 1 | 0.9 | 0 | 0 | 0
Uskmouth | Cwmbran Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 30.5 | 30.3 | 30.1 | 29.9 | 29.7 | 29.5 | 30.6 | 30.3 | 30 | 29.8 | 29.5 | 29.3 | 29.2 | 29.2 | 29.1 | 29 | 28.9 | 28.3 | 27.3
Uskmouth | Cwmbran Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 30.5 | 30 | 29.6 | 29.3 | 29 | 28.7 | 29.6 | 29.1 | 28.7 | 28.2 | 27.7 | 27.3 | 26.9 | 26.5 | 26 | 25.6 | 25.2 | 22.7 | 21
Uskmouth | Cwmbran Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 30.5 | 29.9 | 29.3 | 28.9 | 28.5 | 28 | 28.6 | 28 | 27.4 | 26.9 | 26.4 | 26 | 25.6 | 25 | 24.4 | 24 | 23.6 | 21.4 | 19.5
Uskmouth | Cwmbran Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 30.5 | 30.2 | 29.9 | 29.6 | 29.3 | 29 | 29.9 | 29.6 | 29.4 | 29.2 | 28.9 | 28.7 | 28.5 | 28.4 | 28.2 | 28 | 27.7 | 26.5 | 25.4
Uskmouth | Llantarnam Bsp | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 33.2 | 33 | 32.9 | 32.7 | 32.5 | 32.4 | 28.5 | 27.1 | 25.7 | 24 | 22.1 | 20.9 | 19.9 | 19.3 | 18.2 | 17.7 | 16.8 | 9.9 | 4.4
Uskmouth | Llantarnam Bsp | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 33.2 | 32.7 | 32.3 | 32.1 | 31.5 | 28.8 | 21.3 | 18.3 | 15.3 | 12.2 | 8.9 | 6.3 | 4.5 | 1.4 | 0 | 0 | 1.9 | 0 | 0
Uskmouth | Llantarnam Bsp | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 33.2 | 32.5 | 32 | 31.5 | 28.3 | 24.8 | 16.6 | 12.9 | 9.2 | 4.7 | 0.6 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0
Uskmouth | Llantarnam Bsp | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 33.2 | 33 | 32.7 | 32.5 | 32.3 | 31.3 | 23.6 | 21.1 | 18.8 | 16.3 | 13.4 | 4.6 | 3.4 | 2.2 | 0 | 0 | 0 | 0 | 0
Uskmouth | Llantarnam Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 25.2 | 25 | 24.8 | 24.7 | 24.5 | 24.5 | 22.1 | 21.7 | 21.3 | 20.9 | 20.3 | 20 | 19.8 | 19.6 | 19.4 | 19.3 | 19.1 | 12 | 5.2
Uskmouth | Llantarnam Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 25.2 | 24.7 | 24.4 | 24.1 | 23.5 | 23 | 20.3 | 19.6 | 18.9 | 14.9 | 10.3 | 6.9 | 4.9 | 0.9 | 0 | 0 | 4.2 | 0 | 0
Uskmouth | Llantarnam Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 25.2 | 24.6 | 24.1 | 23.7 | 23 | 22.3 | 19.4 | 16.1 | 10.9 | 4.2 | 0 | 0 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0
Uskmouth | Llantarnam Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 25.2 | 24.9 | 24.7 | 24.4 | 24 | 23.7 | 21.2 | 20.8 | 20.4 | 18.2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Magor Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 13.2 | 13.1 | 13 | 12.8 | 12.5 | 12.1 | 10.9 | 10.5 | 10 | 9.6 | 9.1 | 8.6 | 8.4 | 8.1 | 15 | 14.8 | 14.7 | 13.9 | 12.9
Uskmouth | Magor Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 13.2 | 12.9 | 12.4 | 11.7 | 10.8 | 9.6 | 3.5 | 2.4 | 1.1 | 0 | 0 | 0 | 0 | 0 | 2.4 | 1.9 | 0.6 | 0 | 0
Uskmouth | Magor Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 13.2 | 12.8 | 12.3 | 11.6 | 10.5 | 9.7 | 7.9 | 6.7 | 5.3 | 4.3 | 3.2 | 2.4 | 0.9 | 0 | 5.8 | 5.5 | 4.2 | 0 | 0
Uskmouth | Magor Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 13.2 | 12.9 | 12.4 | 11.8 | 10.9 | 9.7 | 8.2 | 7.3 | 6.3 | 5.8 | 4.9 | 4.4 | 3.5 | 3.1 | 10.1 | 10 | 9.3 | 7.1 | 3.2
Uskmouth | Newhouse Primary S/S | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.8 | 5.8 | 5.7 | 5.6 | 5.6 | 5.5 | 5.3 | 5.2 | 5 | 4.8 | 4.7 | 4.6 | 4.6 | 4.5 | 4.4 | 4.3 | 3.7 | 2.9
Uskmouth | Newhouse Primary S/S | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.8 | 5.6 | 5.4 | 5.1 | 5 | 4.7 | 4.5 | 4.1 | 3.7 | 3.3 | 2.9 | 2.4 | 2 | 1.6 | 1.2 | 0 | 0 | 0
Uskmouth | Newhouse Primary S/S | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.7 | 5.5 | 5.3 | 5 | 4.8 | 4.4 | 3.9 | 3.4 | 2.9 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Newhouse Primary S/S | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.8 | 5.7 | 5.5 | 5.3 | 5.2 | 5 | 4.9 | 4.8 | 4.6 | 4.3 | 4.1 | 3.9 | 3.7 | 3.6 | 3.4 | 3 | 0 | 0
Uskmouth | Newport East Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 38.7 | 38.1 | 37.4 | 36.7 | 35.9 | 35 | 20.2 | 19.3 | 18.3 | 17.1 | 15.8 | 15 | 14.2 | 13.7 | 12.7 | 12.3 | 11.6 | 6.3 | 2.7
Uskmouth | Newport East Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 38.7 | 37.4 | 35.6 | 34.3 | 32.2 | 29.9 | 14.7 | 12.4 | 10.2 | 7.8 | 5.4 | 3.6 | 2.6 | 0 | 0 | 0 | 2.2 | 0 | 0
Uskmouth | Newport East Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 38.7 | 36.9 | 34.6 | 32.4 | 29.8 | 26.8 | 11.3 | 8.5 | 5.7 | 2.2 | 0 | 0 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0
Uskmouth | Newport East Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 38.7 | 37.9 | 36.7 | 35.6 | 33.7 | 31.5 | 15.7 | 13.6 | 11.7 | 9.6 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Newport South Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 24.5 | 24.5 | 24.5 | 24.4 | 24.3 | 24.6 | 20.4 | 19.4 | 18.4 | 17.2 | 15.9 | 15.1 | 14.3 | 13.8 | 12.8 | 12.4 | 11.7 | 6.3 | 2.7
Uskmouth | Newport South Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 24.5 | 24.5 | 24.5 | 24.4 | 24.4 | 23.8 | 14.8 | 12.5 | 10.3 | 7.9 | 5.4 | 3.7 | 2.6 | 0 | 0 | 0 | 2.2 | 0 | 0
Uskmouth | Newport South Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 24.5 | 24.5 | 24.5 | 24.6 | 24.1 | 23.4 | 11.3 | 8.5 | 5.8 | 2.2 | 0 | 0 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0
Uskmouth | Newport South Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 24.5 | 24.5 | 24.5 | 24.4 | 24.5 | 23.9 | 15.8 | 13.7 | 11.7 | 9.6 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Newport West Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 23.2 | 23.2 | 23 | 22.8 | 22.6 | 22.4 | 20.4 | 19.4 | 18.4 | 17.2 | 15.9 | 15.1 | 14.2 | 13.8 | 12.8 | 12.4 | 11.7 | 6.3 | 2.7
Uskmouth | Newport West Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 23.2 | 23 | 22.6 | 22.4 | 22.1 | 21.7 | 14.7 | 12.5 | 10.2 | 7.9 | 5.4 | 3.7 | 2.6 | 0 | 0 | 0 | 2.2 | 0 | 0
Uskmouth | Newport West Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 23.2 | 22.9 | 22.4 | 22 | 21.6 | 21.2 | 11.3 | 8.5 | 5.8 | 2.2 | 0 | 0 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0
Uskmouth | Newport West Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 23.2 | 23.1 | 22.8 | 22.6 | 22.4 | 22.1 | 15.8 | 13.7 | 11.7 | 9.6 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | Panteg Primary | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 33.4 | 33.3 | 33.1 | 32.9 | 32.7 | 32.5 | 30.4 | 30 | 29.6 | 29.2 | 28.6 | 28.3 | 28.2 | 28.1 | 27.9 | 27.8 | 27.7 | 26.5 | 24.3
Uskmouth | Panteg Primary | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 33.4 | 33.1 | 32.7 | 32.4 | 32 | 31.5 | 29.2 | 28.6 | 28 | 27.4 | 26.7 | 26 | 25.5 | 24.8 | 24.2 | 23.6 | 23.2 | 18.3 | 15.7
Uskmouth | Panteg Primary | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 33.4 | 33 | 32.4 | 32 | 31.5 | 30.8 | 28.4 | 27.6 | 26.8 | 26 | 25.2 | 24.7 | 24 | 22.6 | 21.3 | 20.3 | 19.8 | 17 | 15.1
Uskmouth | Panteg Primary | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 33.4 | 33.3 | 33 | 32.7 | 32.5 | 32.1 | 29.9 | 29.5 | 29.2 | 28.7 | 28.1 | 27.7 | 27.4 | 27.2 | 26.5 | 25.8 | 25 | 22.5 | 20.6
Uskmouth | Pontypool North Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.2 | 15.2 | 15.1 | 15.1 | 15 | 15 | 14.7 | 14.6 | 14.5 | 14.4 | 14.3 | 14.2 | 14.2 | 14.1 | 14.1 | 14.1 | 14 | 13.5 | 12.9
Uskmouth | Pontypool North Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.2 | 15.1 | 15 | 14.9 | 14.9 | 14.7 | 14.5 | 14.3 | 14.2 | 14 | 13.8 | 13.6 | 13.4 | 13.2 | 12.9 | 12.5 | 12.4 | 10.2 | 9.4
Uskmouth | Pontypool North Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.2 | 15.1 | 15 | 14.9 | 14.7 | 14.6 | 14.3 | 14.1 | 13.9 | 13.7 | 13.4 | 13.2 | 12.9 | 11.1 | 10.6 | 10.2 | 10.1 | 9.3 | 8.8
Uskmouth | Pontypool North Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.2 | 15.2 | 15.1 | 15 | 15 | 14.9 | 14.6 | 14.6 | 14.5 | 14.4 | 14.2 | 14.1 | 14 | 13.9 | 13.7 | 13.5 | 13.3 | 11.9 | 11
Uskmouth | Ringland Newport | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.1 | 16.6 | 16.4 | 16.2 | 15.7 | 15.6 | 15.4 | 15.1 | 14.9 | 14.5 | 14.1 | 13.9 | 13.6 | 13.3 | 12.9 | 12.6 | 12.2 | 11.4 | 10.6
Uskmouth | Ringland Newport | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.1 | 16.4 | 15.7 | 15.3 | 14.9 | 14.3 | 13.9 | 13.4 | 12.9 | 12.4 | 11.7 | 11.1 | 10.3 | 9.5 | 8.2 | 7.4 | 6.6 | 4.4 | 2.6
Uskmouth | Ringland Newport | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.1 | 16.3 | 15.5 | 15 | 14.4 | 13.8 | 13.2 | 12.5 | 11.7 | 10 | 9.1 | 8.4 | 7.7 | 7 | 6.4 | 5.7 | 5 | 2.9 | 1.2
Uskmouth | Ringland Newport | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.1 | 16.5 | 15.8 | 15.6 | 15.2 | 14.7 | 14.2 | 13.6 | 13 | 12.4 | 11.7 | 11.2 | 10.6 | 10.2 | 9.2 | 8.8 | 8.3 | 7.1 | 5.6
Uskmouth | Rogerstone | Primary Substation | 11 | Counterfactual | Headroom (MW) | 33 | 32.9 | 32.7 | 32.6 | 32.4 | 32.2 | 31.6 | 31.3 | 31.1 | 30.8 | 30.4 | 30.2 | 30.1 | 30 | 29.9 | 29.8 | 29.7 | 28.7 | 27.5
Uskmouth | Rogerstone | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 33 | 32.6 | 32.2 | 32 | 31.7 | 31.3 | 30.5 | 30 | 29.5 | 29 | 28.4 | 27.9 | 27.4 | 26.8 | 26.1 | 25.2 | 24.6 | 20.9 | 18.1
Uskmouth | Rogerstone | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 33 | 32.4 | 31.9 | 31.5 | 31 | 30.5 | 29.6 | 29 | 28.4 | 27.7 | 26.8 | 26.3 | 25.7 | 23.6 | 23.1 | 22.5 | 22 | 18.9 | 16.4
Uskmouth | Rogerstone | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 33 | 32.8 | 32.6 | 32.4 | 32.2 | 31.9 | 31.3 | 31 | 30.8 | 30.5 | 30 | 29.8 | 29.5 | 29.2 | 29 | 28.7 | 28.5 | 26.4 | 24.1
Uskmouth | St Arvans | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.8 | 2.7 | 2.6 | 2.6 | 2.5 | 2.4 | 2.3 | 2.2 | 2.1 | 1.9 | 1.7 | 1.6 | 1.5 | 1.5 | 1.4 | 1.4 | 1.3 | 0.9 | 0
Uskmouth | St Arvans | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.8 | 2.5 | 2.4 | 2.2 | 2.1 | 1.9 | 1.7 | 1.4 | 1.2 | 0.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | St Arvans | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.8 | 2.5 | 2.2 | 2.1 | 1.8 | 1.6 | 1.3 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uskmouth | St Arvans | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.8 | 2.6 | 2.5 | 2.4 | 2.4 | 2.2 | 2.1 | 1.9 | 1.8 | 1.6 | 1.4 | 1.2 | 1.1 | 1 | 0.9 | 0.8 | 0 | 0 | 0
Uskmouth | Sudbrook Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 24.5 | 24.2 | 23.9 | 23.7 | 23.4 | 23.1 | 22.5 | 21.9 | 21.3 | 20.6 | 19.8 | 19.3 | 18.9 | 18.7 | 18.4 | 18.2 | 17.9 | 16.1 | 13.9
Uskmouth | Sudbrook Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 24.5 | 23.8 | 23 | 22.4 | 21.7 | 20.9 | 19.7 | 18.7 | 17.7 | 16.6 | 15.3 | 14.1 | 12.9 | 11.5 | 10.5 | 9.4 | 7.4 | 0 | 0
Uskmouth | Sudbrook Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 24.5 | 23.5 | 22.5 | 21.8 | 20.8 | 19.8 | 18.5 | 17.2 | 15.9 | 14.4 | 12.8 | 9.8 | 7.2 | 2.5 | 1.6 | 0.7 | 0 | 0 | 0
Uskmouth | Sudbrook Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 24.5 | 24.1 | 23.5 | 23.1 | 22.5 | 22 | 21.2 | 20.6 | 19.9 | 19.2 | 18.1 | 17.4 | 16.8 | 16.3 | 15.9 | 15.6 | 14.3 | 8.3 | 3.2
Uskmouth | Sudbrook Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.1 | 14.1 | 13.9 | 13.8 | 13.7 | 13.5 | 13.1 | 12.8 | 12.5 | 12.2 | 11.8 | 11.5 | 11.3 | 11.2 | 11.1 | 11 | 10.8 | 9.9 | 8.8
Uskmouth | Sudbrook Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.1 | 13.9 | 13.6 | 13.3 | 13 | 12.6 | 12 | 11.4 | 10.9 | 10.3 | 9.7 | 9.1 | 8.5 | 7.8 | 7.3 | 6.7 | 6.2 | 3.1 | 0.8
Uskmouth | Sudbrook Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.1 | 13.8 | 13.4 | 13.1 | 12.6 | 12.2 | 11.5 | 10.9 | 10.2 | 9.5 | 8.6 | 8 | 7.4 | 6.9 | 6.4 | 6 | 5.5 | 2.7 | 1.1
Uskmouth | Sudbrook Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.1 | 14 | 13.8 | 13.6 | 13.4 | 13.1 | 12.6 | 12.3 | 12 | 11.6 | 11.1 | 10.7 | 10.4 | 10.1 | 9.9 | 9.7 | 9.5 | 7.8 | 5.8

## Fault Level Contribution
[5 empty] | Break contribution (kA) | [17 empty] | Make contribution (kA)
Associated GSP | Substation | Supply Level | Voltage Level (kV) | Scenario | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050
Cardiff East / Aberthaw | Ashgrove | Primary Substation | 11 | Counterfactual | 0.51802 | 0.56001 | 0.60847 | 0.66216 | 0.72298 | 0.79516 | 0.87276 | 0.99333 | 1.0818 | 1.1766 | 1.2747 | 1.3837 | 1.5048 | 1.622 | 1.7358 | 1.8495 | 2.3816 | 2.4605 | 1.0729 | 1.1615 | 1.2623 | 1.3739 | 1.4995 | 1.6485 | 1.8086 | 2.0547 | 2.2366 | 2.4316 | 2.6327 | 2.8553 | 3.1018 | 3.3399 | 3.571 | 3.8019 | 4.8839 | 5.056
Cardiff East / Aberthaw | Ashgrove | Primary Substation | 11 | Electric Engagement | 0.54594 | 0.62956 | 0.77172 | 0.93386 | 1.0876 | 1.262 | 1.4681 | 1.7206 | 1.9419 | 2.1249 | 2.2825 | 2.4435 | 2.5029 | 2.5431 | 2.5852 | 2.6225 | 2.7361 | 2.8911 | 1.14 | 1.3188 | 1.6129 | 1.9464 | 2.264 | 2.6233 | 3.0462 | 3.5624 | 4.0158 | 4.3923 | 4.7176 | 5.0487 | 5.1792 | 5.2703 | 5.3649 | 5.4496 | 5.7186 | 6.0729
Cardiff East / Aberthaw | Ashgrove | Primary Substation | 11 | Holistic Transition | 0.55946 | 0.63653 | 0.71767 | 0.81002 | 0.91304 | 1.0347 | 1.1686 | 1.355 | 1.5063 | 1.6851 | 1.8774 | 2.0715 | 2.252 | 2.4217 | 2.5754 | 2.7256 | 3.0117 | 3.1955 | 1.1737 | 1.3441 | 1.5186 | 1.7177 | 1.9384 | 2.1963 | 2.4786 | 2.8652 | 3.1808 | 3.5542 | 3.9549 | 4.3575 | 4.7304 | 5.0807 | 5.3988 | 5.7128 | 6.35 | 6.7753
Cardiff East / Aberthaw | Ashgrove | Primary Substation | 11 | Hydrogen Evolution | 0.53223 | 0.59267 | 0.6597 | 0.73521 | 0.82173 | 0.92269 | 1.0387 | 1.207 | 1.3493 | 1.5052 | 1.6633 | 1.8186 | 1.9723 | 2.108 | 2.2352 | 2.344 | 2.5029 | 2.5905 | 1.1055 | 1.2333 | 1.3732 | 1.5301 | 1.7099 | 1.9187 | 2.1579 | 2.5011 | 2.7924 | 3.112 | 3.4345 | 3.7509 | 4.064 | 4.3402 | 4.5995 | 4.8217 | 5.162 | 5.3589
Cardiff East / Aberthaw | Barry Grid Primary | Primary Substation | 11 | Counterfactual | 0.35367 | 0.43406 | 0.52413 | 0.61668 | 0.72761 | 0.86231 | 1.0196 | 1.2608 | 1.4451 | 1.642 | 1.84 | 2.0412 | 2.2624 | 2.4874 | 2.7006 | 2.9177 | 3.8798 | 4.1373 | 0.8084 | 0.97627 | 1.1627 | 1.3541 | 1.5838 | 1.8629 | 2.1904 | 2.6876 | 3.0717 | 3.4839 | 3.8948 | 4.3091 | 4.7615 | 5.2224 | 5.6579 | 6.1022 | 8.0862 | 8.6552
Cardiff East / Aberthaw | Barry Grid Primary | Primary Substation | 11 | Electric Engagement | 0.39314 | 0.53826 | 0.79381 | 1.0888 | 1.3626 | 1.6916 | 2.0908 | 2.5746 | 3.0061 | 3.3703 | 3.7076 | 4.0315 | 4.1652 | 4.2781 | 4.3927 | 4.5102 | 5.0999 | 5.4657 | 0.90384 | 1.2112 | 1.7396 | 2.3489 | 2.9162 | 3.5969 | 4.4212 | 5.4177 | 6.3102 | 7.0684 | 7.7741 | 8.4514 | 8.7478 | 8.9969 | 9.2487 | 9.5076 | 10.8089 | 11.655
Cardiff East / Aberthaw | Barry Grid Primary | Primary Substation | 11 | Holistic Transition | 0.4105 | 0.53909 | 0.67983 | 0.83797 | 1.0197 | 1.2532 | 1.5271 | 1.8963 | 2.2059 | 2.5493 | 2.9026 | 3.2468 | 3.5852 | 3.8972 | 4.1879 | 4.4538 | 5.118 | 5.4477 | 0.94709 | 1.2269 | 1.5283 | 1.8692 | 2.2595 | 2.7558 | 3.3373 | 4.112 | 4.7655 | 5.4918 | 6.232 | 6.9535 | 7.6625 | 8.3124 | 8.9188 | 9.4756 | 10.9324 | 11.6844
Cardiff East / Aberthaw | Barry Grid Primary | Primary Substation | 11 | Hydrogen Evolution | 0.37146 | 0.48246 | 0.59995 | 0.72937 | 0.88585 | 1.0758 | 1.304 | 1.6207 | 1.8809 | 2.1785 | 2.4817 | 2.7757 | 3.0595 | 3.3229 | 3.5667 | 3.7861 | 4.2533 | 4.5908 | 0.84924 | 1.0825 | 1.3272 | 1.5968 | 1.9241 | 2.3202 | 2.7947 | 3.4461 | 3.9852 | 4.6064 | 5.2339 | 5.8407 | 6.4257 | 6.9674 | 7.4695 | 7.9235 | 8.9442 | 9.7076
Cardiff East / Aberthaw | Birchgrove | Primary Substation | 11 | Counterfactual | 0.17596 | 0.21452 | 0.26043 | 0.31181 | 0.36769 | 0.4315 | 0.50342 | 0.61595 | 0.69806 | 0.78605 | 0.87638 | 0.9695 | 1.0741 | 1.1774 | 1.2779 | 1.3791 | 1.805 | 1.8896 | 0.38539 | 0.46594 | 0.56094 | 0.66713 | 0.78233 | 0.91376 | 1.0619 | 1.2913 | 1.4599 | 1.6407 | 1.8255 | 2.0152 | 2.2275 | 2.4372 | 2.6411 | 2.8463 | 3.7138 | 3.8959
Cardiff East / Aberthaw | Birchgrove | Primary Substation | 11 | Electric Engagement | 0.19772 | 0.26996 | 0.39594 | 0.54078 | 0.67666 | 0.82446 | 1.0035 | 1.2221 | 1.4123 | 1.5677 | 1.7066 | 1.8391 | 1.8914 | 1.9293 | 1.9668 | 2.0028 | 2.1422 | 2.267 | 0.43793 | 0.59116 | 0.85111 | 1.1491 | 1.4294 | 1.7333 | 2.1001 | 2.5463 | 2.9358 | 3.2555 | 3.5423 | 3.8154 | 3.9301 | 4.0146 | 4.0978 | 4.1783 | 4.4935 | 4.7799
Cardiff East / Aberthaw | Birchgrove | Primary Substation | 11 | Holistic Transition | 0.20928 | 0.2751 | 0.34881 | 0.42533 | 0.5107 | 0.61393 | 0.73026 | 0.89201 | 1.026 | 1.1824 | 1.3478 | 1.4991 | 1.6401 | 1.7691 | 1.8899 | 2.0049 | 2.2277 | 2.3755 | 0.46665 | 0.61079 | 0.76927 | 0.93359 | 1.1157 | 1.3338 | 1.5782 | 1.9135 | 2.193 | 2.52 | 2.8643 | 3.1791 | 3.4715 | 3.7385 | 3.9888 | 4.2295 | 4.7271 | 5.0655
Cardiff East / Aberthaw | Birchgrove | Primary Substation | 11 | Hydrogen Evolution | 0.18689 | 0.23984 | 0.30041 | 0.36999 | 0.44522 | 0.53197 | 0.63503 | 0.78303 | 0.91028 | 1.0471 | 1.1896 | 1.3252 | 1.4594 | 1.5766 | 1.6884 | 1.7837 | 1.9383 | 2.03 | 0.41054 | 0.52166 | 0.64768 | 0.7921 | 0.94776 | 1.1266 | 1.3383 | 1.6396 | 1.8995 | 2.1797 | 2.4704 | 2.7469 | 3.0203 | 3.2588 | 3.4864 | 3.6809 | 4.0109 | 4.2143
Cardiff East / Aberthaw | Boverton | Primary Substation | 11 | Counterfactual | 0.28602 | 0.33566 | 0.39609 | 0.46669 | 0.55059 | 0.65775 | 0.77854 | 0.94915 | 1.0866 | 1.2322 | 1.38 | 1.5201 | 1.6641 | 1.8066 | 1.9402 | 2.0866 | 2.7317 | 2.971 | 0.67253 | 0.77695 | 0.90259 | 1.0493 | 1.2239 | 1.4465 | 1.6988 | 2.0523 | 2.3401 | 2.6466 | 2.9552 | 3.2452 | 3.5399 | 3.8323 | 4.1059 | 4.4061 | 5.7435 | 6.2601
Cardiff East / Aberthaw | Boverton | Primary Substation | 11 | Electric Engagement | 0.31081 | 0.39931 | 0.55461 | 0.74195 | 0.92698 | 1.1724 | 1.4654 | 1.8093 | 2.127 | 2.4121 | 2.6879 | 2.9448 | 3.0886 | 3.227 | 3.3696 | 3.5142 | 4.258 | 4.5682 | 0.73228 | 0.92168 | 1.2442 | 1.6335 | 2.0207 | 2.531 | 3.1396 | 3.8526 | 4.5139 | 5.1102 | 5.6894 | 6.2278 | 6.5377 | 6.8337 | 7.1376 | 7.446 | 9.0366 | 9.7393
Cardiff East / Aberthaw | Boverton | Primary Substation | 11 | Holistic Transition | 0.3214 | 0.40394 | 0.4993 | 0.61603 | 0.74824 | 0.94956 | 1.167 | 1.4432 | 1.6876 | 1.9701 | 2.2592 | 2.5175 | 2.786 | 3.0067 | 3.2243 | 3.4259 | 4.0563 | 4.372 | 0.75847 | 0.9404 | 1.1457 | 1.3988 | 1.6848 | 2.1115 | 2.5739 | 3.156 | 3.6741 | 4.2743 | 4.8838 | 5.4283 | 6.0042 | 6.4641 | 6.9173 | 7.3387 | 8.6942 | 9.3884
Cardiff East / Aberthaw | Boverton | Primary Substation | 11 | Hydrogen Evolution | 0.2984 | 0.36596 | 0.44529 | 0.54813 | 0.66904 | 0.82062 | 0.99142 | 1.2155 | 1.4235 | 1.6566 | 1.8876 | 2.0977 | 2.3 | 2.468 | 2.6376 | 2.7856 | 3.2331 | 3.5991 | 0.70091 | 0.84402 | 1.0104 | 1.226 | 1.4808 | 1.7989 | 2.1567 | 2.6212 | 3.0548 | 3.5455 | 4.0285 | 4.4672 | 4.8862 | 5.2331 | 5.5828 | 5.8901 | 6.8584 | 7.6545
Cardiff East / Aberthaw | Broad St.Barry | Primary Substation | 11 | Counterfactual | 0.13575 | 0.18379 | 0.2399 | 0.29964 | 0.37094 | 0.454 | 0.54618 | 0.68931 | 0.79574 | 0.90828 | 1.0253 | 1.1479 | 1.2866 | 1.4255 | 1.5558 | 1.688 | 2.2353 | 2.4023 | 0.29407 | 0.39542 | 0.51173 | 0.63532 | 0.78234 | 0.95325 | 1.1428 | 1.4343 | 1.6526 | 1.883 | 2.1225 | 2.3727 | 2.655 | 2.9381 | 3.203 | 3.4714 | 4.587 | 4.9418
Cardiff East / Aberthaw | Broad St.Barry | Primary Substation | 11 | Electric Engagement | 0.1591 | 0.25286 | 0.41068 | 0.59391 | 0.762 | 0.94838 | 1.1739 | 1.4462 | 1.6806 | 1.8713 | 2.0398 | 2.3199 | 2.3707 | 2.4037 | 2.6676 | 2.7014 | 2.9016 | 3.0853 | 0.35067 | 0.55166 | 0.87789 | 1.2553 | 1.602 | 1.9858 | 2.449 | 3.0056 | 3.4861 | 3.8785 | 4.2267 | 4.7976 | 4.9082 | 4.9824 | 5.5185 | 5.5952 | 6.0502 | 6.4641
Cardiff East / Aberthaw | Broad St.Barry | Primary Substation | 11 | Holistic Transition | 0.17043 | 0.2553 | 0.34692 | 0.44569 | 0.55741 | 0.69309 | 0.84426 | 1.0511 | 1.2113 | 1.3795 | 1.5566 | 1.8493 | 2.0331 | 2.2045 | 2.5987 | 2.7435 | 3.0303 | 3.2593 | 0.37863 | 0.56634 | 0.7634 | 0.97505 | 1.2131 | 1.4996 | 1.8175 | 2.2462 | 2.5795 | 2.9273 | 3.2928 | 3.8909 | 4.2724 | 4.6291 | 5.4311 | 5.7342 | 6.3737 | 6.8904
Cardiff East / Aberthaw | Broad St.Barry | Primary Substation | 11 | Hydrogen Evolution | 0.14642 | 0.21459 | 0.28978 | 0.37695 | 0.47847 | 0.59806 | 0.73781 | 0.93414 | 1.0954 | 1.2621 | 1.4332 | 1.7406 | 1.9072 | 2.0685 | 2.2726 | 2.4064 | 2.6689 | 2.8481 | 0.31847 | 0.46268 | 0.61912 | 0.79993 | 1.0104 | 1.2577 | 1.5461 | 1.9474 | 2.2768 | 2.6165 | 2.9644 | 3.5845 | 3.9236 | 4.2537 | 4.6698 | 4.9451 | 5.5061 | 5.896
Cardiff East / Aberthaw | Canton | Primary Substation | 11 | Counterfactual | 0.10503 | 0.15681 | 0.21808 | 0.28442 | 0.35197 | 0.42783 | 0.51174 | 0.63797 | 0.73633 | 0.83627 | 0.93788 | 1.0478 | 1.1686 | 1.2865 | 1.4038 | 1.5187 | 2.0236 | 2.1167 | 0.23121 | 0.33994 | 0.46704 | 0.60461 | 0.74421 | 0.90075 | 1.0732 | 1.3303 | 1.5321 | 1.7368 | 1.9445 | 2.1683 | 2.4137 | 2.6529 | 2.8908 | 3.1239 | 4.15 | 4.3489
Cardiff East / Aberthaw | Canton | Primary Substation | 11 | Electric Engagement | 0.13049 | 0.22715 | 0.38803 | 0.55712 | 0.71436 | 0.88762 | 1.0929 | 1.347 | 1.5639 | 1.7407 | 1.9 | 2.0599 | 2.121 | 2.167 | 2.2119 | 2.2543 | 2.3957 | 2.5658 | 0.29253 | 0.49907 | 0.83284 | 1.1813 | 1.506 | 1.8626 | 2.2836 | 2.8025 | 3.2466 | 3.61 | 3.9381 | 4.2663 | 4.3993 | 4.5011 | 4.6005 | 4.6951 | 5.0173 | 5.3977
Cardiff East / Aberthaw | Canton | Primary Substation | 11 | Holistic Transition | 0.14398 | 0.23723 | 0.33963 | 0.43343 | 0.53897 | 0.66317 | 0.79778 | 0.9837 | 1.1353 | 1.3103 | 1.5022 | 1.6875 | 1.8598 | 2.0198 | 2.1686 | 2.3115 | 2.6156 | 2.8169 | 0.32596 | 0.53124 | 0.75254 | 0.95426 | 1.1799 | 1.4426 | 1.7256 | 2.1107 | 2.426 | 2.7908 | 3.1896 | 3.5735 | 3.9293 | 4.26 | 4.5677 | 4.8664 | 5.5364 | 5.9937
Cardiff East / Aberthaw | Canton | Primary Substation | 11 | Hydrogen Evolution | 0.11643 | 0.18751 | 0.26868 | 0.36188 | 0.45676 | 0.56743 | 0.6899 | 0.8699 | 1.0136 | 1.168 | 1.3297 | 1.4867 | 1.6434 | 1.7806 | 1.9112 | 2.0248 | 2.2063 | 2.3083 | 0.25729 | 0.40748 | 0.57711 | 0.77188 | 0.96904 | 1.1983 | 1.4506 | 1.8181 | 2.1111 | 2.4258 | 2.7549 | 3.0743 | 3.393 | 3.672 | 3.9379 | 4.1694 | 4.5532 | 4.7763
Cardiff East / Aberthaw | Cardiff East Grid Primary | Bulk Supply Point | 11 | Counterfactual | 2.4301 | 2.5661 | 2.7221 | 2.898 | 3.1021 | 3.3298 | 3.5856 | 3.9618 | 4.2368 | 4.5355 | 4.8407 | 5.1644 | 5.5378 | 5.8961 | 6.2435 | 6.5985 | 8.1594 | 8.5225 | 5.9869 | 6.2733 | 6.5975 | 6.9621 | 7.385 | 7.8552 | 8.382 | 9.1485 | 9.7122 | 10.3238 | 10.9475 | 11.6064 | 12.3642 | 13.0912 | 13.7962 | 14.516 | 17.6918 | 18.459
Cardiff East / Aberthaw | Cardiff East Grid Primary | Bulk Supply Point | 11 | Electric Engagement | 2.4968 | 2.7603 | 3.1991 | 3.7107 | 4.18 | 4.6804 | 5.2916 | 6.0325 | 6.6733 | 7.2072 | 7.676 | 8.1436 | 8.3394 | 8.4863 | 8.6323 | 8.7676 | 9.2922 | 9.8044 | 6.1478 | 6.7106 | 7.6186 | 8.6772 | 9.646 | 10.6755 | 11.9285 | 13.4406 | 14.7522 | 15.8492 | 16.8159 | 17.7766 | 18.2011 | 18.5248 | 18.8463 | 19.1464 | 20.3304 | 21.4817
Cardiff East / Aberthaw | Cardiff East Grid Primary | Bulk Supply Point | 11 | Holistic Transition | 2.5348 | 2.7885 | 3.0739 | 3.3452 | 3.6476 | 4.0236 | 4.4266 | 4.9886 | 5.4431 | 5.9862 | 6.5612 | 7.1111 | 7.6258 | 8.1026 | 8.5613 | 8.9939 | 10.0312 | 10.6852 | 6.2418 | 6.8016 | 7.4198 | 8.0028 | 8.6484 | 9.4411 | 10.287 | 11.4494 | 12.3955 | 13.527 | 14.7227 | 15.8634 | 16.9282 | 17.9149 | 18.8648 | 19.7698 | 22.0393 | 23.5146
Cardiff East / Aberthaw | Cardiff East Grid Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 2.4608 | 2.6525 | 2.8679 | 3.1323 | 3.4205 | 3.7448 | 4.1221 | 4.6409 | 5.1098 | 5.593 | 6.0891 | 6.5582 | 7.0501 | 7.4586 | 7.87 | 8.2096 | 8.8467 | 9.2458 | 6.0566 | 6.4614 | 6.9101 | 7.4629 | 8.0598 | 8.7294 | 9.5067 | 10.5624 | 11.5181 | 12.5034 | 13.5137 | 14.4697 | 15.4704 | 16.3027 | 17.1404 | 17.8345 | 19.1814 | 20.0423
Cardiff East / Aberthaw | Cardiff South Grid | Bulk Supply Point | 11 | Counterfactual | 0.38953 | 0.43114 | 0.47238 | 0.51498 | 0.64158 | 0.75729 | 0.865 | 0.99295 | 1.0954 | 1.1952 | 1.2975 | 1.4098 | 1.5495 | 1.6886 | 1.824 | 1.9633 | 2.9443 | 3.1114 | 0.79393 | 0.88121 | 0.96656 | 1.0548 | 1.3471 | 1.6081 | 1.8448 | 2.1172 | 2.3356 | 2.544 | 2.7561 | 2.9882 | 3.2777 | 3.5662 | 3.8471 | 4.1359 | 6.1425 | 6.4869
Cardiff East / Aberthaw | Cardiff South Grid | Bulk Supply Point | 11 | Electric Engagement | 0.39046 | 0.46585 | 0.57938 | 0.99153 | 1.2235 | 1.4657 | 1.6995 | 1.9702 | 2.219 | 2.5118 | 2.7503 | 2.9178 | 2.9618 | 2.9954 | 3.0316 | 3.0631 | 3.2035 | 3.3095 | 0.80132 | 0.96282 | 1.1997 | 2.1656 | 2.6904 | 3.2388 | 3.7512 | 4.3329 | 4.8607 | 5.4877 | 5.9979 | 6.3519 | 6.4466 | 6.5199 | 6.5982 | 6.6673 | 6.9796 | 7.2177
Cardiff East / Aberthaw | Cardiff South Grid | Bulk Supply Point | 11 | Holistic Transition | 0.39814 | 0.48717 | 0.79999 | 1.0207 | 1.2527 | 1.4784 | 1.7093 | 2.0111 | 2.3036 | 2.4211 | 2.5437 | 2.6568 | 2.7611 | 2.8602 | 2.9584 | 3.0482 | 3.2818 | 3.4322 | 0.82014 | 1.0156 | 1.7622 | 2.2676 | 2.8011 | 3.3096 | 3.8205 | 4.4713 | 5.1049 | 5.3495 | 5.604 | 5.8386 | 6.0547 | 6.26 | 6.4633 | 6.6511 | 7.159 | 7.4923
Cardiff East / Aberthaw | Cardiff South Grid | Bulk Supply Point | 11 | Hydrogen Evolution | 0.39684 | 0.45263 | 0.50671 | 0.83399 | 1.0387 | 1.7713 | 1.9634 | 2.1699 | 2.3398 | 2.5392 | 2.8663 | 3.0222 | 3.1868 | 3.3326 | 3.4807 | 3.6099 | 3.9733 | 4.1025 | 0.81051 | 0.92876 | 1.0413 | 1.8256 | 2.2994 | 3.827 | 4.255 | 4.7004 | 5.0585 | 5.4715 | 6.1398 | 6.4652 | 6.8083 | 7.1133 | 7.4229 | 7.6947 | 8.4724 | 8.7447
Cardiff East / Aberthaw | Court Road Barry | Primary Substation | 11 | Counterfactual | 0.045306 | 0.056454 | 0.06966 | 0.083495 | 0.10041 | 0.11966 | 0.14188 | 0.17524 | 0.20064 | 0.22702 | 0.25439 | 0.28534 | 0.32009 | 0.3555 | 0.38791 | 0.41936 | 0.57338 | 0.62134 | 0.10264 | 0.12636 | 0.15406 | 0.18299 | 0.21821 | 0.25821 | 0.30432 | 0.37275 | 0.42529 | 0.47975 | 0.53621 | 0.59984 | 0.67108 | 0.74372 | 0.81001 | 0.87424 | 1.1891 | 1.2926
Cardiff East / Aberthaw | Court Road Barry | Primary Substation | 11 | Electric Engagement | 0.051914 | 0.074053 | 0.11231 | 0.15718 | 0.19815 | 0.24477 | 0.30155 | 0.37023 | 0.43016 | 0.48102 | 0.5254 | 0.57279 | 0.58606 | 0.59507 | 0.60433 | 0.61438 | 0.67541 | 0.73601 | 0.11844 | 0.16599 | 0.2455 | 0.33838 | 0.42336 | 0.51987 | 0.63705 | 0.77806 | 0.90142 | 1.0065 | 1.0987 | 1.1969 | 1.2261 | 1.2466 | 1.2676 | 1.2905 | 1.4306 | 1.568
Cardiff East / Aberthaw | Court Road Barry | Primary Substation | 11 | Holistic Transition | 0.055179 | 0.074998 | 0.098155 | 0.12346 | 0.15246 | 0.18687 | 0.22675 | 0.28023 | 0.32084 | 0.36306 | 0.40833 | 0.46104 | 0.51612 | 0.56878 | 0.61778 | 0.66171 | 0.76154 | 0.83426 | 0.12654 | 0.17043 | 0.22059 | 0.27514 | 0.33735 | 0.41072 | 0.49523 | 0.60678 | 0.69159 | 0.77924 | 0.87297 | 0.98217 | 1.0968 | 1.2067 | 1.3091 | 1.4014 | 1.6233 | 1.79
Cardiff East / Aberthaw | Court Road Barry | Primary Substation | 11 | Hydrogen Evolution | 0.04855 | 0.064585 | 0.082661 | 0.10372 | 0.129 | 0.15837 | 0.19339 | 0.24207 | 0.28024 | 0.31939 | 0.35978 | 0.39976 | 0.44065 | 0.48232 | 0.52168 | 0.55618 | 0.62869 | 0.67902 | 0.10989 | 0.14394 | 0.18185 | 0.22595 | 0.27887 | 0.34029 | 0.41329 | 0.51353 | 0.59193 | 0.67204 | 0.75439 | 0.83589 | 0.9195 | 1.0056 | 1.087 | 1.1586 | 1.316 | 1.428
Cardiff East / Aberthaw | Cowbridge | Primary Substation | 11 | Counterfactual | 0.23034 | 0.27717 | 0.33528 | 0.4117 | 0.47393 | 0.56346 | 0.67203 | 0.82348 | 0.94995 | 1.0899 | 1.2189 | 1.3346 | 1.4532 | 1.5734 | 1.6869 | 1.8006 | 2.3427 | 2.6661 | 0.52866 | 0.62724 | 0.74853 | 0.90828 | 1.0401 | 1.2301 | 1.4646 | 1.7893 | 2.0653 | 2.3751 | 2.6547 | 2.9005 | 3.1484 | 3.4002 | 3.6372 | 3.8746 | 5.0332 | 5.7571
Cardiff East / Aberthaw | Cowbridge | Primary Substation | 11 | Electric Engagement | 0.24713 | 0.31889 | 0.44607 | 0.61941 | 0.78026 | 1.0002 | 1.2662 | 1.5887 | 1.8976 | 2.1856 | 2.4778 | 2.7422 | 2.9361 | 3.097 | 3.2546 | 3.4219 | 4.3902 | 4.8378 | 0.56946 | 0.72334 | 0.98983 | 1.3571 | 1.7012 | 2.1656 | 2.7297 | 3.4149 | 4.0754 | 4.6951 | 5.3263 | 5.8976 | 6.329 | 6.676 | 7.0159 | 7.3775 | 9.4767 | 10.5244
Cardiff East / Aberthaw | Cowbridge | Primary Substation | 11 | Holistic Transition | 0.25471 | 0.32882 | 0.41305 | 0.5422 | 0.66017 | 0.85182 | 1.0685 | 1.3399 | 1.5808 | 1.852 | 2.1134 | 2.3623 | 2.6159 | 2.846 | 3.0619 | 3.2616 | 4.0411 | 4.3459 | 0.58821 | 0.75116 | 0.93241 | 1.2177 | 1.4805 | 1.8955 | 2.3695 | 2.96 | 3.4878 | 4.085 | 4.6498 | 5.1896 | 5.7383 | 6.2257 | 6.6835 | 7.1074 | 8.8041 | 9.4801
Cardiff East / Aberthaw | Cowbridge | Primary Substation | 11 | Hydrogen Evolution | 0.23862 | 0.30481 | 0.38934 | 0.50071 | 0.59447 | 0.71695 | 0.8555 | 1.0333 | 1.2045 | 1.4117 | 1.6017 | 1.7729 | 1.9376 | 2.0931 | 2.2421 | 2.381 | 2.8906 | 3.3741 | 0.54785 | 0.68905 | 0.86866 | 1.1064 | 1.3089 | 1.5708 | 1.8672 | 2.2426 | 2.6112 | 3.0665 | 3.4759 | 3.843 | 4.1933 | 4.5201 | 4.8342 | 5.1295 | 6.2673 | 7.3627
Cardiff East / Aberthaw | Crwys Road | Primary Substation | 11 | Counterfactual | 0.093783 | 0.14915 | 0.21097 | 0.27849 | 0.3556 | 0.44241 | 0.54015 | 0.69539 | 0.80764 | 0.9267 | 1.0497 | 1.1743 | 1.3151 | 1.4541 | 1.5893 | 1.7247 | 2.2561 | 2.3457 | 0.20051 | 0.31609 | 0.44384 | 0.58314 | 0.74175 | 0.92005 | 1.1204 | 1.4356 | 1.6648 | 1.9074 | 2.1577 | 2.411 | 2.6962 | 2.9777 | 3.2516 | 3.5258 | 4.6052 | 4.7971
Cardiff East / Aberthaw | Crwys Road | Primary Substation | 11 | Electric Engagement | 0.12028 | 0.22217 | 0.39218 | 0.58753 | 0.77014 | 0.96475 | 1.2013 | 1.4906 | 1.739 | 1.9362 | 2.1099 | 2.2699 | 2.324 | 2.3651 | 2.4021 | 2.4368 | 2.5565 | 2.694 | 0.26455 | 0.48079 | 0.83103 | 1.232 | 1.6075 | 2.0072 | 2.4908 | 3.0798 | 3.5869 | 3.9909 | 4.348 | 4.6763 | 4.7953 | 4.8873 | 4.971 | 5.0501 | 5.3293 | 5.6437
Cardiff East / Aberthaw | Crwys Road | Primary Substation | 11 | Holistic Transition | 0.13548 | 0.22854 | 0.32562 | 0.431 | 0.54815 | 0.68153 | 0.83293 | 1.0439 | 1.2142 | 1.4097 | 1.6198 | 1.8008 | 1.9697 | 2.1259 | 2.2703 | 2.4105 | 2.6715 | 2.8528 | 0.30232 | 0.50643 | 0.71525 | 0.94101 | 1.1903 | 1.4717 | 1.7889 | 2.2245 | 2.5778 | 2.9841 | 3.4197 | 3.7952 | 4.1447 | 4.4682 | 4.7677 | 5.0613 | 5.6455 | 6.0626
Cardiff East / Aberthaw | Crwys Road | Primary Substation | 11 | Hydrogen Evolution | 0.1056 | 0.18054 | 0.26065 | 0.35267 | 0.45622 | 0.57435 | 0.71715 | 0.91609 | 1.0839 | 1.2615 | 1.4487 | 1.626 | 1.8014 | 1.9566 | 2.1032 | 2.2278 | 2.4099 | 2.4994 | 0.22748 | 0.38463 | 0.55093 | 0.74153 | 0.95536 | 1.1986 | 1.4916 | 1.8956 | 2.237 | 2.5981 | 2.9783 | 3.3384 | 3.6946 | 4.0099 | 4.3077 | 4.5615 | 4.9467 | 5.144
Cardiff East / Aberthaw | Cyncoed | Primary Substation | 11 | Counterfactual | 0.54944 | 0.63882 | 0.86118 | 0.97858 | 1.1182 | 1.2688 | 1.4418 | 1.7143 | 1.9183 | 2.136 | 2.3621 | 2.5901 | 2.839 | 3.0787 | 3.3128 | 3.5437 | 4.5527 | 4.6695 | 1.2435 | 1.4306 | 1.8834 | 2.1267 | 2.4155 | 2.7264 | 3.0833 | 3.64 | 4.0601 | 4.5081 | 4.9731 | 5.439 | 5.9458 | 6.4324 | 6.9075 | 7.3761 | 9.4268 | 9.6869
Cardiff East / Aberthaw | Cyncoed | Primary Substation | 11 | Electric Engagement | 0.6038 | 0.89014 | 1.1925 | 1.5384 | 1.862 | 2.2273 | 2.6684 | 3.2162 | 3.6939 | 4.0764 | 4.4055 | 4.7223 | 4.8226 | 4.892 | 4.9593 | 5.024 | 5.2039 | 5.4738 | 1.3743 | 1.9676 | 2.5925 | 3.3048 | 3.9724 | 4.7263 | 5.633 | 6.7554 | 7.737 | 8.5254 | 9.2057 | 9.8582 | 10.0813 | 10.2401 | 10.3941 | 10.5431 | 10.9772 | 11.5987
Cardiff East / Aberthaw | Cyncoed | Primary Substation | 11 | Holistic Transition | 0.63274 | 0.90356 | 1.0862 | 1.2873 | 1.5313 | 1.7925 | 2.0899 | 2.4905 | 2.7958 | 3.1521 | 3.5332 | 3.9015 | 4.2426 | 4.5577 | 4.8446 | 5.122 | 5.4655 | 5.771 | 1.4465 | 2.0174 | 2.4115 | 2.8443 | 3.3675 | 3.924 | 4.5526 | 5.3862 | 6.0222 | 6.7657 | 7.5589 | 8.3227 | 9.0275 | 9.6784 | 10.2722 | 10.8522 | 11.6593 | 12.3773
Cardiff East / Aberthaw | Cyncoed | Primary Substation | 11 | Hydrogen Evolution | 0.57363 | 0.81299 | 0.95429 | 1.1271 | 1.3275 | 1.5488 | 1.8237 | 2.1845 | 2.4788 | 2.7879 | 3.1059 | 3.4179 | 3.7201 | 3.9926 | 4.2434 | 4.4599 | 4.7386 | 4.8619 | 1.2985 | 1.7896 | 2.0845 | 2.4456 | 2.8643 | 3.3251 | 3.8962 | 4.6343 | 5.2384 | 5.8712 | 6.5189 | 7.154 | 7.769 | 8.3228 | 8.8332 | 9.2746 | 9.8715 | 10.1576
Cardiff East / Aberthaw | East Aberthaw Primary | Primary Substation | 11 | Counterfactual | 0.93172 | 0.96714 | 1.3188 | 1.3658 | 1.4234 | 1.5046 | 1.6003 | 1.7387 | 1.8513 | 1.9735 | 2.0914 | 2.2021 | 2.3189 | 2.4384 | 2.5973 | 2.7664 | 3.4814 | 3.7184 | 2.0207 | 2.0948 | 2.9558 | 3.0537 | 3.1747 | 3.3454 | 3.549 | 3.8408 | 4.0819 | 4.3465 | 4.5975 | 4.8297 | 5.0715 | 5.3193 | 5.6517 | 6.0046 | 7.5155 | 8.0435
Cardiff East / Aberthaw | East Aberthaw Primary | Primary Substation | 11 | Electric Engagement | 0.9307 | 1.3029 | 1.4229 | 1.5679 | 1.7061 | 1.9077 | 2.1486 | 2.4393 | 2.7116 | 2.9589 | 3.2037 | 3.4328 | 3.666 | 3.8665 | 4.0676 | 4.2581 | 4.9833 | 5.3229 | 2.0264 | 2.9326 | 3.1818 | 3.4848 | 3.7755 | 4.1969 | 4.7006 | 5.3091 | 5.8823 | 6.4063 | 6.9278 | 7.4156 | 7.9301 | 8.3664 | 8.803 | 9.2163 | 10.7816 | 11.5709
Cardiff East / Aberthaw | East Aberthaw Primary | Primary Substation | 11 | Holistic Transition | 1.2472 | 1.302 | 1.3673 | 1.4523 | 1.5513 | 1.7085 | 1.8896 | 2.1238 | 2.4262 | 2.7468 | 3.0646 | 3.3335 | 3.5552 | 3.7547 | 3.9464 | 4.1289 | 4.7417 | 4.9935 | 2.8177 | 2.937 | 3.0772 | 3.2642 | 3.4816 | 3.8185 | 4.2094 | 4.7107 | 5.3669 | 6.0642 | 6.7477 | 7.3246 | 7.7968 | 8.2156 | 8.6179 | 9.0021 | 10.3326 | 10.8949
Cardiff East / Aberthaw | East Aberthaw Primary | Primary Substation | 11 | Hydrogen Evolution | 0.92047 | 1.2751 | 1.3297 | 1.3939 | 1.4752 | 1.5853 | 1.7125 | 1.8822 | 2.1069 | 2.3363 | 2.5682 | 2.7996 | 3.0146 | 3.161 | 3.2969 | 3.4231 | 3.8121 | 4.1639 | 2.0006 | 2.8686 | 2.9829 | 3.118 | 3.2914 | 3.5242 | 3.7928 | 4.1468 | 4.6288 | 5.1253 | 5.6214 | 6.1158 | 6.5726 | 6.8775 | 7.1604 | 7.4252 | 8.2853 | 9.0784
Cardiff East / Aberthaw | Ely | Primary Substation | 11 | Counterfactual | 0.12039 | 0.16984 | 0.23168 | 0.29403 | 0.37154 | 0.45601 | 0.55036 | 0.68943 | 0.79747 | 0.91323 | 1.0295 | 1.1516 | 1.3082 | 1.4261 | 1.5428 | 1.6558 | 2.1132 | 2.2348 | 0.26821 | 0.37141 | 0.49898 | 0.6278 | 0.78747 | 0.96134 | 1.155 | 1.4382 | 1.6599 | 1.897 | 2.135 | 2.3844 | 2.706 | 2.9448 | 3.1809 | 3.4098 | 4.3397 | 4.5983
Cardiff East / Aberthaw | Ely | Primary Substation | 11 | Electric Engagement | 0.14198 | 0.22951 | 0.37764 | 0.55586 | 0.71676 | 0.892 | 1.1082 | 1.3774 | 1.6108 | 1.7941 | 1.9568 | 2.1016 | 2.1583 | 2.1984 | 2.2383 | 2.2793 | 2.4881 | 2.6373 | 0.3204 | 0.50623 | 0.81206 | 1.1796 | 1.512 | 1.8738 | 2.3189 | 2.8721 | 3.3533 | 3.7319 | 4.0686 | 4.3669 | 4.4892 | 4.5779 | 4.6657 | 4.7558 | 5.2186 | 5.5506
Cardiff East / Aberthaw | Ely | Primary Substation | 11 | Holistic Transition | 0.15492 | 0.23857 | 0.33791 | 0.45357 | 0.58682 | 0.73406 | 0.88851 | 1.0893 | 1.2351 | 1.4 | 1.5795 | 1.7458 | 1.9075 | 2.0596 | 2.2054 | 2.3258 | 2.5727 | 2.7633 | 0.35254 | 0.53571 | 0.74885 | 0.99759 | 1.2831 | 1.5958 | 1.9221 | 2.3401 | 2.6425 | 2.9854 | 3.3572 | 3.7026 | 4.039 | 4.3558 | 4.6591 | 4.911 | 5.4577 | 5.8839
Cardiff East / Aberthaw | Ely | Primary Substation | 11 | Hydrogen Evolution | 0.1299 | 0.19608 | 0.27441 | 0.37319 | 0.48488 | 0.6104 | 0.75483 | 0.94409 | 1.1024 | 1.2694 | 1.4445 | 1.6088 | 1.7628 | 1.9067 | 2.0462 | 2.164 | 2.385 | 2.4963 | 0.28995 | 0.42898 | 0.59174 | 0.79763 | 1.0305 | 1.292 | 1.5912 | 1.9787 | 2.3025 | 2.6442 | 3.0017 | 3.338 | 3.6505 | 3.9441 | 4.2292 | 4.4703 | 4.9356 | 5.1746
Cardiff East / Aberthaw | Fairwater | Primary Substation | 11 | Counterfactual | 0.20315 | 0.26097 | 0.32831 | 0.4021 | 0.49197 | 0.59374 | 0.71224 | 0.90025 | 1.0456 | 1.2031 | 1.3644 | 1.5176 | 1.6813 | 1.8354 | 1.9859 | 2.1345 | 2.7645 | 2.8529 | 0.45783 | 0.57882 | 0.71848 | 0.87124 | 1.0571 | 1.2674 | 1.5125 | 1.8979 | 2.1986 | 2.5247 | 2.8581 | 3.1722 | 3.5061 | 3.8193 | 4.125 | 4.4267 | 5.7104 | 5.9069
Cardiff East / Aberthaw | Fairwater | Primary Substation | 11 | Electric Engagement | 0.23746 | 0.34624 | 0.53732 | 0.75819 | 0.96524 | 1.2089 | 1.5054 | 1.8769 | 2.2013 | 2.4592 | 2.6818 | 2.8882 | 2.9569 | 3.005 | 3.0518 | 3.0972 | 3.2417 | 3.4258 | 0.54075 | 0.77146 | 1.1661 | 1.6209 | 2.0483 | 2.5528 | 3.1649 | 3.9301 | 4.6007 | 5.1354 | 5.5984 | 6.0257 | 6.1791 | 6.2888 | 6.3955 | 6.4996 | 6.8425 | 7.2682
Cardiff East / Aberthaw | Fairwater | Primary Substation | 11 | Holistic Transition | 0.25597 | 0.35446 | 0.46875 | 0.60946 | 0.78754 | 0.9753 | 1.1847 | 1.4584 | 1.658 | 1.8899 | 2.1347 | 2.3654 | 2.5792 | 2.7755 | 2.9549 | 3.1284 | 3.4079 | 3.6059 | 0.58691 | 0.80261 | 1.049 | 1.3523 | 1.7357 | 2.1375 | 2.5826 | 3.1554 | 3.5726 | 4.0587 | 4.5697 | 5.0501 | 5.4936 | 5.9002 | 6.2726 | 6.6363 | 7.2761 | 7.7403
Cardiff East / Aberthaw | Fairwater | Primary Substation | 11 | Hydrogen Evolution | 0.21846 | 0.29832 | 0.38714 | 0.50359 | 0.63807 | 0.79338 | 0.99166 | 1.238 | 1.4443 | 1.6492 | 1.8557 | 2.0567 | 2.2513 | 2.4263 | 2.5874 | 2.7271 | 2.9213 | 3.016 | 0.49302 | 0.66076 | 0.8458 | 1.0894 | 1.3709 | 1.6959 | 2.1105 | 2.6169 | 3.0433 | 3.4648 | 3.8866 | 4.2967 | 4.6936 | 5.0499 | 5.378 | 5.6634 | 6.082 | 6.3016
Cardiff East / Aberthaw | Grangetown Grid Primary | Bulk Supply Point | 11 | Counterfactual | 2.7732 | 2.8638 | 2.9765 | 3.0735 | 3.1906 | 3.3239 | 3.4571 | 3.6598 | 3.814 | 3.9822 | 4.1505 | 4.3268 | 4.5307 | 4.7231 | 4.9077 | 5.0992 | 5.9585 | 6.3091 | 6.8706 | 7.0622 | 7.297 | 7.4988 | 7.7426 | 8.0188 | 8.2942 | 8.7092 | 9.0272 | 9.3742 | 9.7206 | 10.0811 | 10.497 | 10.8889 | 11.2652 | 11.6551 | 13.4112 | 14.1517
Cardiff East / Aberthaw | Grangetown Grid Primary | Bulk Supply Point | 11 | Electric Engagement | 2.8061 | 2.9511 | 3.1885 | 3.4649 | 3.7241 | 4.023 | 4.3582 | 4.7748 | 5.1399 | 5.439 | 5.6941 | 5.9397 | 6.043 | 5.4911 | 5.5701 | 5.6493 | 6.2066 | 6.4698 | 6.9499 | 7.2613 | 7.7554 | 8.3315 | 8.8712 | 9.4945 | 10.1881 | 11.0478 | 11.8032 | 12.4233 | 12.9537 | 13.4602 | 13.6828 | 12.28 | 12.4527 | 12.6255 | 13.8607 | 14.454
Cardiff East / Aberthaw | Grangetown Grid Primary | Bulk Supply Point | 11 | Holistic Transition | 2.825 | 2.9789 | 3.1638 | 3.3375 | 3.5651 | 3.8333 | 4.0883 | 4.4135 | 4.6385 | 4.9085 | 5.1951 | 5.5085 | 5.8476 | 3.6693 | 3.9707 | 4.1882 | 4.6487 | 5.0046 | 6.9966 | 7.3369 | 7.7388 | 8.1133 | 8.6043 | 9.1776 | 9.7187 | 10.3982 | 10.867 | 11.4299 | 12.0255 | 12.6804 | 13.393 | 7.8201 | 8.4547 | 8.9111 | 9.9377 | 10.738
Cardiff East / Aberthaw | Grangetown Grid Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 2.7903 | 2.9145 | 3.0613 | 3.2267 | 3.4026 | 3.6053 | 3.8258 | 4.1056 | 4.3674 | 4.6229 | 4.8822 | 5.1256 | 5.3862 | 4.9805 | 5.2164 | 5.4091 | 5.9077 | 6.2344 | 6.9095 | 7.1742 | 7.4831 | 7.8322 | 8.2003 | 8.6239 | 9.0827 | 9.6559 | 10.1929 | 10.7159 | 11.246 | 11.744 | 12.2762 | 11.162 | 11.6467 | 12.0443 | 13.1081 | 13.8132
Cardiff East / Aberthaw | Heath | Primary Substation | 11 | Counterfactual | 0.26108 | 0.33978 | 0.42899 | 0.52368 | 0.63444 | 0.75826 | 0.89849 | 1.1128 | 1.268 | 1.4366 | 1.6073 | 1.7857 | 1.987 | 2.189 | 2.3829 | 2.5766 | 3.3856 | 3.517 | 0.57658 | 0.7409 | 0.92562 | 1.1216 | 1.3499 | 1.6047 | 1.8925 | 2.3281 | 2.6455 | 2.9898 | 3.338 | 3.701 | 4.1094 | 4.5191 | 4.9122 | 5.3049 | 6.9485 | 7.2316
Cardiff East / Aberthaw | Heath | Primary Substation | 11 | Electric Engagement | 0.30094 | 0.44282 | 0.68714 | 0.9658 | 1.2263 | 1.5103 | 1.8479 | 2.2596 | 2.617 | 2.9023 | 3.1512 | 3.3958 | 3.4785 | 3.5377 | 3.5977 | 3.6526 | 3.8224 | 4.0481 | 0.67271 | 0.97356 | 1.4774 | 2.0501 | 2.5866 | 3.1698 | 3.8605 | 4.6986 | 5.428 | 6.0129 | 6.5245 | 7.0267 | 7.2089 | 7.3429 | 7.4779 | 7.6029 | 8.0022 | 8.5167
Cardiff East / Aberthaw | Heath | Primary Substation | 11 | Holistic Transition | 0.323 | 0.45399 | 0.59595 | 0.74418 | 0.91191 | 1.104 | 1.3247 | 1.6286 | 1.8771 | 2.1701 | 2.4782 | 2.7677 | 3.0393 | 3.2884 | 3.5208 | 3.7389 | 4.1218 | 4.3948 | 0.7276 | 1.0137 | 1.3188 | 1.6365 | 1.9932 | 2.3983 | 2.8603 | 3.4879 | 4.004 | 4.6134 | 5.2535 | 5.8534 | 6.4142 | 6.929 | 7.4095 | 7.8659 | 8.7272 | 9.3588
Cardiff East / Aberthaw | Heath | Primary Substation | 11 | Hydrogen Evolution | 0.27857 | 0.38521 | 0.50174 | 0.62883 | 0.77508 | 0.94068 | 1.1392 | 1.4211 | 1.657 | 1.9108 | 2.1752 | 2.431 | 2.6861 | 2.9103 | 3.1204 | 3.3002 | 3.5581 | 3.688 | 0.61634 | 0.83974 | 1.0819 | 1.3455 | 1.6477 | 1.9888 | 2.3958 | 2.9688 | 3.4495 | 3.9662 | 4.5038 | 5.0239 | 5.5424 | 5.9979 | 6.4252 | 6.7914 | 7.3386 | 7.6278
Cardiff East / Aberthaw | Heath Hospital Primary | Primary Substation | 11 | Counterfactual | 0.047873 | 0.055441 | 0.064443 | 0.074431 | 0.085815 | 0.098239 | 0.11211 | 0.13446 | 0.15029 | 0.1671 | 0.18436 | 0.20259 | 0.22313 | 0.24361 | 0.26356 | 0.28334 | 0.36748 | 0.37803 | 0.10274 | 0.1186 | 0.13726 | 0.15793 | 0.18146 | 0.20706 | 0.23555 | 0.28105 | 0.31343 | 0.34781 | 0.38298 | 0.42008 | 0.46175 | 0.50327 | 0.54375 | 0.58384 | 0.75471 | 0.77786
Cardiff East / Aberthaw | Heath Hospital Primary | Primary Substation | 11 | Electric Engagement | 0.052087 | 0.066757 | 0.092434 | 0.12215 | 0.14997 | 0.17966 | 0.21578 | 0.25931 | 0.29696 | 0.32751 | 0.3536 | 0.37927 | 0.38781 | 0.39361 | 0.39935 | 0.4048 | 0.4198 | 0.44355 | 0.1129 | 0.144 | 0.19699 | 0.25807 | 0.31537 | 0.3763 | 0.45017 | 0.53872 | 0.6155 | 0.67807 | 0.73163 | 0.78429 | 0.80318 | 0.81638 | 0.82943 | 0.8419 | 0.87804 | 0.93232
Cardiff East / Aberthaw | Heath Hospital Primary | Primary Substation | 11 | Holistic Transition | 0.05447 | 0.067639 | 0.082272 | 0.097824 | 0.11529 | 0.13505 | 0.15763 | 0.1895 | 0.21553 | 0.24559 | 0.27774 | 0.30851 | 0.33703 | 0.36346 | 0.38768 | 0.41123 | 0.45518 | 0.48085 | 0.1188 | 0.14759 | 0.17909 | 0.2124 | 0.24956 | 0.2913 | 0.33857 | 0.40439 | 0.45846 | 0.52098 | 0.58766 | 0.65139 | 0.71018 | 0.76474 | 0.81482 | 0.86403 | 0.96194 | 1.0223
Cardiff East / Aberthaw | Heath Hospital Primary | Primary Substation | 11 | Hydrogen Evolution | 0.049626 | 0.060134 | 0.071954 | 0.084991 | 0.099708 | 0.11633 | 0.13618 | 0.16508 | 0.18867 | 0.21422 | 0.24115 | 0.26762 | 0.29346 | 0.31673 | 0.33804 | 0.35634 | 0.38007 | 0.38996 | 0.10672 | 0.12877 | 0.15335 | 0.18041 | 0.21085 | 0.24506 | 0.28574 | 0.34446 | 0.39251 | 0.44454 | 0.49925 | 0.55304 | 0.60556 | 0.65287 | 0.69617 | 0.73342 | 0.7841 | 0.80681
Cardiff East / Aberthaw | Highmead | Primary Substation | 11 | Counterfactual | 0.31768 | 0.40416 | 0.50762 | 0.62056 | 0.7514 | 0.90157 | 1.0717 | 1.3377 | 1.5339 | 1.7497 | 1.9656 | 2.1839 | 2.4274 | 2.6672 | 2.9003 | 3.132 | 4.0951 | 4.2583 | 0.72971 | 0.91026 | 1.1245 | 1.358 | 1.628 | 1.9377 | 2.2886 | 2.8317 | 3.2357 | 3.6807 | 4.1238 | 4.5697 | 5.065 | 5.5524 | 6.0259 | 6.4965 | 8.4609 | 8.8198
Cardiff East / Aberthaw | Highmead | Primary Substation | 11 | Electric Engagement | 0.36698 | 0.53117 | 0.82176 | 1.1586 | 1.4736 | 1.8294 | 2.2584 | 2.7823 | 3.2396 | 3.6103 | 3.9409 | 4.2534 | 4.371 | 4.457 | 4.5574 | 4.6419 | 4.9744 | 5.2702 | 0.84872 | 1.1964 | 1.7959 | 2.489 | 3.1389 | 3.8718 | 4.7525 | 5.8242 | 6.7627 | 7.5271 | 8.2115 | 8.8573 | 9.1172 | 9.3097 | 9.5381 | 9.7274 | 10.4794 | 11.1604
Cardiff East / Aberthaw | Highmead | Primary Substation | 11 | Holistic Transition | 0.39371 | 0.53944 | 0.70538 | 0.89232 | 1.103 | 1.3505 | 1.6316 | 2.0176 | 2.3318 | 2.724 | 3.1028 | 3.4538 | 3.7842 | 4.0883 | 4.3694 | 4.6384 | 5.1619 | 5.4824 | 0.9153 | 1.2339 | 1.5909 | 1.9929 | 2.4435 | 2.9679 | 3.5605 | 4.3629 | 5.0193 | 5.8532 | 6.6427 | 7.3734 | 8.0595 | 8.6896 | 9.2728 | 9.836 | 11.0054 | 11.7467
Cardiff East / Aberthaw | Highmead | Primary Substation | 11 | Hydrogen Evolution | 0.33938 | 0.45824 | 0.59324 | 0.74756 | 0.92536 | 1.1318 | 1.3789 | 1.7289 | 2.0237 | 2.332 | 2.6542 | 2.9635 | 3.266 | 3.538 | 3.8075 | 4.0271 | 4.3715 | 4.5686 | 0.77932 | 1.0284 | 1.3092 | 1.6299 | 1.9992 | 2.4268 | 2.9363 | 3.6514 | 4.2565 | 4.8892 | 5.5476 | 6.179 | 6.7957 | 7.3499 | 7.9066 | 8.3556 | 9.0953 | 9.5404
Cardiff East / Aberthaw | Llandough | Primary Substation | 11 | Counterfactual | 0.16914 | 0.20869 | 0.25359 | 0.3017 | 0.35898 | 0.42986 | 0.50921 | 0.63451 | 0.72738 | 0.82915 | 0.92943 | 1.0351 | 1.1483 | 1.2663 | 1.3749 | 1.4844 | 1.9518 | 2.0878 | 0.38142 | 0.46363 | 0.5565 | 0.65593 | 0.77433 | 0.92076 | 1.0854 | 1.3428 | 1.5356 | 1.7473 | 1.9547 | 2.1715 | 2.4028 | 2.644 | 2.8656 | 3.0885 | 4.0474 | 4.3441
Cardiff East / Aberthaw | Llandough | Primary Substation | 11 | Electric Engagement | 0.19031 | 0.26383 | 0.39201 | 0.54268 | 0.68265 | 0.84601 | 1.0446 | 1.286 | 1.5018 | 1.6796 | 1.8423 | 1.9993 | 2.0607 | 2.1029 | 2.1453 | 2.1932 | 2.4465 | 2.6243 | 0.43268 | 0.58781 | 0.85239 | 1.1632 | 1.4527 | 1.7903 | 2.1999 | 2.696 | 3.1411 | 3.5103 | 3.8497 | 4.1773 | 4.3127 | 4.4061 | 4.5 | 4.6057 | 5.1687 | 5.5771
Cardiff East / Aberthaw | Llandough | Primary Substation | 11 | Holistic Transition | 0.19968 | 0.26341 | 0.3347 | 0.41592 | 0.50873 | 0.62685 | 0.76217 | 0.94855 | 1.098 | 1.2596 | 1.4236 | 1.5908 | 1.7599 | 1.9162 | 2.0592 | 2.1919 | 2.4678 | 2.6398 | 0.45601 | 0.59415 | 0.7468 | 0.92147 | 1.1202 | 1.3706 | 1.6573 | 2.0471 | 2.3613 | 2.7005 | 3.0423 | 3.391 | 3.7443 | 4.0694 | 4.3674 | 4.6451 | 5.2589 | 5.6494
Cardiff East / Aberthaw | Llandough | Primary Substation | 11 | Hydrogen Evolution | 0.17911 | 0.23359 | 0.29296 | 0.36036 | 0.44154 | 0.54122 | 0.65759 | 0.82307 | 0.95533 | 1.1026 | 1.2496 | 1.3936 | 1.5318 | 1.6681 | 1.7949 | 1.9084 | 2.141 | 2.3002 | 0.40439 | 0.51803 | 0.64145 | 0.78152 | 0.95089 | 1.1582 | 1.3996 | 1.7391 | 2.012 | 2.317 | 2.6191 | 2.9141 | 3.1973 | 3.4769 | 3.7374 | 3.9717 | 4.4766 | 4.8346
Cardiff East / Aberthaw | Llanishen | Primary Substation | 11 | Counterfactual | 0.32885 | 0.38768 | 0.45874 | 0.53603 | 0.62406 | 0.72528 | 0.8397 | 1.0211 | 1.1531 | 1.2941 | 1.4385 | 1.5859 | 1.7507 | 1.9151 | 2.076 | 2.2351 | 2.8807 | 2.9511 | 0.74978 | 0.87195 | 1.0185 | 1.1778 | 1.359 | 1.5672 | 1.8025 | 2.1722 | 2.4429 | 2.7327 | 3.0279 | 3.3282 | 3.6627 | 3.9962 | 4.3223 | 4.6449 | 5.955 | 6.1123
Cardiff East / Aberthaw | Llanishen | Primary Substation | 11 | Electric Engagement | 0.36274 | 0.4745 | 0.67604 | 0.9084 | 1.1267 | 1.3673 | 1.6581 | 2.0133 | 2.3226 | 2.5711 | 2.7914 | 2.9945 | 3.0582 | 3.1036 | 3.149 | 3.1927 | 3.346 | 3.5038 | 0.83146 | 1.067 | 1.4819 | 1.9591 | 2.4085 | 2.903 | 3.498 | 4.2225 | 4.8551 | 5.3661 | 5.8208 | 6.2367 | 6.3761 | 6.4776 | 6.579 | 6.6762 | 7.02 | 7.3846
Cardiff East / Aberthaw | Llanishen | Primary Substation | 11 | Holistic Transition | 0.38088 | 0.47817 | 0.58862 | 0.70954 | 0.845 | 1.0026 | 1.1823 | 1.4351 | 1.6431 | 1.8816 | 2.1318 | 2.361 | 2.5765 | 2.7754 | 2.958 | 3.1329 | 3.3659 | 3.5529 | 0.87681 | 1.0883 | 1.3253 | 1.5847 | 1.8734 | 2.2064 | 2.5826 | 3.1049 | 3.5366 | 4.0326 | 4.5503 | 5.0236 | 5.4678 | 5.8773 | 6.2541 | 6.6181 | 7.1431 | 7.5799
Cardiff East / Aberthaw | Llanishen | Primary Substation | 11 | Hydrogen Evolution | 0.34395 | 0.42502 | 0.51705 | 0.61834 | 0.73435 | 0.86884 | 1.0302 | 1.2635 | 1.4557 | 1.6661 | 1.8874 | 2.0994 | 2.304 | 2.4886 | 2.6582 | 2.8048 | 2.997 | 3.0851 | 0.78433 | 0.9535 | 1.1445 | 1.3544 | 1.5946 | 1.872 | 2.2031 | 2.6778 | 3.0708 | 3.5021 | 3.9537 | 4.385 | 4.8007 | 5.1747 | 5.5186 | 5.8161 | 6.2227 | 6.4229
Cardiff East / Aberthaw | Northcote St. | Primary Substation | 11 | Counterfactual | 0.1506 | 0.23564 | 0.3304 | 0.4338 | 0.55166 | 0.68372 | 0.83121 | 1.0628 | 1.2297 | 1.4081 | 1.5927 | 1.7869 | 2.0067 | 2.224 | 2.4351 | 2.6465 | 3.5352 | 3.6723 | 0.3308 | 0.50955 | 0.70605 | 0.92013 | 1.1632 | 1.4351 | 1.7379 | 2.2085 | 2.5495 | 2.9136 | 3.29 | 3.6849 | 4.1309 | 4.5714 | 4.9994 | 5.428 | 7.2331 | 7.5291
Cardiff East / Aberthaw | Northcote St. | Primary Substation | 11 | Electric Engagement | 0.19517 | 0.35736 | 0.6238 | 0.93001 | 1.2161 | 1.5232 | 1.8936 | 2.3451 | 2.7338 | 3.0465 | 3.3195 | 3.5846 | 3.6783 | 3.7466 | 3.8097 | 3.8725 | 4.0606 | 4.2976 | 0.4383 | 0.78495 | 1.3354 | 1.9654 | 2.5551 | 3.1866 | 3.9445 | 4.8642 | 5.6577 | 6.2987 | 6.86 | 7.4043 | 7.6099 | 7.7635 | 7.9063 | 8.0486 | 8.4918 | 9.0344
Cardiff East / Aberthaw | Northcote St. | Primary Substation | 11 | Holistic Transition | 0.22002 | 0.3713 | 0.5267 | 0.69131 | 0.87371 | 1.0829 | 1.3199 | 1.6511 | 1.9212 | 2.2374 | 2.5714 | 2.8832 | 3.1765 | 3.4461 | 3.6976 | 3.9354 | 4.3954 | 4.7067 | 0.49994 | 0.83447 | 1.17 | 1.5239 | 1.9131 | 2.3555 | 2.8526 | 3.5371 | 4.0986 | 4.7564 | 5.4507 | 6.0972 | 6.7036 | 7.2617 | 7.783 | 8.2812 | 9.3081 | 10.0265
Cardiff East / Aberthaw | Northcote St. | Primary Substation | 11 | Hydrogen Evolution | 0.17094 | 0.28876 | 0.41527 | 0.55653 | 0.7155 | 0.89537 | 1.109 | 1.4183 | 1.6779 | 1.953 | 2.2428 | 2.5232 | 2.8031 | 3.0488 | 3.2799 | 3.4768 | 3.7582 | 3.9098 | 0.37716 | 0.62583 | 0.8893 | 1.1825 | 1.5113 | 1.8819 | 2.32 | 2.949 | 3.4778 | 4.0378 | 4.6269 | 5.1971 | 5.7659 | 6.2653 | 6.7356 | 7.1369 | 7.7347 | 8.0693
Cardiff East / Aberthaw | Park Lane SWAE | Primary Substation | 11 | Counterfactual | 0.10455 | 0.12294 | 0.1393 | 0.15757 | 0.17874 | 0.20293 | 0.23015 | 0.27244 | 0.3059 | 0.34008 | 0.37463 | 0.40977 | 0.44886 | 0.48713 | 0.52401 | 0.56113 | 0.71437 | 0.77814 | 0.22224 | 0.26094 | 0.29483 | 0.33256 | 0.37616 | 0.42593 | 0.48187 | 0.56803 | 0.63683 | 0.70692 | 0.77761 | 0.8491 | 0.92836 | 1.0059 | 1.0807 | 1.1559 | 1.4683 | 1.6003
Cardiff East / Aberthaw | Park Lane SWAE | Primary Substation | 11 | Electric Engagement | 0.10862 | 0.14004 | 0.18259 | 0.23237 | 0.2776 | 0.32778 | 0.38803 | 0.4631 | 0.52609 | 0.57811 | 0.62371 | 0.66561 | 0.68671 | 0.70355 | 0.71921 | 0.73262 | 0.77748 | 0.82432 | 0.23226 | 0.30005 | 0.38793 | 0.49032 | 0.58363 | 0.68717 | 0.81137 | 0.96543 | 1.0953 | 1.2029 | 1.2976 | 1.3841 | 1.4296 | 1.4664 | 1.5006 | 1.5303 | 1.6352 | 1.7419
Cardiff East / Aberthaw | Park Lane SWAE | Primary Substation | 11 | Holistic Transition | 0.11171 | 0.14375 | 0.17164 | 0.20283 | 0.23799 | 0.27782 | 0.32091 | 0.37917 | 0.42386 | 0.47514 | 0.52884 | 0.57824 | 0.62364 | 0.66595 | 0.70573 | 0.74362 | 0.84593 | 0.9128 | 0.23963 | 0.31103 | 0.37092 | 0.4379 | 0.51312 | 0.59752 | 0.68837 | 0.80938 | 0.90265 | 1.0098 | 1.1217 | 1.2246 | 1.319 | 1.4071 | 1.4901 | 1.5702 | 1.7955 | 1.9467
Cardiff East / Aberthaw | Park Lane SWAE | Primary Substation | 11 | Hydrogen Evolution | 0.10754 | 0.1325 | 0.15661 | 0.18535 | 0.21716 | 0.25291 | 0.2962 | 0.36048 | 0.40846 | 0.4589 | 0.5109 | 0.56062 | 0.60971 | 0.65254 | 0.69317 | 0.72705 | 0.7928 | 0.84599 | 0.22881 | 0.28159 | 0.33146 | 0.39088 | 0.45662 | 0.53022 | 0.61951 | 0.75135 | 0.84908 | 0.95191 | 1.0578 | 1.1591 | 1.2591 | 1.3464 | 1.4293 | 1.4988 | 1.6389 | 1.7524
Cardiff East / Aberthaw | Penarth | Primary Substation | 11 | Counterfactual | 0.30929 | 0.38585 | 0.48758 | 0.6052 | 0.7466 | 0.90446 | 1.0843 | 1.3477 | 1.5476 | 1.7585 | 1.9739 | 2.1995 | 2.4496 | 2.679 | 2.8947 | 3.1056 | 4.0167 | 4.2387 | 0.68824 | 0.84833 | 1.059 | 1.3023 | 1.5945 | 1.9205 | 2.2918 | 2.8306 | 3.2425 | 3.6772 | 4.1203 | 4.5835 | 5.0953 | 5.5626 | 6.0011 | 6.4296 | 8.2847 | 8.7632
Cardiff East / Aberthaw | Penarth | Primary Substation | 11 | Electric Engagement | 0.35076 | 0.49715 | 0.76245 | 1.0746 | 1.3802 | 1.7292 | 2.1494 | 2.6543 | 3.096 | 3.4626 | 3.7882 | 4.1065 | 4.2142 | 4.2727 | 4.3273 | 4.3852 | 4.7203 | 4.9949 | 0.7879 | 1.0985 | 1.6463 | 2.2892 | 2.9218 | 3.6446 | 4.5121 | 5.5494 | 6.4594 | 7.2181 | 7.8939 | 8.5541 | 8.7901 | 8.9211 | 9.0433 | 9.1732 | 9.9284 | 10.553
Cardiff East / Aberthaw | Penarth | Primary Substation | 11 | Holistic Transition | 0.36967 | 0.49782 | 0.65709 | 0.8401 | 1.0594 | 1.3145 | 1.606 | 1.9886 | 2.2881 | 2.601 | 2.9293 | 3.2655 | 3.6082 | 3.9057 | 4.1804 | 4.4258 | 4.885 | 5.2011 | 0.83488 | 1.115 | 1.4567 | 1.8483 | 2.3166 | 2.8585 | 3.4743 | 4.2716 | 4.8967 | 5.5469 | 6.2269 | 6.9252 | 7.6387 | 8.2556 | 8.8265 | 9.3386 | 10.3604 | 11.0851
Cardiff East / Aberthaw | Penarth | Primary Substation | 11 | Hydrogen Evolution | 0.32904 | 0.44778 | 0.59149 | 0.74532 | 0.9331 | 1.1515 | 1.4093 | 1.7597 | 2.0412 | 2.3392 | 2.6457 | 2.9434 | 3.2392 | 3.5029 | 3.7483 | 3.9641 | 4.3533 | 4.595 | 0.73293 | 0.9831 | 1.2838 | 1.6044 | 1.9967 | 2.4528 | 2.989 | 3.7095 | 4.2891 | 4.9015 | 5.5292 | 6.1383 | 6.7445 | 7.2843 | 7.7872 | 8.2308 | 9.0667 | 9.6025
Cardiff East / Aberthaw | Rover Way Primary | Bulk Supply Point | 11 | Counterfactual | 3.1652 | 3.1718 | 3.1779 | 3.1849 | 3.2051 | 3.2274 | 3.2496 | 3.907 | 3.9328 | 3.9622 | 3.9936 | 4.025 | 4.0481 | 4.0666 | 4.0825 | 4.1043 | 4.2057 | 4.2767 | 7.911 | 7.9255 | 7.9385 | 7.9534 | 7.9996 | 8.0502 | 8.1 | 9.7357 | 9.7941 | 9.8605 | 9.9312 | 10.0014 | 10.0485 | 10.0862 | 10.1188 | 10.1633 | 10.3726 | 10.5189
Cardiff East / Aberthaw | Rover Way Primary | Bulk Supply Point | 11 | Electric Engagement | 3.1668 | 3.1799 | 3.1959 | 3.2505 | 3.291 | 3.3382 | 4.0245 | 4.0829 | 4.1378 | 4.1925 | 4.2393 | 4.2659 | 4.2884 | 4.3063 | 4.3256 | 4.3435 | 4.466 | 4.5201 | 7.9148 | 7.9441 | 7.9778 | 8.1066 | 8.2005 | 8.3101 | 10.0137 | 10.1467 | 10.2724 | 10.3976 | 10.5044 | 10.5594 | 10.6065 | 10.6444 | 10.6848 | 10.7226 | 10.9916 | 11.112
Cardiff East / Aberthaw | Rover Way Primary | Bulk Supply Point | 11 | Holistic Transition | 3.1679 | 3.1831 | 3.2251 | 3.2585 | 3.2985 | 0.83976 | 0.89426 | 0.95627 | 1.0103 | 1.0732 | 1.1066 | 1.1361 | 1.1655 | 1.1922 | 1.2254 | 4.4027 | 4.5357 | 4.6225 | 7.9173 | 7.9526 | 8.0536 | 8.1329 | 8.228 | 2.0686 | 2.1953 | 2.3371 | 2.4629 | 2.6071 | 2.6776 | 2.7401 | 2.8025 | 2.8592 | 2.929 | 10.8618 | 11.147 | 11.3331
Cardiff East / Aberthaw | Rover Way Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 3.1663 | 3.1756 | 3.1853 | 3.2376 | 3.2812 | 3.3296 | 3.3783 | 4.0639 | 4.133 | 4.1961 | 5.8253 | 5.8493 | 5.8868 | 5.9065 | 5.9397 | 5.9609 | 6.0628 | 6.1512 | 7.9133 | 7.9339 | 7.9542 | 8.0769 | 8.1771 | 8.2885 | 8.4008 | 10.1019 | 10.2549 | 10.3961 | 14.455 | 14.5051 | 14.5821 | 14.6233 | 14.6915 | 14.736 | 14.9511 | 15.1359
Cardiff East / Aberthaw | Sanatorium | Primary Substation | 11 | Counterfactual | 0.093825 | 0.14466 | 0.21106 | 0.27836 | 0.35827 | 0.45041 | 0.5467 | 0.6953 | 0.80252 | 0.91862 | 1.0356 | 1.1534 | 1.2907 | 1.4189 | 1.5422 | 1.6722 | 2.2007 | 2.3114 | 0.20847 | 0.31553 | 0.45282 | 0.59218 | 0.75719 | 0.94709 | 1.1452 | 1.4479 | 1.6677 | 1.9051 | 2.1441 | 2.3839 | 2.6622 | 2.9221 | 3.172 | 3.4354 | 4.5099 | 4.7444
Cardiff East / Aberthaw | Sanatorium | Primary Substation | 11 | Electric Engagement | 0.11771 | 0.21377 | 0.37952 | 0.57315 | 0.75373 | 0.9353 | 1.1631 | 1.4367 | 1.6764 | 1.8675 | 2.0427 | 2.2069 | 2.2749 | 2.3238 | 2.3757 | 2.4228 | 2.6214 | 2.7978 | 0.26619 | 0.47176 | 0.81427 | 1.2143 | 1.5878 | 1.9618 | 2.4294 | 2.9891 | 3.4806 | 3.8741 | 4.2352 | 4.5726 | 4.7192 | 4.8269 | 4.9404 | 5.0444 | 5.4867 | 5.8799
Cardiff East / Aberthaw | Sanatorium | Primary Substation | 11 | Holistic Transition | 0.13258 | 0.2266 | 0.33258 | 0.45061 | 0.56651 | 0.71179 | 0.86508 | 1.0721 | 1.2332 | 1.4214 | 1.6227 | 1.806 | 1.9792 | 2.1428 | 2.2975 | 2.4448 | 2.7676 | 3.0007 | 0.303 | 0.51103 | 0.73945 | 0.99361 | 1.2415 | 1.5487 | 1.8714 | 2.3007 | 2.6355 | 3.0268 | 3.4444 | 3.8247 | 4.1828 | 4.5214 | 4.8418 | 5.1498 | 5.8601 | 6.3811
Cardiff East / Aberthaw | Sanatorium | Primary Substation | 11 | Hydrogen Evolution | 0.10455 | 0.17556 | 0.26142 | 0.36482 | 0.48402 | 0.61514 | 0.76544 | 0.95339 | 1.1281 | 1.2992 | 1.4804 | 1.6473 | 1.8219 | 1.9714 | 2.1193 | 2.2439 | 2.4795 | 2.6185 | 0.23298 | 0.38323 | 0.56195 | 0.77738 | 1.0254 | 1.2981 | 1.6088 | 1.9916 | 2.348 | 2.6963 | 3.0647 | 3.4042 | 3.7591 | 4.0633 | 4.3643 | 4.6184 | 5.1136 | 5.4113
Cardiff East / Aberthaw | Sandon St. | Primary Substation | 11 | Counterfactual | 0.075654 | 0.11104 | 0.14963 | 0.19323 | 0.24274 | 0.30055 | 0.36233 | 0.45507 | 0.5285 | 0.61018 | 0.6882 | 0.77015 | 0.85661 | 0.94112 | 1.0232 | 1.0971 | 1.3949 | 1.4619 | 0.16529 | 0.23915 | 0.31892 | 0.40891 | 0.51089 | 0.62972 | 0.75678 | 0.94586 | 1.0968 | 1.2645 | 1.4246 | 1.592 | 1.7683 | 1.9403 | 2.1071 | 2.2567 | 2.8606 | 3.0012
Cardiff East / Aberthaw | Sandon St. | Primary Substation | 11 | Electric Engagement | 0.088503 | 0.15662 | 0.26552 | 0.41405 | 0.54303 | 0.64979 | 0.78259 | 0.94281 | 1.0797 | 1.1894 | 1.2872 | 1.376 | 1.4106 | 1.4369 | 1.4619 | 1.482 | 1.5538 | 1.6313 | 0.19637 | 0.34155 | 0.56772 | 0.87713 | 1.1462 | 1.3656 | 1.6376 | 1.9647 | 2.2448 | 2.4703 | 2.6713 | 2.8536 | 2.9283 | 2.9861 | 3.0413 | 3.0866 | 3.2515 | 3.4276
Cardiff East / Aberthaw | Sandon St. | Primary Substation | 11 | Holistic Transition | 0.096365 | 0.1707 | 0.25599 | 0.36058 | 0.43102 | 0.50891 | 0.59853 | 0.71694 | 0.80803 | 0.91271 | 1.027 | 1.1314 | 1.2258 | 1.3162 | 1.4002 | 1.4796 | 1.6358 | 1.7477 | 0.21562 | 0.37834 | 0.56214 | 0.7871 | 0.93702 | 1.1015 | 1.2891 | 1.5339 | 1.7226 | 1.9397 | 2.1764 | 2.3923 | 2.587 | 2.7735 | 2.9472 | 3.1129 | 3.4586 | 3.712
Cardiff East / Aberthaw | Sandon St. | Primary Substation | 11 | Hydrogen Evolution | 0.082288 | 0.12992 | 0.18173 | 0.24408 | 0.31433 | 0.39688 | 0.49071 | 0.62269 | 0.7274 | 0.83376 | 0.94786 | 1.058 | 1.167 | 1.2621 | 1.3509 | 1.4186 | 1.5257 | 1.5918 | 0.18026 | 0.28037 | 0.38827 | 0.51814 | 0.66447 | 0.83609 | 1.0307 | 1.3023 | 1.5168 | 1.7344 | 1.9676 | 2.1928 | 2.4157 | 2.6103 | 2.7917 | 2.9294 | 3.1548 | 3.297
Cardiff East / Aberthaw | Ship Hill Barry | Primary Substation | 11 | Counterfactual | 0.0876 | 0.1164 | 0.15084 | 0.18742 | 0.23045 | 0.27903 | 0.33547 | 0.42444 | 0.49016 | 0.55966 | 0.63097 | 0.70373 | 0.78501 | 0.86776 | 0.9461 | 1.0223 | 1.3268 | 1.3854 | 0.19331 | 0.25327 | 0.32438 | 0.39984 | 0.48842 | 0.58835 | 0.70438 | 0.88562 | 1.0204 | 1.163 | 1.3088 | 1.4573 | 1.6227 | 1.7912 | 1.9504 | 2.105 | 2.726 | 2.8554
Cardiff East / Aberthaw | Ship Hill Barry | Primary Substation | 11 | Electric Engagement | 0.10372 | 0.15729 | 0.25442 | 0.36661 | 0.47077 | 0.58357 | 0.72224 | 0.89028 | 1.035 | 1.15 | 1.2519 | 1.3483 | 1.3717 | 1.3863 | 1.4007 | 1.4167 | 1.5127 | 1.596 | 0.23219 | 0.34554 | 0.54582 | 0.77649 | 0.99108 | 1.2232 | 1.5077 | 1.851 | 2.1473 | 2.3841 | 2.5948 | 2.794 | 2.8466 | 2.8807 | 2.9142 | 2.9514 | 3.1729 | 3.3657
Cardiff East / Aberthaw | Ship Hill Barry | Primary Substation | 11 | Holistic Transition | 0.11107 | 0.15731 | 0.21103 | 0.26956 | 0.33611 | 0.41214 | 0.50187 | 0.62535 | 0.72246 | 0.82341 | 0.92946 | 1.0306 | 1.1337 | 1.2306 | 1.3192 | 1.3986 | 1.5352 | 1.631 | 0.25049 | 0.35125 | 0.46647 | 0.59178 | 0.73341 | 0.89435 | 1.0831 | 1.3393 | 1.5414 | 1.7507 | 1.9698 | 2.1797 | 2.3939 | 2.5955 | 2.7802 | 2.9464 | 3.2553 | 3.4774
Cardiff East / Aberthaw | Ship Hill Barry | Primary Substation | 11 | Hydrogen Evolution | 0.094874 | 0.13364 | 0.17745 | 0.22656 | 0.28444 | 0.35123 | 0.4333 | 0.54878 | 0.63974 | 0.73647 | 0.83767 | 0.93449 | 1.0294 | 1.1228 | 1.2091 | 1.2852 | 1.4102 | 1.48 | 0.20994 | 0.29109 | 0.38207 | 0.48398 | 0.60409 | 0.7424 | 0.91173 | 1.1478 | 1.3338 | 1.5316 | 1.7376 | 1.9345 | 2.1276 | 2.3186 | 2.4953 | 2.6516 | 2.9216 | 3.0794
Cardiff East / Aberthaw | St Mellons | Primary Substation | 11 | Counterfactual | 0.497 | 0.55821 | 0.63404 | 0.71809 | 0.80456 | 0.9079 | 1.0207 | 1.1954 | 1.3271 | 1.4682 | 1.6259 | 1.7938 | 1.9798 | 2.1691 | 2.35 | 2.5332 | 3.2862 | 3.5413 | 1.1718 | 1.2967 | 1.4509 | 1.6217 | 1.7977 | 2.0092 | 2.2406 | 2.5973 | 2.8682 | 3.1605 | 3.483 | 3.8235 | 4.1989 | 4.5809 | 4.9462 | 5.3159 | 6.848 | 7.3828
Cardiff East / Aberthaw | St Mellons | Primary Substation | 11 | Electric Engagement | 0.50428 | 0.60667 | 0.79815 | 1.0207 | 1.2309 | 1.4531 | 1.7222 | 2.0941 | 2.4156 | 2.6815 | 2.9234 | 3.1495 | 3.2526 | 3.3246 | 3.3905 | 3.4541 | 3.7671 | 3.9875 | 1.1885 | 1.3986 | 1.7882 | 2.2416 | 2.6712 | 3.1243 | 3.6729 | 4.4292 | 5.0856 | 5.6316 | 6.1306 | 6.5962 | 6.8191 | 6.9738 | 7.1159 | 7.2539 | 7.9606 | 8.4624
Cardiff East / Aberthaw | St Mellons | Primary Substation | 11 | Holistic Transition | 0.50763 | 0.60089 | 0.71037 | 0.82006 | 0.93324 | 1.0777 | 1.251 | 1.4938 | 1.7047 | 1.9678 | 2.2386 | 2.485 | 2.8277 | 3.0319 | 3.2197 | 3.3941 | 3.679 | 3.8573 | 1.1966 | 1.3919 | 1.619 | 1.8475 | 2.0828 | 2.382 | 2.742 | 3.2432 | 3.6812 | 4.2296 | 4.7891 | 5.2978 | 6.0516 | 6.4683 | 6.8522 | 7.2116 | 7.8412 | 8.2337
Cardiff East / Aberthaw | St Mellons | Primary Substation | 11 | Hydrogen Evolution | 0.50279 | 0.58775 | 0.68883 | 0.79812 | 0.91526 | 1.0592 | 1.215 | 1.4753 | 1.7089 | 1.9711 | 2.2392 | 2.4919 | 2.7405 | 2.9594 | 3.1629 | 3.3386 | 3.7389 | 3.9271 | 1.1842 | 1.3585 | 1.5653 | 1.7891 | 2.0293 | 2.3249 | 2.6424 | 3.1696 | 3.6455 | 4.184 | 4.7309 | 5.2455 | 5.7505 | 6.193 | 6.6048 | 6.9614 | 7.8291 | 8.2517
Cardiff East / Aberthaw | Sully Grid Primary | Bulk Supply Point | 11 | Counterfactual | 0.55658 | 0.60285 | 0.6516 | 0.71672 | 0.79438 | 0.87881 | 0.95465 | 1.0667 | 1.1532 | 1.2466 | 1.3428 | 1.4434 | 1.5593 | 1.6706 | 1.7722 | 1.88 | 2.3655 | 2.5583 | 1.3547 | 1.4529 | 1.5547 | 1.6904 | 1.8521 | 2.0278 | 2.1853 | 2.4157 | 2.5953 | 2.7892 | 2.9881 | 3.1945 | 3.4311 | 3.6588 | 3.8663 | 4.086 | 5.0828 | 5.4924
Cardiff East / Aberthaw | Sully Grid Primary | Bulk Supply Point | 11 | Electric Engagement | 0.57477 | 0.65322 | 0.77576 | 0.93098 | 1.0935 | 1.2752 | 1.4634 | 1.6799 | 1.8714 | 2.0365 | 2.1846 | 2.3343 | 2.3987 | 2.446 | 2.4951 | 2.5452 | 2.917 | 3.117 | 1.3984 | 1.5677 | 1.8224 | 2.1451 | 2.486 | 2.8673 | 3.2572 | 3.7033 | 4.0997 | 4.443 | 4.7528 | 5.0642 | 5.204 | 5.3078 | 5.4151 | 5.525 | 6.3687 | 6.8215
Cardiff East / Aberthaw | Sully Grid Primary | Bulk Supply Point | 11 | Holistic Transition | 0.58326 | 0.66266 | 0.74279 | 0.84618 | 0.96291 | 1.1139 | 1.2461 | 1.4225 | 1.5595 | 1.7113 | 1.8673 | 2.1554 | 2.3177 | 2.4691 | 2.6209 | 2.7532 | 3.1088 | 3.3611 | 1.4192 | 1.5954 | 1.7685 | 1.9918 | 2.2437 | 2.5653 | 2.845 | 3.2137 | 3.5017 | 3.8191 | 4.1439 | 4.7993 | 5.1392 | 5.4559 | 5.7733 | 6.0518 | 6.8342 | 7.3936
Cardiff East / Aberthaw | Sully Grid Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 0.56577 | 0.62994 | 0.69527 | 0.79547 | 0.90972 | 1.0356 | 1.1518 | 1.3114 | 1.4659 | 1.6182 | 1.7655 | 1.8969 | 2.0482 | 2.1741 | 2.313 | 2.4245 | 2.8025 | 3.042 | 1.3755 | 1.5127 | 1.6498 | 1.8598 | 2.0999 | 2.3643 | 2.6057 | 2.9338 | 3.2506 | 3.5642 | 3.8664 | 4.1361 | 4.4458 | 4.7059 | 4.9919 | 5.2233 | 6.0566 | 6.5737
Cardiff East / Aberthaw | Taff Bank | Primary Substation | 11 | Counterfactual | 0.24338 | 0.28051 | 0.32448 | 0.37735 | 0.44588 | 0.51876 | 0.60585 | 0.72019 | 0.82874 | 0.94862 | 1.0736 | 1.2026 | 1.3552 | 1.5001 | 1.6411 | 1.7769 | 2.3046 | 2.5623 | 0.59816 | 0.67656 | 0.7685 | 0.87869 | 1.0216 | 1.1738 | 1.3557 | 1.5952 | 1.8259 | 2.0824 | 2.351 | 2.6272 | 2.9541 | 3.264 | 3.5655 | 3.8539 | 4.9568 | 5.5034
Cardiff East / Aberthaw | Taff Bank | Primary Substation | 11 | Electric Engagement | 0.25222 | 0.35103 | 0.50332 | 0.75277 | 1.0152 | 1.1497 | 1.3316 | 1.6176 | 1.9721 | 2.5412 | 2.9836 | 3.2567 | 3.3068 | 3.3316 | 3.3568 | 3.3802 | 3.4784 | 3.5628 | 0.61929 | 0.83335 | 1.1576 | 1.6896 | 2.2547 | 2.5406 | 2.9318 | 3.5499 | 4.3243 | 5.5747 | 6.5465 | 7.1467 | 7.2607 | 7.3151 | 7.3701 | 7.4217 | 7.6415 | 7.8307
Cardiff East / Aberthaw | Taff Bank | Primary Substation | 11 | Holistic Transition | 0.25778 | 0.40644 | 0.61861 | 0.91842 | 1.0915 | 1.3107 | 1.6138 | 2.1393 | 2.7706 | 2.8993 | 3.0223 | 3.1234 | 3.2041 | 3.2765 | 3.3476 | 3.4141 | 3.3671 | 3.4847 | 0.63292 | 0.95966 | 1.421 | 2.0712 | 2.4484 | 2.9314 | 3.6013 | 4.7593 | 6.161 | 6.4492 | 6.7211 | 6.9386 | 7.1054 | 7.2556 | 7.403 | 7.5427 | 7.379 | 7.6423
Cardiff East / Aberthaw | Taff Bank | Primary Substation | 11 | Hydrogen Evolution | 0.24794 | 0.29742 | 0.35508 | 0.45897 | 0.57751 | 0.70992 | 0.88714 | 1.0801 | 1.2855 | 1.4914 | 1.6723 | 1.8499 | 2.0336 | 2.1773 | 2.3206 | 2.4343 | 2.8288 | 3.0852 | 0.60828 | 0.7142 | 0.83666 | 1.0578 | 1.3115 | 1.5962 | 1.9817 | 2.3994 | 2.8484 | 3.3 | 3.6943 | 4.0826 | 4.4818 | 4.7895 | 5.093 | 5.3345 | 6.1878 | 6.7431
Cardiff East / Aberthaw | Trowbridge Primary | Bulk Supply Point | 11 | Counterfactual | 2.8792 | 2.9601 | 3.056 | 3.1594 | 3.2826 | 3.4167 | 3.561 | 3.794 | 2.1394 | 2.3463 | 2.5532 | 2.7706 | 3.0178 | 3.2653 | 3.4997 | 3.7256 | 4.6094 | 4.8416 | 7.0048 | 7.174 | 7.3729 | 7.5871 | 7.8444 | 8.122 | 8.42 | 8.8992 | 4.6881 | 5.1235 | 5.5587 | 6.0146 | 6.5342 | 7.0564 | 7.5502 | 8.0209 | 9.8236 | 10.3227
Cardiff East / Aberthaw | Trowbridge Primary | Bulk Supply Point | 11 | Electric Engagement | 2.9204 | 3.0682 | 3.3223 | 3.6396 | 3.9147 | 4.2131 | 4.6062 | 5.0926 | 3.703 | 4.0908 | 4.4392 | 5.0428 | 5.2231 | 5.3042 | 5.3875 | 5.4676 | 5.8565 | 6.2477 | 7.1039 | 7.4179 | 7.9433 | 8.6071 | 9.1762 | 9.7919 | 10.6129 | 11.6299 | 7.9833 | 8.8141 | 9.5625 | 10.8302 | 11.2461 | 11.4263 | 11.6105 | 11.7883 | 12.6607 | 13.5612
Cardiff East / Aberthaw | Trowbridge Primary | Bulk Supply Point | 11 | Holistic Transition | 2.9429 | 3.0821 | 3.2584 | 3.4342 | 3.6238 | 3.876 | 4.1731 | 4.5684 | 3.0738 | 3.4778 | 3.9071 | 4.5506 | 4.8707 | 5.169 | 5.4447 | 5.6898 | 6.3072 | 6.6643 | 7.1598 | 7.4648 | 7.8502 | 8.2291 | 8.6347 | 9.1823 | 9.8292 | 10.6771 | 6.8314 | 7.7137 | 8.6472 | 9.9976 | 10.6649 | 11.2857 | 11.8598 | 12.3724 | 13.8049 | 14.6104
Cardiff East / Aberthaw | Trowbridge Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 2.8979 | 3.0084 | 3.1377 | 3.3087 | 3.4796 | 3.6698 | 3.9184 | 4.2666 | 2.7496 | 3.0876 | 3.4272 | 3.8955 | 4.2599 | 4.5295 | 4.7772 | 4.9862 | 5.3846 | 5.6875 | 7.0474 | 7.2798 | 7.549 | 7.9139 | 8.2698 | 8.6644 | 9.1891 | 9.9192 | 6.0056 | 6.7259 | 7.4447 | 8.4298 | 9.213 | 9.7733 | 10.2807 | 10.7104 | 11.5601 | 12.2491
Cardiff East / Aberthaw | Wood Street | Primary Substation | 11 | Counterfactual | 0.038913 | 0.086141 | 0.11463 | 0.14641 | 0.18648 | 0.22964 | 0.28106 | 0.35589 | 0.41038 | 0.46733 | 0.52511 | 0.58478 | 0.65182 | 0.71745 | 0.78066 | 0.84401 | 1.1062 | 1.2006 | 0.084755 | 0.18406 | 0.24358 | 0.30976 | 0.39375 | 0.48338 | 0.58991 | 0.74306 | 0.8554 | 0.97258 | 1.0912 | 1.2131 | 1.3496 | 1.4833 | 1.612 | 1.7409 | 2.2776 | 2.4766
Cardiff East / Aberthaw | Wood Street | Primary Substation | 11 | Electric Engagement | 0.046771 | 0.12165 | 0.19843 | 0.2944 | 0.37575 | 0.46555 | 0.57313 | 0.70606 | 0.8187 | 0.91099 | 0.99234 | 1.0682 | 1.1041 | 1.1326 | 1.1595 | 1.1834 | 1.2713 | 1.3599 | 0.10397 | 0.2662 | 0.42593 | 0.62762 | 0.7966 | 0.98301 | 1.2055 | 1.4793 | 1.7122 | 1.9039 | 2.0737 | 2.2314 | 2.3101 | 2.3735 | 2.4335 | 2.4877 | 2.6946 | 2.9006
Cardiff East / Aberthaw | Wood Street | Primary Substation | 11 | Holistic Transition | 0.052523 | 0.1319 | 0.1885 | 0.24317 | 0.30879 | 0.38227 | 0.46166 | 0.56636 | 0.64636 | 0.73899 | 0.83596 | 0.92541 | 1.0089 | 1.0865 | 1.1594 | 1.2282 | 1.3797 | 1.5089 | 0.11777 | 0.29486 | 0.41992 | 0.53863 | 0.68044 | 0.83772 | 1.0066 | 1.2257 | 1.3939 | 1.5887 | 1.7923 | 1.98 | 2.155 | 2.3179 | 2.4715 | 2.6178 | 2.9646 | 3.2613
Cardiff East / Aberthaw | Wood Street | Primary Substation | 11 | Hydrogen Evolution | 0.043648 | 0.10328 | 0.14483 | 0.20343 | 0.26281 | 0.33231 | 0.40439 | 0.50081 | 0.58303 | 0.6688 | 0.75708 | 0.84126 | 0.92523 | 0.99879 | 1.0692 | 1.1281 | 1.2432 | 1.3351 | 0.095263 | 0.22178 | 0.30856 | 0.43368 | 0.55784 | 0.70301 | 0.85214 | 1.0489 | 1.2171 | 1.3926 | 1.5731 | 1.7452 | 1.9168 | 2.0674 | 2.2119 | 2.333 | 2.5805 | 2.7794
Margam (Grange) | Caerau Primary | Primary Substation | 11 | Counterfactual | 0.1831 | 0.2553 | 0.33749 | 0.42993 | 0.53916 | 0.70441 | 0.89424 | 1.1654 | 1.3916 | 1.6403 | 1.8893 | 2.1361 | 2.3986 | 2.6064 | 2.8072 | 3.0107 | 3.9409 | 4.2164 | 0.4117 | 0.56396 | 0.73512 | 0.92772 | 1.1559 | 1.5133 | 1.9267 | 2.5085 | 3.0037 | 3.5516 | 4.0965 | 4.6309 | 5.1935 | 5.6208 | 6.0336 | 6.4522 | 8.3925 | 9.0063
Margam (Grange) | Caerau Primary | Primary Substation | 11 | Electric Engagement | 0.22079 | 0.35746 | 0.58711 | 0.8614 | 1.2107 | 1.6472 | 2.1483 | 2.7283 | 3.2665 | 3.7518 | 4.1949 | 4.6246 | 4.8133 | 4.9659 | 5.1211 | 5.279 | 6.043 | 6.4785 | 0.50231 | 0.79541 | 1.2724 | 1.8434 | 2.6101 | 3.564 | 4.6515 | 5.9011 | 7.0686 | 8.1314 | 9.1014 | 10.0413 | 10.4612 | 10.7998 | 11.1426 | 11.486 | 13.1578 | 14.1737
Margam (Grange) | Caerau Primary | Primary Substation | 11 | Holistic Transition | 0.24206 | 0.37255 | 0.51029 | 0.74871 | 1.0271 | 1.398 | 1.7962 | 2.2921 | 2.7374 | 3.2168 | 3.6757 | 4.0376 | 4.406 | 4.7365 | 5.04 | 5.3231 | 6.1952 | 6.5744 | 0.55397 | 0.842 | 1.1387 | 1.681 | 2.3152 | 3.1463 | 4.037 | 5.1282 | 6.118 | 7.182 | 8.1841 | 8.9508 | 9.7341 | 10.4303 | 11.0646 | 11.6574 | 13.5555 | 14.4123
Margam (Grange) | Caerau Primary | Primary Substation | 11 | Hydrogen Evolution | 0.20063 | 0.30157 | 0.41337 | 0.54805 | 0.7924 | 1.0904 | 1.4146 | 1.8201 | 2.2028 | 2.6141 | 2.9968 | 3.3605 | 3.6414 | 3.8823 | 4.1258 | 4.3473 | 4.8716 | 5.3245 | 0.45153 | 0.66562 | 0.90014 | 1.1827 | 1.7322 | 2.4003 | 3.1218 | 4.0064 | 4.8496 | 5.7603 | 6.5949 | 7.388 | 7.971 | 8.471 | 8.9788 | 9.4425 | 10.5924 | 11.6105
Margam (Grange) | Llynfi | Primary Substation | 11 | Counterfactual | 0.31536 | 0.36893 | 0.43698 | 0.51417 | 0.60462 | 0.71494 | 0.84304 | 1.0361 | 1.1879 | 1.3556 | 1.5176 | 1.6744 | 1.8415 | 2.0088 | 2.1714 | 2.3561 | 3.2191 | 3.5321 | 0.69543 | 0.8074 | 0.94852 | 1.1088 | 1.2975 | 1.5289 | 1.8 | 2.2041 | 2.5267 | 2.8863 | 3.2285 | 3.5551 | 3.8992 | 4.2441 | 4.5791 | 4.9623 | 6.788 | 7.4859
Margam (Grange) | Llynfi | Primary Substation | 11 | Electric Engagement | 0.34202 | 0.4437 | 0.62909 | 1.4302 | 1.6458 | 1.9039 | 2.2111 | 2.5839 | 2.9204 | 3.21 | 3.482 | 3.7396 | 3.8914 | 4.0558 | 4.2167 | 4.4398 | 5.075 | 5.4163 | 0.76048 | 0.97603 | 1.3603 | 2.9807 | 3.4323 | 3.9733 | 4.616 | 5.3944 | 6.1016 | 6.7161 | 7.2975 | 7.8473 | 8.1937 | 8.5688 | 8.935 | 9.4116 | 10.8362 | 11.6441
Margam (Grange) | Llynfi | Primary Substation | 11 | Holistic Transition | 0.36062 | 0.45615 | 1.1447 | 1.2866 | 1.4483 | 1.6529 | 1.8883 | 2.2036 | 2.4927 | 2.8439 | 3.1884 | 3.5226 | 3.8761 | 4.1948 | 4.4595 | 4.7466 | 5.2959 | 5.5501 | 0.80536 | 1.0136 | 2.4065 | 2.716 | 3.068 | 3.5097 | 4.0181 | 4.6915 | 5.3156 | 6.0771 | 6.8146 | 7.5348 | 8.3034 | 8.9904 | 9.5516 | 10.1475 | 11.3757 | 11.9623
Margam (Grange) | Llynfi | Primary Substation | 11 | Hydrogen Evolution | 0.32638 | 0.97939 | 1.0708 | 1.1784 | 1.3065 | 1.4609 | 1.6386 | 1.8819 | 2.1009 | 2.3735 | 2.6453 | 2.9098 | 3.1585 | 3.3901 | 3.6264 | 3.8829 | 4.3332 | 4.6475 | 0.72091 | 2.0344 | 2.2255 | 2.4514 | 2.7224 | 3.0486 | 3.4224 | 3.9278 | 4.3892 | 4.9726 | 5.5475 | 6.1053 | 6.6276 | 7.1166 | 7.622 | 8.1656 | 9.1686 | 9.8977
Margam (Grange) | Ogmore Vale | Primary Substation | 11 | Counterfactual | 0.10361 | 0.13466 | 0.17456 | 0.22062 | 0.27516 | 0.3456 | 0.4235 | 0.53701 | 0.62732 | 0.72542 | 0.82209 | 0.91845 | 1.0219 | 1.1245 | 1.2235 | 1.3251 | 1.8259 | 1.9952 | 0.22927 | 0.29473 | 0.37779 | 0.47368 | 0.58754 | 0.73465 | 0.8988 | 1.1357 | 1.3268 | 1.536 | 1.7395 | 1.9399 | 2.1529 | 2.3643 | 2.5681 | 2.7782 | 3.8361 | 4.2053
Margam (Grange) | Ogmore Vale | Primary Substation | 11 | Electric Engagement | 0.11665 | 0.17646 | 0.28319 | 0.41395 | 0.53997 | 0.70903 | 0.9064 | 1.1426 | 1.3595 | 1.5566 | 1.7456 | 1.9281 | 2.0471 | 2.1641 | 2.281 | 2.3737 | 2.825 | 3.0757 | 0.26083 | 0.38807 | 0.60915 | 0.88087 | 1.1445 | 1.4965 | 1.9071 | 2.3979 | 2.8508 | 3.2652 | 3.6642 | 4.0487 | 4.312 | 4.5747 | 4.8356 | 5.0354 | 6.0086 | 6.5829
Margam (Grange) | Ogmore Vale | Primary Substation | 11 | Holistic Transition | 0.12619 | 0.18394 | 0.25132 | 0.336 | 0.43287 | 0.57417 | 0.72803 | 0.93002 | 1.1077 | 1.3021 | 1.4983 | 1.6987 | 1.918 | 2.1171 | 2.2788 | 2.4257 | 2.8952 | 3.1148 | 0.28377 | 0.41015 | 0.55422 | 0.73797 | 0.948 | 1.249 | 1.5778 | 2.0057 | 2.3848 | 2.8003 | 3.2145 | 3.6415 | 4.1158 | 4.5427 | 4.8792 | 5.1858 | 6.205 | 6.6966
Margam (Grange) | Ogmore Vale | Primary Substation | 11 | Hydrogen Evolution | 0.10935 | 0.15449 | 0.20947 | 0.27726 | 0.35653 | 0.45665 | 0.56723 | 0.71728 | 0.85584 | 1.0076 | 1.1556 | 1.2955 | 1.4344 | 1.5643 | 1.7057 | 1.828 | 2.1097 | 2.3654 | 0.24226 | 0.33736 | 0.45229 | 0.59427 | 0.76149 | 0.97185 | 1.2036 | 1.5146 | 1.8048 | 2.1261 | 2.4361 | 2.728 | 3.0165 | 3.2914 | 3.5957 | 3.8599 | 4.4742 | 5.0432
Pembroke | Brawdy | Primary Substation | 11 | Counterfactual | 0.31461 | 0.34237 | 0.37496 | 0.40617 | 0.4431 | 0.48406 | 0.52964 | 0.60265 | 0.65714 | 0.71567 | 0.77639 | 0.83997 | 0.91336 | 0.98392 | 1.0513 | 1.1213 | 1.426 | 1.5315 | 0.71067 | 0.76989 | 0.83769 | 0.90238 | 0.97854 | 1.0628 | 1.1562 | 1.3046 | 1.416 | 1.5355 | 1.6593 | 1.7887 | 1.9376 | 2.0809 | 2.2177 | 2.3598 | 2.9794 | 3.1992
Pembroke | Brawdy | Primary Substation | 11 | Electric Engagement | 0.32606 | 0.37881 | 0.46194 | 0.55727 | 0.6453 | 0.73974 | 0.85681 | 0.99822 | 1.1233 | 1.2297 | 1.3236 | 1.4153 | 1.4505 | 1.4788 | 1.5022 | 1.5544 | 1.7216 | 1.7958 | 0.73846 | 0.85323 | 1.0257 | 1.2223 | 1.4041 | 1.5984 | 1.838 | 2.1264 | 2.3823 | 2.6005 | 2.7935 | 2.9821 | 3.0574 | 3.1185 | 3.1697 | 3.2786 | 3.6391 | 3.8082
Pembroke | Brawdy | Primary Substation | 11 | Holistic Transition | 0.33246 | 0.38445 | 0.43624 | 0.48728 | 0.54307 | 0.61698 | 0.69481 | 0.80443 | 0.89459 | 0.99542 | 1.0996 | 1.1963 | 1.2899 | 1.3796 | 1.4626 | 1.5628 | 1.7875 | 1.8984 | 0.7544 | 0.87131 | 0.98358 | 1.0933 | 1.2123 | 1.3673 | 1.5299 | 1.7561 | 1.9432 | 2.1512 | 2.3659 | 2.5658 | 2.7598 | 2.9457 | 3.118 | 3.3248 | 3.8052 | 4.0545
Pembroke | Brawdy | Primary Substation | 11 | Hydrogen Evolution | 0.31997 | 0.35937 | 0.40319 | 0.45306 | 0.5083 | 0.57184 | 0.64508 | 0.75068 | 0.85262 | 0.9564 | 1.0593 | 1.1522 | 1.2513 | 1.3333 | 1.4171 | 1.4992 | 1.6711 | 1.7637 | 0.72301 | 0.80751 | 0.89931 | 1.0024 | 1.1163 | 1.2469 | 1.3967 | 1.6114 | 1.8187 | 2.0294 | 2.238 | 2.4267 | 2.6277 | 2.7949 | 2.9657 | 3.1328 | 3.4916 | 3.6889
Pembroke | Broadfield | Primary Substation | 11 | Counterfactual | 0.55788 | 0.62292 | 0.70633 | 0.79508 | 0.88582 | 1.0176 | 1.1631 | 1.3686 | 1.5389 | 1.7256 | 1.9043 | 2.0711 | 2.2466 | 2.4228 | 2.5936 | 2.7621 | 3.5348 | 3.9283 | 1.231 | 1.3689 | 1.543 | 1.7283 | 1.9199 | 2.1973 | 2.5079 | 2.9436 | 3.3113 | 3.7189 | 4.1019 | 4.4536 | 4.8186 | 5.1858 | 5.5413 | 5.8911 | 7.5202 | 8.388
Pembroke | Broadfield | Primary Substation | 11 | Electric Engagement | 0.57805 | 0.68953 | 0.88117 | 1.1219 | 1.3444 | 1.6594 | 2.0407 | 2.4909 | 2.9204 | 3.3224 | 3.7236 | 4.0951 | 4.3643 | 4.5815 | 4.8898 | 5.1803 | 6.5214 | 7.0494 | 1.2805 | 1.5211 | 1.9217 | 2.4302 | 2.9018 | 3.561 | 4.3644 | 5.313 | 6.2227 | 7.0791 | 7.9358 | 8.7294 | 9.3202 | 9.7854 | 10.432 | 11.0462 | 13.9037 | 15.1291
Pembroke | Broadfield | Primary Substation | 11 | Holistic Transition | 0.59062 | 0.70885 | 0.84642 | 0.98884 | 1.1331 | 1.4005 | 1.6982 | 2.0693 | 2.4139 | 2.7981 | 3.1747 | 3.5252 | 3.868 | 4.1705 | 4.5513 | 4.884 | 6.0737 | 6.4557 | 1.3117 | 1.5741 | 1.8727 | 2.1869 | 2.5056 | 3.0813 | 3.7278 | 4.5272 | 5.2745 | 6.1105 | 6.9165 | 7.6675 | 8.3993 | 9.0348 | 9.8256 | 10.5199 | 13.0584 | 13.9034
Pembroke | Broadfield | Primary Substation | 11 | Hydrogen Evolution | 0.56642 | 0.65841 | 0.76974 | 0.90079 | 1.0326 | 1.216 | 1.4238 | 1.689 | 1.946 | 2.2431 | 2.5209 | 2.7775 | 3.0257 | 3.237 | 3.4844 | 3.696 | 4.3737 | 4.9527 | 1.2508 | 1.4474 | 1.6828 | 1.962 | 2.2435 | 2.6318 | 3.0742 | 3.6314 | 4.1801 | 4.8238 | 5.4157 | 5.9606 | 6.4839 | 6.9243 | 7.4362 | 7.8775 | 9.3581 | 10.6549
Pembroke | Fishguard | Primary Substation | 11 | Counterfactual | 0.58932 | 0.63896 | 0.70454 | 0.77783 | 0.87807 | 0.98089 | 1.0762 | 1.2377 | 1.3732 | 1.5263 | 1.6899 | 1.8641 | 2.0701 | 2.2769 | 2.4836 | 2.673 | 3.6833 | 4.2561 | 1.4147 | 1.5195 | 1.6554 | 1.807 | 2.0145 | 2.2267 | 2.4222 | 2.7567 | 3.0445 | 3.3724 | 3.7241 | 4.0987 | 4.5436 | 4.9925 | 5.4441 | 5.85 | 7.8906 | 9.0512
Pembroke | Fishguard | Primary Substation | 11 | Electric Engagement | 0.60653 | 0.71281 | 0.89334 | 1.1372 | 1.3764 | 1.5829 | 1.8662 | 2.2097 | 2.5512 | 2.8679 | 3.1443 | 3.4415 | 3.6009 | 3.6806 | 3.7344 | 3.7897 | 4.0049 | 4.1461 | 1.4582 | 1.6859 | 2.0618 | 2.5713 | 3.0732 | 3.5017 | 4.1089 | 4.8426 | 5.5882 | 6.2896 | 6.9021 | 7.5682 | 7.943 | 8.1256 | 8.2415 | 8.3607 | 8.8385 | 9.1597
Pembroke | Fishguard | Primary Substation | 11 | Holistic Transition | 0.61878 | 0.73072 | 0.8665 | 1.0227 | 1.1546 | 1.3729 | 1.5928 | 1.8933 | 2.1796 | 2.4944 | 2.8106 | 3.0824 | 3.2886 | 3.4555 | 3.6207 | 3.7681 | 4.0261 | 4.207 | 1.4887 | 1.7353 | 2.0293 | 2.3654 | 2.6466 | 3.1315 | 3.6209 | 4.2812 | 4.9242 | 5.6292 | 6.3345 | 6.9334 | 7.3717 | 7.7168 | 8.058 | 8.3635 | 8.9327 | 9.3411
Pembroke | Fishguard | Primary Substation | 11 | Hydrogen Evolution | 0.59549 | 0.67005 | 0.75976 | 0.87351 | 1.0162 | 1.1695 | 1.3737 | 1.6517 | 1.9432 | 2.2506 | 2.543 | 2.8452 | 3.1674 | 3.3954 | 3.5697 | 3.72 | 4.0196 | 4.1652 | 1.4298 | 1.5874 | 1.7747 | 2.012 | 2.3099 | 2.629 | 3.0718 | 3.667 | 4.3038 | 4.9773 | 5.6123 | 6.2789 | 6.9927 | 7.4854 | 7.8417 | 8.1497 | 8.7794 | 9.0925
Pembroke | Golden Hill Primary | Primary Substation | 11 | Counterfactual | 0.8223 | 0.92831 | 1.0522 | 1.1834 | 1.3478 | 1.5737 | 1.7834 | 2.1054 | 2.3448 | 2.5997 | 2.8579 | 3.1243 | 3.4291 | 3.7348 | 4.0383 | 4.3449 | 5.5679 | 5.969 | 1.9694 | 2.1932 | 2.4508 | 2.7231 | 3.0711 | 3.5511 | 3.9974 | 4.6779 | 5.1873 | 5.7312 | 6.2789 | 6.8398 | 7.4809 | 8.1269 | 8.7713 | 9.4153 | 11.9354 | 12.7933
Pembroke | Golden Hill Primary | Primary Substation | 11 | Electric Engagement | 0.86441 | 1.0481 | 1.3509 | 1.7698 | 2.1883 | 2.7028 | 3.3171 | 3.9645 | 4.551 | 5.0633 | 5.5213 | 5.9896 | 6.2523 | 6.4505 | 6.6261 | 6.8884 | 7.608 | 8.0034 | 2.0721 | 2.4657 | 3.0937 | 3.987 | 4.8859 | 5.9905 | 7.3238 | 8.6947 | 9.9458 | 11.047 | 12.0312 | 13.0442 | 13.6415 | 14.0812 | 14.4637 | 15.0583 | 16.6381 | 17.5499
Pembroke | Golden Hill Primary | Primary Substation | 11 | Holistic Transition | 0.88881 | 1.0718 | 1.3075 | 1.5673 | 1.8566 | 2.3456 | 2.7533 | 3.2708 | 3.7368 | 4.2659 | 4.9643 | 5.4509 | 5.8727 | 6.2304 | 6.5738 | 6.897 | 7.6535 | 8.0498 | 2.1325 | 2.5366 | 3.0601 | 3.639 | 4.2831 | 5.3805 | 6.2776 | 7.3935 | 8.4113 | 9.5639 | 11.1294 | 12.1754 | 13.0691 | 13.813 | 14.5274 | 15.2016 | 16.8582 | 17.7518
Pembroke | Golden Hill Primary | Primary Substation | 11 | Hydrogen Evolution | 0.84192 | 0.99366 | 1.1609 | 1.4087 | 1.687 | 2.0487 | 2.4593 | 2.9194 | 3.349 | 3.8177 | 4.2723 | 4.7294 | 5.2026 | 5.556 | 5.8523 | 6.2016 | 6.7921 | 7.2096 | 2.0148 | 2.3371 | 2.6874 | 3.2281 | 3.8366 | 4.6257 | 5.5344 | 6.5113 | 7.4328 | 8.441 | 9.408 | 10.3887 | 11.4068 | 12.1547 | 12.762 | 13.5157 | 14.7872 | 15.71
Pembroke | Haverfordwest Power Stn | Primary Substation | 11 | Counterfactual | 0.92575 | 0.9736 | 1.0333 | 1.1022 | 1.2033 | 1.3414 | 1.4919 | 1.7154 | 1.9211 | 2.1344 | 2.3403 | 2.5423 | 2.7578 | 2.9751 | 3.1918 | 3.391 | 4.1225 | 4.5037 | 2.2054 | 2.3065 | 2.4306 | 2.5743 | 2.795 | 3.0989 | 3.4308 | 3.9211 | 4.3848 | 4.8644 | 5.3227 | 5.768 | 6.2377 | 6.7141 | 7.1914 | 7.623 | 9.1621 | 9.9977
Pembroke | Haverfordwest Power Stn | Primary Substation | 11 | Electric Engagement | 0.94281 | 1.0372 | 1.2001 | 1.4741 | 1.7444 | 2.0768 | 2.521 | 3.0453 | 3.5177 | 3.9671 | 4.3876 | 4.8068 | 5.0966 | 5.2886 | 5.4317 | 5.6567 | 6.4421 | 6.8764 | 2.2477 | 2.45 | 2.7895 | 3.3945 | 3.9968 | 4.7299 | 5.7222 | 6.8901 | 7.943 | 8.9524 | 9.8973 | 10.844 | 11.5166 | 11.9421 | 12.2541 | 12.77 | 14.5026 | 15.5264
Pembroke | Haverfordwest Power Stn | Primary Substation | 11 | Holistic Transition | 0.95432 | 1.0459 | 1.2033 | 1.3873 | 1.5938 | 1.9467 | 2.3383 | 2.7665 | 3.176 | 3.6377 | 4.2199 | 4.594 | 4.8979 | 5.1528 | 5.3827 | 5.5956 | 6.3456 | 6.6588 | 2.276 | 2.4785 | 2.837 | 3.2617 | 3.7378 | 4.5484 | 5.4526 | 6.4177 | 7.3523 | 8.4064 | 9.7556 | 10.5922 | 11.2549 | 11.7912 | 12.2767 | 12.7282 | 14.3719 | 15.0716
Pembroke | Haverfordwest Power Stn | Primary Substation | 11 | Hydrogen Evolution | 0.93339 | 1.0054 | 1.0896 | 1.2714 | 1.4802 | 1.724 | 2.0385 | 2.4282 | 2.7887 | 3.1855 | 3.5431 | 3.8872 | 4.2425 | 4.4963 | 4.684 | 4.9231 | 5.4583 | 5.9309 | 2.2232 | 2.3757 | 2.5517 | 2.9619 | 3.4363 | 3.9841 | 4.7005 | 5.5748 | 6.383 | 7.2787 | 8.0755 | 8.8463 | 9.6419 | 10.1937 | 10.5836 | 11.1158 | 12.3013 | 13.3726
Pembroke | Merlins Bridge | Primary Substation | 11 | Counterfactual | 0.58229 | 0.66257 | 0.76558 | 0.88558 | 1.0047 | 1.1403 | 1.2799 | 1.4941 | 1.6673 | 1.8536 | 2.0389 | 2.2194 | 2.4166 | 2.6125 | 2.8022 | 2.9896 | 3.7913 | 4.1233 | 1.2763 | 1.4451 | 1.6592 | 1.9085 | 2.1565 | 2.4386 | 2.731 | 3.1784 | 3.5468 | 3.9456 | 4.3374 | 4.715 | 5.1246 | 5.5315 | 5.9251 | 6.312 | 7.9719 | 8.6893
Pembroke | Merlins Bridge | Primary Substation | 11 | Electric Engagement | 0.61186 | 0.74243 | 0.97113 | 1.2534 | 1.522 | 2.0278 | 2.4344 | 2.9097 | 3.3535 | 3.7547 | 4.1339 | 4.4872 | 4.7087 | 4.8704 | 5.0464 | 5.2379 | 6.2772 | 6.7524 | 1.3484 | 1.6273 | 2.1037 | 2.6927 | 3.2567 | 4.295 | 5.1524 | 6.15 | 7.0863 | 7.9365 | 8.7391 | 9.488 | 9.9697 | 10.3145 | 10.6874 | 11.0932 | 13.2944 | 14.3579
Pembroke | Merlins Bridge | Primary Substation | 11 | Holistic Transition | 0.62865 | 0.75747 | 0.90732 | 1.0951 | 1.2792 | 1.5696 | 1.8701 | 2.2483 | 2.5914 | 2.9632 | 3.3329 | 3.6661 | 3.9901 | 4.2728 | 4.5561 | 4.8286 | 5.8064 | 6.224 | 1.3902 | 1.6732 | 1.9963 | 2.404 | 2.8029 | 3.4328 | 4.0846 | 4.8931 | 5.6321 | 6.4306 | 7.2146 | 7.9193 | 8.5993 | 9.1877 | 9.7764 | 10.3436 | 12.4175 | 13.3223
Pembroke | Merlins Bridge | Primary Substation | 11 | Hydrogen Evolution | 0.59596 | 0.70577 | 0.83899 | 1.0045 | 1.1723 | 1.3643 | 1.5982 | 1.9023 | 2.1888 | 2.5033 | 2.8022 | 3.0824 | 3.357 | 3.5801 | 3.7973 | 3.9942 | 4.5679 | 5.0378 | 1.3081 | 1.5412 | 1.8221 | 2.171 | 2.5257 | 2.9274 | 3.4267 | 4.0658 | 4.6748 | 5.3467 | 5.9756 | 6.565 | 7.14 | 7.6009 | 8.0474 | 8.4545 | 9.6857 | 10.7143
Pembroke | Milford Haven | Primary Substation | 11 | Counterfactual | 0.12855 | 0.161 | 0.19386 | 0.23103 | 0.26615 | 0.36387 | 0.41217 | 0.48891 | 0.54453 | 0.60353 | 0.66353 | 0.72718 | 0.79902 | 0.86986 | 0.93802 | 1.0045 | 1.6906 | 2.1738 | 0.30509 | 0.37349 | 0.4417 | 0.51871 | 0.59216 | 0.79642 | 0.89627 | 1.0563 | 1.1738 | 1.2982 | 1.4241 | 1.5565 | 1.7057 | 1.8528 | 1.994 | 2.1309 | 3.514 | 4.4901
Pembroke | Milford Haven | Primary Substation | 11 | Electric Engagement | 0.13807 | 0.18872 | 0.26853 | 0.37072 | 0.45609 | 0.63212 | 0.77733 | 0.93385 | 1.0669 | 1.1785 | 1.2736 | 1.3692 | 1.4053 | 1.4267 | 1.4478 | 1.4978 | 1.5971 | 1.6718 | 0.32856 | 0.43693 | 0.60228 | 0.81712 | 0.99399 | 1.3687 | 1.6815 | 2.0118 | 2.2934 | 2.5307 | 2.7321 | 2.9345 | 3.0149 | 3.0621 | 3.1086 | 3.2132 | 3.4378 | 3.6094
Pembroke | Milford Haven | Primary Substation | 11 | Holistic Transition | 0.14402 | 0.19757 | 0.25462 | 0.31111 | 0.36083 | 0.53313 | 0.63257 | 0.75378 | 0.85081 | 0.95084 | 1.0518 | 1.1507 | 1.244 | 1.3301 | 1.4109 | 1.5115 | 1.6281 | 1.7096 | 0.34331 | 0.46096 | 0.58586 | 0.70728 | 0.81306 | 1.1958 | 1.414 | 1.6735 | 1.8827 | 2.0965 | 2.3102 | 2.517 | 2.7103 | 2.8885 | 3.056 | 3.2629 | 3.5253 | 3.712
Pembroke | Milford Haven | Primary Substation | 11 | Hydrogen Evolution | 0.13283 | 0.17907 | 0.22404 | 0.28479 | 0.33224 | 0.4658 | 0.56436 | 0.68111 | 0.77906 | 0.8783 | 0.97388 | 1.0679 | 1.1612 | 1.2387 | 1.3105 | 1.4016 | 1.5197 | 1.5894 | 0.31507 | 0.4134 | 0.50751 | 0.63773 | 0.73603 | 1.0224 | 1.2378 | 1.4852 | 1.6938 | 1.904 | 2.1037 | 2.3005 | 2.4954 | 2.6547 | 2.8012 | 2.9864 | 3.2389 | 3.393
Pembroke | Nevern | Primary Substation | 11 | Counterfactual | 0.12344 | 0.13959 | 0.15796 | 0.17806 | 0.20128 | 0.22728 | 0.25593 | 0.3026 | 0.3375 | 0.37501 | 0.41371 | 0.45452 | 0.50129 | 0.54661 | 0.59001 | 0.63436 | 0.82548 | 0.89305 | 0.29608 | 0.33066 | 0.36885 | 0.41051 | 0.4584 | 0.51187 | 0.57065 | 0.66585 | 0.73758 | 0.81455 | 0.89377 | 0.9771 | 1.0724 | 1.1647 | 1.2532 | 1.3433 | 1.7319 | 1.8731
Pembroke | Nevern | Primary Substation | 11 | Electric Engagement | 0.12996 | 0.16334 | 0.21446 | 0.27395 | 0.32917 | 0.38887 | 0.46463 | 0.55521 | 0.63517 | 0.7025 | 0.76141 | 0.81897 | 0.83979 | 0.85302 | 0.86643 | 0.87875 | 0.94082 | 0.98698 | 0.31216 | 0.38487 | 0.49078 | 0.61335 | 0.72737 | 0.85027 | 1.0067 | 1.1923 | 1.3568 | 1.4956 | 1.6174 | 1.7362 | 1.7812 | 1.8106 | 1.8402 | 1.8677 | 2.0076 | 2.1131
Pembroke | Nevern | Primary Substation | 11 | Holistic Transition | 0.13392 | 0.166 | 0.19594 | 0.22834 | 0.26323 | 0.31108 | 0.36124 | 0.43101 | 0.48856 | 0.55112 | 0.61572 | 0.6762 | 0.73482 | 0.78793 | 0.83935 | 0.88268 | 0.98587 | 1.0506 | 0.32204 | 0.39442 | 0.4593 | 0.52901 | 0.60343 | 0.70526 | 0.81106 | 0.95596 | 1.0762 | 1.206 | 1.3397 | 1.465 | 1.5865 | 1.6969 | 1.8037 | 1.8943 | 2.1203 | 2.2675
Pembroke | Nevern | Primary Substation | 11 | Hydrogen Evolution | 0.12608 | 0.15034 | 0.17588 | 0.20736 | 0.24178 | 0.28159 | 0.33008 | 0.39843 | 0.4621 | 0.52709 | 0.59208 | 0.65218 | 0.7144 | 0.76555 | 0.81778 | 0.85978 | 0.94764 | 0.9975 | 0.3023 | 0.3543 | 0.40759 | 0.47277 | 0.54375 | 0.6256 | 0.72597 | 0.8658 | 0.99612 | 1.1288 | 1.2611 | 1.3837 | 1.5104 | 1.6148 | 1.7212 | 1.8071 | 1.9918 | 2.0993
Pembroke | Neyland | Primary Substation | 11 | Counterfactual | 0.30589 | 0.33822 | 0.37912 | 0.42085 | 0.47257 | 0.57617 | 0.65726 | 0.77253 | 0.87203 | 0.9842 | 1.0949 | 1.2011 | 1.3186 | 1.4341 | 1.5446 | 1.6513 | 2.0673 | 2.2361 | 0.67255 | 0.74037 | 0.82517 | 0.91167 | 1.02 | 1.2367 | 1.407 | 1.6497 | 1.8649 | 2.1102 | 2.3496 | 2.5766 | 2.8263 | 3.0719 | 3.3064 | 3.5302 | 4.394 | 4.7612
Pembroke | Neyland | Primary Substation | 11 | Electric Engagement | 0.31998 | 0.38087 | 0.48883 | 0.62143 | 0.74044 | 0.94149 | 1.1698 | 1.4357 | 1.6994 | 1.9344 | 2.1435 | 2.3427 | 2.4593 | 2.5355 | 2.6139 | 2.6953 | 3.285 | 3.4891 | 0.707 | 0.83662 | 1.0606 | 1.3391 | 1.5878 | 2.0113 | 2.5007 | 3.0714 | 3.6465 | 4.1614 | 4.6164 | 5.0506 | 5.3117 | 5.4759 | 5.644 | 5.8191 | 7.069 | 7.5409
Pembroke | Neyland | Primary Substation | 11 | Holistic Transition | 0.32839 | 0.38646 | 0.4581 | 0.52649 | 0.6037 | 0.80551 | 0.99411 | 1.2241 | 1.4332 | 1.6501 | 1.8573 | 2.0336 | 2.1916 | 2.3331 | 2.4721 | 2.5992 | 3.1472 | 3.3215 | 0.72789 | 0.8554 | 1.0114 | 1.1604 | 1.3281 | 1.7732 | 2.1934 | 2.7007 | 3.1667 | 3.6466 | 4.0977 | 4.4772 | 4.8109 | 5.1066 | 5.3966 | 5.663 | 6.8248 | 7.2114
Pembroke | Neyland | Primary Substation | 11 | Hydrogen Evolution | 0.31187 | 0.35842 | 0.41333 | 0.48235 | 0.55549 | 0.69777 | 0.84031 | 1.0197 | 1.2072 | 1.4031 | 1.5777 | 1.7436 | 1.9084 | 2.029 | 2.1421 | 2.2404 | 2.5928 | 2.8214 | 0.68647 | 0.78456 | 0.89928 | 1.0459 | 1.1994 | 1.5021 | 1.8122 | 2.1989 | 2.6116 | 3.0435 | 3.4211 | 3.7812 | 4.1357 | 4.3877 | 4.6205 | 4.8244 | 5.5772 | 6.0844
Pembroke | Penblewin | Primary Substation | 11 | Counterfactual | 0.43285 | 0.48267 | 0.62293 | 0.70384 | 0.79755 | 0.91114 | 1.0441 | 1.2379 | 1.4036 | 1.5933 | 1.7658 | 1.9186 | 2.0765 | 2.2324 | 2.3817 | 2.5351 | 3.2771 | 3.7356 | 1.0045 | 1.1096 | 1.4309 | 1.6002 | 1.8024 | 2.0456 | 2.3352 | 2.7547 | 3.1202 | 3.5444 | 3.9216 | 4.2483 | 4.5793 | 4.907 | 5.2206 | 5.542 | 7.1319 | 8.152
Pembroke | Penblewin | Primary Substation | 11 | Electric Engagement | 0.55127 | 0.70575 | 0.86041 | 1.0977 | 1.3056 | 1.5834 | 1.9229 | 2.3271 | 2.7184 | 3.0946 | 3.4742 | 3.8246 | 4.0869 | 4.2977 | 4.515 | 4.7506 | 6.0639 | 6.6704 | 1.2478 | 1.6034 | 1.9272 | 2.4428 | 2.8893 | 3.4784 | 4.2049 | 5.0703 | 5.9136 | 6.7297 | 7.556 | 8.3185 | 8.8999 | 9.3572 | 9.8267 | 10.3356 | 13.1782 | 14.6059
Pembroke | Penblewin | Primary Substation | 11 | Holistic Transition | 0.52494 | 0.61209 | 0.73964 | 0.88444 | 1.0315 | 1.2846 | 1.5596 | 1.9115 | 2.2408 | 2.6204 | 2.9591 | 3.2847 | 3.6012 | 3.8666 | 4.1325 | 4.3936 | 5.5578 | 5.9471 | 1.2344 | 1.4265 | 1.7093 | 2.032 | 2.3616 | 2.9139 | 3.5205 | 4.2922 | 5.0204 | 5.8631 | 6.5954 | 7.3061 | 7.9941 | 8.5581 | 9.1219 | 9.6764 | 12.1902 | 13.0497
Pembroke | Penblewin | Primary Substation | 11 | Hydrogen Evolution | 0.43867 | 0.58089 | 0.67681 | 0.83048 | 0.96504 | 1.1266 | 1.3162 | 1.5599 | 1.8173 | 2.1232 | 2.3946 | 2.6356 | 2.8742 | 3.0598 | 3.2515 | 3.4264 | 4.1606 | 4.8303 | 1.0181 | 1.346 | 1.5488 | 1.8863 | 2.177 | 2.5219 | 2.931 | 3.4486 | 4.0044 | 4.6795 | 5.2675 | 5.7882 | 6.2973 | 6.6881 | 7.0904 | 7.4613 | 9.0892 | 10.6101
Pembroke | St Davids | Primary Substation | 11 | Counterfactual | 0.067125 | 0.079317 | 0.092203 | 0.10595 | 0.1219 | 0.13994 | 0.15964 | 0.1934 | 0.21891 | 0.24591 | 0.27353 | 0.3023 | 0.33518 | 0.36701 | 0.39755 | 0.42792 | 0.54525 | 0.57701 | 0.15255 | 0.17873 | 0.2056 | 0.2342 | 0.26724 | 0.30447 | 0.34501 | 0.41482 | 0.46824 | 0.52458 | 0.58202 | 0.64169 | 0.70976 | 0.77559 | 0.83875 | 0.90118 | 1.1408 | 1.2089
Pembroke | St Davids | Primary Substation | 11 | Electric Engagement | 0.072274 | 0.095719 | 0.13104 | 0.17144 | 0.20918 | 0.24916 | 0.3078 | 0.37345 | 0.43092 | 0.47755 | 0.51697 | 0.55521 | 0.56841 | 0.57605 | 0.58375 | 0.59127 | 0.63468 | 0.66634 | 0.16499 | 0.21641 | 0.28972 | 0.3732 | 0.45136 | 0.53394 | 0.65902 | 0.79659 | 0.91758 | 1.0163 | 1.0995 | 1.1803 | 1.21 | 1.2275 | 1.2451 | 1.2623 | 1.3616 | 1.435
Pembroke | St Davids | Primary Substation | 11 | Holistic Transition | 0.075218 | 0.098312 | 0.11937 | 0.1417 | 0.16566 | 0.20613 | 0.24507 | 0.29538 | 0.33676 | 0.37975 | 0.42353 | 0.46271 | 0.50026 | 0.53508 | 0.56868 | 0.5976 | 0.64826 | 0.69185 | 0.17226 | 0.22468 | 0.27051 | 0.31889 | 0.37031 | 0.46022 | 0.54519 | 0.65221 | 0.74107 | 0.83251 | 0.92501 | 1.0074 | 1.0857 | 1.1585 | 1.2289 | 1.2897 | 1.4058 | 1.5061
Pembroke | St Davids | Primary Substation | 11 | Hydrogen Evolution | 0.069602 | 0.086382 | 0.10374 | 0.12352 | 0.14567 | 0.17101 | 0.20886 | 0.25702 | 0.30129 | 0.34477 | 0.38663 | 0.42608 | 0.46766 | 0.50112 | 0.5341 | 0.56119 | 0.61596 | 0.64946 | 0.15816 | 0.19437 | 0.23073 | 0.27182 | 0.31772 | 0.3701 | 0.45196 | 0.55311 | 0.64644 | 0.73759 | 0.82442 | 0.90662 | 0.99296 | 1.0618 | 1.1292 | 1.1848 | 1.3015 | 1.3745
Pembroke | St Florence | Primary Substation | 11 | Counterfactual | 0.20976 | 0.22496 | 0.24322 | 0.26385 | 0.28859 | 0.32799 | 0.37203 | 0.4369 | 0.49093 | 0.54932 | 0.60581 | 0.65944 | 0.71548 | 0.77125 | 0.82543 | 0.88043 | 1.1726 | 1.3542 | 0.46997 | 0.50216 | 0.54026 | 0.58341 | 0.63557 | 0.71817 | 0.81199 | 0.94893 | 1.0647 | 1.1915 | 1.3118 | 1.4241 | 1.5399 | 1.6553 | 1.7673 | 1.8809 | 2.4918 | 2.8807
Pembroke | St Florence | Primary Substation | 11 | Electric Engagement | 0.21654 | 0.24535 | 0.29526 | 0.36068 | 0.42576 | 0.54064 | 0.6736 | 0.83453 | 0.99477 | 1.1552 | 1.3186 | 1.4671 | 1.5799 | 1.671 | 1.7656 | 1.92 | 2.4619 | 2.6498 | 0.48642 | 0.54855 | 0.6524 | 0.78922 | 0.92653 | 1.1652 | 1.4413 | 1.7765 | 2.1114 | 2.4474 | 2.7903 | 3.1026 | 3.3445 | 3.5362 | 3.7347 | 4.0536 | 5.194 | 5.6236
Pembroke | St Florence | Primary Substation | 11 | Holistic Transition | 0.22044 | 0.24776 | 0.27607 | 0.31912 | 0.36649 | 0.46134 | 0.56663 | 0.70144 | 0.83263 | 0.98419 | 1.1347 | 1.2715 | 1.4008 | 1.5109 | 1.6209 | 1.7822 | 2.2396 | 2.3853 | 0.49614 | 0.55708 | 0.61812 | 0.71257 | 0.81658 | 1.0166 | 1.2407 | 1.5267 | 1.8059 | 2.1291 | 2.4459 | 2.7347 | 3.0078 | 3.2374 | 3.4662 | 3.7979 | 4.7629 | 5.0788
Pembroke | St Florence | Primary Substation | 11 | Hydrogen Evolution | 0.2128 | 0.23422 | 0.25882 | 0.29342 | 0.33425 | 0.3963 | 0.46624 | 0.559 | 0.65499 | 0.77031 | 0.87869 | 0.97604 | 1.0651 | 1.1363 | 1.2079 | 1.2999 | 1.5439 | 1.7684 | 0.47696 | 0.52258 | 0.5743 | 0.64677 | 0.73351 | 0.86326 | 1.0092 | 1.2013 | 1.4025 | 1.6475 | 1.8747 | 2.0783 | 2.2638 | 2.4114 | 2.5598 | 2.7495 | 3.2775 | 3.7712
Pembroke | St Twynells | Primary Substation | 11 | Counterfactual | 0.095893 | 0.10669 | 0.12148 | 0.13885 | 0.18944 | 0.25788 | 0.32821 | 0.41862 | 0.50399 | 0.5995 | 0.69313 | 0.77988 | 0.82976 | 0.87972 | 0.92761 | 0.97691 | 1.2279 | 1.4052 | 0.22832 | 0.25095 | 0.28174 | 0.31816 | 0.43648 | 0.59248 | 0.75313 | 0.95788 | 1.155 | 1.3777 | 1.5941 | 1.7931 | 1.8976 | 2.0026 | 2.103 | 2.2062 | 2.7442 | 3.1339
Pembroke | St Twynells | Primary Substation | 11 | Electric Engagement | 0.099808 | 0.12062 | 0.16073 | 0.31655 | 0.43366 | 0.61372 | 0.81243 | 1.0362 | 1.2591 | 1.4813 | 1.6953 | 1.8343 | 1.954 | 2.051 | 2.1517 | 2.257 | 2.8436 | 3.0716 | 0.23816 | 0.28237 | 0.36606 | 0.73522 | 1.0089 | 1.4174 | 1.8664 | 2.3699 | 2.8731 | 3.3757 | 3.856 | 4.1547 | 4.4165 | 4.6227 | 4.8361 | 5.0597 | 6.3066 | 6.8351
Pembroke | St Twynells | Primary Substation | 11 | Holistic Transition | 0.1024 | 0.12154 | 0.21983 | 0.30741 | 0.41289 | 0.5825 | 0.76072 | 0.96283 | 1.1617 | 1.3808 | 1.5188 | 1.6429 | 1.7633 | 1.8656 | 1.9693 | 2.0695 | 2.5552 | 2.7076 | 0.24466 | 0.2866 | 0.52437 | 0.73364 | 0.98664 | 1.3768 | 1.7889 | 2.2525 | 2.7103 | 3.2139 | 3.5108 | 3.7791 | 4.0386 | 4.2541 | 4.4719 | 4.6829 | 5.7164 | 6.0459
Pembroke | St Twynells | Primary Substation | 11 | Hydrogen Evolution | 0.097388 | 0.11388 | 0.13455 | 0.26159 | 0.3662 | 0.4997 | 0.63855 | 0.79284 | 0.95429 | 1.1351 | 1.2896 | 1.3726 | 1.4521 | 1.5145 | 1.5791 | 1.638 | 1.9106 | 2.1777 | 0.23197 | 0.2666 | 0.31004 | 0.61633 | 0.86548 | 1.1775 | 1.5014 | 1.8563 | 2.2296 | 2.6496 | 3.0035 | 3.1818 | 3.3509 | 3.4821 | 3.6176 | 3.7426 | 4.3422 | 4.9387
Pembroke | Steynton | Primary Substation | 11 | Counterfactual | 0.61305 | 0.69372 | 0.79749 | 0.91976 | 1.063 | 1.2482 | 1.4392 | 1.7058 | 1.9371 | 2.1896 | 2.4432 | 2.69 | 2.9313 | 3.1649 | 3.3889 | 3.6064 | 4.4309 | 4.7392 | 1.3208 | 1.4906 | 1.7059 | 1.9594 | 2.2643 | 2.6622 | 3.0712 | 3.6389 | 4.1442 | 4.6982 | 5.2513 | 5.786 | 6.2955 | 6.7884 | 7.2607 | 7.7146 | 9.413 | 10.075
Pembroke | Steynton | Primary Substation | 11 | Electric Engagement | 0.6416 | 0.77993 | 1.0148 | 1.3666 | 1.7373 | 2.2514 | 2.7861 | 3.3786 | 3.9391 | 4.4379 | 5.0293 | 5.3938 | 5.5931 | 5.766 | 5.942 | 6.0656 | 6.7668 | 7.0821 | 1.3909 | 1.6865 | 2.1737 | 2.932 | 3.7408 | 4.8369 | 6.0092 | 7.2997 | 8.5322 | 9.6362 | 10.9046 | 11.6934 | 12.1385 | 12.5042 | 12.8754 | 13.143 | 14.6571 | 15.3856
Pembroke | Steynton | Primary Substation | 11 | Holistic Transition | 0.65912 | 0.79867 | 1.0064 | 1.2563 | 1.5007 | 1.9076 | 2.3405 | 2.8396 | 3.2916 | 3.7573 | 4.3066 | 4.6388 | 4.9352 | 5.2516 | 5.5607 | 5.791 | 6.4843 | 6.7838 | 1.4344 | 1.7416 | 2.2063 | 2.7686 | 3.3183 | 4.2395 | 5.2192 | 6.329 | 7.3445 | 8.3829 | 9.5445 | 10.2545 | 10.8773 | 11.5326 | 12.1727 | 12.655 | 14.1515 | 14.821
Pembroke | Steynton | Primary Substation | 11 | Hydrogen Evolution | 0.62554 | 0.74035 | 0.87706 | 1.1126 | 1.3718 | 1.672 | 2.0442 | 2.4875 | 2.9219 | 3.3681 | 3.847 | 4.1806 | 4.5098 | 4.7803 | 5.0367 | 5.2328 | 5.7401 | 6.0906 | 1.3501 | 1.5934 | 1.8803 | 2.3997 | 2.9769 | 3.6389 | 4.4709 | 5.4451 | 6.4102 | 7.4008 | 8.431 | 9.1473 | 9.8496 | 10.4096 | 10.9345 | 11.3397 | 12.4279 | 13.2026
Pembroke | Tenby | Primary Substation | 11 | Counterfactual | 0.20744 | 0.24094 | 0.27883 | 0.32078 | 0.3657 | 0.41714 | 0.47368 | 0.56341 | 0.63048 | 0.70169 | 0.77574 | 0.85281 | 0.94014 | 1.0262 | 1.1097 | 1.1932 | 1.5456 | 1.65 | 0.49348 | 0.56543 | 0.64442 | 0.73162 | 0.82461 | 0.9308 | 1.0472 | 1.2302 | 1.3681 | 1.5142 | 1.666 | 1.8234 | 2.0013 | 2.1766 | 2.3466 | 2.5166 | 3.2364 | 3.4588
Pembroke | Tenby | Primary Substation | 11 | Electric Engagement | 0.22079 | 0.28757 | 0.38941 | 0.50829 | 0.61797 | 0.738 | 0.88193 | 1.0578 | 1.2113 | 1.3382 | 1.4518 | 1.5613 | 1.6035 | 1.6357 | 1.6681 | 1.699 | 1.8917 | 1.9915 | 0.52617 | 0.67211 | 0.8835 | 1.1294 | 1.3568 | 1.6043 | 1.9002 | 2.2603 | 2.5757 | 2.8377 | 3.073 | 3.2997 | 3.3914 | 3.4625 | 3.5336 | 3.6022 | 4.0406 | 4.2708
Pembroke | Tenby | Primary Substation | 11 | Holistic Transition | 0.229 | 0.29504 | 0.35672 | 0.42366 | 0.49244 | 0.57916 | 0.67354 | 0.80592 | 0.91535 | 1.0309 | 1.1524 | 1.3319 | 1.4489 | 1.5587 | 1.6625 | 1.7545 | 1.9363 | 2.0614 | 0.5465 | 0.69579 | 0.82974 | 0.97458 | 1.122 | 1.3059 | 1.5047 | 1.7797 | 2.0086 | 2.2491 | 2.5014 | 2.9007 | 3.1443 | 3.373 | 3.5895 | 3.7824 | 4.1902 | 4.4783
Pembroke | Tenby | Primary Substation | 11 | Hydrogen Evolution | 0.21335 | 0.26263 | 0.3147 | 0.37462 | 0.43775 | 0.51118 | 0.59665 | 0.72009 | 0.82779 | 0.93858 | 1.0519 | 1.16 | 1.2698 | 1.3688 | 1.4645 | 1.5457 | 1.7392 | 1.8356 | 0.5072 | 0.61322 | 0.72218 | 0.84711 | 0.97803 | 1.1297 | 1.3057 | 1.5577 | 1.7783 | 2.005 | 2.2361 | 2.4566 | 2.6805 | 2.883 | 3.0788 | 3.2457 | 3.6702 | 3.8817
Pyle | Bridgend Trading Estate | Primary Substation | 11 | Counterfactual | 0.16445 | 0.20842 | 0.25972 | 0.31831 | 0.38757 | 0.46791 | 0.55334 | 0.68024 | 0.77709 | 0.88139 | 0.98951 | 1.1037 | 1.2342 | 1.3579 | 1.4781 | 1.6201 | 2.4846 | 2.6442 | 0.35947 | 0.45318 | 0.56017 | 0.68213 | 0.82568 | 0.99181 | 1.1685 | 1.4282 | 1.6281 | 1.8431 | 2.0655 | 2.2994 | 2.5652 | 2.8176 | 3.0629 | 3.3606 | 5.2779 | 5.6138
Pyle | Bridgend Trading Estate | Primary Substation | 11 | Electric Engagement | 0.18372 | 0.26976 | 0.40665 | 0.56805 | 0.72102 | 0.8916 | 1.0966 | 1.3381 | 1.55 | 1.7305 | 1.8927 | 2.0542 | 2.1743 | 2.4137 | 2.7022 | 2.8279 | 3.0624 | 3.2469 | 0.40596 | 0.59234 | 0.87651 | 1.2105 | 1.5284 | 1.8821 | 2.3056 | 2.8021 | 3.2392 | 3.6136 | 3.9513 | 4.2862 | 4.5639 | 5.1482 | 5.8533 | 6.1535 | 6.679 | 7.0966
Pyle | Bridgend Trading Estate | Primary Substation | 11 | Holistic Transition | 0.19669 | 0.2843 | 0.37507 | 0.47673 | 0.59011 | 0.74141 | 0.89362 | 1.0987 | 1.2644 | 1.4453 | 1.6331 | 1.8756 | 2.2589 | 2.6832 | 2.9133 | 3.0484 | 3.3944 | 3.6548 | 0.43697 | 0.63279 | 0.82894 | 1.0481 | 1.2915 | 1.6114 | 1.9327 | 2.3594 | 2.7069 | 3.0842 | 3.4745 | 4.0061 | 4.8903 | 5.8813 | 6.3885 | 6.6712 | 7.437 | 8.0184
Pyle | Bridgend Trading Estate | Primary Substation | 11 | Hydrogen Evolution | 0.1738 | 0.23731 | 0.3088 | 0.40161 | 0.50542 | 0.62515 | 0.75557 | 0.936 | 1.1118 | 1.2844 | 1.455 | 1.6133 | 1.7867 | 2.0158 | 2.3721 | 2.7216 | 3.0155 | 3.2429 | 0.3806 | 0.51628 | 0.66594 | 0.85902 | 1.075 | 1.3235 | 1.5936 | 1.9636 | 2.3241 | 2.6783 | 3.0278 | 3.3525 | 3.7072 | 4.221 | 5.0468 | 5.8705 | 6.4966 | 6.9839
Pyle | Litchard | Primary Substation | 11 | Counterfactual | 0.47627 | 0.54889 | 0.63737 | 0.73736 | 0.85602 | 0.99533 | 1.1515 | 1.3835 | 1.5633 | 1.7588 | 1.9563 | 2.158 | 2.3834 | 2.6007 | 2.8083 | 3.0289 | 4.0425 | 4.3372 | 1.0891 | 1.2426 | 1.4267 | 1.6345 | 1.881 | 2.1706 | 2.4962 | 2.9752 | 3.3506 | 3.7601 | 4.1704 | 4.5859 | 5.0471 | 5.492 | 5.917 | 6.3709 | 8.4915 | 9.1248
Pyle | Litchard | Primary Substation | 11 | Electric Engagement | 0.51126 | 0.65208 | 0.89005 | 1.1737 | 1.4441 | 1.7596 | 2.1399 | 2.5756 | 2.9609 | 3.2987 | 3.6183 | 3.9073 | 4.0775 | 4.2725 | 4.4629 | 4.5926 | 5.1497 | 5.5291 | 1.1736 | 1.4757 | 1.9693 | 2.5573 | 3.1208 | 3.777 | 4.5656 | 5.459 | 6.2514 | 6.9525 | 7.6243 | 8.2187 | 8.5978 | 9.051 | 9.4913 | 9.7756 | 11.0085 | 11.8796
Pyle | Litchard | Primary Substation | 11 | Holistic Transition | 0.53526 | 0.67436 | 0.82725 | 1.0063 | 1.2082 | 1.4778 | 1.7483 | 2.114 | 2.4136 | 2.7409 | 3.0992 | 3.4655 | 3.8867 | 4.2706 | 4.5647 | 4.8294 | 5.5211 | 5.9419 | 1.2313 | 1.5386 | 1.8675 | 2.2547 | 2.6899 | 3.2633 | 3.832 | 4.5927 | 5.2188 | 5.9012 | 6.6525 | 7.4324 | 8.3504 | 9.1841 | 9.7966 | 10.3498 | 11.8756 | 12.8197
Pyle | Litchard | Primary Substation | 11 | Hydrogen Evolution | 0.49267 | 0.59717 | 0.71943 | 0.87352 | 1.0491 | 1.2544 | 1.4844 | 1.8012 | 2.1021 | 2.4126 | 2.7176 | 2.9898 | 3.2799 | 3.5486 | 3.8626 | 4.1382 | 4.655 | 5.0769 | 1.1265 | 1.3479 | 1.6037 | 1.9251 | 2.2923 | 2.721 | 3.1998 | 3.8523 | 4.4748 | 5.1214 | 5.7522 | 6.3108 | 6.9044 | 7.4716 | 8.1471 | 8.7436 | 9.8582 | 10.7855
Pyle | Llangewydd | Primary Substation | 11 | Counterfactual | 0.38186 | 0.44569 | 0.52568 | 0.6154 | 0.71681 | 0.83206 | 0.96089 | 1.1599 | 1.3092 | 1.4682 | 1.6303 | 1.7972 | 1.9803 | 2.1636 | 2.3427 | 2.5166 | 3.2784 | 3.6805 | 0.83688 | 0.96993 | 1.1356 | 1.3212 | 1.5308 | 1.769 | 2.0353 | 2.4427 | 2.7508 | 3.0796 | 3.4133 | 3.7554 | 4.1291 | 4.503 | 4.8683 | 5.2224 | 6.7835 | 7.6577
Pyle | Llangewydd | Primary Substation | 11 | Electric Engagement | 0.41817 | 0.5374 | 0.75453 | 1.0098 | 1.2528 | 1.5241 | 1.8453 | 2.235 | 2.5758 | 2.855 | 3.105 | 3.3467 | 3.4269 | 3.4808 | 3.534 | 3.5886 | 4.3456 | 4.5575 | 0.92437 | 1.1763 | 1.6249 | 2.1512 | 2.6544 | 3.2153 | 3.8765 | 4.6752 | 5.3761 | 5.9534 | 6.4727 | 6.9746 | 7.1533 | 7.2753 | 7.3954 | 7.519 | 9.1874 | 9.6777
Pyle | Llangewydd | Primary Substation | 11 | Holistic Transition | 0.44118 | 0.5521 | 0.685 | 0.83718 | 1.0081 | 1.2074 | 1.4356 | 1.7472 | 2.0076 | 2.2807 | 2.5661 | 2.8973 | 3.3086 | 3.7017 | 4.0503 | 4.2399 | 4.64 | 4.8628 | 0.97989 | 1.2205 | 1.5054 | 1.8317 | 2.1965 | 2.6196 | 3.1008 | 3.7495 | 4.2949 | 4.8657 | 5.4585 | 6.1535 | 7.0255 | 7.8587 | 8.5974 | 8.9912 | 9.8804 | 10.3995
Pyle | Llangewydd | Primary Substation | 11 | Hydrogen Evolution | 0.39767 | 0.48501 | 0.58965 | 0.70936 | 0.8463 | 1.0052 | 1.1904 | 1.4498 | 1.6654 | 1.8957 | 2.1346 | 2.3678 | 2.5924 | 2.8694 | 3.1443 | 3.3883 | 3.8846 | 4.0547 | 0.8729 | 1.0558 | 1.2743 | 1.5242 | 1.8102 | 2.1413 | 2.525 | 3.0568 | 3.5013 | 3.9764 | 4.4664 | 4.9444 | 5.4042 | 5.9814 | 6.5572 | 7.0694 | 8.1443 | 8.5319
Pyle | Nottage | Primary Substation | 11 | Counterfactual | 0.75466 | 0.81856 | 0.89833 | 0.98877 | 0.70273 | 0.8269 | 0.96493 | 1.1743 | 1.3342 | 1.5052 | 1.678 | 1.8534 | 2.0442 | 2.2352 | 2.4212 | 2.6031 | 3.4283 | 3.9644 | 1.8208 | 1.9547 | 2.1201 | 2.3074 | 1.5482 | 1.8056 | 2.0925 | 2.5237 | 2.8563 | 3.2134 | 3.5718 | 3.9328 | 4.3233 | 4.7139 | 5.0941 | 5.4658 | 7.1663 | 8.3264
Pyle | Nottage | Primary Substation | 11 | Electric Engagement | 0.78764 | 0.90956 | 1.1263 | 1.3839 | 1.2397 | 1.5353 | 1.8826 | 2.3021 | 2.6756 | 2.9946 | 3.2903 | 3.5734 | 3.7035 | 3.8024 | 3.9019 | 4.0044 | 5.0545 | 5.357 | 1.9007 | 2.16 | 2.6084 | 3.1409 | 2.677 | 3.2895 | 4.0067 | 4.8706 | 5.6427 | 6.3061 | 6.9238 | 7.515 | 7.8003 | 8.0163 | 8.233 | 8.4565 | 10.7652 | 11.4608
Pyle | Nottage | Primary Substation | 11 | Holistic Transition | 0.80957 | 0.92559 | 1.0597 | 1.2169 | 1.0048 | 1.2319 | 1.4871 | 1.8293 | 2.1218 | 2.4337 | 2.7557 | 3.1863 | 3.6627 | 4.117 | 4.5243 | 4.749 | 5.2956 | 5.5895 | 1.9534 | 2.2072 | 2.4948 | 2.8333 | 2.2407 | 2.723 | 3.2638 | 3.9805 | 4.5973 | 5.2546 | 5.9275 | 6.8556 | 7.8694 | 8.8345 | 9.699 | 10.1665 | 11.3707 | 12.0411
Pyle | Nottage | Primary Substation | 11 | Hydrogen Evolution | 0.76941 | 0.8596 | 0.96688 | 1.0914 | 0.84567 | 1.0187 | 1.2171 | 1.4917 | 1.7271 | 1.982 | 2.2405 | 2.4904 | 2.7321 | 3.0368 | 3.3442 | 3.6171 | 4.2441 | 4.5316 | 1.8546 | 2.0444 | 2.2684 | 2.5286 | 1.8562 | 2.2176 | 2.6297 | 3.1944 | 3.6824 | 4.2133 | 4.7472 | 5.2623 | 5.7596 | 6.3974 | 7.0439 | 7.6192 | 8.9933 | 9.636
Pyle | Pyle Primary | Primary Substation | 11 | Counterfactual | 0.62877 | 0.6911 | 0.76368 | 0.84842 | 0.94681 | 1.0698 | 1.2137 | 1.4262 | 1.5943 | 1.7845 | 1.9713 | 2.152 | 2.3549 | 2.5536 | 2.7445 | 2.9378 | 3.8844 | 4.8693 | 1.4923 | 1.6234 | 1.7745 | 1.9508 | 2.1564 | 2.4141 | 2.7183 | 3.1631 | 3.521 | 3.9291 | 4.3252 | 4.7037 | 5.1257 | 5.5401 | 5.9377 | 6.3392 | 8.3281 | 10.4527
Pyle | Pyle Primary | Primary Substation | 11 | Electric Engagement | 0.65827 | 0.77495 | 0.97281 | 1.2117 | 1.442 | 1.7289 | 2.0827 | 2.5038 | 2.8938 | 3.2471 | 3.5803 | 3.9131 | 4.113 | 4.266 | 4.4174 | 4.6285 | 6.5059 | 6.928 | 1.5635 | 1.8127 | 2.2236 | 2.7213 | 3.2043 | 3.805 | 4.5461 | 5.4279 | 6.2515 | 7.0051 | 7.7207 | 8.437 | 8.8894 | 9.232 | 9.5702 | 10.0189 | 14.1545 | 15.1371
Pyle | Pyle Primary | Primary Substation | 11 | Holistic Transition | 0.67722 | 0.79031 | 0.91223 | 1.0679 | 1.2414 | 1.4907 | 1.7667 | 2.133 | 2.458 | 2.8185 | 3.187 | 3.5565 | 4.1396 | 4.6084 | 5.2417 | 6.0668 | 6.8373 | 7.2141 | 1.6091 | 1.8577 | 2.1198 | 2.459 | 2.8371 | 3.3727 | 3.9684 | 4.7513 | 5.4544 | 6.237 | 7.0283 | 7.8247 | 9.1349 | 10.1391 | 11.4929 | 13.2745 | 14.9617 | 15.8052
Pyle | Pyle Primary | Primary Substation | 11 | Hydrogen Evolution | 0.64232 | 0.72909 | 0.82754 | 0.95465 | 1.1004 | 1.278 | 1.4847 | 1.7648 | 2.0408 | 2.3398 | 2.6299 | 2.9044 | 3.1926 | 3.4731 | 3.8194 | 4.312 | 5.5878 | 6.0479 | 1.5232 | 1.7063 | 1.9127 | 2.1786 | 2.4863 | 2.8604 | 3.2959 | 3.8799 | 4.4621 | 5.1026 | 5.7166 | 6.3002 | 6.9099 | 7.5032 | 8.2378 | 9.2976 | 12.1123 | 13.1416
Pyle | Schwyll | Primary Substation | 11 | Counterfactual | 0.12879 | 0.15043 | 0.17254 | 0.19679 | 0.22712 | 0.27755 | 0.33572 | 0.41797 | 0.48636 | 0.56099 | 0.63245 | 0.69709 | 0.7642 | 0.8328 | 0.89843 | 0.96408 | 1.2995 | 1.7092 | 0.29836 | 0.34366 | 0.38964 | 0.44028 | 0.50425 | 0.61022 | 0.73445 | 0.90891 | 1.0563 | 1.2194 | 1.3724 | 1.5086 | 1.6479 | 1.7906 | 1.9267 | 2.0629 | 2.7747 | 3.6668
Pyle | Schwyll | Primary Substation | 11 | Electric Engagement | 0.13871 | 0.17491 | 0.24036 | 0.32027 | 0.39749 | 0.53102 | 0.68749 | 0.87533 | 1.0573 | 1.229 | 1.4068 | 1.568 | 1.6909 | 1.7958 | 1.905 | 2.0218 | 3.066 | 3.315 | 0.32226 | 0.39916 | 0.53532 | 0.70304 | 0.86659 | 1.1451 | 1.4722 | 1.866 | 2.2495 | 2.6131 | 2.9908 | 3.3336 | 3.6008 | 3.8233 | 4.054 | 4.3011 | 6.5453 | 7.1172
Pyle | Schwyll | Primary Substation | 11 | Holistic Transition | 0.1434 | 0.1777 | 0.2125 | 0.26103 | 0.31788 | 0.42826 | 0.55161 | 0.70649 | 0.85058 | 1.0112 | 1.1707 | 1.3777 | 1.6559 | 1.9221 | 2.1651 | 2.2938 | 2.8249 | 3.01 | 0.33386 | 0.40872 | 0.48325 | 0.59081 | 0.71676 | 0.95171 | 1.2175 | 1.5497 | 1.8604 | 2.2086 | 2.5487 | 2.9948 | 3.5966 | 4.1678 | 4.688 | 4.9573 | 6.0885 | 6.4925
Pyle | Schwyll | Primary Substation | 11 | Hydrogen Evolution | 0.1334 | 0.16269 | 0.19167 | 0.22624 | 0.27109 | 0.3397 | 0.41652 | 0.51548 | 0.60956 | 0.72122 | 0.82639 | 0.92286 | 1.0157 | 1.1688 | 1.3312 | 1.4809 | 1.944 | 2.2287 | 0.3089 | 0.37073 | 0.43149 | 0.50451 | 0.60081 | 0.74606 | 0.90871 | 1.1159 | 1.3166 | 1.5594 | 1.784 | 1.9889 | 2.1846 | 2.5118 | 2.86 | 3.1817 | 4.1987 | 4.8304
Pyle | Waterton Industrial Primary | Bulk Supply Point | 11 | Counterfactual | 0.55234 | 0.5938 | 0.63995 | 0.69195 | 0.75845 | 0.83662 | 0.92398 | 1.0481 | 1.1471 | 1.2569 | 1.3681 | 1.4789 | 1.6092 | 1.7263 | 1.8345 | 1.9664 | 2.6542 | 2.8886 | 1.2806 | 1.3701 | 1.467 | 1.5761 | 1.715 | 1.8782 | 2.0612 | 2.3186 | 2.5262 | 2.757 | 2.9888 | 3.2172 | 3.4836 | 3.7239 | 3.9459 | 4.2198 | 5.7043 | 6.2019
Pyle | Waterton Industrial Primary | Bulk Supply Point | 11 | Electric Engagement | 0.5683 | 0.65113 | 0.77298 | 0.91745 | 1.0554 | 1.745 | 1.9488 | 2.1801 | 2.3908 | 2.5794 | 2.7509 | 2.922 | 3.0451 | 3.2075 | 3.3941 | 3.4874 | 4.0171 | 4.2716 | 1.3192 | 1.5014 | 1.7562 | 2.0578 | 2.3473 | 3.981 | 4.4069 | 4.8893 | 5.331 | 5.7288 | 6.0934 | 6.4533 | 6.7302 | 7.1142 | 7.5561 | 7.7646 | 8.9529 | 9.5347
Pyle | Waterton Industrial Primary | Bulk Supply Point | 11 | Holistic Transition | 0.58222 | 0.67081 | 0.75336 | 0.84946 | 0.95726 | 1.1235 | 1.2824 | 1.4904 | 1.6584 | 1.8547 | 2.0501 | 2.3269 | 2.667 | 2.95 | 3.1328 | 3.2799 | 3.8418 | 4.1827 | 1.353 | 1.5546 | 1.7349 | 1.9457 | 2.1812 | 2.5349 | 2.8747 | 3.3137 | 3.6727 | 4.0896 | 4.5018 | 5.1263 | 5.9079 | 6.5521 | 6.9397 | 7.2519 | 8.4775 | 9.2276
Pyle | Waterton Industrial Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 0.56038 | 0.62038 | 0.68422 | 0.7791 | 0.88574 | 1.0072 | 1.1383 | 1.3148 | 1.5175 | 1.7116 | 1.8909 | 2.041 | 2.2298 | 2.4024 | 2.6636 | 2.8723 | 3.3704 | 3.7185 | 1.2988 | 1.4286 | 1.5631 | 1.7606 | 1.9833 | 2.2367 | 2.5105 | 2.875 | 3.2935 | 3.6974 | 4.0693 | 4.382 | 4.7714 | 5.1495 | 5.7315 | 6.2038 | 7.2941 | 8.0426
Rassau | Abergavenny Primary | Bulk Supply Point | 11 | Counterfactual | 0.73572 | 0.85655 | 0.9976 | 1.1528 | 1.3418 | 1.572 | 1.8483 | 2.2733 | 2.6109 | 2.9921 | 3.3514 | 3.6894 | 4.0513 | 4.4095 | 4.7559 | 5.1069 | 6.6853 | 7.2565 | 1.7243 | 1.9794 | 2.2724 | 2.5957 | 2.9915 | 3.4775 | 4.068 | 4.9656 | 5.6911 | 6.5181 | 7.2842 | 7.9911 | 8.7378 | 9.4777 | 10.1926 | 10.9169 | 14.2291 | 15.5207
Rassau | Abergavenny Primary | Bulk Supply Point | 11 | Electric Engagement | 0.79147 | 1.028 | 1.4244 | 1.9031 | 2.3629 | 2.9122 | 3.5895 | 4.4106 | 5.1573 | 5.8129 | 6.4302 | 7.0087 | 7.3217 | 7.5288 | 7.7378 | 7.9473 | 9.0755 | 9.8272 | 1.8592 | 2.368 | 3.191 | 4.1902 | 5.1572 | 6.3131 | 7.7397 | 9.4647 | 11.0455 | 12.4476 | 13.7783 | 15.0224 | 15.7391 | 16.2084 | 16.6803 | 17.1559 | 19.7304 | 21.5489
Rassau | Abergavenny Primary | Bulk Supply Point | 11 | Holistic Transition | 0.81788 | 1.0337 | 1.2516 | 1.5302 | 1.8487 | 2.2754 | 2.7636 | 3.4239 | 4.0038 | 4.6607 | 5.2858 | 5.8735 | 6.4415 | 6.9218 | 7.3795 | 7.7855 | 8.8139 | 9.2871 | 1.9247 | 2.4034 | 2.8714 | 3.4843 | 4.1837 | 5.1106 | 6.1731 | 7.594 | 8.8554 | 10.2888 | 11.6295 | 12.8932 | 14.113 | 15.1289 | 16.0979 | 16.9626 | 19.3052 | 20.4023
Rassau | Abergavenny Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 0.76164 | 0.93675 | 1.1275 | 1.3576 | 1.6364 | 1.9687 | 2.3623 | 2.9033 | 3.4115 | 4.0003 | 4.5578 | 5.0723 | 5.5707 | 5.9834 | 6.3858 | 6.7336 | 7.6385 | 8.3737 | 1.7834 | 2.1561 | 2.5551 | 3.037 | 3.6279 | 4.3303 | 5.1614 | 6.2882 | 7.3617 | 8.6261 | 9.8047 | 10.8882 | 11.9306 | 12.7862 | 13.6209 | 14.3479 | 16.3839 | 18.1032
Rassau | Abersychan | Primary Substation | 11 | Counterfactual | 0.25365 | 0.32037 | 0.39959 | 0.48513 | 0.5873 | 0.71135 | 0.85401 | 1.0748 | 1.2458 | 1.4365 | 1.625 | 1.8099 | 2.0103 | 2.2123 | 2.4079 | 2.6077 | 3.47 | 3.7172 | 0.59008 | 0.72968 | 0.89375 | 1.071 | 1.2829 | 1.5407 | 1.8388 | 2.2957 | 2.6537 | 3.0555 | 3.4485 | 3.8297 | 4.2392 | 4.6528 | 5.0532 | 5.4617 | 7.244 | 7.7897
Rassau | Abersychan | Primary Substation | 11 | Electric Engagement | 0.2899 | 0.41749 | 0.643 | 0.90985 | 1.1661 | 1.4672 | 1.8299 | 2.2713 | 2.6664 | 3.0023 | 3.3153 | 3.6154 | 3.7627 | 3.874 | 3.9879 | 4.1042 | 4.7189 | 5.0546 | 0.67745 | 0.94853 | 1.4149 | 1.9675 | 2.5008 | 3.1258 | 3.8768 | 4.7892 | 5.6098 | 6.3125 | 6.971 | 7.6013 | 7.9279 | 8.1729 | 8.4225 | 8.678 | 10.0319 | 10.8155
Rassau | Abersychan | Primary Substation | 11 | Holistic Transition | 0.30611 | 0.41908 | 0.54485 | 0.69382 | 0.86038 | 1.0846 | 1.3338 | 1.671 | 1.9676 | 2.2961 | 2.6277 | 2.9347 | 3.2452 | 3.526 | 3.7938 | 4.0328 | 4.6983 | 5.0045 | 0.71774 | 0.96511 | 1.2351 | 1.558 | 1.9177 | 2.3948 | 2.9253 | 3.6351 | 4.2655 | 4.9642 | 5.6622 | 6.3087 | 6.9629 | 7.5495 | 8.1089 | 8.6106 | 10.0643 | 10.7551
Rassau | Abersychan | Primary Substation | 11 | Hydrogen Evolution | 0.27014 | 0.36138 | 0.46541 | 0.59106 | 0.73738 | 0.91556 | 1.1267 | 1.4185 | 1.6905 | 1.9806 | 2.2674 | 2.5359 | 2.8085 | 3.0391 | 3.2688 | 3.4661 | 3.917 | 4.2409 | 0.62783 | 0.81945 | 1.0361 | 1.2977 | 1.6037 | 1.9754 | 2.4151 | 3.016 | 3.5815 | 4.1896 | 4.7849 | 5.3415 | 5.9041 | 6.3783 | 6.8508 | 7.2592 | 8.2413 | 8.9694
Rassau | Abertillery | Primary Substation | 11 | Counterfactual | 0.25324 | 0.30626 | 0.36858 | 0.43605 | 0.51541 | 0.61223 | 0.72504 | 0.89904 | 1.0315 | 1.1751 | 1.3181 | 1.4602 | 1.6163 | 1.7755 | 1.9267 | 2.085 | 2.779 | 2.9722 | 0.5539 | 0.66526 | 0.79457 | 0.93458 | 1.0994 | 1.3008 | 1.5368 | 1.8973 | 2.1754 | 2.4782 | 2.7766 | 3.0698 | 3.3895 | 3.7159 | 4.0254 | 4.3498 | 5.7853 | 6.2127
Rassau | Abertillery | Primary Substation | 11 | Electric Engagement | 0.28178 | 0.38464 | 0.56182 | 0.76982 | 0.9683 | 1.2047 | 1.4947 | 1.8461 | 2.1596 | 2.4266 | 2.6729 | 2.907 | 3.0209 | 3.1162 | 3.2123 | 3.3062 | 3.8574 | 4.1145 | 0.62293 | 0.84234 | 1.2088 | 1.6393 | 2.0521 | 2.5425 | 3.1451 | 3.8728 | 4.5252 | 5.0847 | 5.6035 | 6.0955 | 6.3488 | 6.559 | 6.7703 | 6.9773 | 8.1767 | 8.7792
Rassau | Abertillery | Primary Substation | 11 | Holistic Transition | 0.29489 | 0.38692 | 0.48556 | 0.60224 | 0.73443 | 0.91335 | 1.113 | 1.3831 | 1.6183 | 1.8897 | 2.1629 | 2.4188 | 2.6605 | 2.8817 | 3.0909 | 3.2793 | 3.808 | 4.0303 | 0.65538 | 0.8578 | 1.0697 | 1.3231 | 1.609 | 1.9928 | 2.4202 | 2.9908 | 3.4924 | 4.0725 | 4.6499 | 5.1904 | 5.6992 | 6.1611 | 6.5984 | 6.9939 | 8.1504 | 8.6587
Rassau | Abertillery | Primary Substation | 11 | Hydrogen Evolution | 0.26627 | 0.34106 | 0.42545 | 0.52343 | 0.63802 | 0.77735 | 0.94043 | 1.1657 | 1.3675 | 1.5953 | 1.8246 | 2.0488 | 2.2674 | 2.4496 | 2.6244 | 2.7781 | 3.1725 | 3.4259 | 0.58372 | 0.74135 | 0.91732 | 1.1216 | 1.3616 | 1.6525 | 1.9932 | 2.4574 | 2.8778 | 3.3569 | 3.8342 | 4.3008 | 4.7539 | 5.1284 | 5.488 | 5.8062 | 6.6603 | 7.2333
Rassau | Blaenavon | Primary Substation | 11 | Counterfactual | 0.11592 | 0.14083 | 0.17122 | 0.2038 | 0.24591 | 0.29091 | 0.34005 | 0.41988 | 0.47768 | 0.541 | 0.60638 | 0.67362 | 0.74957 | 0.82516 | 0.8975 | 0.97484 | 1.3236 | 1.4356 | 0.27331 | 0.32575 | 0.38869 | 0.45611 | 0.54426 | 0.63731 | 0.73848 | 0.90126 | 1.0201 | 1.1504 | 1.2844 | 1.4215 | 1.5756 | 1.7294 | 1.8765 | 2.0345 | 2.7605 | 2.9967
Rassau | Blaenavon | Primary Substation | 11 | Electric Engagement | 0.12777 | 0.17767 | 0.26236 | 0.37242 | 0.46584 | 0.56735 | 0.69296 | 0.83959 | 0.9667 | 1.0717 | 1.1674 | 1.2627 | 1.3106 | 1.3635 | 1.4153 | 1.4472 | 1.6164 | 1.7134 | 0.30234 | 0.40877 | 0.58377 | 0.81544 | 1.0087 | 1.2178 | 1.4754 | 1.7746 | 2.0346 | 2.2501 | 2.448 | 2.6448 | 2.7508 | 2.8731 | 2.9924 | 3.0626 | 3.4358 | 3.6558
Rassau | Blaenavon | Primary Substation | 11 | Holistic Transition | 0.13367 | 0.17864 | 0.23541 | 0.28754 | 0.34522 | 0.42469 | 0.5043 | 0.61482 | 0.70857 | 0.81366 | 0.92285 | 1.034 | 1.1617 | 1.283 | 1.3777 | 1.4579 | 1.6187 | 1.7355 | 0.31693 | 0.41585 | 0.54067 | 0.65258 | 0.77566 | 0.94248 | 1.1088 | 1.3369 | 1.5321 | 1.751 | 1.9776 | 2.2122 | 2.4875 | 2.748 | 2.945 | 3.1127 | 3.4695 | 3.7301
Rassau | Blaenavon | Primary Substation | 11 | Hydrogen Evolution | 0.12092 | 0.15729 | 0.19829 | 0.25861 | 0.31519 | 0.38282 | 0.45843 | 0.56787 | 0.66958 | 0.7739 | 0.87832 | 0.97481 | 1.0783 | 1.1767 | 1.2878 | 1.382 | 1.5451 | 1.6399 | 0.28496 | 0.36147 | 0.44662 | 0.57582 | 0.69283 | 0.8319 | 0.98731 | 1.2107 | 1.4187 | 1.6327 | 1.8462 | 2.0436 | 2.2548 | 2.4617 | 2.6983 | 2.8995 | 3.2457 | 3.4506
Rassau | Brecon | Primary Substation | 11 | Counterfactual | 0.55023 | 0.6364 | 0.73283 | 0.84308 | 0.99304 | 1.2456 | 1.553 | 1.9789 | 2.3529 | 2.7849 | 3.1692 | 3.4895 | 3.811 | 4.1264 | 4.4303 | 4.7481 | 6.3076 | 7.2785 | 1.3101 | 1.4958 | 1.6991 | 1.9336 | 2.2576 | 2.8021 | 3.4808 | 4.4141 | 5.2493 | 6.229 | 7.08 | 7.7713 | 8.4492 | 9.1166 | 9.7591 | 10.4299 | 13.8155 | 16.0203
Rassau | Brecon | Primary Substation | 11 | Electric Engagement | 0.58618 | 0.75914 | 1.04 | 1.411 | 1.7859 | 2.4228 | 3.1815 | 4.0737 | 4.9561 | 5.8178 | 6.7088 | 7.5227 | 8.2007 | 8.7363 | 9.2931 | 9.8782 | 13.1297 | 14.6597 | 1.3972 | 1.7777 | 2.371 | 3.1686 | 3.9853 | 5.3471 | 6.9744 | 8.8916 | 10.7996 | 12.6748 | 14.6196 | 16.3954 | 17.907 | 19.067 | 20.2678 | 21.5298 | 28.5532 | 32.1627
Rassau | Brecon | Primary Substation | 11 | Holistic Transition | 0.60325 | 0.77228 | 0.92402 | 1.1861 | 1.4935 | 2.0726 | 2.6998 | 3.4921 | 4.2472 | 5.1283 | 5.9372 | 6.6764 | 7.4072 | 8.021 | 8.6438 | 9.2428 | 11.9689 | 12.9485 | 1.4395 | 1.8242 | 2.154 | 2.753 | 3.4568 | 4.7199 | 6.1066 | 7.8539 | 9.5309 | 11.4975 | 13.2625 | 14.8844 | 16.4817 | 17.7909 | 19.1156 | 20.3931 | 26.2907 | 28.4537
Rassau | Brecon | Primary Substation | 11 | Hydrogen Evolution | 0.56672 | 0.68866 | 0.82253 | 1.0059 | 1.2532 | 1.6106 | 1.999 | 2.4906 | 3.027 | 3.6863 | 4.2611 | 4.7628 | 5.2624 | 5.6455 | 6.0514 | 6.4168 | 8.0874 | 9.7946 | 1.3478 | 1.6118 | 1.8972 | 2.2902 | 2.8334 | 3.6075 | 4.4502 | 5.5036 | 6.6717 | 8.1445 | 9.4049 | 10.5019 | 11.5776 | 12.3908 | 13.2491 | 14.0301 | 17.7667 | 21.6382
Rassau | Brynmawr | Primary Substation | 11 | Counterfactual | 0.23236 | 0.29069 | 0.35917 | 0.43389 | 0.5214 | 0.62539 | 0.74435 | 0.92957 | 1.0705 | 1.2247 | 1.3816 | 1.5409 | 1.7372 | 1.9078 | 2.0689 | 2.2374 | 2.9678 | 3.1908 | 0.51132 | 0.63431 | 0.77654 | 0.93158 | 1.1131 | 1.3289 | 1.5766 | 1.9588 | 2.253 | 2.5761 | 2.902 | 3.2305 | 3.6345 | 3.9836 | 4.3129 | 4.6577 | 6.1628 | 6.6469
Rassau | Brynmawr | Primary Substation | 11 | Electric Engagement | 0.26068 | 0.37354 | 0.56397 | 0.78668 | 0.99817 | 1.246 | 1.5489 | 1.9148 | 2.2406 | 2.5192 | 2.7779 | 3.032 | 3.1763 | 3.2696 | 3.3641 | 3.4551 | 3.8985 | 4.1565 | 0.57997 | 0.82153 | 1.2153 | 1.6755 | 2.1145 | 2.6275 | 3.2554 | 4.0109 | 4.6868 | 5.2687 | 5.8116 | 6.3448 | 6.6629 | 6.868 | 7.075 | 7.2749 | 8.2566 | 8.8553
Rassau | Brynmawr | Primary Substation | 11 | Holistic Transition | 0.27403 | 0.37647 | 0.48435 | 0.60824 | 0.74862 | 0.93846 | 1.148 | 1.436 | 1.6867 | 1.9701 | 2.257 | 2.5291 | 2.7969 | 3.0291 | 3.25 | 3.4466 | 3.8689 | 4.1192 | 0.61297 | 0.83907 | 1.0708 | 1.3388 | 1.6411 | 2.0465 | 2.4929 | 3.0988 | 3.6312 | 4.2334 | 4.8376 | 5.4102 | 5.9732 | 6.4572 | 6.9183 | 7.3303 | 8.2741 | 8.8438
Rassau | Brynmawr | Primary Substation | 11 | Hydrogen Evolution | 0.24526 | 0.3299 | 0.42591 | 0.5353 | 0.66183 | 0.8126 | 0.99153 | 1.2402 | 1.4634 | 1.7085 | 1.9543 | 2.19 | 2.4378 | 2.6354 | 2.8244 | 2.9869 | 3.3493 | 3.6074 | 0.54075 | 0.71977 | 0.92007 | 1.1478 | 1.4119 | 1.7255 | 2.0987 | 2.6108 | 3.0738 | 3.5861 | 4.0959 | 4.5843 | 5.0981 | 5.5042 | 5.8924 | 6.228 | 7.0147 | 7.5906
Rassau | Builth Wells | Primary Substation | 11 | Counterfactual | 0.44192 | 0.49239 | 0.54923 | 0.61923 | 0.71464 | 0.90136 | 1.1384 | 1.4549 | 1.7511 | 2.1044 | 2.4009 | 2.6301 | 2.8456 | 3.057 | 3.2601 | 3.4748 | 4.6099 | 5.5559 | 1.0776 | 1.1882 | 1.31 | 1.4619 | 1.6747 | 2.0864 | 2.6244 | 3.3401 | 4.0213 | 4.8469 | 5.5234 | 6.0321 | 6.4969 | 6.955 | 7.3949 | 7.8584 | 10.3648 | 12.5241
Rassau | Builth Wells | Primary Substation | 11 | Electric Engagement | 0.46033 | 0.56452 | 0.72765 | 0.95823 | 1.2109 | 1.6913 | 2.2672 | 2.9433 | 3.6409 | 4.3584 | 5.1193 | 5.7469 | 6.3835 | 6.8713 | 7.3774 | 7.918 | 10.8752 | 12.3468 | 1.1223 | 1.3558 | 1.7072 | 2.2178 | 2.7884 | 3.8324 | 5.0913 | 6.5751 | 8.1133 | 9.7009 | 11.3869 | 12.7598 | 14.1905 | 15.2524 | 16.3496 | 17.5204 | 23.9484 | 27.4428
Rassau | Builth Wells | Primary Substation | 11 | Holistic Transition | 0.46815 | 0.57594 | 0.66709 | 0.86061 | 1.0929 | 1.564 | 2.0183 | 2.6619 | 3.2985 | 4.0592 | 4.7305 | 5.3452 | 5.9459 | 6.4238 | 6.9154 | 7.4052 | 9.8525 | 10.6848 | 1.1416 | 1.3907 | 1.5907 | 2.0443 | 2.5909 | 3.632 | 4.6381 | 6.0869 | 7.5263 | 9.2542 | 10.7431 | 12.1147 | 13.4499 | 14.482 | 15.5392 | 16.5935 | 21.9152 | 23.754
Rassau | Builth Wells | Primary Substation | 11 | Hydrogen Evolution | 0.45096 | 0.52335 | 0.60508 | 0.73499 | 0.90925 | 1.1804 | 1.4712 | 1.8235 | 2.2447 | 2.7976 | 3.2562 | 3.5824 | 3.9578 | 4.2241 | 4.5152 | 4.7862 | 6.2826 | 7.8981 | 1.0987 | 1.2582 | 1.4358 | 1.72 | 2.1137 | 2.7124 | 3.3577 | 4.1306 | 5.0685 | 6.3328 | 7.3627 | 8.0777 | 8.9046 | 9.4819 | 10.1085 | 10.6992 | 14.0902 | 17.7898
Rassau | Crickhowell | Primary Substation | 11 | Counterfactual | 0.21351 | 0.24071 | 0.27056 | 0.30373 | 0.34582 | 0.40272 | 0.46905 | 0.56695 | 0.64742 | 0.7375 | 0.8233 | 0.9039 | 0.99158 | 1.0755 | 1.1563 | 1.2413 | 1.6559 | 1.8688 | 0.51058 | 0.56916 | 0.63169 | 0.70137 | 0.79011 | 0.91047 | 1.0526 | 1.26 | 1.4333 | 1.6293 | 1.8127 | 1.9812 | 2.1621 | 2.3354 | 2.5024 | 2.6779 | 3.5442 | 4.0059
Rassau | Crickhowell | Primary Substation | 11 | Electric Engagement | 0.2252 | 0.28069 | 0.36612 | 0.47418 | 0.57878 | 0.71889 | 0.8897 | 1.0894 | 1.2787 | 1.4573 | 1.6296 | 1.7924 | 1.8968 | 1.9755 | 2.0572 | 2.1378 | 2.5723 | 2.805 | 0.53892 | 0.66071 | 0.8395 | 1.0667 | 1.2883 | 1.5834 | 1.9426 | 2.3607 | 2.7592 | 3.1372 | 3.5036 | 3.8486 | 4.0772 | 4.2475 | 4.4236 | 4.5973 | 5.5389 | 6.0819
Rassau | Crickhowell | Primary Substation | 11 | Holistic Transition | 0.23059 | 0.28493 | 0.3338 | 0.40157 | 0.4784 | 0.59948 | 0.72792 | 0.89667 | 1.0495 | 1.2277 | 1.3975 | 1.5567 | 1.7104 | 1.8418 | 1.9737 | 2.0915 | 2.4885 | 2.6831 | 0.55229 | 0.67554 | 0.78166 | 0.93159 | 1.1014 | 1.3615 | 1.6381 | 1.9986 | 2.3274 | 2.7112 | 3.0703 | 3.4084 | 3.7351 | 4.011 | 4.2879 | 4.5365 | 5.3989 | 5.8314
Rassau | Crickhowell | Primary Substation | 11 | Hydrogen Evolution | 0.21879 | 0.25847 | 0.30026 | 0.35683 | 0.42597 | 0.51447 | 0.61477 | 0.74906 | 0.88649 | 1.0425 | 1.1878 | 1.3174 | 1.4485 | 1.548 | 1.6539 | 1.7403 | 2.0309 | 2.2905 | 0.52268 | 0.60837 | 0.69641 | 0.81509 | 0.96194 | 1.1488 | 1.3602 | 1.64 | 1.928 | 2.26 | 2.5651 | 2.8373 | 3.1104 | 3.3166 | 3.5358 | 3.7158 | 4.3506 | 4.9292
Rassau | Crumlin Primary | Bulk Supply Point | 11 | Counterfactual | 1.4022 | 1.4683 | 1.5467 | 1.6332 | 1.7409 | 1.8714 | 2.0185 | 2.2351 | 2.4038 | 2.5889 | 2.772 | 2.9568 | 3.1609 | 3.3607 | 3.5524 | 3.7646 | 4.8204 | 5.1276 | 3.1422 | 3.2818 | 3.4449 | 3.6251 | 3.851 | 4.126 | 4.4368 | 4.8873 | 5.2428 | 5.6351 | 6.0188 | 6.4008 | 6.819 | 7.2291 | 7.6223 | 8.0602 | 10.2904 | 10.9624
Rassau | Crumlin Primary | Bulk Supply Point | 11 | Electric Engagement | 1.4369 | 1.5656 | 1.785 | 2.058 | 2.3222 | 2.631 | 2.9906 | 3.4248 | 3.815 | 4.1546 | 4.469 | 4.778 | 4.9482 | 5.143 | 5.7729 | 5.9845 | 6.9003 | 7.2821 | 3.2258 | 3.5015 | 3.9562 | 4.5282 | 5.086 | 5.7346 | 6.4824 | 7.3836 | 8.1982 | 8.9123 | 9.5778 | 10.2293 | 10.6118 | 11.0578 | 12.3806 | 12.8444 | 14.888 | 15.7787
Rassau | Crumlin Primary | Bulk Supply Point | 11 | Holistic Transition | 1.4525 | 1.5702 | 1.7067 | 1.87 | 2.0516 | 2.284 | 2.5385 | 2.8837 | 3.1804 | 3.5398 | 3.8992 | 4.2569 | 4.9052 | 5.2576 | 5.9793 | 6.2818 | 7.0922 | 7.4374 | 3.2645 | 3.5242 | 3.8212 | 4.1804 | 4.578 | 5.0739 | 5.6186 | 6.3486 | 6.9823 | 7.7519 | 8.5136 | 9.2767 | 10.7736 | 11.5383 | 13.0179 | 13.6489 | 15.409 | 16.1887
Rassau | Crumlin Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 1.4187 | 1.5134 | 1.6221 | 1.767 | 1.9375 | 2.1324 | 2.3403 | 2.6309 | 2.9051 | 3.2013 | 3.4943 | 3.777 | 4.0956 | 4.3642 | 4.864 | 5.1512 | 5.862 | 6.2542 | 3.1796 | 3.3799 | 3.6071 | 3.9145 | 4.2782 | 4.6911 | 5.1248 | 5.7245 | 6.2946 | 6.9176 | 7.5282 | 8.1176 | 8.7817 | 9.3494 | 10.3926 | 11.0157 | 12.5993 | 13.4787
Rassau | Cwmfelinfach | Primary Substation | 11 | Counterfactual | 0.26728 | 0.29071 | 0.31903 | 0.35077 | 0.38895 | 0.43703 | 0.4932 | 0.5774 | 0.64417 | 0.71845 | 0.78971 | 0.85947 | 0.93464 | 1.0092 | 1.0817 | 1.1687 | 1.5878 | 1.7225 | 0.57585 | 0.62507 | 0.68398 | 0.75009 | 0.83001 | 0.93109 | 1.0505 | 1.2276 | 1.3703 | 1.5305 | 1.6817 | 1.8272 | 1.9821 | 2.1359 | 2.2854 | 2.4659 | 3.346 | 3.6446
Rassau | Cwmfelinfach | Primary Substation | 11 | Electric Engagement | 0.27877 | 0.32351 | 0.40227 | 0.49737 | 0.58873 | 0.70408 | 0.84201 | 1.01 | 1.1636 | 1.3001 | 1.4298 | 1.5554 | 1.6334 | 1.7228 | 1.8109 | 1.9436 | 2.3311 | 2.5073 | 0.60364 | 0.69897 | 0.86235 | 1.0605 | 1.2523 | 1.494 | 1.7829 | 2.1346 | 2.4584 | 2.7484 | 3.0261 | 3.2943 | 3.4692 | 3.6668 | 3.8609 | 4.143 | 4.9842 | 5.399
Rassau | Cwmfelinfach | Primary Substation | 11 | Holistic Transition | 0.28411 | 0.32417 | 0.36841 | 0.42509 | 0.48961 | 0.57953 | 0.68049 | 0.8161 | 0.94387 | 1.1165 | 1.2856 | 1.4353 | 1.5599 | 1.6692 | 1.777 | 1.9275 | 2.3034 | 2.4312 | 0.61698 | 0.70496 | 0.79989 | 0.92409 | 1.0653 | 1.2587 | 1.4771 | 1.7673 | 2.044 | 2.4196 | 2.7833 | 3.104 | 3.3691 | 3.5987 | 3.8255 | 4.1377 | 4.9508 | 5.2413
Rassau | Cwmfelinfach | Primary Substation | 11 | Hydrogen Evolution | 0.27331 | 0.30728 | 0.34713 | 0.39505 | 0.45201 | 0.52141 | 0.60022 | 0.70989 | 0.81299 | 0.94499 | 1.0766 | 1.2067 | 1.3359 | 1.4356 | 1.519 | 1.6174 | 1.8669 | 2.0379 | 0.58941 | 0.66094 | 0.7442 | 0.84455 | 0.96495 | 1.1112 | 1.2769 | 1.5047 | 1.7219 | 2.0052 | 2.2846 | 2.5604 | 2.8331 | 3.0414 | 3.2141 | 3.4171 | 3.9604 | 4.3516
Rassau | Ebbw Vale Primary | Bulk Supply Point | 11 | Counterfactual | 1.1492 | 1.2027 | 1.2651 | 1.3369 | 1.4197 | 2.7795 | 2.8945 | 4.3284 | 4.4571 | 4.5942 | 4.7316 | 4.8696 | 5.0217 | 5.1771 | 5.3247 | 4.663 | 5.3408 | 5.5149 | 2.76 | 2.8729 | 3.0025 | 3.1514 | 3.3234 | 6.0528 | 6.2951 | 9.1771 | 9.4467 | 9.7348 | 10.0208 | 10.3055 | 10.6172 | 10.9361 | 11.2386 | 9.514 | 10.9136 | 11.2968
Rassau | Ebbw Vale Primary | Bulk Supply Point | 11 | Electric Engagement | 2.4354 | 2.5391 | 3.9726 | 4.1756 | 4.3681 | 4.6107 | 4.9112 | 5.2649 | 5.566 | 5.8173 | 6.0446 | 6.2593 | 6.3554 | 6.4392 | 6.522 | 5.7814 | 6.2566 | 6.4709 | 5.3435 | 5.5659 | 8.445 | 8.8646 | 9.2644 | 9.7753 | 10.4101 | 11.1492 | 11.7768 | 12.3041 | 12.7829 | 13.2341 | 13.4488 | 13.6349 | 13.8187 | 11.9456 | 12.9805 | 13.4848
Rassau | Ebbw Vale Primary | Bulk Supply Point | 11 | Holistic Transition | 1.1883 | 1.2826 | 1.3811 | 2.7571 | 2.9074 | 4.3625 | 4.5694 | 4.8289 | 5.0494 | 5.3053 | 5.5635 | 5.8017 | 6.022 | 6.225 | 6.415 | 5.766 | 6.2975 | 6.4949 | 2.8555 | 3.0639 | 3.2759 | 6.0473 | 6.3769 | 9.3249 | 9.7734 | 10.322 | 10.7923 | 11.3386 | 11.8846 | 12.387 | 12.8495 | 13.2734 | 13.6707 | 11.9804 | 13.1324 | 13.5884
Rassau | Ebbw Vale Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 1.161 | 1.2388 | 1.3282 | 1.4321 | 1.5522 | 2.9447 | 3.1249 | 4.6244 | 4.8313 | 5.0532 | 5.2775 | 5.4974 | 5.7096 | 5.8853 | 6.0511 | 5.3772 | 5.7437 | 5.9504 | 2.7869 | 2.9515 | 3.1384 | 3.3557 | 3.6074 | 6.4036 | 6.7891 | 9.8116 | 10.2481 | 10.7144 | 11.1809 | 11.6384 | 12.0785 | 12.4393 | 12.7799 | 11.0322 | 11.8205 | 12.289
Rassau | Glasbury | Primary Substation | 11 | Counterfactual | 0.75348 | 0.79729 | 0.84685 | 0.90506 | 0.98214 | 1.0978 | 1.2426 | 1.4461 | 1.6238 | 1.8327 | 2.0152 | 2.1699 | 2.3243 | 2.4761 | 2.6215 | 2.7737 | 3.5534 | 4.0258 | 1.855 | 1.9492 | 2.0536 | 2.1772 | 2.3436 | 2.5948 | 2.9165 | 3.3645 | 3.7634 | 4.239 | 4.6453 | 4.9798 | 5.306 | 5.6275 | 5.9355 | 6.2573 | 7.9506 | 9.0268
Rassau | Glasbury | Primary Substation | 11 | Electric Engagement | 0.77084 | 0.85838 | 1.0253 | 1.242 | 1.4577 | 1.7668 | 2.1309 | 2.5717 | 3.0066 | 3.4152 | 3.8225 | 4.2053 | 4.5241 | 4.7531 | 4.9682 | 5.2041 | 6.4789 | 7.2297 | 1.8972 | 2.0887 | 2.451 | 2.9272 | 3.406 | 4.0815 | 4.8761 | 5.8402 | 6.8003 | 7.7053 | 8.6104 | 9.4612 | 10.1934 | 10.7064 | 11.1811 | 11.7066 | 14.5501 | 16.3522
Rassau | Glasbury | Primary Substation | 11 | Holistic Transition | 0.7791 | 0.86428 | 0.96581 | 1.1219 | 1.3039 | 1.5734 | 1.863 | 2.2369 | 2.5857 | 2.9929 | 3.3625 | 3.7107 | 4.049 | 4.323 | 4.597 | 4.8543 | 5.9498 | 6.3733 | 1.9176 | 2.1099 | 2.3374 | 2.6979 | 3.1185 | 3.7166 | 4.3643 | 5.1966 | 5.9801 | 6.8979 | 7.7138 | 8.4849 | 9.2323 | 9.8235 | 10.4135 | 10.9703 | 13.399 | 14.3586
Rassau | Glasbury | Primary Substation | 11 | Hydrogen Evolution | 0.7615 | 0.8278 | 0.90303 | 0.99783 | 1.1226 | 1.2901 | 1.4757 | 1.7158 | 1.9761 | 2.3001 | 2.5822 | 2.8309 | 3.0733 | 3.2561 | 3.4469 | 3.6154 | 4.3451 | 5.0765 | 1.8734 | 2.0162 | 2.1761 | 2.3787 | 2.652 | 3.0161 | 3.4196 | 3.9343 | 4.5023 | 5.2275 | 5.8471 | 6.3911 | 6.9141 | 7.3031 | 7.7076 | 8.0697 | 9.7283 | 11.42
Rassau | Llandrindod Wells | Primary Substation | 11 | Counterfactual | 0.55598 | 0.61815 | 0.68815 | 0.77064 | 0.88168 | 1.0509 | 1.2595 | 1.5481 | 1.803 | 2.1035 | 2.3636 | 2.5804 | 2.7955 | 3.0058 | 3.2079 | 3.4191 | 4.5193 | 5.2039 | 1.3068 | 1.4408 | 1.5888 | 1.7645 | 2.0055 | 2.374 | 2.839 | 3.4772 | 4.0522 | 4.7395 | 5.3211 | 5.792 | 6.2473 | 6.6943 | 7.1237 | 7.5716 | 9.9677 | 11.5307
Rassau | Llandrindod Wells | Primary Substation | 11 | Electric Engagement | 0.5801 | 0.70078 | 0.89781 | 1.1644 | 1.4306 | 1.8442 | 2.3488 | 2.9385 | 3.5212 | 4.0888 | 4.6668 | 5.1984 | 5.628 | 5.9463 | 6.2777 | 6.621 | 8.5271 | 9.5591 | 1.3654 | 1.6308 | 2.0491 | 2.6269 | 3.2097 | 4.1038 | 5.1974 | 6.4771 | 7.7506 | 8.9994 | 10.2769 | 11.4501 | 12.4253 | 13.1267 | 13.8526 | 14.6063 | 18.8001 | 21.2692
Rassau | Llandrindod Wells | Primary Substation | 11 | Holistic Transition | 0.59114 | 0.71199 | 0.82624 | 1.0206 | 1.249 | 1.6291 | 2.0463 | 2.5778 | 3.0781 | 3.6695 | 4.1997 | 4.6937 | 5.1744 | 5.5655 | 5.9643 | 6.3387 | 7.9935 | 8.5765 | 1.3928 | 1.6671 | 1.9175 | 2.3623 | 2.8863 | 3.7254 | 4.6579 | 5.8412 | 6.9642 | 8.2972 | 9.4653 | 10.5583 | 11.6192 | 12.4597 | 13.3142 | 14.1203 | 17.7522 | 19.0603
Rassau | Llandrindod Wells | Primary Substation | 11 | Hydrogen Evolution | 0.56739 | 0.66001 | 0.7642 | 0.90472 | 1.0833 | 1.327 | 1.5932 | 1.9312 | 2.3033 | 2.7709 | 3.1745 | 3.5262 | 3.8693 | 4.1255 | 4.399 | 4.6404 | 5.7369 | 6.8247 | 1.333 | 1.5336 | 1.7562 | 2.0596 | 2.4528 | 2.9844 | 3.5652 | 4.2927 | 5.1069 | 6.1559 | 7.0447 | 7.8165 | 8.5584 | 9.1043 | 9.6845 | 10.2031 | 12.685 | 15.1964
Rassau | Monmouth | Primary Substation | 11 | Counterfactual | 0.69025 | 0.7582 | 0.83835 | 0.92722 | 1.0406 | 1.1885 | 1.37 | 1.6451 | 1.8706 | 2.1257 | 2.3928 | 2.6604 | 2.9418 | 3.2164 | 3.4816 | 3.7478 | 4.9432 | 5.5339 | 1.6038 | 1.7473 | 1.9143 | 2.1002 | 2.3392 | 2.6534 | 3.0447 | 3.6307 | 4.12 | 4.6793 | 5.2503 | 5.8091 | 6.3887 | 6.9545 | 7.5007 | 8.0488 | 10.5536 | 11.8442
Rassau | Monmouth | Primary Substation | 11 | Electric Engagement | 0.72272 | 0.85517 | 1.0876 | 1.3741 | 1.652 | 2.0186 | 2.4696 | 3.0996 | 3.6709 | 4.1814 | 4.6662 | 5.1106 | 5.3848 | 5.5763 | 5.7427 | 5.9271 | 6.882 | 7.4654 | 1.6824 | 1.9667 | 2.4525 | 3.0552 | 3.6449 | 4.4223 | 5.3797 | 6.7059 | 7.9182 | 9.0103 | 10.0546 | 11.0101 | 11.6272 | 12.0516 | 12.4138 | 12.8255 | 14.9737 | 16.3791
Rassau | Monmouth | Primary Substation | 11 | Holistic Transition | 0.73795 | 0.85886 | 0.98688 | 1.1704 | 1.3967 | 1.704 | 2.0508 | 2.5031 | 2.9029 | 3.3968 | 3.8659 | 4.2827 | 4.7011 | 5.0493 | 5.3789 | 5.672 | 6.5471 | 6.8991 | 1.7201 | 1.9883 | 2.264 | 2.6702 | 3.1707 | 3.8403 | 4.5996 | 5.5806 | 6.4538 | 7.529 | 8.5336 | 9.4206 | 10.3182 | 11.0534 | 11.75 | 12.3738 | 14.3315 | 15.1393
Rassau | Monmouth | Primary Substation | 11 | Hydrogen Evolution | 0.7051 | 0.80123 | 0.91186 | 1.0613 | 1.2445 | 1.4743 | 1.7498 | 2.159 | 2.5733 | 3.0363 | 3.4751 | 3.8815 | 4.2723 | 4.5973 | 4.9094 | 5.1797 | 5.956 | 6.537 | 1.6378 | 1.8414 | 2.0739 | 2.3893 | 2.7815 | 3.272 | 3.86 | 4.7137 | 5.5875 | 6.5779 | 7.5025 | 8.3557 | 9.1709 | 9.8426 | 10.4883 | 11.0521 | 12.7746 | 14.1258
Rassau | Pengam Grid | Bulk Supply Point | 11 | Counterfactual | 0.94761 | 1.0928 | 1.2668 | 1.4572 | 1.6797 | 1.9303 | 2.2155 | 2.6635 | 3.0028 | 3.371 | 3.7469 | 4.1324 | 4.5652 | 4.9899 | 5.4002 | 5.8896 | 8.1054 | 8.6234 | 2.2197 | 2.5246 | 2.8851 | 3.2795 | 3.7393 | 4.2575 | 4.8478 | 5.767 | 6.471 | 7.2372 | 8.0153 | 8.8076 | 9.693 | 10.562 | 11.4012 | 12.4081 | 16.9915 | 18.1117
Rassau | Pengam Grid | Bulk Supply Point | 11 | Electric Engagement | 1.0139 | 1.2927 | 1.7736 | 2.3354 | 2.8655 | 3.448 | 4.1674 | 5.0443 | 5.8226 | 6.469 | 7.0405 | 7.5674 | 7.7831 | 8.1535 | 8.5135 | 8.9553 | 9.7536 | 10.2541 | 2.3815 | 2.975 | 3.9678 | 5.126 | 6.2223 | 7.4257 | 8.9112 | 10.7175 | 12.3319 | 13.682 | 14.8799 | 15.9688 | 16.4372 | 17.2516 | 18.043 | 19.059 | 20.8524 | 22.0176
Rassau | Pengam Grid | Bulk Supply Point | 11 | Holistic Transition | 1.0487 | 1.2983 | 1.5718 | 1.8782 | 2.2221 | 2.6549 | 3.121 | 3.7729 | 4.363 | 5.2184 | 6.2172 | 6.959 | 7.529 | 8.0416 | 8.5443 | 8.9826 | 10.029 | 10.5659 | 2.4678 | 3.0154 | 3.6025 | 4.2617 | 4.9978 | 5.9182 | 6.901 | 8.2596 | 9.5042 | 11.3215 | 13.4838 | 15.0508 | 16.2391 | 17.3032 | 18.3497 | 19.2671 | 21.567 | 22.7956
Rassau | Pengam Grid | Bulk Supply Point | 11 | Hydrogen Evolution | 0.97419 | 1.1798 | 1.4142 | 1.6913 | 2.0074 | 2.367 | 2.7948 | 3.4063 | 3.9667 | 4.6289 | 5.313 | 6.1765 | 6.9124 | 7.4177 | 7.9066 | 8.3112 | 9.1758 | 9.7166 | 2.281 | 2.7137 | 3.2016 | 3.777 | 4.4336 | 5.1787 | 6.0655 | 7.3219 | 8.4832 | 9.8691 | 11.2941 | 13.1702 | 14.7087 | 15.7486 | 16.7527 | 17.5862 | 19.4438 | 20.6485
Rassau | Pontllanffraith | Primary Substation | 11 | Counterfactual | 0.22098 | 0.28372 | 0.36059 | 0.4448 | 0.54267 | 0.65141 | 0.7755 | 0.9704 | 1.1161 | 1.2729 | 1.4333 | 1.6017 | 1.79 | 1.9758 | 2.1563 | 2.3654 | 3.3156 | 3.5119 | 0.50066 | 0.63263 | 0.79207 | 0.96653 | 1.1689 | 1.3939 | 1.6508 | 2.0502 | 2.3516 | 2.6764 | 3.0067 | 3.3514 | 3.7348 | 4.1133 | 4.4809 | 4.9096 | 6.8677 | 7.2914
Rassau | Pontllanffraith | Primary Substation | 11 | Electric Engagement | 0.25161 | 0.3768 | 0.59177 | 0.84323 | 1.0799 | 1.3384 | 1.651 | 2.0326 | 2.3654 | 2.6402 | 2.883 | 3.125 | 3.2176 | 3.3355 | 3.4493 | 3.5467 | 3.7961 | 4.0123 | 0.57601 | 0.84275 | 1.2871 | 1.8057 | 2.2957 | 2.8298 | 3.4738 | 4.2567 | 4.9422 | 5.5115 | 6.0173 | 6.52 | 6.7258 | 6.9892 | 7.2432 | 7.4623 | 8.044 | 8.5481
Rassau | Pontllanffraith | Primary Substation | 11 | Holistic Transition | 0.26724 | 0.37897 | 0.50206 | 0.63943 | 0.79332 | 0.97613 | 1.1817 | 1.4691 | 1.7186 | 2.0427 | 2.3748 | 2.6755 | 2.9301 | 3.163 | 3.3884 | 3.585 | 3.9654 | 4.1852 | 0.61479 | 0.86014 | 1.1246 | 1.4203 | 1.7497 | 2.1376 | 2.5719 | 3.1709 | 3.6963 | 4.3825 | 5.0818 | 5.7119 | 6.2412 | 6.724 | 7.193 | 7.6041 | 8.455 | 8.9639
Rassau | Pontllanffraith | Primary Substation | 11 | Hydrogen Evolution | 0.23274 | 0.32548 | 0.43156 | 0.55511 | 0.69604 | 0.85526 | 1.0416 | 1.309 | 1.5444 | 1.8201 | 2.1088 | 2.4084 | 2.7039 | 2.9155 | 3.1158 | 3.2841 | 3.5909 | 3.7736 | 0.52824 | 0.72356 | 0.9445 | 1.2012 | 1.4942 | 1.8243 | 2.209 | 2.7558 | 3.2397 | 3.8117 | 4.409 | 5.0315 | 5.6438 | 6.0761 | 6.485 | 6.8298 | 7.4907 | 7.9036
Rassau | Rassau West Primary | Bulk Supply Point | 11 | Counterfactual | 0.6205 | 0.65984 | 0.70764 | 0.76089 | 0.82322 | 0.99522 | 1.0845 | 1.2293 | 1.3489 | 1.4794 | 1.6107 | 1.7458 | 1.8972 | 2.0477 | 2.2731 | 2.6315 | 3.3386 | 3.5217 | 1.3819 | 1.4649 | 1.5642 | 1.675 | 1.8047 | 2.1552 | 2.3424 | 2.648 | 2.9066 | 3.1903 | 3.4738 | 3.763 | 4.0858 | 4.4067 | 4.8878 | 5.7109 | 7.1831 | 7.5829
Rassau | Rassau West Primary | Bulk Supply Point | 11 | Electric Engagement | 0.73548 | 0.81351 | 0.94687 | 1.1041 | 1.2538 | 1.4383 | 1.7151 | 2.0445 | 2.3526 | 2.6295 | 2.8788 | 3.1265 | 3.7133 | 3.8502 | 3.9856 | 4.1065 | 4.5977 | 4.9152 | 1.6205 | 1.7872 | 2.0632 | 2.3888 | 2.7004 | 3.0835 | 3.6805 | 4.3867 | 5.0541 | 5.6601 | 6.2066 | 6.7492 | 8.1207 | 8.4215 | 8.7184 | 8.9838 | 10.0476 | 10.7545
Rassau | Rassau West Primary | Bulk Supply Point | 11 | Holistic Transition | 0.65027 | 0.7209 | 0.79711 | 0.98179 | 1.0857 | 1.2888 | 1.5092 | 1.7821 | 2.0738 | 2.4136 | 2.7712 | 3.3902 | 3.6419 | 3.8247 | 3.9999 | 4.1564 | 4.644 | 4.937 | 1.4545 | 1.61 | 1.7737 | 2.1587 | 2.3837 | 2.8377 | 3.3303 | 3.9288 | 4.5774 | 5.3323 | 6.1172 | 7.5487 | 8.0722 | 8.4535 | 8.8192 | 9.1474 | 10.2032 | 10.8416
Rassau | Rassau West Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 0.63009 | 0.69338 | 0.76166 | 0.83964 | 0.92993 | 1.1426 | 1.3156 | 1.5372 | 1.8611 | 2.1202 | 2.3669 | 2.6665 | 2.99 | 3.4199 | 3.5622 | 3.6843 | 4.0366 | 4.3085 | 1.4038 | 1.5378 | 1.6804 | 1.8429 | 2.0319 | 2.4684 | 2.8478 | 3.3249 | 4.0339 | 4.6029 | 5.1385 | 5.7926 | 6.4905 | 7.5006 | 7.7935 | 8.0465 | 8.8048 | 9.4021
Rassau | Rhayader | Primary Substation | 11 | Counterfactual | 1.8084 | 1.8298 | 1.8536 | 1.8834 | 1.9295 | 2.0215 | 2.1398 | 2.2966 | 2.445 | 2.6232 | 2.771 | 2.8836 | 2.9883 | 3.0907 | 3.1888 | 3.2932 | 3.8942 | 4.3872 | 4.5045 | 4.5519 | 4.6032 | 4.6685 | 4.7719 | 4.9757 | 5.2456 | 5.6025 | 5.9455 | 6.3641 | 6.7032 | 6.9545 | 7.1812 | 7.4041 | 7.6177 | 7.8439 | 9.185 | 10.3097
Rassau | Rhayader | Primary Substation | 11 | Electric Engagement | 1.8152 | 1.8613 | 2.0129 | 2.2045 | 2.4067 | 2.7297 | 3.0916 | 3.5046 | 3.9326 | 4.3757 | 4.8444 | 5.2624 | 5.6575 | 5.9752 | 6.3035 | 6.645 | 8.443 | 9.5217 | 4.5212 | 4.6252 | 4.9798 | 5.4289 | 5.9065 | 6.6385 | 7.4558 | 8.389 | 9.3592 | 10.3652 | 11.43 | 12.3785 | 13.2858 | 14.0021 | 14.7392 | 15.5063 | 19.5203 | 22.1271
Rassau | Rhayader | Primary Substation | 11 | Holistic Transition | 1.8187 | 1.8671 | 1.9284 | 2.0482 | 2.1881 | 2.4485 | 2.7326 | 3.08 | 3.4248 | 3.8356 | 4.1978 | 4.5306 | 4.8551 | 5.1146 | 5.382 | 5.6429 | 6.9715 | 7.5103 | 4.5298 | 4.6425 | 4.7842 | 5.0697 | 5.4035 | 5.9874 | 6.6342 | 7.4247 | 8.2124 | 9.1535 | 9.9657 | 10.717 | 11.4472 | 12.0175 | 12.6024 | 13.1747 | 16.1134 | 17.341
Rassau | Rhayader | Primary Substation | 11 | Hydrogen Evolution | 1.8115 | 1.8432 | 1.9023 | 1.9849 | 2.095 | 2.2534 | 2.4222 | 2.6213 | 2.8593 | 3.1664 | 3.4237 | 3.6433 | 3.8558 | 4.0097 | 4.1777 | 4.3325 | 5.2188 | 6.1671 | 4.5118 | 4.582 | 4.7184 | 4.9067 | 5.162 | 5.5194 | 5.9016 | 6.3473 | 6.8846 | 7.5935 | 8.1787 | 8.6787 | 9.1552 | 9.4981 | 9.869 | 10.2157 | 12.2564 | 14.4596
Rassau | Tredegar | Primary Substation | 11 | Counterfactual | 0.44598 | 0.48605 | 0.53341 | 0.58942 | 0.6544 | 0.73317 | 0.82142 | 0.95335 | 1.0576 | 1.1743 | 1.2992 | 1.4171 | 1.542 | 1.6617 | 1.7749 | 1.8876 | 2.4134 | 2.5741 | 1.0156 | 1.1006 | 1.1996 | 1.3165 | 1.4521 | 1.6165 | 1.8018 | 2.0761 | 2.2961 | 2.5434 | 2.8062 | 3.051 | 3.3083 | 3.5547 | 3.7871 | 4.0183 | 5.1028 | 5.4559
Rassau | Tredegar | Primary Substation | 11 | Electric Engagement | 0.46811 | 0.54699 | 0.68753 | 0.85258 | 1.01 | 1.2105 | 1.4518 | 1.7532 | 2.0266 | 2.259 | 2.4642 | 2.6611 | 2.757 | 2.8262 | 2.889 | 3.0401 | 3.4512 | 3.6787 | 1.069 | 1.2386 | 1.5342 | 1.8812 | 2.2137 | 2.6354 | 3.143 | 3.7768 | 4.3554 | 4.8479 | 5.2843 | 5.7019 | 5.9183 | 6.073 | 6.2115 | 6.5294 | 7.4377 | 7.9699
Rassau | Tredegar | Primary Substation | 11 | Holistic Transition | 0.47795 | 0.55056 | 0.63728 | 0.74758 | 0.87898 | 1.0482 | 1.2276 | 1.4563 | 1.6322 | 1.8245 | 2.0219 | 2.2218 | 2.4172 | 2.5978 | 2.7709 | 3.0079 | 3.3902 | 3.5831 | 1.0933 | 1.2544 | 1.4443 | 1.6867 | 1.9746 | 2.3411 | 2.7284 | 3.2154 | 3.5916 | 4.0026 | 4.42 | 4.8413 | 5.2526 | 5.6302 | 5.9925 | 6.4823 | 7.3303 | 7.7746
Rassau | Tredegar | Primary Substation | 11 | Hydrogen Evolution | 0.45619 | 0.51811 | 0.59024 | 0.67895 | 0.7758 | 0.89129 | 1.0259 | 1.2103 | 1.3797 | 1.5594 | 1.7228 | 1.8811 | 2.0366 | 2.1742 | 2.3093 | 2.4672 | 2.7604 | 2.9585 | 1.0387 | 1.1704 | 1.322 | 1.5087 | 1.7129 | 1.9552 | 2.2387 | 2.6223 | 2.9785 | 3.358 | 3.6981 | 4.0268 | 4.3486 | 4.632 | 4.9102 | 5.2345 | 5.8716 | 6.3181
Rassau | Usk | Primary Substation | 11 | Counterfactual | 2.4255 | 2.4632 | 2.509 | 2.5627 | 2.6325 | 2.7252 | 2.836 | 2.9962 | 3.1309 | 3.2849 | 3.4254 | 3.5539 | 3.6896 | 3.8216 | 3.9471 | 4.0787 | 4.7119 | 5.0648 | 6.0272 | 6.1076 | 6.2031 | 6.3159 | 6.4636 | 6.6615 | 6.9024 | 7.2469 | 7.5422 | 7.8834 | 8.1886 | 8.4614 | 8.7443 | 9.0203 | 9.2828 | 9.5571 | 10.905 | 11.6892
Rassau | Usk | Primary Substation | 11 | Electric Engagement | 2.4397 | 2.5148 | 2.6419 | 2.8064 | 2.9659 | 3.1744 | 3.4339 | 3.7391 | 4.0256 | 4.293 | 4.5512 | 4.7949 | 5.0248 | 5.1392 | 5.2555 | 5.3717 | 4.1204 | 4.55 | 6.0619 | 6.2245 | 6.4898 | 6.8367 | 7.1767 | 7.6216 | 8.1772 | 8.8294 | 9.4467 | 10.0279 | 10.5935 | 11.1255 | 11.6623 | 11.9185 | 12.178 | 12.4386 | 9.1571 | 10.1804
Rassau | Usk | Primary Substation | 11 | Holistic Transition | 2.4475 | 2.5186 | 2.5913 | 2.7 | 2.825 | 3.0151 | 3.2217 | 3.6146 | 3.86 | 4.1437 | 4.4035 | 4.6459 | 4.878 | 5.0679 | 5.2573 | 5.4262 | 4.1246 | 4.4217 | 6.0811 | 6.2401 | 6.3964 | 6.6383 | 6.9167 | 7.3331 | 7.789 | 8.6867 | 9.2292 | 9.8579 | 10.4231 | 10.9522 | 11.4583 | 11.8651 | 12.2702 | 12.6346 | 9.2329 | 9.9021
Rassau | Usk | Primary Substation | 11 | Hydrogen Evolution | 2.4319 | 2.4929 | 2.5592 | 2.6471 | 2.7579 | 2.8977 | 3.0569 | 3.2677 | 3.4872 | 3.7421 | 3.9713 | 4.1744 | 4.439 | 4.5921 | 4.7537 | 4.889 | 3.4939 | 3.9468 | 6.0419 | 6.1722 | 6.3114 | 6.4961 | 6.7334 | 7.032 | 7.3732 | 7.8183 | 8.2877 | 8.8437 | 9.3359 | 9.7713 | 10.3555 | 10.6777 | 11.0165 | 11.304 | 7.692 | 8.7332
Swansea North | Aberaeron | Primary Substation | 11 | Counterfactual | 0.11232 | 0.13111 | 0.15542 | 0.18301 | 0.21709 | 0.26847 | 0.33009 | 0.42027 | 0.49562 | 0.58086 | 0.65913 | 0.72853 | 0.79919 | 0.871 | 0.94062 | 1.0105 | 1.3394 | 1.5174 | 0.26539 | 0.30482 | 0.35531 | 0.41295 | 0.48508 | 0.59423 | 0.72767 | 0.921 | 1.0857 | 1.2746 | 1.4442 | 1.5915 | 1.7387 | 1.8885 | 2.0336 | 2.1793 | 2.8819 | 3.2814
Swansea North | Aberaeron | Primary Substation | 11 | Electric Engagement | 0.12023 | 0.15811 | 0.2275 | 0.31518 | 0.40082 | 0.53053 | 0.68488 | 0.87367 | 1.0536 | 1.223 | 1.395 | 1.5501 | 1.6675 | 1.7582 | 1.8512 | 1.9476 | 2.4649 | 2.7099 | 0.28502 | 0.36566 | 0.50989 | 0.69437 | 0.87656 | 1.1501 | 1.4767 | 1.877 | 2.2613 | 2.6259 | 2.9977 | 3.3335 | 3.5956 | 3.7926 | 3.9938 | 4.2031 | 5.3296 | 5.9098
Swansea North | Aberaeron | Primary Substation | 11 | Holistic Transition | 0.12689 | 0.16149 | 0.1985 | 0.25506 | 0.32152 | 0.42989 | 0.55502 | 0.71712 | 0.86886 | 1.043 | 1.2067 | 1.3567 | 1.5018 | 1.6234 | 1.7418 | 1.8551 | 2.3011 | 2.4467 | 0.30154 | 0.37781 | 0.45705 | 0.58363 | 0.73256 | 0.96802 | 1.2429 | 1.5969 | 1.931 | 2.3166 | 2.6722 | 2.9992 | 3.3145 | 3.573 | 3.8244 | 4.0656 | 5.0413 | 5.368
Swansea North | Aberaeron | Primary Substation | 11 | Hydrogen Evolution | 0.11558 | 0.144 | 0.17793 | 0.21866 | 0.27111 | 0.3442 | 0.42697 | 0.53739 | 0.64408 | 0.7763 | 0.89834 | 1.0093 | 1.1127 | 1.1998 | 1.2833 | 1.3607 | 1.635 | 1.893 | 0.27311 | 0.33277 | 0.40373 | 0.48956 | 0.60234 | 0.75811 | 0.93427 | 1.1664 | 1.3956 | 1.6856 | 1.9482 | 2.1856 | 2.4051 | 2.5873 | 2.7622 | 2.9259 | 3.5412 | 4.1328
Swansea North | Abercrave | Primary Substation | 11 | Counterfactual | 0.3554 | 0.37316 | 0.39392 | 0.41707 | 0.44699 | 0.49 | 0.54236 | 0.6181 | 0.68184 | 0.75564 | 0.82251 | 0.88066 | 0.94102 | 1 | 1.0572 | 1.1162 | 1.3912 | 1.5196 | 0.74535 | 0.78317 | 0.82661 | 0.87534 | 0.93904 | 1.0311 | 1.1454 | 1.309 | 1.4494 | 1.6141 | 1.7601 | 1.884 | 2.0101 | 2.1335 | 2.253 | 2.3764 | 2.9655 | 3.2608
Swansea North | Abercrave | Primary Substation | 11 | Electric Engagement | 0.36379 | 0.39943 | 0.45935 | 0.5345 | 0.60899 | 0.71399 | 0.84086 | 0.99105 | 1.1341 | 1.2662 | 1.3971 | 1.5188 | 1.6045 | 1.6681 | 1.7338 | 1.803 | 2.1903 | 2.4013 | 0.76572 | 0.84298 | 0.96829 | 1.1275 | 1.2871 | 1.5106 | 1.7811 | 2.1011 | 2.4082 | 2.6946 | 2.9802 | 3.2451 | 3.4389 | 3.5791 | 3.7234 | 3.875 | 4.7255 | 5.228
Swansea North | Abercrave | Primary Substation | 11 | Holistic Transition | 0.36775 | 0.40096 | 0.43279 | 0.48088 | 0.53694 | 0.62554 | 0.72377 | 0.85205 | 0.96919 | 1.1041 | 1.2286 | 1.3444 | 1.4594 | 1.5563 | 1.6523 | 1.7421 | 2.0996 | 2.2335 | 0.77552 | 0.85001 | 0.91884 | 1.0271 | 1.1533 | 1.3469 | 1.5634 | 1.8442 | 2.1032 | 2.403 | 2.6736 | 2.9263 | 3.1766 | 3.3829 | 3.5872 | 3.779 | 4.5609 | 4.8619
Swansea North | Abercrave | Primary Substation | 11 | Hydrogen Evolution | 0.35923 | 0.38465 | 0.41271 | 0.44831 | 0.49465 | 0.55552 | 0.62341 | 0.71302 | 0.80413 | 0.9133 | 1.0115 | 1.0993 | 1.1868 | 1.2563 | 1.3273 | 1.3901 | 1.6223 | 1.8458 | 0.75418 | 0.80853 | 0.86777 | 0.94335 | 1.0436 | 1.1745 | 1.3203 | 1.5102 | 1.7065 | 1.9472 | 2.1598 | 2.349 | 2.5354 | 2.6813 | 2.8302 | 2.963 | 3.4845 | 3.9977
Swansea North | Aberdare | Primary Substation | 11 | Counterfactual | 1.7262 | 1.8497 | 2.0021 | 2.1735 | 2.365 | 2.5391 | 2.7404 | 3.0559 | 3.2928 | 3.5507 | 3.8077 | 3.0742 | 3.3623 | 3.7147 | 4.0581 | 4.3352 | 5.5685 | 5.8201 | 4.2382 | 4.499 | 4.8159 | 5.1723 | 5.5709 | 5.9335 | 6.3543 | 7.0061 | 7.5017 | 8.0434 | 8.578 | 6.6286 | 7.2174 | 7.9445 | 8.6527 | 9.219 | 11.7652 | 12.3313
Swansea North | Aberdare | Primary Substation | 11 | Electric Engagement | 1.783 | 2.0109 | 2.4073 | 2.8715 | 3.3151 | 3.7569 | 4.2825 | 4.9312 | 5.5081 | 5.9816 | 6.4043 | 5.8149 | 6.117 | 6.2373 | 6.3394 | 6.4381 | 6.8933 | 7.271 | 4.3753 | 4.8659 | 5.6986 | 6.6739 | 7.6103 | 8.5374 | 9.6342 | 10.9845 | 12.1939 | 13.1915 | 14.0869 | 12.4508 | 13.1358 | 13.4197 | 13.6585 | 13.8905 | 14.9741 | 15.8881
Swansea North | Aberdare | Primary Substation | 11 | Holistic Transition | 1.8086 | 2.0164 | 2.2629 | 2.5454 | 2.8636 | 3.1698 | 3.5128 | 3.9983 | 4.4675 | 4.9133 | 5.3708 | 4.821 | 5.2562 | 5.6468 | 5.9966 | 6.3058 | 6.8142 | 7.1048 | 4.4388 | 4.8984 | 5.4356 | 6.0533 | 6.7477 | 7.4077 | 8.1407 | 9.1653 | 10.1684 | 11.1161 | 12.0813 | 10.5317 | 11.4525 | 12.274 | 13.0065 | 13.6578 | 14.8389 | 15.5355
Swansea North | Aberdare | Primary Substation | 11 | Hydrogen Evolution | 1.7521 | 1.9321 | 2.1413 | 2.3734 | 2.636 | 2.8797 | 3.1687 | 3.635 | 4.0334 | 4.4403 | 4.851 | 4.2354 | 4.6039 | 4.9375 | 5.2556 | 5.53 | 5.9888 | 6.2632 | 4.2972 | 4.682 | 5.1221 | 5.6099 | 6.1638 | 6.6724 | 7.2728 | 8.2389 | 9.07 | 9.9214 | 10.7728 | 9.067 | 9.8248 | 10.5118 | 11.1703 | 11.7403 | 12.7532 | 13.3985
Swansea North | Aberpergwm | Primary Substation | 11 | Counterfactual | 0.194 | 0.23397 | 0.28693 | 0.33942 | 0.40243 | 0.47133 | 0.55437 | 0.67862 | 0.78005 | 0.89572 | 1.0072 | 1.1218 | 1.2371 | 1.3379 | 1.4352 | 1.5349 | 1.9826 | 2.1431 | 0.44487 | 0.52945 | 0.63992 | 0.74952 | 0.88186 | 1.0276 | 1.2053 | 1.4683 | 1.6866 | 1.9379 | 2.1762 | 2.417 | 2.6559 | 2.8642 | 3.0653 | 3.2709 | 4.2112 | 4.5757
Swansea North | Aberpergwm | Primary Substation | 11 | Electric Engagement | 0.21098 | 0.28218 | 0.40448 | 0.55436 | 0.70194 | 0.86782 | 1.0728 | 1.3224 | 1.5506 | 1.7482 | 1.933 | 2.1038 | 2.1961 | 2.2603 | 2.326 | 2.394 | 2.7708 | 3.0066 | 0.48579 | 0.63934 | 0.89467 | 1.2093 | 1.5219 | 1.8722 | 2.305 | 2.831 | 3.3153 | 3.7383 | 4.1369 | 4.5037 | 4.7136 | 4.8574 | 5.0041 | 5.1559 | 5.9998 | 6.5638
Swansea North | Aberpergwm | Primary Substation | 11 | Holistic Transition | 0.21871 | 0.28917 | 0.37151 | 0.47092 | 0.5741 | 0.71948 | 0.87711 | 1.0816 | 1.2456 | 1.4322 | 1.6098 | 1.7782 | 1.9443 | 2.0881 | 2.2281 | 2.354 | 2.7536 | 2.9232 | 0.50499 | 0.66136 | 0.83911 | 1.0578 | 1.2852 | 1.6009 | 1.9441 | 2.3849 | 2.742 | 3.1494 | 3.5298 | 3.8915 | 4.2478 | 4.5518 | 4.8475 | 5.1151 | 5.998 | 6.3845
Swansea North | Aberpergwm | Primary Substation | 11 | Hydrogen Evolution | 0.20187 | 0.25755 | 0.32764 | 0.40893 | 0.50407 | 0.60717 | 0.72768 | 0.88914 | 1.0448 | 1.2206 | 1.3829 | 1.5236 | 1.6651 | 1.7812 | 1.8982 | 1.9983 | 2.2827 | 2.5255 | 0.46278 | 0.58154 | 0.72969 | 0.90132 | 1.1044 | 1.3235 | 1.5792 | 1.9173 | 2.2472 | 2.6258 | 2.97 | 3.2671 | 3.5631 | 3.8039 | 4.0465 | 4.2555 | 4.8894 | 5.4478
Swansea North | Bishopston | Primary Substation | 11 | Counterfactual | 0.17082 | 0.19987 | 0.23525 | 0.27564 | 0.31747 | 0.36083 | 0.40953 | 0.48579 | 0.54187 | 0.60185 | 0.66363 | 0.72717 | 0.79698 | 0.86714 | 0.93613 | 1.0045 | 1.2893 | 1.3526 | 0.38585 | 0.44679 | 0.52026 | 0.60403 | 0.69066 | 0.7803 | 0.88103 | 1.0371 | 1.1529 | 1.2769 | 1.404 | 1.534 | 1.6761 | 1.8189 | 1.9593 | 2.0984 | 2.6805 | 2.8198
Swansea North | Bishopston | Primary Substation | 11 | Electric Engagement | 0.18483 | 0.236 | 0.32467 | 0.43339 | 0.53259 | 0.63409 | 0.75583 | 0.90454 | 1.0366 | 1.1454 | 1.2442 | 1.3401 | 1.37 | 1.3892 | 1.4081 | 1.427 | 1.546 | 1.6433 | 0.41967 | 0.52868 | 0.71226 | 0.93738 | 1.1432 | 1.3525 | 1.6025 | 1.9068 | 2.1782 | 2.4033 | 2.6087 | 2.808 | 2.8747 | 2.9181 | 2.9609 | 3.0037 | 3.2738 | 3.4985
Swansea North | Bishopston | Primary Substation | 11 | Holistic Transition | 0.19136 | 0.23919 | 0.29344 | 0.35539 | 0.41259 | 0.48011 | 0.55768 | 0.66867 | 0.7619 | 0.85928 | 0.96031 | 1.0576 | 1.1558 | 1.246 | 1.3339 | 1.4119 | 1.5365 | 1.6347 | 0.43588 | 0.54066 | 0.65741 | 0.79077 | 0.91306 | 1.0562 | 1.2196 | 1.4506 | 1.646 | 1.8494 | 2.0591 | 2.2612 | 2.4658 | 2.6531 | 2.8364 | 3 | 3.2859 | 3.5129
Swansea North | Bishopston | Primary Substation | 11 | Hydrogen Evolution | 0.1771 | 0.21664 | 0.26299 | 0.31554 | 0.37027 | 0.42843 | 0.49704 | 0.59572 | 0.6799 | 0.77078 | 0.86472 | 0.95438 | 1.0408 | 1.1192 | 1.1931 | 1.2576 | 1.3707 | 1.4448 | 0.40012 | 0.48364 | 0.58078 | 0.69079 | 0.80503 | 0.9255 | 1.0669 | 1.2682 | 1.4413 | 1.6285 | 1.8208 | 2.0041 | 2.1805 | 2.34 | 2.4912 | 2.6232 | 2.8681 | 3.0364
Swansea North | Blaenporth | Primary Substation | 11 | Counterfactual | 0.33083 | 0.35562 | 0.38511 | 0.41722 | 0.45584 | 0.50339 | 0.55757 | 0.64815 | 0.72793 | 0.8277 | 0.93026 | 1.0367 | 1.1691 | 1.3128 | 1.4759 | 1.6106 | 1.9241 | 2.0267 | 0.80992 | 0.86205 | 0.92305 | 0.98941 | 1.0691 | 1.1669 | 1.2785 | 1.4663 | 1.6367 | 1.8526 | 2.0762 | 2.3096 | 2.6044 | 2.929 | 3.3031 | 3.6057 | 4.2446 | 4.4598
Swansea North | Blaenporth | Primary Substation | 11 | Electric Engagement | 0.3427 | 0.39091 | 0.47293 | 0.56934 | 0.65971 | 0.77828 | 0.95017 | 1.1715 | 1.4016 | 1.6339 | 1.8547 | 2.1118 | 2.3116 | 2.4311 | 2.4786 | 2.5442 | 2.7857 | 2.8732 | 0.83877 | 0.94173 | 1.1109 | 1.3091 | 1.4955 | 1.7392 | 2.1043 | 2.578 | 3.0817 | 3.5998 | 4.0937 | 4.6841 | 5.1622 | 5.4432 | 5.5434 | 5.6892 | 6.2005 | 6.3979
Swansea North | Blaenporth | Primary Substation | 11 | Holistic Transition | 0.35529 | 0.39976 | 0.44777 | 0.50738 | 0.57632 | 0.70109 | 0.85527 | 1.0628 | 1.276 | 1.5263 | 1.847 | 2.1165 | 2.3095 | 2.4123 | 2.5109 | 2.5992 | 2.8454 | 2.9442 | 0.87014 | 0.96857 | 1.0719 | 1.2001 | 1.3479 | 1.6232 | 1.9678 | 2.4289 | 2.9143 | 3.4873 | 4.2342 | 4.8577 | 5.2921 | 5.5044 | 5.708 | 5.8908 | 6.4154 | 6.6363
Swansea North | Blaenporth | Primary Substation | 11 | Hydrogen Evolution | 0.33635 | 0.37275 | 0.41347 | 0.46511 | 0.52319 | 0.59693 | 0.70878 | 0.86688 | 1.0377 | 1.2278 | 1.4094 | 1.626 | 1.8891 | 2.0873 | 2.1706 | 2.2605 | 2.4106 | 2.5105 | 0.82257 | 0.89938 | 0.98403 | 1.0913 | 1.212 | 1.3647 | 1.6062 | 1.9473 | 2.3257 | 2.7508 | 3.1547 | 3.6493 | 4.2607 | 4.7163 | 4.8859 | 5.0781 | 5.3947 | 5.6089
Swansea North | Bridell | Primary Substation | 11 | Counterfactual | 0.45766 | 0.49085 | 0.52603 | 0.56101 | 0.60304 | 0.64902 | 0.69988 | 0.78366 | 0.84655 | 0.91394 | 0.98385 | 1.0569 | 1.1397 | 1.2197 | 1.2959 | 1.3744 | 1.7025 | 1.8165 | 1.0782 | 1.148 | 1.2206 | 1.2926 | 1.3791 | 1.4732 | 1.577 | 1.7477 | 1.8767 | 2.0147 | 2.1576 | 2.3067 | 2.4751 | 2.6379 | 2.7929 | 2.9521 | 3.6169 | 3.8524
Swansea North | Bridell | Primary Substation | 11 | Electric Engagement | 0.46812 | 0.52504 | 0.61693 | 0.72511 | 0.82261 | 0.92539 | 1.0612 | 1.2217 | 1.3622 | 1.4803 | 1.5834 | 1.6848 | 1.7578 | 1.7798 | 1.8023 | 1.8746 | 2.0078 | 2.076 | 1.1041 | 1.2255 | 1.415 | 1.6382 | 1.8387 | 2.0492 | 2.33 | 2.6592 | 2.948 | 3.1916 | 3.404 | 3.6133 | 3.7799 | 3.8278 | 3.8765 | 4.0248 | 4.313 | 4.4666
Swansea North | Bridell | Primary Substation | 11 | Holistic Transition | 0.47472 | 0.53137 | 0.58608 | 0.6403 | 0.69977 | 0.78657 | 0.87549 | 1.0609 | 1.1612 | 1.2716 | 1.3847 | 1.488 | 1.5909 | 1.6785 | 1.7645 | 1.8886 | 2.0926 | 2.1921 | 1.1205 | 1.245 | 1.3629 | 1.4783 | 1.6038 | 1.7886 | 1.9759 | 2.3872 | 2.5962 | 2.8247 | 3.0581 | 3.2714 | 3.4831 | 3.6638 | 3.8413 | 4.0948 | 4.529 | 4.7508
Swansea North | Bridell | Primary Substation | 11 | Hydrogen Evolution | 0.46172 | 0.51005 | 0.55713 | 0.61467 | 0.67595 | 0.74616 | 0.83514 | 0.95789 | 1.0741 | 1.1922 | 1.3087 | 1.4161 | 1.5617 | 1.6505 | 1.7422 | 1.8412 | 2.0089 | 2.0932 | 1.0878 | 1.1901 | 1.2878 | 1.4073 | 1.5331 | 1.6767 | 1.8616 | 2.113 | 2.3513 | 2.5926 | 2.8299 | 3.049 | 3.36 | 3.5407 | 3.7267 | 3.9273 | 4.2751 | 4.454
Swansea North | Britton Ferry Primary | Primary Substation | 11 | Counterfactual | 0.52414 | 0.55806 | 0.59727 | 0.64273 | 0.70327 | 0.77288 | 0.85071 | 0.95837 | 1.0431 | 1.125 | 1.1962 | 1.2685 | 1.3483 | 1.4264 | 1.5023 | 1.5777 | 1.9009 | 1.977 | 1.0716 | 1.1427 | 1.224 | 1.3181 | 1.4467 | 1.5943 | 1.7589 | 1.9843 | 2.1643 | 2.3376 | 2.4852 | 2.6335 | 2.7964 | 2.9559 | 3.1107 | 3.2642 | 3.9251 | 4.0904
Swansea North | Britton Ferry Primary | Primary Substation | 11 | Electric Engagement | 0.53807 | 0.60226 | 0.70344 | 0.86156 | 0.99472 | 1.1297 | 1.2953 | 1.4945 | 1.6668 | 1.7946 | 1.9087 | 2.0144 | 2.0479 | 2.0692 | 2.09 | 2.1103 | 2.2105 | 2.2913 | 1.1055 | 1.2428 | 1.4526 | 1.7927 | 2.0768 | 2.3647 | 2.7174 | 3.1381 | 3.5027 | 3.7698 | 4.009 | 4.2299 | 4.3052 | 4.3538 | 4.4014 | 4.4479 | 4.6816 | 4.873
Swansea North | Britton Ferry Primary | Primary Substation | 11 | Holistic Transition | 0.54459 | 0.60826 | 0.69737 | 0.79326 | 0.88045 | 0.99898 | 1.1253 | 1.2786 | 1.38 | 1.4899 | 1.6054 | 1.7161 | 1.8239 | 1.9226 | 2.014 | 2.0937 | 2.1942 | 2.2761 | 1.1216 | 1.261 | 1.4595 | 1.6702 | 1.8627 | 2.1246 | 2.4016 | 2.7301 | 2.9442 | 3.1759 | 3.4168 | 3.6479 | 3.8725 | 4.0773 | 4.2673 | 4.4337 | 4.6708 | 4.8611
Swansea North | Britton Ferry Primary | Primary Substation | 11 | Hydrogen Evolution | 0.53057 | 0.58165 | 0.64125 | 0.73353 | 0.8313 | 0.94675 | 1.0653 | 1.2081 | 1.3308 | 1.4393 | 1.5461 | 1.6485 | 1.7495 | 1.8383 | 1.9222 | 1.9938 | 2.1212 | 2.1916 | 1.0864 | 1.195 | 1.3202 | 1.5239 | 1.7366 | 1.9877 | 2.2448 | 2.548 | 2.8091 | 3.034 | 3.2537 | 3.4642 | 3.6713 | 3.8529 | 4.0241 | 4.1709 | 4.4463 | 4.6072
Swansea North | Cardigan | Primary Substation | 11 | Counterfactual | 0.5264 | 0.56138 | 0.60368 | 0.64593 | 0.69524 | 0.75022 | 0.81252 | 0.91231 | 0.99122 | 1.0745 | 1.16 | 1.2491 | 1.3508 | 1.4496 | 1.5446 | 1.6551 | 2.0554 | 2.1867 | 1.2889 | 1.3633 | 1.4513 | 1.5388 | 1.6406 | 1.7538 | 1.8818 | 2.0857 | 2.2489 | 2.4211 | 2.5977 | 2.7807 | 2.9891 | 3.1915 | 3.386 | 3.6131 | 4.4271 | 4.6996
Swansea North | Cardigan | Primary Substation | 11 | Electric Engagement | 0.54015 | 0.60812 | 0.73485 | 0.88167 | 1.0176 | 1.1631 | 1.341 | 1.5619 | 1.7635 | 1.9285 | 2.071 | 2.2153 | 2.2883 | 2.3374 | 2.3733 | 2.4143 | 2.5694 | 2.6856 | 1.3227 | 1.4695 | 1.7395 | 2.0512 | 2.3405 | 2.6482 | 3.0232 | 3.4885 | 3.9178 | 4.2684 | 4.5702 | 4.8769 | 5.0428 | 5.1551 | 5.2345 | 5.3286 | 5.6922 | 5.9661
Swansea North | Cardigan | Primary Substation | 11 | Holistic Transition | 0.54868 | 0.61522 | 0.699 | 0.78498 | 0.88134 | 0.99633 | 1.1152 | 1.2769 | 1.4087 | 1.5483 | 1.6939 | 1.832 | 1.9618 | 2.081 | 2.1952 | 2.3055 | 2.4823 | 2.6145 | 1.3438 | 1.4927 | 1.679 | 1.869 | 2.0808 | 2.3308 | 2.5858 | 2.9274 | 3.2075 | 3.5011 | 3.8067 | 4.0955 | 4.3662 | 4.6154 | 4.8543 | 5.088 | 5.4911 | 5.7988
Swansea North | Cardigan | Primary Substation | 11 | Hydrogen Evolution | 0.53267 | 0.58554 | 0.64542 | 0.71292 | 0.78773 | 0.87377 | 0.98248 | 1.139 | 1.2759 | 1.416 | 1.5555 | 1.6878 | 1.8215 | 1.9314 | 2.0393 | 2.1326 | 2.2939 | 2.3755 | 1.3034 | 1.4159 | 1.5409 | 1.6809 | 1.8355 | 2.013 | 2.2397 | 2.5634 | 2.8473 | 3.1365 | 3.423 | 3.6951 | 3.9698 | 4.1948 | 4.4149 | 4.607 | 4.9472 | 5.1233
Swansea North | Clase | Primary Substation | 11 | Counterfactual | 0.94994 | 0.9595 | 0.97092 | 0.98375 | 0.99839 | 1.0165 | 1.0367 | 1.0704 | 1.0982 | 1.1279 | 1.1574 | 1.1863 | 1.2179 | 1.2493 | 1.2801 | 1.3225 | 1.6859 | 1.7187 | 2.3656 | 2.3857 | 2.4095 | 2.4362 | 2.4667 | 2.5045 | 2.5468 | 2.6181 | 2.6783 | 2.7426 | 2.806 | 2.867 | 2.9337 | 2.9994 | 3.0641 | 3.1529 | 3.9201 | 3.9911
Swansea North | Clase | Primary Substation | 11 | Electric Engagement | 0.95545 | 0.97389 | 1.0068 | 1.0456 | 1.0825 | 1.1268 | 1.1931 | 1.2673 | 1.3347 | 1.3924 | 1.4418 | 1.4909 | 1.5139 | 1.5575 | 0.75531 | 0.9466 | 1.0544 | 1.1151 | 2.3789 | 2.418 | 2.486 | 2.5664 | 2.6431 | 2.7351 | 2.8783 | 3.0361 | 3.1804 | 3.3039 | 3.4091 | 3.5131 | 3.5637 | 3.6586 | 1.6309 | 2.0519 | 2.2913 | 2.4309
Swansea North | Clase | Primary Substation | 11 | Holistic Transition | 0.95778 | 0.9739 | 0.9927 | 1.0142 | 1.0384 | 1.0839 | 1.1307 | 1.1886 | 1.2489 | 1.3239 | 1.417 | 1.5398 | 1.6607 | 1.7703 | 0.94174 | 0.98119 | 1.0474 | 1.0998 | 2.3847 | 2.4197 | 2.46 | 2.5064 | 2.5586 | 2.6609 | 2.765 | 2.8901 | 3.0213 | 3.184 | 3.3844 | 3.6488 | 3.9085 | 4.1435 | 2.0543 | 2.137 | 2.2896 | 2.4096
Swansea North | Clase | Primary Substation | 11 | Hydrogen Evolution | 0.95229 | 0.96568 | 0.98121 | 0.99821 | 1.0181 | 1.0425 | 1.0822 | 1.1338 | 1.1788 | 1.2313 | 1.2849 | 1.3473 | 1.4239 | 1.4941 | 0.66806 | 0.73336 | 0.90787 | 0.95675 | 2.3709 | 2.399 | 2.4315 | 2.467 | 2.5087 | 2.5596 | 2.6473 | 2.759 | 2.8567 | 2.9705 | 3.0852 | 3.2191 | 3.3843 | 3.534 | 1.444 | 1.5841 | 1.9681 | 2.0792
Swansea North | Commercial St Neath | Primary Substation | 11 | Counterfactual | 0.30814 | 0.40907 | 0.52935 | 0.65916 | 0.81089 | 0.98929 | 1.1967 | 1.5215 | 1.7681 | 2.0388 | 2.3057 | 2.5695 | 2.8588 | 3.1466 | 3.426 | 3.7194 | 4.9879 | 5.2725 | 0.69568 | 0.90695 | 1.1562 | 1.4253 | 1.7403 | 2.1118 | 2.5462 | 3.2188 | 3.7361 | 4.3074 | 4.864 | 5.408 | 5.9995 | 6.5881 | 7.1594 | 7.7604 | 10.386 | 11.0285
Swansea North | Commercial St Neath | Primary Substation | 11 | Electric Engagement | 0.36265 | 0.55458 | 0.89128 | 1.2866 | 1.6613 | 2.0885 | 2.6057 | 3.2379 | 3.797 | 4.2628 | 4.6874 | 5.091 | 5.2621 | 5.4047 | 5.5458 | 5.68 | 6.2671 | 6.6781 | 0.82728 | 1.2351 | 1.931 | 2.7487 | 3.5274 | 4.415 | 5.4868 | 6.7934 | 7.9554 | 8.9316 | 9.8275 | 10.6774 | 11.0657 | 11.3875 | 11.7055 | 12.009 | 13.3513 | 14.3329
Swansea North | Commercial St Neath | Primary Substation | 11 | Holistic Transition | 0.38729 | 0.5561 | 0.74128 | 0.95723 | 1.2017 | 1.503 | 1.8494 | 2.3286 | 2.7445 | 3.2255 | 3.7073 | 4.1553 | 4.5766 | 4.954 | 5.3065 | 5.6195 | 6.212 | 6.5377 | 0.88858 | 1.2584 | 1.6557 | 2.124 | 2.6521 | 3.2965 | 4.0365 | 5.047 | 5.9331 | 6.9608 | 7.979 | 8.9256 | 9.8136 | 10.6023 | 11.3401 | 11.9984 | 13.3518 | 14.1123
Swansea North | Commercial St Neath | Primary Substation | 11 | Hydrogen Evolution | 0.3328 | 0.47274 | 0.63218 | 0.81311 | 1.0251 | 1.2739 | 1.5663 | 1.9812 | 2.346 | 2.7704 | 3.197 | 3.6071 | 4.0038 | 4.3352 | 4.6466 | 4.9178 | 5.4514 | 5.8196 | 0.75191 | 1.046 | 1.3783 | 1.7554 | 2.1991 | 2.7187 | 3.3266 | 4.1797 | 4.9378 | 5.8299 | 6.718 | 7.5699 | 8.3908 | 9.0711 | 9.7107 | 10.2704 | 11.4484 | 12.3032
Swansea North | Cross Hands | Primary Substation | 11 | Counterfactual | 0.33846 | 0.35492 | 0.46213 | 0.48484 | 0.51218 | 0.54893 | 0.59477 | 0.6848 | 0.75789 | 0.83042 | 0.89764 | 0.95913 | 1.0264 | 1.1281 | 1.1884 | 1.2488 | 1.476 | 1.5794 | 0.74974 | 0.78472 | 1.0008 | 1.0481 | 1.1051 | 1.1816 | 1.2778 | 1.4699 | 1.6292 | 1.7887 | 1.9357 | 2.069 | 2.2143 | 2.4335 | 2.5634 | 2.6917 | 3.1636 | 3.3873
Swansea North | Cross Hands | Primary Substation | 11 | Electric Engagement | 0.34472 | 0.46403 | 0.51667 | 0.57926 | 0.63851 | 0.71926 | 0.8635 | 1.0437 | 1.221 | 1.3692 | 1.4944 | 1.6503 | 1.7106 | 1.753 | 1.7965 | 1.8391 | 2.1937 | 2.2883 | 0.76515 | 1.0092 | 1.1184 | 1.2484 | 1.3721 | 1.5402 | 1.8598 | 2.2539 | 2.6462 | 2.9754 | 3.2508 | 3.5943 | 3.73 | 3.8214 | 3.9148 | 4.0065 | 4.7554 | 4.9732
Swansea North | Cross Hands | Primary Substation | 11 | Holistic Transition | 0.3491 | 0.46785 | 0.49993 | 0.53887 | 0.58437 | 0.70918 | 0.84171 | 1.1023 | 1.2255 | 1.3546 | 1.476 | 1.5799 | 1.6728 | 1.7587 | 1.8397 | 1.9033 | 2.2202 | 2.3152 | 0.77592 | 1.0213 | 1.0907 | 1.1758 | 1.2749 | 1.5611 | 1.8623 | 2.4436 | 2.7235 | 3.0135 | 3.2823 | 3.5082 | 3.7057 | 3.8869 | 4.0577 | 4.1911 | 4.8584 | 5.0711
Swansea North | Cross Hands | Primary Substation | 11 | Hydrogen Evolution | 0.34103 | 0.45571 | 0.48892 | 0.52418 | 0.56694 | 0.63025 | 0.75172 | 0.93587 | 1.0424 | 1.1544 | 1.2533 | 1.3507 | 1.446 | 1.5163 | 1.5812 | 1.6369 | 1.8386 | 1.947 | 0.75568 | 0.98898 | 1.0589 | 1.1329 | 1.2231 | 1.3572 | 1.6303 | 2.0359 | 2.2751 | 2.5258 | 2.7426 | 2.9573 | 3.1659 | 3.3145 | 3.4492 | 3.5656 | 3.9938 | 4.2321
Swansea North | Cwmffrwd | Primary Substation | 11 | Counterfactual | 0.50935 | 0.53161 | 0.55778 | 0.5871 | 0.62378 | 0.67203 | 0.73095 | 0.81882 | 0.89279 | 0.97848 | 1.0596 | 1.1345 | 1.2146 | 1.2934 | 1.3696 | 1.4449 | 1.7898 | 2.0799 | 1.1289 | 1.176 | 1.2306 | 1.2919 | 1.3692 | 1.4714 | 1.5981 | 1.7856 | 1.9473 | 2.1371 | 2.314 | 2.4747 | 2.6443 | 2.8113 | 2.9725 | 3.1308 | 3.86 | 4.4965
Swansea North | Cwmffrwd | Primary Substation | 11 | Electric Engagement | 0.51985 | 0.56345 | 0.63768 | 0.7296 | 0.81934 | 0.93567 | 1.0856 | 1.2709 | 1.4536 | 1.6224 | 1.7784 | 1.9247 | 2.0167 | 2.077 | 2.1387 | 2.2639 | 2.8318 | 3.0345 | 1.1543 | 1.2482 | 1.4027 | 1.5956 | 1.7856 | 2.0312 | 2.3513 | 2.7482 | 3.1456 | 3.5166 | 3.8592 | 4.1802 | 4.3896 | 4.5228 | 4.6587 | 4.922 | 6.1751 | 6.6555
Swansea North | Cwmffrwd | Primary Substation | 11 | Holistic Transition | 0.52592 | 0.56772 | 0.61032 | 0.66893 | 0.73576 | 0.84433 | 0.97399 | 1.1455 | 1.3023 | 1.473 | 1.6302 | 1.7964 | 1.9963 | 2.1787 | 2.346 | 2.5057 | 2.8169 | 2.9671 | 1.1693 | 1.2626 | 1.3545 | 1.4848 | 1.6334 | 1.8729 | 2.1621 | 2.5423 | 2.8946 | 3.2774 | 3.623 | 3.9853 | 4.421 | 4.8149 | 5.1754 | 5.508 | 6.204 | 6.5434
Swansea North | Cwmffrwd | Primary Substation | 11 | Hydrogen Evolution | 0.51414 | 0.54585 | 0.58141 | 0.62746 | 0.68341 | 0.75396 | 0.84518 | 0.96405 | 1.0893 | 1.2327 | 1.3603 | 1.4791 | 1.5968 | 1.7227 | 1.853 | 1.9983 | 2.326 | 2.5416 | 1.1399 | 1.2072 | 1.2817 | 1.3786 | 1.4979 | 1.6477 | 1.8444 | 2.0982 | 2.3718 | 2.6895 | 2.9665 | 3.2249 | 3.4782 | 3.7466 | 4.0236 | 4.3299 | 5.0566 | 5.5488
Swansea North | Garngoch | Primary Substation | 11 | Counterfactual | 0.35583 | 0.39309 | 0.44159 | 0.4986 | 0.56455 | 0.63798 | 0.72021 | 0.8357 | 0.93117 | 1.0344 | 1.1538 | 1.2906 | 1.455 | 1.5915 | 1.7236 | 1.8564 | 2.3218 | 2.5265 | 0.78655 | 0.86501 | 0.96581 | 1.0842 | 1.2213 | 1.3744 | 1.5465 | 1.7866 | 1.9874 | 2.2051 | 2.4545 | 2.7376 | 3.0775 | 3.3579 | 3.6292 | 3.9017 | 4.8541 | 5.2828
Swansea North | Garngoch | Primary Substation | 11 | Electric Engagement | 0.37005 | 0.44036 | 0.55643 | 0.70245 | 0.87628 | 1.0749 | 1.3064 | 1.6296 | 1.8297 | 1.9975 | 2.1468 | 2.287 | 2.3473 | 2.3872 | 2.4239 | 2.4559 | 2.624 | 2.7578 | 0.82132 | 0.97188 | 1.214 | 1.5189 | 1.887 | 2.3093 | 2.8015 | 3.4818 | 3.898 | 4.2486 | 4.5619 | 4.8552 | 4.987 | 5.0743 | 5.155 | 5.2268 | 5.6116 | 5.9231
Swansea North | Garngoch | Primary Substation | 11 | Holistic Transition | 0.37668 | 0.45418 | 0.55005 | 0.67039 | 0.81699 | 0.98326 | 1.1578 | 1.3706 | 1.4882 | 1.6338 | 1.7802 | 1.9204 | 2.0585 | 2.1814 | 2.2988 | 2.3995 | 2.5976 | 2.729 | 0.83763 | 1.0073 | 1.2137 | 1.4736 | 1.7912 | 2.1522 | 2.5299 | 2.9853 | 3.2346 | 3.5406 | 3.8458 | 4.1379 | 4.4258 | 4.6808 | 4.9255 | 5.1365 | 5.583 | 5.882
Swansea North | Garngoch | Primary Substation | 11 | Hydrogen Evolution | 0.36269 | 0.41614 | 0.48118 | 0.56492 | 0.65986 | 0.76775 | 0.89405 | 1.0855 | 1.2728 | 1.4703 | 1.669 | 1.8524 | 2.0299 | 2.1878 | 2.34 | 2.473 | 2.7209 | 2.8474 | 0.80259 | 0.91601 | 1.0529 | 1.2291 | 1.4299 | 1.6584 | 1.9265 | 2.3243 | 2.715 | 3.1281 | 3.5415 | 3.9219 | 4.2889 | 4.6147 | 4.9294 | 5.2056 | 5.7346 | 6.0194
Swansea North | Gethin Street Swansea | Primary Substation | 11 | Counterfactual | 0.079218 | 0.11554 | 0.16384 | 0.208 | 0.26089 | 0.31989 | 0.38131 | 0.48352 | 0.56265 | 0.64431 | 0.73244 | 0.82573 | 0.92694 | 1.0309 | 1.1315 | 1.2272 | 1.6263 | 1.7465 | 0.16713 | 0.24465 | 0.34455 | 0.43631 | 0.54563 | 0.66736 | 0.79399 | 1.0037 | 1.1687 | 1.3395 | 1.5232 | 1.7166 | 1.9263 | 2.1412 | 2.349 | 2.5461 | 3.3597 | 3.6152
Swansea North | Gethin Street Swansea | Primary Substation | 11 | Electric Engagement | 0.094381 | 0.16505 | 0.28303 | 0.41205 | 0.52913 | 0.6587 | 0.82737 | 1.0316 | 1.2192 | 1.3788 | 1.5248 | 1.6718 | 1.729 | 1.7629 | 1.7986 | 1.8318 | 2.0196 | 2.1977 | 0.20391 | 0.35741 | 0.60115 | 0.86702 | 1.1091 | 1.376 | 1.7288 | 2.1549 | 2.5502 | 2.8889 | 3.1969 | 3.5068 | 3.6325 | 3.7069 | 3.7847 | 3.8576 | 4.2783 | 4.6725
Swansea North | Gethin Street Swansea | Primary Substation | 11 | Holistic Transition | 0.10204 | 0.16967 | 0.2382 | 0.31026 | 0.38665 | 0.48956 | 0.6114 | 0.77359 | 0.91489 | 1.0539 | 1.2066 | 1.3545 | 1.4968 | 1.6302 | 1.7603 | 1.8766 | 2.1474 | 2.3449 | 0.22261 | 0.37423 | 0.52168 | 0.67627 | 0.83947 | 1.0632 | 1.3271 | 1.6724 | 1.9763 | 2.2729 | 2.5946 | 2.9031 | 3.1978 | 3.4743 | 3.7455 | 3.9887 | 4.5834 | 5.0258
Swansea North | Gethin Street Swansea | Primary Substation | 11 | Hydrogen Evolution | 0.086812 | 0.13898 | 0.2034 | 0.26783 | 0.3365 | 0.41808 | 0.52441 | 0.67357 | 0.80925 | 0.94936 | 1.0912 | 1.2329 | 1.3676 | 1.4812 | 1.5898 | 1.6813 | 1.8746 | 2.0112 | 0.18424 | 0.29573 | 0.42932 | 0.56303 | 0.70534 | 0.8737 | 1.0977 | 1.4093 | 1.6963 | 1.9914 | 2.2865 | 2.5815 | 2.8618 | 3.0945 | 3.3165 | 3.5039 | 3.9152 | 4.2114
Swansea North | Gwaun Cae Gurwen | Primary Substation | 11 | Counterfactual | 0.24747 | 0.2916 | 0.34421 | 0.40127 | 0.46968 | 0.55281 | 0.64906 | 0.79853 | 0.91366 | 1.0413 | 1.1659 | 1.2868 | 1.4192 | 1.55 | 1.6768 | 1.8058 | 2.3782 | 2.5946 | 0.56255 | 0.65514 | 0.76422 | 0.88263 | 1.025 | 1.1987 | 1.4014 | 1.7127 | 1.9559 | 2.2275 | 2.4889 | 2.739 | 3.0102 | 3.2781 | 3.5381 | 3.8022 | 4.9904 | 5.469
Swansea North | Gwaun Cae Gurwen | Primary Substation | 11 | Electric Engagement | 0.27016 | 0.35503 | 0.50327 | 0.68088 | 0.85077 | 1.0487 | 1.2892 | 1.5806 | 1.8421 | 2.066 | 2.2735 | 2.4697 | 2.5648 | 2.6297 | 2.696 | 2.7631 | 3.2469 | 3.4813 | 0.61732 | 0.79811 | 1.1048 | 1.4732 | 1.8277 | 2.2405 | 2.741 | 3.346 | 3.8923 | 4.364 | 4.8041 | 5.2192 | 5.4333 | 5.5786 | 5.7262 | 5.8762 | 6.9465 | 7.5023
Swansea North | Gwaun Cae Gurwen | Primary Substation | 11 | Holistic Transition | 0.28185 | 0.35869 | 0.44166 | 0.54308 | 0.65688 | 0.80626 | 0.97448 | 1.2044 | 1.4009 | 1.6205 | 1.8366 | 2.0485 | 2.2721 | 2.4726 | 2.6601 | 2.8117 | 3.3465 | 3.5416 | 0.64636 | 0.8156 | 0.99392 | 1.2152 | 1.4628 | 1.7832 | 2.1446 | 2.6328 | 3.0542 | 3.5258 | 3.9835 | 4.4342 | 4.9105 | 5.3341 | 5.7299 | 6.0502 | 7.2105 | 7.656
Swansea North | Gwaun Cae Gurwen | Primary Substation | 11 | Hydrogen Evolution | 0.25777 | 0.31953 | 0.38986 | 0.47331 | 0.57233 | 0.69025 | 0.82723 | 1.0192 | 1.1962 | 1.3933 | 1.5855 | 1.7641 | 1.9436 | 2.1065 | 2.2686 | 2.4082 | 2.7684 | 3.007 | 0.58608 | 0.71605 | 0.86271 | 1.0366 | 1.2444 | 1.4913 | 1.777 | 2.173 | 2.5418 | 2.9578 | 3.3584 | 3.7297 | 4.1014 | 4.4384 | 4.7739 | 5.0648 | 5.8531 | 6.3976
Swansea North | Hendy | Primary Substation | 11 | Counterfactual | 0.18681 | 0.23598 | 0.29679 | 0.36533 | 0.43886 | 0.52562 | 0.62708 | 0.78443 | 0.9074 | 1.0442 | 1.1767 | 1.3053 | 1.4449 | 1.61 | 1.7825 | 1.9316 | 2.7007 | 3.0331 | 0.42684 | 0.5299 | 0.65612 | 0.79846 | 0.95164 | 1.1333 | 1.3476 | 1.6764 | 1.9373 | 2.2295 | 2.5089 | 2.776 | 3.0628 | 3.4047 | 3.7628 | 4.0703 | 5.6801 | 6.4134
Swansea North | Hendy | Primary Substation | 11 | Electric Engagement | 0.21139 | 0.30353 | 0.46531 | 0.66001 | 0.84659 | 1.0526 | 1.305 | 1.6111 | 1.886 | 2.1193 | 2.3326 | 2.543 | 2.7103 | 2.8102 | 2.9422 | 3.2125 | 3.5892 | 3.8469 | 0.48634 | 0.68237 | 1.0175 | 1.422 | 1.8122 | 2.2431 | 2.7718 | 3.4104 | 3.988 | 4.483 | 4.9389 | 5.3878 | 5.765 | 5.9907 | 6.2867 | 6.8875 | 7.7541 | 8.3679
Swansea North | Hendy | Primary Substation | 11 | Holistic Transition | 0.22353 | 0.308 | 0.4026 | 0.52027 | 0.64305 | 0.79704 | 0.97274 | 1.2241 | 1.509 | 1.7687 | 2.0475 | 2.36 | 2.6733 | 2.9513 | 3.1373 | 3.2943 | 3.68 | 3.8816 | 0.51656 | 0.70182 | 0.90509 | 1.1617 | 1.429 | 1.7634 | 2.1441 | 2.6818 | 3.3002 | 3.8634 | 4.4616 | 5.1341 | 5.8084 | 6.4025 | 6.7958 | 7.1288 | 8.0023 | 8.4695
Swansea North | Hendy | Primary Substation | 11 | Hydrogen Evolution | 0.19786 | 0.26774 | 0.34924 | 0.44605 | 0.55003 | 0.67168 | 0.81998 | 1.036 | 1.2334 | 1.4556 | 1.6781 | 1.8982 | 2.1333 | 2.3448 | 2.5392 | 2.7133 | 3.2043 | 3.4476 | 0.45218 | 0.59938 | 0.76988 | 0.97271 | 1.1915 | 1.447 | 1.7593 | 2.2088 | 2.6245 | 3.0978 | 3.5663 | 4.0293 | 4.5238 | 4.9672 | 5.374 | 5.7406 | 6.83 | 7.3953
Swansea North | Hirwaun Primary | Primary Substation | 11 | Counterfactual | 0.62793 | 0.7732 | 0.81652 | 1.3456 | 1.4059 | 1.5156 | 1.6062 | 1.725 | 1.8199 | 1.918 | 2.0156 | 2.115 | 2.2184 | 2.3065 | 2.3903 | 2.4855 | 2.9789 | 3.1018 | 1.55 | 1.8441 | 1.9339 | 3.2354 | 3.3608 | 3.6031 | 3.793 | 4.04 | 4.2399 | 4.447 | 4.6515 | 4.8588 | 5.0727 | 5.2541 | 5.4267 | 5.6255 | 6.6971 | 6.9613
Swansea North | Hirwaun Primary | Primary Substation | 11 | Electric Engagement | 1.0822 | 1.2555 | 1.8303 | 1.9396 | 2.1481 | 2.2909 | 2.4802 | 2.7223 | 2.9437 | 3.1312 | 3.3155 | 3.4718 | 3.5547 | 3.6507 | 3.8396 | 3.897 | 4.164 | 4.5189 | 2.464 | 2.8195 | 4.2149 | 4.4408 | 4.9183 | 5.2163 | 5.6152 | 6.1264 | 6.5963 | 6.9955 | 7.3896 | 7.722 | 7.9099 | 8.1353 | 8.592 | 8.7203 | 9.3083 | 10.1716
Swansea North | Hirwaun Primary | Primary Substation | 11 | Holistic Transition | 0.6477 | 1.2966 | 1.359 | 1.4368 | 1.642 | 1.8006 | 1.9702 | 2.1765 | 2.3192 | 2.4746 | 2.635 | 2.787 | 2.9629 | 3.1222 | 3.3371 | 3.4366 | 4.1476 | 4.2852 | 1.598 | 3.1474 | 3.2814 | 3.4496 | 3.9289 | 4.2722 | 4.6407 | 5.0826 | 5.3891 | 5.7218 | 6.0627 | 6.3911 | 6.78 | 7.131 | 7.6212 | 7.83 | 9.5291 | 9.8367
Swansea North | Hirwaun Primary | Primary Substation | 11 | Hydrogen Evolution | 0.63433 | 0.80994 | 1.3707 | 1.4532 | 1.658 | 1.7681 | 1.8882 | 2.0358 | 2.1798 | 2.3249 | 2.4645 | 2.5818 | 2.7059 | 2.8291 | 3.0321 | 3.199 | 3.4126 | 3.7909 | 1.5645 | 1.9242 | 3.2945 | 3.4678 | 3.9416 | 4.1737 | 4.4286 | 4.7376 | 5.0405 | 5.3469 | 5.6391 | 5.8836 | 6.1409 | 6.406 | 6.8682 | 7.2493 | 7.7101 | 8.6084
Swansea North | Jersey Marine | Primary Substation | 11 | Counterfactual | 0.015903 | 0.019378 | 0.022837 | 0.026884 | 0.0361 | 0.043595 | 0.051379 | 0.063094 | 0.072694 | 0.084004 | 0.094098 | 0.10357 | 0.11338 | 0.12297 | 0.13215 | 0.14173 | 0.18751 | 0.21072 | 0.034735 | 0.04244 | 0.049673 | 0.058144 | 0.079223 | 0.095662 | 0.11261 | 0.13781 | 0.1589 | 0.18398 | 0.20589 | 0.22593 | 0.24632 | 0.26628 | 0.2854 | 0.30532 | 0.40271 | 0.45472
Swansea North | Jersey Marine | Primary Substation | 11 | Electric Engagement | 0.016853 | 0.025871 | 0.035644 | 0.062789 | 0.074525 | 0.088697 | 0.10613 | 0.1275 | 0.14694 | 0.16455 | 0.18144 | 0.19736 | 0.20777 | 0.21446 | 0.22126 | 0.22779 | 0.2627 | 0.29044 | 0.037139 | 0.057662 | 0.077995 | 0.14101 | 0.16596 | 0.19623 | 0.23351 | 0.27919 | 0.32119 | 0.35968 | 0.39699 | 0.432 | 0.45619 | 0.47154 | 0.48705 | 0.50212 | 0.5838 | 0.65108
Swansea North | Jersey Marine | Primary Substation | 11 | Holistic Transition | 0.017415 | 0.025892 | 0.042482 | 0.050041 | 0.058921 | 0.070689 | 0.08423 | 0.10273 | 0.11875 | 0.13743 | 0.1544 | 0.17068 | 0.18641 | 0.19933 | 0.21191 | 0.22327 | 0.26272 | 0.27803 | 0.038515 | 0.058176 | 0.097719 | 0.11454 | 0.13431 | 0.16018 | 0.19019 | 0.23078 | 0.26643 | 0.30817 | 0.34537 | 0.38104 | 0.41542 | 0.44307 | 0.46998 | 0.4945 | 0.58353 | 0.61883
Swansea North | Jersey Marine | Primary Substation | 11 | Hydrogen Evolution | 0.016276 | 0.024023 | 0.02924 | 0.050051 | 0.058659 | 0.068143 | 0.07916 | 0.094119 | 0.10911 | 0.12667 | 0.14257 | 0.15697 | 0.17137 | 0.1826 | 0.19401 | 0.20382 | 0.23588 | 0.26314 | 0.035638 | 0.053274 | 0.06418 | 0.11358 | 0.13221 | 0.15244 | 0.17592 | 0.20738 | 0.23944 | 0.27783 | 0.31204 | 0.34282 | 0.37325 | 0.39672 | 0.42058 | 0.4413 | 0.51405 | 0.57826
Swansea North | Kidwelly | Primary Substation | 11 | Counterfactual | 0.14226 | 0.16494 | 0.19145 | 0.22118 | 0.25915 | 0.31852 | 0.38884 | 0.48989 | 0.57488 | 0.6716 | 0.75959 | 0.83763 | 0.91719 | 1.0274 | 1.1056 | 1.1848 | 1.5875 | 1.8261 | 0.33717 | 0.38528 | 0.44081 | 0.50346 | 0.58453 | 0.71146 | 0.86488 | 1.0832 | 1.2705 | 1.4867 | 1.679 | 1.8454 | 2.0119 | 2.2443 | 2.4082 | 2.5738 | 3.4359 | 3.9736
Swansea North | Kidwelly | Primary Substation | 11 | Electric Engagement | 0.15377 | 0.19829 | 0.27672 | 0.3766 | 0.47623 | 0.6314 | 0.81502 | 1.0349 | 1.2499 | 1.4521 | 1.6569 | 1.8802 | 2.0228 | 2.1332 | 2.2473 | 2.3678 | 3.0994 | 3.4202 | 0.36482 | 0.46086 | 0.62489 | 0.83656 | 1.0501 | 1.3786 | 1.7682 | 2.2356 | 2.6956 | 3.1312 | 3.5745 | 4.0587 | 4.3769 | 4.6167 | 4.8634 | 5.1242 | 6.7124 | 7.4685
Swansea North | Kidwelly | Primary Substation | 11 | Holistic Transition | 0.16005 | 0.20261 | 0.24578 | 0.31301 | 0.39088 | 0.52233 | 0.67069 | 0.87652 | 1.0793 | 1.286 | 1.4802 | 1.6761 | 1.8813 | 2.0593 | 2.2297 | 2.3754 | 2.995 | 3.2062 | 0.3804 | 0.47567 | 0.56896 | 0.72071 | 0.89667 | 1.183 | 1.5098 | 1.961 | 2.4087 | 2.8677 | 3.2897 | 3.7164 | 4.1628 | 4.5426 | 4.9056 | 5.2157 | 6.5603 | 7.033
Swansea North | Kidwelly | Primary Substation | 11 | Hydrogen Evolution | 0.14775 | 0.17945 | 0.21556 | 0.26013 | 0.31877 | 0.40081 | 0.49349 | 0.62715 | 0.76901 | 0.91808 | 1.0537 | 1.1774 | 1.2973 | 1.4081 | 1.5195 | 1.6219 | 1.994 | 2.3357 | 0.34961 | 0.41716 | 0.49337 | 0.58818 | 0.7155 | 0.8916 | 1.0904 | 1.3743 | 1.6816 | 2.0108 | 2.3045 | 2.5708 | 2.8264 | 3.0605 | 3.2961 | 3.5144 | 4.3472 | 5.126
Swansea North | Lampeter Primary | Primary Substation | 11 | Counterfactual | 0.35558 | 0.39395 | 0.44425 | 0.50011 | 1.1038 | 1.2273 | 1.3843 | 1.6011 | 1.8002 | 2.0287 | 2.2229 | 2.3801 | 2.5321 | 2.6828 | 2.828 | 2.9757 | 3.7407 | 4.2682 | 0.7971 | 0.87853 | 0.9842 | 1.1028 | 2.3232 | 2.5919 | 2.942 | 3.4224 | 3.872 | 4.3965 | 4.8324 | 5.1767 | 5.5015 | 5.8247 | 6.1354 | 6.451 | 8.1331 | 9.342
Swansea North | Lampeter Primary | Primary Substation | 11 | Electric Engagement | 0.89521 | 0.96941 | 1.1034 | 1.2767 | 1.454 | 1.849 | 2.22 | 2.675 | 3.1259 | 3.5603 | 4.0043 | 4.4056 | 4.7387 | 4.9829 | 5.2428 | 5.5157 | 7.1389 | 7.9195 | 1.8829 | 2.0431 | 2.326 | 2.6997 | 3.088 | 3.9257 | 4.7325 | 5.7262 | 6.7187 | 7.681 | 8.6677 | 9.5597 | 10.3184 | 10.857 | 11.426 | 12.0247 | 15.585 | 17.4536
Swansea North | Lampeter Primary | Primary Substation | 11 | Holistic Transition | 0.90424 | 0.97654 | 1.0527 | 1.1948 | 1.3759 | 1.6765 | 2.0209 | 2.45 | 2.8436 | 3.3042 | 3.7116 | 4.0979 | 4.4821 | 4.791 | 5.1047 | 5.3912 | 6.7338 | 7.155 | 1.9052 | 2.0669 | 2.2312 | 2.5577 | 2.9738 | 3.6429 | 4.4209 | 5.3872 | 6.2811 | 7.3326 | 8.242 | 9.1065 | 9.962 | 10.6317 | 11.3088 | 11.928 | 14.8816 | 15.8305
Swansea North | Lampeter Primary | Primary Substation | 11 | Hydrogen Evolution | 0.36227 | 0.42137 | 1.0234 | 1.1202 | 1.2558 | 1.4334 | 1.636 | 1.885 | 2.1457 | 2.4814 | 2.7681 | 3.0222 | 3.2617 | 3.4548 | 3.6564 | 3.8451 | 4.7138 | 5.5301 | 0.81249 | 0.93857 | 2.1527 | 2.3612 | 2.6609 | 3.0497 | 3.4955 | 4.0364 | 4.6158 | 5.3795 | 6.0186 | 6.5822 | 7.1067 | 7.5214 | 7.9528 | 8.3615 | 10.3309 | 12.2257
Swansea North | Lime Street Gorseinon | Primary Substation | 11 | Counterfactual | 0.54488 | 0.6626 | 0.80908 | 0.97739 | 1.1711 | 1.3937 | 1.6362 | 1.9897 | 2.2653 | 2.553 | 2.8376 | 3.1233 | 3.4272 | 3.7092 | 3.984 | 4.2683 | 5.5853 | 5.8944 | 1.2122 | 1.4591 | 1.7632 | 2.1124 | 2.515 | 2.9786 | 3.4856 | 4.2178 | 4.7949 | 5.3997 | 5.9933 | 6.5836 | 7.2064 | 7.7826 | 8.3435 | 8.9252 | 11.6447 | 12.3319
Swansea North | Lime Street Gorseinon | Primary Substation | 11 | Electric Engagement | 0.60636 | 0.83159 | 1.2163 | 1.6897 | 2.1479 | 2.6301 | 3.1968 | 3.8357 | 4.4095 | 4.8933 | 5.3356 | 5.7625 | 5.9368 | 6.0908 | 6.2441 | 6.4125 | 7.0736 | 7.5476 | 1.3594 | 1.84 | 2.6407 | 3.6272 | 4.5879 | 5.5951 | 6.7745 | 8.0941 | 9.2857 | 10.2974 | 11.2277 | 12.1239 | 12.5145 | 12.8586 | 13.2005 | 13.5718 | 15.0621 | 16.168
Swansea North | Lime Street Gorseinon | Primary Substation | 11 | Holistic Transition | 0.63035 | 0.84594 | 1.1034 | 1.4187 | 1.7266 | 2.0872 | 2.4908 | 2.9806 | 3.3955 | 3.875 | 4.3616 | 4.8185 | 5.2499 | 5.639 | 6.0174 | 6.3801 | 7.1319 | 7.5581 | 1.419 | 1.8904 | 2.4444 | 3.126 | 3.7907 | 4.5639 | 5.4267 | 6.4576 | 7.3377 | 8.3572 | 9.3823 | 10.3427 | 11.2473 | 12.0578 | 12.849 | 13.6085 | 15.2872 | 16.2656
Swansea North | Lime Street Gorseinon | Primary Substation | 11 | Hydrogen Evolution | 0.57111 | 0.73355 | 0.92671 | 1.1639 | 1.4368 | 1.7541 | 2.109 | 2.5694 | 2.9482 | 3.3674 | 3.7974 | 4.2134 | 4.62 | 4.9623 | 5.2821 | 5.576 | 6.1655 | 6.5743 | 1.2724 | 1.6158 | 2.0215 | 2.5205 | 3.0971 | 3.7671 | 4.5122 | 5.4657 | 6.2541 | 7.1327 | 8.0268 | 8.8902 | 9.7323 | 10.436 | 11.0942 | 11.7014 | 12.9947 | 13.9275
Swansea North | Llanarth Primary | Primary Substation | 11 | Counterfactual | 0.24999 | 0.27663 | 0.31226 | 0.35432 | 0.40878 | 0.60868 | 0.72168 | 0.87902 | 1.0174 | 1.1714 | 1.3221 | 1.4458 | 1.5657 | 1.6811 | 1.7936 | 1.9071 | 2.4637 | 2.8037 | 0.58343 | 0.63929 | 0.71348 | 0.80173 | 0.91786 | 1.3295 | 1.5747 | 1.9141 | 2.2177 | 2.561 | 2.889 | 3.1535 | 3.4046 | 3.647 | 3.8823 | 4.1202 | 5.3166 | 6.0773
Swansea North | Llanarth Primary | Primary Substation | 11 | Electric Engagement | 0.36725 | 0.42016 | 0.52057 | 0.65012 | 0.77913 | 1.0329 | 1.3322 | 1.6981 | 2.0589 | 2.406 | 2.7653 | 3.084 | 3.3468 | 3.5736 | 3.8272 | 4.0645 | 5.3564 | 5.86 | 0.82347 | 0.93599 | 1.1453 | 1.4198 | 1.6965 | 2.2311 | 2.8646 | 3.6426 | 4.4134 | 5.1586 | 5.9313 | 6.6178 | 7.1949 | 7.6773 | 8.2126 | 8.7178 | 11.4727 | 12.647
Swansea North | Llanarth Primary | Primary Substation | 11 | Holistic Transition | 0.27095 | 0.31916 | 0.37545 | 0.58051 | 0.71146 | 0.9432 | 1.2001 | 1.5168 | 1.8061 | 2.1385 | 2.4558 | 2.7449 | 3.0282 | 3.2799 | 3.5493 | 3.7863 | 4.8686 | 5.1883 | 0.63509 | 0.74124 | 0.86181 | 1.2968 | 1.5915 | 2.0921 | 2.6547 | 3.3467 | 3.9816 | 4.7159 | 5.4027 | 6.0309 | 6.6441 | 7.1749 | 7.7397 | 8.2401 | 10.5576 | 11.2574
Swansea North | Llanarth Primary | Primary Substation | 11 | Hydrogen Evolution | 0.25536 | 0.29827 | 0.3531 | 0.4206 | 0.50805 | 0.74799 | 0.90051 | 1.0957 | 1.287 | 1.525 | 1.7305 | 1.9154 | 2.0886 | 2.2393 | 2.3961 | 2.5325 | 3.1003 | 3.6702 | 0.59594 | 0.68636 | 0.80197 | 0.94561 | 1.1358 | 1.6346 | 1.9615 | 2.3756 | 2.7898 | 3.3158 | 3.7613 | 4.1598 | 4.5295 | 4.8456 | 5.1736 | 5.463 | 6.7233 | 8.0053
Swansea North | Llandarcy | Primary Substation | 11 | Counterfactual | 0.23128 | 0.30981 | 0.42566 | 0.55097 | 0.68918 | 0.84303 | 1.0143 | 1.2489 | 1.4362 | 1.6346 | 1.8333 | 2.0333 | 2.2512 | 2.4639 | 2.6703 | 2.8813 | 3.8146 | 4.2308 | 0.54117 | 0.70621 | 0.94719 | 1.2072 | 1.4958 | 1.8164 | 2.1738 | 2.6592 | 3.0505 | 3.4661 | 3.8802 | 4.2944 | 4.7429 | 5.181 | 5.6061 | 6.0404 | 7.9756 | 8.8724
Swansea North | Llandarcy | Primary Substation | 11 | Electric Engagement | 0.26116 | 0.3926 | 0.63438 | 0.93641 | 1.2104 | 1.5087 | 1.865 | 2.2889 | 2.6682 | 2.9902 | 3.2827 | 3.5614 | 3.6999 | 3.8115 | 3.9236 | 4.0338 | 4.6074 | 5.0779 | 0.61354 | 0.89432 | 1.3983 | 2.0331 | 2.6069 | 3.2318 | 3.9754 | 4.8571 | 5.6498 | 6.3269 | 6.9452 | 7.5325 | 7.8388 | 8.0869 | 8.3354 | 8.5807 | 9.8643 | 10.9292
Swansea North | Llandarcy | Primary Substation | 11 | Holistic Transition | 0.27489 | 0.40164 | 0.5759 | 0.75871 | 0.95849 | 1.2093 | 1.4768 | 1.8166 | 2.0893 | 2.3852 | 2.6859 | 2.977 | 3.2654 | 3.5325 | 3.7908 | 4.0219 | 4.5943 | 5.0737 | 0.64752 | 0.9254 | 1.3039 | 1.6981 | 2.1286 | 2.6663 | 3.2383 | 3.9558 | 4.535 | 5.1626 | 5.7958 | 6.4102 | 7.0189 | 7.5811 | 8.1252 | 8.6149 | 9.8985 | 10.97
Swansea North | Llandarcy | Primary Substation | 11 | Hydrogen Evolution | 0.24521 | 0.35916 | 0.5185 | 0.71203 | 0.90532 | 1.1236 | 1.3552 | 1.6523 | 1.9277 | 2.2151 | 2.5024 | 2.7739 | 3.0521 | 3.2967 | 3.5414 | 3.754 | 4.3466 | 4.8254 | 0.57324 | 0.81529 | 1.1522 | 1.565 | 1.9733 | 2.4345 | 2.9209 | 3.5367 | 4.1106 | 4.7119 | 5.3098 | 5.8749 | 6.4524 | 6.961 | 7.4698 | 7.9143 | 9.2041 | 10.2641
Swansea North | Llandeilo | Primary Substation | 11 | Counterfactual | 0.2137 | 0.24249 | 0.27351 | 0.30782 | 0.35005 | 0.4058 | 0.47027 | 0.5676 | 0.64556 | 0.73263 | 0.81592 | 0.89401 | 0.97915 | 1.0617 | 1.1416 | 1.2241 | 1.6239 | 1.891 | 0.48746 | 0.54938 | 0.61428 | 0.68622 | 0.77506 | 0.89269 | 1.0303 | 1.236 | 1.4034 | 1.5922 | 1.7697 | 1.9328 | 2.1084 | 2.2787 | 2.4437 | 2.6138 | 3.4487 | 4.0276
Swansea North | Llandeilo | Primary Substation | 11 | Electric Engagement | 0.2255 | 0.2826 | 0.3699 | 0.4784 | 0.5833 | 0.71948 | 0.88751 | 1.0829 | 1.2656 | 1.4343 | 1.5957 | 1.7456 | 1.8384 | 1.9063 | 1.9766 | 2.0467 | 2.6082 | 2.8201 | 0.51599 | 0.64128 | 0.82361 | 1.0511 | 1.2727 | 1.5589 | 1.9126 | 2.3216 | 2.7059 | 3.0628 | 3.4055 | 3.7232 | 3.9269 | 4.0739 | 4.2258 | 4.3771 | 5.5904 | 6.0854
Swansea North | Llandeilo | Primary Substation | 11 | Holistic Transition | 0.23233 | 0.29028 | 0.34194 | 0.41079 | 0.48745 | 0.60671 | 0.73315 | 0.89922 | 1.0476 | 1.2182 | 1.3806 | 1.548 | 1.735 | 1.9011 | 2.0593 | 2.1704 | 2.6035 | 2.7923 | 0.5329 | 0.66499 | 0.77751 | 0.93016 | 1.0999 | 1.3583 | 1.6323 | 1.9885 | 2.3093 | 2.6781 | 3.0228 | 3.381 | 3.783 | 4.1374 | 4.4744 | 4.7097 | 5.6456 | 6.0688
Swansea North | Llandeilo | Primary Substation | 11 | Hydrogen Evolution | 0.21927 | 0.25978 | 0.30195 | 0.35692 | 0.42235 | 0.50574 | 0.60348 | 0.7341 | 0.86381 | 1.0103 | 1.1483 | 1.2722 | 1.3976 | 1.5156 | 1.6421 | 1.7484 | 2.0924 | 2.3291 | 0.5001 | 0.58757 | 0.6763 | 0.79157 | 0.93021 | 1.1059 | 1.3124 | 1.5845 | 1.8565 | 2.1679 | 2.4573 | 2.7172 | 2.9784 | 3.2254 | 3.4902 | 3.7139 | 4.4614 | 4.9897
Swansea North | Llandovery | Primary Substation | 11 | Counterfactual | 0.1173 | 0.13726 | 0.15883 | 0.18398 | 0.21651 | 0.26385 | 0.32101 | 0.40295 | 0.47557 | 0.55579 | 0.62823 | 0.69089 | 0.75703 | 0.81933 | 0.87901 | 0.9427 | 1.2631 | 1.4634 | 0.27539 | 0.31902 | 0.36453 | 0.4178 | 0.48728 | 0.58854 | 0.71298 | 0.8896 | 1.0488 | 1.2269 | 1.3846 | 1.5174 | 1.6551 | 1.7849 | 1.9094 | 2.042 | 2.7206 | 3.1596
Swansea North | Llandovery | Primary Substation | 11 | Electric Engagement | 0.12447 | 0.16661 | 0.2271 | 0.30552 | 0.38289 | 0.49868 | 0.64012 | 0.80812 | 0.97148 | 1.1286 | 1.2835 | 1.4246 | 1.5274 | 1.6053 | 1.6866 | 1.7685 | 2.2304 | 2.4644 | 0.29291 | 0.38681 | 0.51438 | 0.68121 | 0.84757 | 1.0938 | 1.3947 | 1.7512 | 2.0996 | 2.436 | 2.7688 | 3.0714 | 3.2972 | 3.465 | 3.6395 | 3.8152 | 4.8105 | 5.3585
Swansea North | Llandovery | Primary Substation | 11 | Holistic Transition | 0.12905 | 0.17412 | 0.21071 | 0.26689 | 0.33172 | 0.44243 | 0.5599 | 0.71607 | 0.85911 | 1.018 | 1.1637 | 1.2987 | 1.4316 | 1.5421 | 1.6548 | 1.756 | 2.1724 | 2.3618 | 0.30423 | 0.40849 | 0.48877 | 0.61573 | 0.7623 | 1.0031 | 1.2603 | 1.6005 | 1.9141 | 2.2626 | 2.5753 | 2.8667 | 3.1539 | 3.389 | 3.6277 | 3.8434 | 4.7468 | 5.1669
Swansea North | Llandovery | Primary Substation | 11 | Hydrogen Evolution | 0.12047 | 0.14963 | 0.18213 | 0.2274 | 0.28296 | 0.35795 | 0.44331 | 0.55464 | 0.66601 | 0.79558 | 0.91225 | 1.0134 | 1.1173 | 1.1933 | 1.2774 | 1.3461 | 1.6261 | 1.8955 | 0.28273 | 0.34659 | 0.41578 | 0.51165 | 0.63127 | 0.79155 | 0.974 | 1.2094 | 1.4455 | 1.7258 | 1.9744 | 2.1898 | 2.4088 | 2.5678 | 2.7431 | 2.8875 | 3.5027 | 4.1049
Swansea North | Llanelli Primary | Bulk Supply Point | 11 | Counterfactual | 0.34492 | 0.44997 | 0.57345 | 0.71269 | 0.8708 | 1.0528 | 1.2622 | 1.5872 | 1.8281 | 2.0858 | 2.3452 | 2.6116 | 2.9069 | 3.3304 | 3.6202 | 3.9067 | 5.1967 | 5.6091 | 0.79006 | 1.0107 | 1.2666 | 1.5551 | 1.8823 | 2.2591 | 2.6933 | 3.3605 | 3.86 | 4.3955 | 4.9309 | 5.4764 | 6.0777 | 6.9546 | 7.5448 | 8.1279 | 10.7722 | 11.6673
Swansea North | Llanelli Primary | Bulk Supply Point | 11 | Electric Engagement | 0.40238 | 0.60615 | 0.95901 | 1.3762 | 1.7707 | 2.218 | 2.7538 | 3.4072 | 3.9857 | 4.4628 | 4.8915 | 5.4542 | 5.6075 | 5.7144 | 5.8209 | 5.9638 | 6.6726 | 7.0591 | 0.92859 | 1.3633 | 2.0925 | 2.954 | 3.7718 | 4.6964 | 5.8004 | 7.1421 | 8.3349 | 9.3235 | 10.2161 | 11.4034 | 11.7433 | 11.982 | 12.2192 | 12.5301 | 14.1152 | 15.0171
Swansea North | Llanelli Primary | Bulk Supply Point | 11 | Holistic Transition | 0.43371 | 0.62046 | 0.82242 | 1.0556 | 1.3128 | 1.6231 | 1.9871 | 2.525 | 2.9702 | 3.437 | 3.9183 | 4.4182 | 4.9214 | 5.3864 | 5.812 | 6.1873 | 6.9351 | 7.3257 | 1.0064 | 1.4185 | 1.8536 | 2.3576 | 2.9107 | 3.5709 | 4.3431 | 5.4739 | 6.4153 | 7.4001 | 8.4076 | 9.4568 | 10.5142 | 11.4884 | 12.3805 | 13.1621 | 14.8205 | 15.7269
Swansea North | Llanelli Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 0.37157 | 0.51919 | 0.68457 | 0.88447 | 1.1056 | 1.3572 | 1.6753 | 2.1351 | 2.5306 | 2.9468 | 3.3728 | 3.7823 | 4.1682 | 4.5416 | 4.899 | 5.248 | 5.8353 | 6.1879 | 0.85077 | 1.1619 | 1.5064 | 1.9234 | 2.3845 | 2.9065 | 3.5663 | 4.5122 | 5.3313 | 6.1948 | 7.0729 | 7.9154 | 8.7059 | 9.4734 | 10.21 | 10.9292 | 12.2058 | 13.0019
Swansea North | Llanfihangel Ystrad | Primary Substation | 11 | Counterfactual | 1.3894 | 1.4124 | 1.4421 | 1.4763 | 1.5233 | 1.6177 | 1.7315 | 1.8817 | 2.0246 | 2.1829 | 2.32 | 2.4302 | 2.5337 | 2.6383 | 2.7398 | 2.8435 | 3.3913 | 3.818 | 3.4408 | 3.4918 | 3.5571 | 3.6326 | 3.7378 | 3.9438 | 4.1982 | 4.5329 | 4.8558 | 5.2205 | 5.5291 | 5.7725 | 5.9959 | 6.2224 | 6.4417 | 6.6655 | 7.8836 | 8.8569
Swansea North | Llanfihangel Ystrad | Primary Substation | 11 | Electric Engagement | 1.3962 | 1.4359 | 1.5117 | 1.615 | 1.7231 | 1.9684 | 2.2544 | 2.6004 | 2.9536 | 3.3101 | 3.6928 | 4.0185 | 4.3365 | 4.5999 | 4.8751 | 5.1644 | 6.7881 | 7.4484 | 3.4576 | 3.5445 | 3.7071 | 3.9336 | 4.1743 | 4.6986 | 5.3137 | 6.0629 | 6.8308 | 7.6085 | 8.4435 | 9.1512 | 9.8556 | 10.421 | 11.009 | 11.6287 | 15.1066 | 16.6591
Swansea North | Llanfihangel Ystrad | Primary Substation | 11 | Holistic Transition | 1.4015 | 1.4388 | 1.4808 | 1.5699 | 1.6802 | 1.9181 | 2.1834 | 2.504 | 2.8152 | 3.1616 | 3.4973 | 3.8037 | 4.1049 | 4.3575 | 4.6146 | 4.8712 | 6.2214 | 6.6271 | 3.4708 | 3.5551 | 3.6472 | 3.8549 | 4.1122 | 4.6324 | 5.2231 | 5.938 | 6.634 | 7.4108 | 8.1502 | 8.8287 | 9.4921 | 10.0331 | 10.5815 | 11.1294 | 14.0335 | 14.9316
Swansea North | Llanfihangel Ystrad | Primary Substation | 11 | Hydrogen Evolution | 1.3922 | 1.4205 | 1.4567 | 1.5098 | 1.586 | 1.715 | 1.856 | 2.0222 | 2.1951 | 2.4237 | 2.6211 | 2.7794 | 2.9405 | 3.072 | 3.205 | 3.3512 | 4.0406 | 4.7503 | 3.4475 | 3.5081 | 3.5864 | 3.7026 | 3.874 | 4.1555 | 4.4644 | 4.8249 | 5.2089 | 5.7294 | 6.1695 | 6.5163 | 6.8694 | 7.1516 | 7.4367 | 7.7587 | 9.3021 | 10.9094
Swansea North | Llanfyrnach | Primary Substation | 11 | Counterfactual | 0.3697 | 0.38016 | 0.39452 | 0.41074 | 0.43368 | 0.45994 | 0.48864 | 0.52502 | 0.55275 | 0.58306 | 0.61372 | 0.64482 | 0.6802 | 0.71407 | 0.74661 | 0.78083 | 0.93571 | 1.0199 | 0.80122 | 0.82328 | 0.8529 | 0.88635 | 0.93374 | 0.98809 | 1.0477 | 1.1223 | 1.1797 | 1.2427 | 1.3059 | 1.3693 | 1.4411 | 1.5098 | 1.5758 | 1.6452 | 1.9611 | 2.1354
Swansea North | Llanfyrnach | Primary Substation | 11 | Electric Engagement | 0.37235 | 0.39466 | 0.43312 | 0.47784 | 0.5234 | 0.57491 | 0.64001 | 0.70971 | 0.77222 | 0.82917 | 0.88157 | 0.93051 | 0.95697 | 0.97575 | 0.99483 | 1.0948 | 1.3261 | 1.3742 | 0.80822 | 0.85573 | 0.93524 | 1.0274 | 1.1221 | 1.2288 | 1.3635 | 1.5061 | 1.6345 | 1.7518 | 1.8601 | 1.9611 | 2.0172 | 2.057 | 2.0974 | 2.2996 | 2.7751 | 2.8842
Swansea North | Llanfyrnach | Primary Substation | 11 | Holistic Transition | 0.37454 | 0.39699 | 0.42145 | 0.4449 | 0.4755 | 0.51828 | 0.5663 | 0.62232 | 0.67017 | 0.72582 | 0.78113 | 0.83101 | 0.87846 | 0.91911 | 0.95983 | 1.077 | 1.3259 | 1.3765 | 0.81364 | 0.86298 | 0.9153 | 0.96545 | 1.0308 | 1.121 | 1.2223 | 1.3385 | 1.4384 | 1.5544 | 1.6687 | 1.7721 | 1.8707 | 1.9549 | 2.0391 | 2.2762 | 2.788 | 2.8992
Swansea North | Llanfyrnach | Primary Substation | 11 | Hydrogen Evolution | 0.37049 | 0.38781 | 0.40814 | 0.43499 | 0.46984 | 0.51118 | 0.5572 | 0.61222 | 0.66577 | 0.72291 | 0.77871 | 0.82882 | 0.87994 | 0.91955 | 0.9611 | 1.0352 | 1.1962 | 1.2546 | 0.80336 | 0.83973 | 0.88189 | 0.93731 | 1.01 | 1.096 | 1.1914 | 1.3034 | 1.4127 | 1.5298 | 1.6436 | 1.7457 | 1.8497 | 1.9303 | 2.0147 | 2.1642 | 2.4953 | 2.6212
Swansea North | Llangadog | Primary Substation | 11 | Counterfactual | 0.11468 | 0.131 | 0.14828 | 0.16789 | 0.19396 | 0.23382 | 0.28126 | 0.34877 | 0.4069 | 0.47382 | 0.5344 | 0.58586 | 0.64039 | 0.69225 | 0.74207 | 0.79489 | 1.0493 | 1.202 | 0.27726 | 0.31289 | 0.34934 | 0.39096 | 0.44682 | 0.53239 | 0.63633 | 0.78323 | 0.91214 | 1.0625 | 1.1955 | 1.3055 | 1.4197 | 1.5286 | 1.6333 | 1.7438 | 2.2869 | 2.6266
Swansea North | Llangadog | Primary Substation | 11 | Electric Engagement | 0.12028 | 0.15392 | 0.20262 | 0.26536 | 0.32766 | 0.42337 | 0.54321 | 0.67758 | 0.80849 | 0.93496 | 1.0613 | 1.1781 | 1.2673 | 1.3361 | 1.4082 | 1.4823 | 1.898 | 2.1082 | 0.29089 | 0.36597 | 0.46885 | 0.60306 | 0.7379 | 0.94226 | 1.1997 | 1.487 | 1.7684 | 2.0418 | 2.3156 | 2.5682 | 2.7655 | 2.9139 | 3.0689 | 3.228 | 4.1216 | 4.6154
Swansea North | Llangadog | Primary Substation | 11 | Holistic Transition | 0.12343 | 0.15959 | 0.1882 | 0.23351 | 0.28533 | 0.38098 | 0.478 | 0.60146 | 0.71503 | 0.84876 | 0.96879 | 1.0779 | 1.1857 | 1.2754 | 1.3685 | 1.4551 | 1.8375 | 2.0012 | 0.29876 | 0.3826 | 0.44548 | 0.54887 | 0.66722 | 0.87735 | 1.0919 | 1.3635 | 1.6152 | 1.912 | 2.1721 | 2.41 | 2.6444 | 2.8354 | 3.033 | 3.218 | 4.0454 | 4.4081
Swansea North | Llangadog | Primary Substation | 11 | Hydrogen Evolution | 0.11752 | 0.14108 | 0.16491 | 0.19902 | 0.2417 | 0.29981 | 0.36637 | 0.45033 | 0.54261 | 0.64936 | 0.74294 | 0.82373 | 0.90895 | 0.96844 | 1.0359 | 1.0914 | 1.3354 | 1.578 | 0.2837 | 0.33536 | 0.38606 | 0.45844 | 0.55089 | 0.67564 | 0.81977 | 0.99872 | 1.1967 | 1.4309 | 1.6328 | 1.8072 | 1.9883 | 2.1132 | 2.2541 | 2.3709 | 2.9081 | 3.4521
Swansea North | Llanllwni | Primary Substation | 11 | Counterfactual | 0.21423 | 0.23132 | 0.25422 | 0.2821 | 0.32365 | 0.41006 | 0.52153 | 0.67049 | 0.81094 | 0.97818 | 1.1187 | 1.2279 | 1.3314 | 1.4365 | 1.5373 | 1.6323 | 2.1684 | 2.5847 | 0.51065 | 0.54691 | 0.59558 | 0.65601 | 0.74887 | 0.93937 | 1.1926 | 1.53 | 1.8534 | 2.2451 | 2.5662 | 2.8098 | 3.0341 | 3.2631 | 3.4818 | 3.6882 | 4.8922 | 5.8548
Swansea North | Llanllwni | Primary Substation | 11 | Electric Engagement | 0.2223 | 0.25547 | 0.32309 | 0.42451 | 0.53359 | 0.76257 | 1.0339 | 1.3623 | 1.7033 | 2.0535 | 2.4329 | 2.7794 | 3.1054 | 3.3595 | 3.6165 | 3.8789 | 5.3435 | 6.0476 | 0.53015 | 0.60192 | 0.74657 | 0.97089 | 1.2164 | 1.7129 | 2.3058 | 3.028 | 3.7814 | 4.5584 | 5.4009 | 6.1717 | 6.9071 | 7.4616 | 8.0181 | 8.5887 | 11.7778 | 13.4547
Swansea North | Llanllwni | Primary Substation | 11 | Holistic Transition | 0.22694 | 0.2589 | 0.29203 | 0.38358 | 0.49591 | 0.72023 | 0.98004 | 1.3068 | 1.6349 | 2.0238 | 2.3668 | 2.6812 | 2.987 | 3.2251 | 3.4692 | 3.7036 | 4.9105 | 5.2766 | 0.54164 | 0.61345 | 0.68494 | 0.90056 | 1.1661 | 1.6648 | 2.2533 | 2.9944 | 3.7409 | 4.6317 | 5.399 | 6.1066 | 6.7914 | 7.3082 | 7.8345 | 8.3418 | 10.9826 | 11.796
Swansea North | Llanllwni | Primary Substation | 11 | Hydrogen Evolution | 0.21793 | 0.24334 | 0.27731 | 0.32575 | 0.40037 | 0.52245 | 0.65579 | 0.81571 | 1.0023 | 1.2585 | 1.4718 | 1.6562 | 1.8252 | 1.958 | 2.0884 | 2.2123 | 2.9047 | 3.6604 | 0.51912 | 0.57348 | 0.64693 | 0.75369 | 0.92402 | 1.1949 | 1.4919 | 1.8444 | 2.2653 | 2.857 | 3.3401 | 3.7561 | 4.1321 | 4.4214 | 4.7038 | 4.976 | 6.5591 | 8.3031
Swansea North | Llanrhidian | Primary Substation | 11 | Counterfactual | 0.19508 | 0.22006 | 0.24839 | 0.28039 | 0.32926 | 0.38709 | 0.45927 | 0.56732 | 0.66403 | 0.76752 | 0.87035 | 0.97722 | 1.0992 | 1.2043 | 1.2936 | 1.3802 | 1.6975 | 1.8218 | 0.46115 | 0.51448 | 0.57339 | 0.63991 | 0.74162 | 0.86223 | 1.0136 | 1.2387 | 1.4424 | 1.6614 | 1.8778 | 2.1014 | 2.3556 | 2.5736 | 2.7584 | 2.9367 | 3.5917 | 3.8589
Swansea North | Llanrhidian | Primary Substation | 11 | Electric Engagement | 0.20524 | 0.25595 | 0.33601 | 0.43044 | 0.51953 | 0.66475 | 0.85183 | 1.0955 | 1.3184 | 1.4968 | 1.6526 | 1.7819 | 1.8348 | 1.8762 | 1.9187 | 1.9592 | 2.1828 | 2.318 | 0.48597 | 0.59614 | 0.76219 | 0.95794 | 1.1436 | 1.4504 | 1.8458 | 2.3612 | 2.8346 | 3.2138 | 3.5458 | 3.8191 | 3.9351 | 4.0259 | 4.1186 | 4.2072 | 4.6992 | 5.0118
Swansea North | Llanrhidian | Primary Substation | 11 | Holistic Transition | 0.21032 | 0.25837 | 0.3146 | 0.40377 | 0.56356 | 0.73084 | 0.9013 | 1.0958 | 1.2005 | 1.3187 | 1.4359 | 1.5431 | 1.6481 | 1.7422 | 1.8382 | 1.9232 | 2.1776 | 2.3185 | 0.49856 | 0.60653 | 0.72803 | 0.92144 | 1.2691 | 1.6311 | 1.9995 | 2.4155 | 2.6376 | 2.8882 | 3.1342 | 3.3595 | 3.5805 | 3.7774 | 3.9788 | 4.158 | 4.7134 | 5.0294
Swansea North | Llanrhidian | Primary Substation | 11 | Hydrogen Evolution | 0.19953 | 0.23595 | 0.27556 | 0.35598 | 0.45135 | 0.56524 | 0.71137 | 0.8715 | 1.0178 | 1.1623 | 1.2963 | 1.4182 | 1.5395 | 1.634 | 1.7189 | 1.7888 | 1.9735 | 2.1167 | 0.47146 | 0.5494 | 0.63216 | 0.80197 | 1.0047 | 1.2473 | 1.5593 | 1.8959 | 2.204 | 2.5092 | 2.7896 | 3.0449 | 3.2971 | 3.4929 | 3.6671 | 3.8114 | 4.2099 | 4.5266
Swansea North | Maerdy | Primary Substation | 11 | Counterfactual | 0.01162 | 0.017425 | 0.024322 | 0.031807 | 0.040829 | 0.052051 | 0.065199 | 0.085322 | 0.10091 | 0.1181 | 0.13472 | 0.15067 | 0.16796 | 0.19075 | 0.21355 | 0.2308 | 0.31043 | 0.33075 | 0.026453 | 0.038598 | 0.052896 | 0.068432 | 0.087264 | 0.11075 | 0.13849 | 0.18047 | 0.21347 | 0.25019 | 0.28515 | 0.31821 | 0.35367 | 0.40096 | 0.4483 | 0.48383 | 0.65225 | 0.69838
Swansea North | Maerdy | Primary Substation | 11 | Electric Engagement | 0.014602 | 0.025823 | 0.045443 | 0.068768 | 0.090912 | 0.11844 | 0.15133 | 0.19148 | 0.22776 | 0.25905 | 0.28857 | 0.31662 | 0.34211 | 0.35749 | 0.37274 | 0.38405 | 0.44363 | 0.47443 | 0.033675 | 0.05763 | 0.098255 | 0.1467 | 0.19297 | 0.25033 | 0.31875 | 0.40217 | 0.478 | 0.54399 | 0.60662 | 0.66605 | 0.7232 | 0.7586 | 0.79348 | 0.81845 | 0.94992 | 1.0233
Swansea North | Maerdy | Primary Substation | 11 | Holistic Transition | 0.015987 | 0.025965 | 0.03673 | 0.049768 | 0.064637 | 0.084787 | 0.10771 | 0.14032 | 0.17596 | 0.20598 | 0.23591 | 0.26587 | 0.29828 | 0.32693 | 0.3501 | 0.37116 | 0.42819 | 0.45048 | 0.037139 | 0.05911 | 0.082246 | 0.11075 | 0.14316 | 0.18633 | 0.23554 | 0.30488 | 0.38171 | 0.44626 | 0.50967 | 0.574 | 0.64455 | 0.7063 | 0.75484 | 0.79914 | 0.92481 | 0.97597
Swansea North | Maerdy | Primary Substation | 11 | Hydrogen Evolution | 0.012833 | 0.020942 | 0.030143 | 0.040635 | 0.053158 | 0.068547 | 0.08644 | 0.117 | 0.14395 | 0.16936 | 0.19423 | 0.21774 | 0.24055 | 0.2632 | 0.28682 | 0.30754 | 0.34729 | 0.37831 | 0.029224 | 0.046293 | 0.065514 | 0.087442 | 0.11384 | 0.14613 | 0.18349 | 0.24735 | 0.30424 | 0.35815 | 0.41019 | 0.45922 | 0.50655 | 0.55436 | 0.60509 | 0.64973 | 0.73772 | 0.80879
Swansea North | Maesarddafen | Primary Substation | 11 | Counterfactual | 0.22377 | 0.26587 | 0.31668 | 0.37538 | 0.44438 | 0.5223 | 0.60784 | 0.74726 | 0.85572 | 0.9754 | 1.1051 | 1.2492 | 1.3928 | 1.5105 | 1.6238 | 1.7389 | 2.2291 | 2.4363 | 0.51572 | 0.60414 | 0.70926 | 0.83068 | 0.97326 | 1.1341 | 1.3112 | 1.5975 | 1.8225 | 2.0714 | 2.3401 | 2.6385 | 2.9332 | 3.1726 | 3.4031 | 3.637 | 4.6423 | 5.0868
Swansea North | Maesarddafen | Primary Substation | 11 | Electric Engagement | 0.24294 | 0.32332 | 0.46006 | 0.62095 | 0.7727 | 0.94179 | 1.1428 | 1.3952 | 1.6198 | 1.8129 | 2.0039 | 2.2215 | 2.2748 | 2.3101 | 2.3455 | 2.3823 | 2.7029 | 2.8416 | 0.56241 | 0.73393 | 1.0162 | 1.348 | 1.6621 | 2.012 | 2.4265 | 2.9466 | 3.4119 | 3.815 | 4.217 | 4.6785 | 4.7974 | 4.877 | 4.9568 | 5.0396 | 5.7647 | 6.0892
Swansea North | Maesarddafen | Primary Substation | 11 | Holistic Transition | 0.25449 | 0.32886 | 0.4083 | 0.50082 | 2.4089 | 2.5361 | 2.6735 | 2.89 | 3.0719 | 3.2654 | 3.4656 | 3.6964 | 3.8861 | 4.0653 | 4.2283 | 4.3465 | 4.5636 | 4.7218 | 0.59101 | 0.75541 | 0.92637 | 1.1262 | 5.8591 | 6.1293 | 6.4209 | 6.8774 | 7.2636 | 7.6741 | 8.0958 | 8.5987 | 8.9997 | 9.3784 | 9.7228 | 9.9712 | 10.4672 | 10.8293
Swansea North | Maesarddafen | Primary Substation | 11 | Hydrogen Evolution | 0.23268 | 0.29204 | 0.36483 | 0.45629 | 0.56279 | 0.67217 | 0.79373 | 0.98996 | 1.1688 | 1.3583 | 1.5452 | 1.7114 | 1.8705 | 2.0242 | 2.1814 | 2.3116 | 2.6067 | 2.7564 | 0.5361 | 0.66108 | 0.81279 | 1.0034 | 1.2259 | 1.4525 | 1.7033 | 2.1082 | 2.4789 | 2.8731 | 3.2601 | 3.6029 | 3.9282 | 4.2452 | 4.5699 | 4.8403 | 5.4826 | 5.8149
Swansea North | Meinciau | Primary Substation | 11 | Counterfactual | 0.054554 | 0.060396 | 0.067933 | 0.077239 | 0.091132 | 0.12119 | 0.15879 | 0.20902 | 0.25681 | 0.31095 | 0.35689 | 0.3913 | 0.42306 | 0.45479 | 0.4855 | 0.51726 | 0.69057 | 0.82699 | 0.12237 | 0.13481 | 0.15082 | 0.17095 | 0.20179 | 0.26741 | 0.35193 | 0.46462 | 0.57341 | 0.69923 | 0.80338 | 0.87965 | 0.94811 | 1.0168 | 1.0832 | 1.1517 | 1.5384 | 1.8508
Swansea North | Meinciau | Primary Substation | 11 | Electric Engagement | 0.057278 | 0.068699 | 0.091263 | 0.12408 | 0.15932 | 0.23916 | 0.3327 | 0.44525 | 0.56431 | 0.68523 | 0.81447 | 0.92876 | 1.0364 | 1.1221 | 1.2114 | 1.3059 | 1.8415 | 2.0706 | 0.12892 | 0.15377 | 0.20196 | 0.27429 | 0.35328 | 0.5249 | 0.7274 | 0.97267 | 1.2332 | 1.4986 | 1.7825 | 2.0341 | 2.2738 | 2.4585 | 2.6498 | 2.8527 | 4.0024 | 4.5425
Swansea North | Meinciau | Primary Substation | 11 | Holistic Transition | 0.058669 | 0.069901 | 0.08158 | 0.11098 | 0.14651 | 0.22501 | 0.31339 | 0.42426 | 0.53463 | 0.66012 | 0.77265 | 0.87432 | 0.97411 | 1.0548 | 1.1369 | 1.2199 | 1.6534 | 1.7846 | 0.13242 | 0.15785 | 0.18313 | 0.25212 | 0.33591 | 0.50856 | 0.7066 | 0.95557 | 1.2041 | 1.4889 | 1.7381 | 1.9648 | 2.1861 | 2.3594 | 2.5354 | 2.7133 | 3.6494 | 3.9372
Swansea North | Meinciau | Primary Substation | 11 | Hydrogen Evolution | 0.055709 | 0.064354 | 0.075733 | 0.091956 | 0.11613 | 0.15812 | 0.20306 | 0.2586 | 0.31825 | 0.39866 | 0.46597 | 0.52363 | 0.57803 | 0.6192 | 0.66189 | 0.70372 | 0.94198 | 1.1979 | 0.12502 | 0.1436 | 0.16819 | 0.20382 | 0.25872 | 0.35109 | 0.45047 | 0.57211 | 0.70555 | 0.89013 | 1.0416 | 1.1709 | 1.291 | 1.38 | 1.4719 | 1.563 | 2.0995 | 2.682
Swansea North | Morriston Primary | Bulk Supply Point | 11 | Counterfactual | 0.62195 | 0.77326 | 0.95735 | 1.1549 | 1.3868 | 1.672 | 1.9942 | 2.4861 | 2.8634 | 3.2768 | 3.6893 | 4.0999 | 4.5508 | 4.9999 | 5.4319 | 5.8718 | 7.7543 | 8.332 | 1.4443 | 1.7621 | 2.1433 | 2.5531 | 3.0343 | 3.6272 | 4.2998 | 5.3182 | 6.1094 | 6.9802 | 7.8405 | 8.688 | 9.6116 | 10.5318 | 11.4167 | 12.3171 | 16.2016 | 17.4717
Swansea North | Morriston Primary | Bulk Supply Point | 11 | Electric Engagement | 0.70346 | 0.99941 | 1.5024 | 2.0853 | 2.6375 | 3.3015 | 4.1178 | 5.1038 | 6.0018 | 6.7593 | 7.4822 | 8.1777 | 8.5022 | 8.7358 | 8.9743 | 9.217 | 10.6369 | 11.4786 | 1.6405 | 2.2723 | 3.3119 | 4.5175 | 5.6648 | 7.041 | 8.7367 | 10.7786 | 12.6488 | 14.233 | 15.7563 | 17.22 | 17.9385 | 18.4511 | 18.9727 | 19.5048 | 22.6302 | 24.5745
Swansea North | Morriston Primary | Bulk Supply Point | 11 | Holistic Transition | 0.73959 | 1.006 | 1.2876 | 1.6116 | 1.98 | 2.4861 | 3.0483 | 3.8049 | 4.4697 | 5.184 | 5.9106 | 6.5972 | 7.2825 | 7.9019 | 8.5161 | 9.0701 | 10.4031 | 11.1957 | 1.73 | 2.3161 | 2.9206 | 3.6229 | 4.4177 | 5.5001 | 6.7022 | 8.2941 | 9.709 | 11.2285 | 12.757 | 14.2015 | 15.6421 | 16.9339 | 18.2183 | 19.3821 | 22.3379 | 24.1206
Swansea North | Morriston Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 0.65843 | 0.87104 | 1.1166 | 1.3976 | 1.7261 | 2.1221 | 2.5857 | 3.2356 | 3.8313 | 4.4759 | 5.1166 | 5.715 | 6.3098 | 6.8185 | 7.3186 | 7.7506 | 8.7927 | 9.6207 | 1.5276 | 1.9759 | 2.4874 | 3.0727 | 3.7591 | 4.5848 | 5.5528 | 6.8936 | 8.1347 | 9.4873 | 10.8183 | 12.0588 | 13.2865 | 14.3303 | 15.3574 | 16.2494 | 18.5162 | 20.3656
Swansea North | Nantgaredig | Primary Substation | 11 | Counterfactual | 0.12686 | 0.1419 | 0.1593 | 0.17928 | 0.20617 | 0.25751 | 0.31696 | 0.39748 | 0.46809 | 0.5473 | 0.61972 | 0.68 | 0.74141 | 0.80167 | 0.85993 | 0.92104 | 1.2244 | 1.4413 | 0.30096 | 0.33361 | 0.37033 | 0.41282 | 0.47078 | 0.58036 | 0.71029 | 0.8854 | 1.0417 | 1.22 | 1.379 | 1.5082 | 1.637 | 1.7638 | 1.8862 | 2.0144 | 2.6672 | 3.1473
Swansea North | Nantgaredig | Primary Substation | 11 | Electric Engagement | 0.13254 | 0.16419 | 0.21512 | 0.28195 | 0.34922 | 0.48513 | 0.64422 | 0.82817 | 1.0131 | 1.198 | 1.3928 | 1.5687 | 1.7224 | 1.8525 | 1.9891 | 2.1323 | 2.9499 | 3.2565 | 0.31487 | 0.38485 | 0.49233 | 0.63567 | 0.78183 | 1.0689 | 1.406 | 1.7967 | 2.191 | 2.5867 | 3.0042 | 3.3812 | 3.7152 | 3.9905 | 4.2786 | 4.5805 | 6.3071 | 7.0152
Swansea North | Nantgaredig | Primary Substation | 11 | Holistic Transition | 0.13618 | 0.16923 | 0.19804 | 0.24766 | 0.30503 | 0.43234 | 0.5659 | 0.73206 | 0.89223 | 1.0788 | 1.254 | 1.4139 | 1.5757 | 1.7159 | 1.8599 | 1.997 | 2.6693 | 2.8983 | 0.32391 | 0.39983 | 0.46269 | 0.57629 | 0.70794 | 0.98229 | 1.2741 | 1.637 | 1.9883 | 2.3994 | 2.7769 | 3.1237 | 3.4733 | 3.7697 | 4.0733 | 4.3622 | 5.7905 | 6.288
Swansea North | Nantgaredig | Primary Substation | 11 | Hydrogen Evolution | 0.12918 | 0.15137 | 0.1753 | 0.20894 | 0.25296 | 0.32433 | 0.40017 | 0.49538 | 0.60022 | 0.72716 | 0.83938 | 0.93653 | 1.035 | 1.1125 | 1.1972 | 1.2738 | 1.6403 | 2.0074 | 0.30639 | 0.35463 | 0.40558 | 0.47736 | 0.57366 | 0.72649 | 0.8893 | 1.0916 | 1.3174 | 1.5976 | 1.8409 | 2.0511 | 2.2611 | 2.4246 | 2.6023 | 2.7645 | 3.5663 | 4.3793
Swansea North | New Lodge | Primary Substation | 11 | Counterfactual | 0.21922 | 0.27131 | 0.33906 | 0.4064 | 0.48771 | 0.59319 | 0.73488 | 0.92362 | 1.0716 | 1.2268 | 1.3743 | 1.511 | 1.6544 | 1.7923 | 1.9269 | 2.0613 | 2.7 | 2.9619 | 0.48694 | 0.59672 | 0.73798 | 0.87843 | 1.0489 | 1.2708 | 1.5718 | 1.9702 | 2.2872 | 2.6225 | 2.9367 | 3.2229 | 3.5196 | 3.8048 | 4.0832 | 4.3604 | 5.6939 | 6.273
Swansea North | New Lodge | Primary Substation | 11 | Electric Engagement | 0.2431 | 0.33758 | 0.49974 | 0.68073 | 0.85555 | 1.0922 | 1.3877 | 1.7669 | 2.1177 | 2.4222 | 2.7059 | 2.967 | 3.1093 | 3.2072 | 3.3065 | 3.4076 | 4.278 | 4.5981 | 0.54462 | 0.74725 | 1.0854 | 1.4632 | 1.8307 | 2.3282 | 2.9528 | 3.7536 | 4.4984 | 5.1478 | 5.7555 | 6.3134 | 6.6314 | 6.8469 | 7.0647 | 7.2871 | 9.1477 | 9.9017
Swansea North | New Lodge | Primary Substation | 11 | Holistic Transition | 0.25607 | 0.34533 | 0.44606 | 0.56601 | 0.71148 | 0.93278 | 1.2096 | 1.5456 | 1.7866 | 2.0578 | 2.3208 | 2.5774 | 2.8301 | 3.0498 | 3.2588 | 3.4403 | 4.2545 | 4.4991 | 0.57697 | 0.77458 | 0.99251 | 1.2565 | 1.5764 | 2.0602 | 2.6657 | 3.3928 | 3.9161 | 4.5061 | 5.0685 | 5.6176 | 6.1576 | 6.6213 | 7.0627 | 7.4468 | 9.1915 | 9.7487
Swansea North | New Lodge | Primary Substation | 11 | Hydrogen Evolution | 0.23064 | 0.31319 | 0.41456 | 0.52674 | 0.66598 | 0.84009 | 1.0474 | 1.2601 | 1.4587 | 1.686 | 1.9034 | 2.1037 | 2.3001 | 2.4679 | 2.6313 | 2.7743 | 3.1939 | 3.5118 | 0.51283 | 0.68861 | 0.90313 | 1.14 | 1.4371 | 1.8084 | 2.2523 | 2.6968 | 3.1166 | 3.6033 | 4.0619 | 4.4828 | 4.8936 | 5.2418 | 5.5809 | 5.8799 | 6.8028 | 7.5287
Swansea North | Newcastle Emlyn South | Primary Substation | 11 | Counterfactual | 0.47938 | 0.51646 | 0.56173 | 0.6122 | 0.67315 | 0.76084 | 0.86192 | 1.0112 | 1.1314 | 1.2635 | 1.3904 | 1.509 | 1.635 | 1.7607 | 1.8828 | 2.007 | 2.5808 | 2.8738 | 1.1269 | 1.2049 | 1.2987 | 1.4036 | 1.5311 | 1.7148 | 1.9295 | 2.2436 | 2.5005 | 2.7861 | 3.0555 | 3.3029 | 3.5623 | 3.8214 | 4.0731 | 4.3289 | 5.5302 | 6.1685
Swansea North | Newcastle Emlyn South | Primary Substation | 11 | Electric Engagement | 0.49474 | 0.56686 | 0.69498 | 0.85266 | 1.0042 | 1.225 | 1.4868 | 1.8036 | 2.1025 | 2.3788 | 2.6528 | 2.9032 | 3.0776 | 3.216 | 3.384 | 3.5588 | 4.3993 | 4.7407 | 1.1645 | 1.3188 | 1.5858 | 1.9164 | 2.2365 | 2.6986 | 3.2463 | 3.9096 | 4.5392 | 5.1238 | 5.7057 | 6.2377 | 6.6201 | 6.9173 | 7.272 | 7.6424 | 9.4407 | 10.2358
Swansea North | Newcastle Emlyn South | Primary Substation | 11 | Holistic Transition | 0.50393 | 0.57062 | 0.64274 | 0.73927 | 0.85007 | 1.0309 | 1.2303 | 1.4903 | 1.7258 | 1.9941 | 2.2559 | 2.4987 | 2.7368 | 2.944 | 3.1747 | 3.39 | 4.1565 | 4.4142 | 1.1874 | 1.3354 | 1.4914 | 1.7052 | 1.9503 | 2.3378 | 2.7678 | 3.3249 | 3.8324 | 4.4128 | 4.97 | 5.4886 | 5.997 | 6.4324 | 6.9142 | 7.3643 | 9.0059 | 9.5777
Swansea North | Newcastle Emlyn South | Primary Substation | 11 | Hydrogen Evolution | 0.4872 | 0.54196 | 0.60479 | 0.68131 | 0.77443 | 0.90042 | 1.0427 | 1.2343 | 1.4184 | 1.6335 | 1.8383 | 2.0252 | 2.2059 | 2.3592 | 2.5249 | 2.6731 | 3.1224 | 3.4999 | 1.1447 | 1.2603 | 1.3914 | 1.5512 | 1.7483 | 2.0128 | 2.311 | 2.708 | 3.0947 | 3.5541 | 3.9849 | 4.3769 | 4.7536 | 5.0708 | 5.413 | 5.7207 | 6.6998 | 7.5431
Swansea North | Pantyffynon | Primary Substation | 11 | Counterfactual | 0.44984 | 0.53325 | 0.63277 | 0.74465 | 0.87937 | 1.0487 | 1.2522 | 1.5637 | 1.8179 | 2.1047 | 2.3904 | 2.6505 | 2.9231 | 3.1821 | 3.4341 | 3.6947 | 4.8892 | 5.3618 | 1.0608 | 1.2365 | 1.4435 | 1.6766 | 1.9587 | 2.3155 | 2.7489 | 3.4067 | 3.953 | 4.5745 | 5.1846 | 5.731 | 6.2965 | 6.8335 | 7.3559 | 7.8954 | 10.3986 | 11.4531
Swansea North | Pantyffynon | Primary Substation | 11 | Electric Engagement | 0.4935 | 0.65591 | 0.93686 | 1.2798 | 1.6106 | 2.0084 | 2.5119 | 3.1241 | 3.6899 | 4.1938 | 4.6939 | 5.1428 | 5.3746 | 5.5446 | 5.7149 | 5.8815 | 6.7984 | 7.3664 | 1.1665 | 1.5143 | 2.0976 | 2.813 | 3.5083 | 4.3444 | 5.4102 | 6.7026 | 7.9063 | 8.9878 | 10.0679 | 11.0348 | 11.5626 | 11.9442 | 12.3254 | 12.7003 | 14.7713 | 16.1247
Swansea North | Pantyffynon | Primary Substation | 11 | Holistic Transition | 0.52335 | 0.67486 | 0.83435 | 1.0427 | 1.2803 | 1.6224 | 2.0164 | 2.5476 | 3.0175 | 3.5588 | 4.0594 | 4.5208 | 4.9724 | 5.3633 | 5.7314 | 6.0387 | 6.9478 | 7.3714 | 1.2408 | 1.5768 | 1.9209 | 2.3798 | 2.9024 | 3.6534 | 4.5192 | 5.6714 | 6.7007 | 7.8878 | 8.9682 | 9.963 | 10.9342 | 11.7645 | 12.5464 | 13.2013 | 15.2393 | 16.2138
Swansea North | Pantyffynon | Primary Substation | 11 | Hydrogen Evolution | 0.47049 | 0.58866 | 0.72563 | 0.89342 | 1.0984 | 1.3544 | 1.6747 | 2.0962 | 2.4939 | 2.9537 | 3.3705 | 3.7594 | 4.1395 | 4.4548 | 4.7638 | 5.0317 | 5.733 | 6.2883 | 1.1082 | 1.3579 | 1.6446 | 1.9966 | 2.4309 | 2.9733 | 3.6574 | 4.5442 | 5.3915 | 6.3829 | 7.2672 | 8.0903 | 8.89 | 9.5465 | 10.1894 | 10.7512 | 12.3173 | 13.6006
Swansea North | Pendine | Primary Substation | 11 | Counterfactual | 0.21281 | 0.22136 | 0.23096 | 0.24285 | 0.25956 | 0.2948 | 0.33633 | 0.39154 | 0.44158 | 0.4986 | 0.5488 | 0.58939 | 0.62855 | 0.68341 | 0.72193 | 0.76117 | 0.97437 | 1.129 | 0.48919 | 0.50771 | 0.52815 | 0.55373 | 0.59045 | 0.6665 | 0.75875 | 0.88105 | 0.99389 | 1.1249 | 1.2373 | 1.3259 | 1.4093 | 1.5267 | 1.6087 | 1.6922 | 2.1593 | 2.5079
Swansea North | Pendine | Primary Substation | 11 | Electric Engagement | 0.2162 | 0.23324 | 0.26357 | 0.30557 | 0.34905 | 0.5508 | 0.66328 | 0.79541 | 0.93157 | 1.0693 | 1.2168 | 1.3672 | 1.4899 | 1.592 | 1.6984 | 1.83 | 2.5031 | 2.756 | 0.49731 | 0.53488 | 0.59928 | 0.69055 | 0.7865 | 1.2022 | 1.4428 | 1.7268 | 2.0208 | 2.319 | 2.6388 | 2.9657 | 3.2354 | 3.4531 | 3.679 | 3.9564 | 5.3829 | 5.9719
Swansea North | Pendine | Primary Substation | 11 | Holistic Transition | 0.22388 | 0.24189 | 0.25821 | 0.29226 | 0.33271 | 0.42399 | 0.52306 | 0.66386 | 0.78522 | 0.92699 | 1.0586 | 1.1798 | 1.3 | 1.4016 | 1.5048 | 1.6268 | 2.1995 | 2.3643 | 0.51643 | 0.55766 | 0.59314 | 0.6721 | 0.76626 | 0.96462 | 1.1838 | 1.4955 | 1.7652 | 2.0823 | 2.3699 | 2.6358 | 2.8984 | 3.1142 | 3.3329 | 3.5896 | 4.8078 | 5.168
Swansea North | Pendine | Primary Substation | 11 | Hydrogen Evolution | 0.21461 | 0.22667 | 0.24062 | 0.25997 | 0.28814 | 0.33584 | 0.38726 | 0.46587 | 0.53506 | 0.62476 | 0.70215 | 0.76974 | 0.83508 | 0.88586 | 0.939 | 0.99901 | 1.2916 | 1.5813 | 0.4932 | 0.51942 | 0.54933 | 0.5913 | 0.65432 | 0.75781 | 0.86994 | 1.0403 | 1.1927 | 1.3954 | 1.5669 | 1.716 | 1.8582 | 1.9665 | 2.0796 | 2.2072 | 2.8529 | 3.5031
Swansea North | Pont Ar Annell | Primary Substation | 11 | Counterfactual | 0.093079 | 0.10557 | 0.11825 | 0.13318 | 0.15446 | 0.19764 | 0.2488 | 0.31678 | 0.37825 | 0.44876 | 0.51111 | 0.56105 | 0.61095 | 0.65915 | 0.70591 | 0.75568 | 1.0159 | 1.2117 | 0.22622 | 0.25371 | 0.28078 | 0.31297 | 0.35963 | 0.45287 | 0.5664 | 0.71676 | 0.8551 | 1.0166 | 1.1558 | 1.2642 | 1.3698 | 1.4722 | 1.5716 | 1.677 | 2.2425 | 2.6791
Swansea North | Pont Ar Annell | Primary Substation | 11 | Electric Engagement | 0.097179 | 0.12259 | 0.15971 | 0.21063 | 0.26327 | 0.37556 | 0.50834 | 0.65922 | 0.81385 | 0.97184 | 1.1391 | 1.2905 | 1.4277 | 1.5408 | 1.6598 | 1.7854 | 2.4852 | 2.7741 | 0.23615 | 0.29358 | 0.37295 | 0.48411 | 0.60074 | 0.84037 | 1.125 | 1.4491 | 1.7825 | 2.1241 | 2.4859 | 2.8134 | 3.1135 | 3.354 | 3.6062 | 3.8721 | 5.3559 | 6.0282
Swansea North | Pont Ar Annell | Primary Substation | 11 | Holistic Transition | 0.099446 | 0.12762 | 0.1488 | 0.19079 | 0.24029 | 0.35196 | 0.4675 | 0.61014 | 0.74913 | 0.91346 | 1.063 | 1.1982 | 1.3334 | 1.4472 | 1.5659 | 1.6825 | 2.2854 | 2.4949 | 0.24182 | 0.30782 | 0.35464 | 0.45246 | 0.5682 | 0.81112 | 1.0663 | 1.3817 | 1.6903 | 2.0567 | 2.382 | 2.6779 | 2.9728 | 3.2145 | 3.466 | 3.7133 | 4.9986 | 5.4553
Swansea North | Pont Ar Annell | Primary Substation | 11 | Hydrogen Evolution | 0.095536 | 0.1132 | 0.13134 | 0.15929 | 0.19683 | 0.2581 | 0.32201 | 0.40078 | 0.49249 | 0.6053 | 0.70145 | 0.78261 | 0.86627 | 0.9261 | 0.99396 | 1.0536 | 1.3778 | 1.7215 | 0.23166 | 0.27081 | 0.30994 | 0.3702 | 0.45347 | 0.58608 | 0.72512 | 0.8947 | 1.0942 | 1.3463 | 1.5573 | 1.7354 | 1.9156 | 2.0427 | 2.1859 | 2.3131 | 3.0273 | 3.7931
Swansea North | Pontardawe | Primary Substation | 11 | Counterfactual | 0.20852 | 0.26805 | 0.34144 | 0.42582 | 0.52645 | 0.64807 | 0.79231 | 1.0103 | 1.1831 | 1.3842 | 1.5707 | 1.7461 | 1.9326 | 2.1137 | 2.2892 | 2.4667 | 3.264 | 3.5248 | 0.47429 | 0.59931 | 0.75166 | 0.92719 | 1.1374 | 1.3928 | 1.6986 | 2.1557 | 2.5238 | 2.9555 | 3.3503 | 3.7156 | 4.0992 | 4.4718 | 4.8326 | 5.1975 | 6.8605 | 7.4476
Swansea North | Pontardawe | Primary Substation | 11 | Electric Engagement | 0.24024 | 0.35639 | 0.5584 | 0.79965 | 1.0304 | 1.3202 | 1.6744 | 2.1121 | 2.509 | 2.8496 | 3.1659 | 3.4617 | 3.6101 | 3.7129 | 3.8172 | 3.9235 | 4.5068 | 4.8762 | 0.55105 | 0.79888 | 1.2175 | 1.7193 | 2.2025 | 2.8102 | 3.5524 | 4.4687 | 5.3052 | 6.0289 | 6.7058 | 7.3367 | 7.673 | 7.9035 | 8.1363 | 8.3746 | 9.6875 | 10.5675
Swansea North | Pontardawe | Primary Substation | 11 | Holistic Transition | 0.25467 | 0.35885 | 0.47483 | 0.63326 | 0.81702 | 1.0465 | 1.3051 | 1.6474 | 1.9306 | 2.2468 | 2.5554 | 2.8536 | 3.1471 | 3.4042 | 3.65 | 3.871 | 4.462 | 4.732 | 0.58681 | 0.81611 | 1.0652 | 1.4115 | 1.8128 | 2.3079 | 2.8671 | 3.5989 | 4.2098 | 4.8937 | 5.551 | 6.1869 | 6.812 | 7.3526 | 7.8699 | 8.3376 | 9.6573 | 10.2762
Swansea North | Pontardawe | Primary Substation | 11 | Hydrogen Evolution | 0.22315 | 0.3144 | 0.42229 | 0.54783 | 0.69386 | 0.86918 | 1.0758 | 1.3573 | 1.6169 | 1.8953 | 2.1643 | 2.4152 | 2.6613 | 2.8721 | 3.0761 | 3.2541 | 3.7013 | 4.0657 | 0.50783 | 0.70057 | 0.92669 | 1.1901 | 1.4989 | 1.8689 | 2.304 | 2.8892 | 3.4358 | 4.0289 | 4.594 | 5.1191 | 5.6311 | 6.0665 | 6.4881 | 6.8588 | 7.8545 | 8.6941
Swansea North | Pontyates | Primary Substation | 11 | Counterfactual | 0.077575 | 0.095058 | 0.11666 | 0.14058 | 0.17071 | 0.21179 | 0.26234 | 0.33602 | 0.39704 | 0.46569 | 0.52888 | 0.58564 | 0.64407 | 0.70241 | 0.75891 | 0.81656 | 1.091 | 1.2203 | 0.18031 | 0.21695 | 0.26191 | 0.31196 | 0.37566 | 0.46314 | 0.57258 | 0.73033 | 0.86349 | 1.0152 | 1.152 | 1.2721 | 1.3935 | 1.5151 | 1.6327 | 1.7526 | 2.3363 | 2.6297
Swansea North | Pontyates | Primary Substation | 11 | Electric Engagement | 0.086875 | 0.12041 | 0.18123 | 0.25796 | 0.33319 | 0.43404 | 0.55677 | 0.70579 | 0.84605 | 0.97469 | 1.1005 | 1.2163 | 1.2931 | 1.3473 | 1.4027 | 1.46 | 1.789 | 1.9728 | 0.20275 | 0.27426 | 0.40088 | 0.56228 | 0.72206 | 0.9357 | 1.1958 | 1.5118 | 1.8114 | 2.0886 | 2.3616 | 2.6125 | 2.7866 | 2.9068 | 3.0293 | 3.1562 | 3.8865 | 4.3251
Swansea North | Pontyates | Primary Substation | 11 | Holistic Transition | 0.09203 | 0.12283 | 0.15628 | 0.20581 | 0.26305 | 0.34729 | 0.44607 | 0.57519 | 0.69064 | 0.82417 | 0.94814 | 1.0647 | 1.1799 | 1.2754 | 1.3681 | 1.4508 | 1.7476 | 1.8668 | 0.21558 | 0.28362 | 0.35568 | 0.46633 | 0.59428 | 0.77835 | 0.99581 | 1.2779 | 1.5324 | 1.828 | 2.0971 | 2.3512 | 2.6021 | 2.806 | 3.004 | 3.1811 | 3.8413 | 4.1116
Swansea North | Pontyates | Primary Substation | 11 | Hydrogen Evolution | 0.081758 | 0.10574 | 0.13488 | 0.17139 | 0.21695 | 0.27621 | 0.34565 | 0.43469 | 0.52317 | 0.63006 | 0.72846 | 0.81745 | 0.90408 | 0.97505 | 1.0464 | 1.1099 | 1.316 | 1.5047 | 0.18987 | 0.24043 | 0.30169 | 0.37875 | 0.47654 | 0.60318 | 0.75124 | 0.93834 | 1.1275 | 1.3607 | 1.5716 | 1.7615 | 1.9449 | 2.0936 | 2.2431 | 2.3775 | 2.8425 | 3.2787
Swansea North | Ravenhill | Primary Substation | 11 | Counterfactual | 0.35431 | 0.47215 | 0.61723 | 0.77559 | 0.95279 | 1.1545 | 1.3787 | 1.7187 | 1.9772 | 2.252 | 2.5362 | 2.8265 | 3.1422 | 3.4626 | 3.7762 | 4.0868 | 5.3903 | 5.7485 | 0.81876 | 1.0652 | 1.3653 | 1.6927 | 2.0586 | 2.4748 | 2.9371 | 3.6316 | 4.1635 | 4.7298 | 5.3139 | 5.9084 | 6.5522 | 7.206 | 7.8461 | 8.4798 | 11.1494 | 11.9245
Swansea North | Ravenhill | Primary Substation | 11 | Electric Engagement | 0.44316 | 0.71081 | 1.1575 | 1.6832 | 2.1917 | 2.7461 | 3.3897 | 4.0038 | 4.5449 | 4.988 | 5.3928 | 5.788 | 5.9217 | 6.0147 | 6.1041 | 6.1919 | 6.685 | 7.0953 | 1.0276 | 1.5992 | 2.5299 | 3.6234 | 4.6869 | 5.8475 | 7.188 | 8.4421 | 9.5517 | 10.4646 | 11.3015 | 12.1182 | 12.4106 | 12.6171 | 12.8156 | 13.011 | 14.1136 | 15.0352
Swansea North | Ravenhill | Primary Substation | 11 | Holistic Transition | 0.46943 | 0.71326 | 1.0075 | 1.3436 | 1.7241 | 2.1493 | 2.6119 | 3.0693 | 3.453 | 3.85 | 4.2766 | 4.6842 | 5.0866 | 5.4628 | 5.8285 | 6.1507 | 6.6545 | 7.0941 | 1.0929 | 1.6254 | 2.2581 | 2.9806 | 3.7977 | 4.7083 | 5.6939 | 6.6422 | 7.4432 | 8.2681 | 9.1503 | 9.9932 | 10.8268 | 11.6052 | 12.365 | 13.0375 | 14.1815 | 15.1766
Swansea North | Ravenhill | Primary Substation | 11 | Hydrogen Evolution | 0.38235 | 0.54347 | 0.7342 | 0.94918 | 1.1921 | 1.4727 | 1.7974 | 2.25 | 2.6373 | 3.044 | 3.4698 | 3.8868 | 4.2916 | 4.6513 | 4.9995 | 5.3048 | 5.948 | 6.3988 | 0.88337 | 1.2224 | 1.62 | 2.0682 | 2.5745 | 3.158 | 3.8303 | 4.7584 | 5.5555 | 6.3926 | 7.2655 | 8.1205 | 8.9497 | 9.6858 | 10.3998 | 11.0278 | 12.4073 | 13.4015
Swansea North | Rhos Primary | Primary Substation | 11 | Counterfactual | 0.43746 | 0.47923 | 0.53129 | 0.59301 | 0.68043 | 0.84541 | 1.0518 | 1.336 | 1.601 | 1.9066 | 2.1684 | 2.3761 | 2.5739 | 2.7716 | 2.9626 | 3.1584 | 4.1858 | 4.9734 | 1.0005 | 1.0894 | 1.1992 | 1.3312 | 1.5226 | 1.8819 | 2.3438 | 2.977 | 3.5778 | 4.2829 | 4.8727 | 5.3295 | 5.7535 | 6.1788 | 6.5891 | 7.0085 | 9.2772 | 11.0709
Swansea North | Rhos Primary | Primary Substation | 11 | Electric Engagement | 0.45514 | 0.53874 | 0.69349 | 0.90945 | 1.1339 | 1.562 | 2.0816 | 2.7055 | 3.3373 | 3.965 | 4.6234 | 5.2299 | 5.7574 | 6.1736 | 6.5939 | 7.0445 | 9.7106 | 10.8784 | 1.0436 | 1.2246 | 1.5521 | 2.0213 | 2.5166 | 3.4373 | 4.5648 | 5.9248 | 7.3104 | 8.6935 | 10.146 | 11.4831 | 12.6681 | 13.5707 | 14.4796 | 15.4547 | 21.2274 | 23.9962
Swansea North | Rhos Primary | Primary Substation | 11 | Holistic Transition | 0.46587 | 0.5473 | 0.62918 | 0.80999 | 1.0274 | 1.4495 | 1.9236 | 2.5134 | 3.0852 | 3.7555 | 4.3536 | 4.9239 | 5.486 | 5.9564 | 6.4149 | 6.845 | 8.9917 | 9.6579 | 1.0702 | 1.2533 | 1.43 | 1.8485 | 2.3539 | 3.288 | 4.3549 | 5.6808 | 6.9731 | 8.4965 | 9.8245 | 11.0937 | 12.3405 | 13.3545 | 14.3409 | 15.2652 | 19.9318 | 21.4088
Swansea North | Rhos Primary | Primary Substation | 11 | Hydrogen Evolution | 0.44519 | 0.50537 | 0.57884 | 0.68425 | 0.83515 | 1.0687 | 1.3345 | 1.6669 | 2.0235 | 2.4856 | 2.8773 | 3.226 | 3.5508 | 3.8186 | 4.0911 | 4.3523 | 5.6472 | 6.9197 | 1.0184 | 1.1468 | 1.3036 | 1.5317 | 1.8687 | 2.38 | 2.9662 | 3.6909 | 4.4847 | 5.5384 | 6.4139 | 7.1887 | 7.9014 | 8.4771 | 9.0618 | 9.6281 | 12.5456 | 15.4619
Swansea North | Sketty Park | Primary Substation | 11 | Counterfactual | 0.34796 | 0.40302 | 0.46959 | 0.5419 | 0.62377 | 0.71314 | 0.8083 | 0.95926 | 1.0687 | 1.1853 | 1.3084 | 1.4376 | 1.5788 | 1.7219 | 1.8644 | 2.0025 | 2.6415 | 2.8208 | 0.79705 | 0.91258 | 1.0509 | 1.2012 | 1.3712 | 1.5564 | 1.7541 | 2.064 | 2.291 | 2.5336 | 2.7879 | 3.053 | 3.3411 | 3.6331 | 3.9236 | 4.2053 | 5.5129 | 5.9023
Swansea North | Sketty Park | Primary Substation | 11 | Electric Engagement | 0.37412 | 0.47835 | 0.65727 | 0.84931 | 1.0299 | 1.2404 | 1.4861 | 1.7911 | 2.0623 | 2.2975 | 2.5137 | 2.7379 | 2.8182 | 2.8756 | 2.9299 | 2.9855 | 3.3083 | 3.5955 | 0.85975 | 1.0808 | 1.4509 | 1.8463 | 2.2193 | 2.6531 | 3.1581 | 3.7825 | 4.3411 | 4.8279 | 5.2781 | 5.7441 | 5.9206 | 6.0468 | 6.1666 | 6.2893 | 7.0109 | 7.6576
Swansea North | Sketty Park | Primary Substation | 11 | Holistic Transition | 0.38631 | 0.47933 | 0.58667 | 0.68964 | 0.80546 | 0.94426 | 1.1071 | 1.3375 | 1.5363 | 1.7413 | 1.9633 | 2.1951 | 2.4296 | 2.6482 | 2.8583 | 3.0498 | 3.4149 | 3.674 | 0.89009 | 1.0925 | 1.3222 | 1.5432 | 1.7906 | 2.0845 | 2.4275 | 2.9077 | 3.325 | 3.7544 | 4.2152 | 4.6961 | 5.1832 | 5.6358 | 6.0729 | 6.4729 | 7.2892 | 7.8791
Swansea North | Sketty Park | Primary Substation | 11 | Hydrogen Evolution | 0.35929 | 0.43631 | 0.52586 | 0.62557 | 0.73616 | 0.85788 | 0.99484 | 1.1971 | 1.37 | 1.5549 | 1.7522 | 1.9424 | 2.1261 | 2.2911 | 2.4493 | 2.5881 | 2.8719 | 3.0716 | 0.82254 | 0.98424 | 1.1709 | 1.3787 | 1.6097 | 1.862 | 2.1445 | 2.5574 | 2.9137 | 3.2958 | 3.7005 | 4.0902 | 4.4654 | 4.802 | 5.1254 | 5.4102 | 6.0232 | 6.4727
Swansea North | St Clears | Primary Substation | 11 | Counterfactual | 0.41824 | 0.45471 | 0.49249 | 0.53731 | 0.60023 | 0.71207 | 0.85374 | 1.049 | 1.2263 | 1.4364 | 1.6152 | 1.7581 | 1.8952 | 2.0312 | 2.1624 | 2.2993 | 3.0443 | 3.6086 | 0.95388 | 1.0319 | 1.1119 | 1.208 | 1.346 | 1.5909 | 1.9096 | 2.3458 | 2.7495 | 3.2354 | 3.6392 | 3.9531 | 4.2462 | 4.5383 | 4.8197 | 5.1127 | 6.7549 | 8.0384
Swansea North | St Clears | Primary Substation | 11 | Electric Engagement | 0.43148 | 0.50072 | 0.61225 | 0.76983 | 0.9336 | 1.2191 | 1.5646 | 1.9764 | 2.3928 | 2.8108 | 3.2479 | 3.6442 | 3.9914 | 4.2496 | 4.5158 | 4.795 | 6.5313 | 7.3425 | 0.98603 | 1.1374 | 1.3742 | 1.7169 | 2.0787 | 2.6961 | 3.4473 | 4.3461 | 5.2602 | 6.1827 | 7.1503 | 8.0278 | 8.8125 | 9.3783 | 9.9591 | 10.5692 | 14.3508 | 16.2833
Swansea North | St Clears | Primary Substation | 11 | Holistic Transition | 0.43914 | 0.50916 | 0.56878 | 0.69687 | 0.84885 | 1.1271 | 1.4409 | 1.8377 | 2.2246 | 2.6859 | 3.0923 | 3.4732 | 3.8545 | 4.1578 | 4.4616 | 4.7393 | 6.1665 | 6.6329 | 1.0051 | 1.1637 | 1.2933 | 1.5905 | 1.9446 | 2.5622 | 3.2695 | 4.1623 | 5.0382 | 6.0875 | 6.9906 | 7.842 | 8.6914 | 9.3494 | 10.0062 | 10.6079 | 13.7287 | 14.7698
Swansea North | St Clears | Primary Substation | 11 | Hydrogen Evolution | 0.42407 | 0.47477 | 0.52778 | 0.6054 | 0.71443 | 0.87617 | 1.0552 | 1.278 | 1.5331 | 1.8645 | 2.1458 | 2.3884 | 2.6202 | 2.8005 | 2.9919 | 3.1669 | 4.0773 | 4.9478 | 0.96731 | 1.0767 | 1.1902 | 1.3579 | 1.601 | 1.9557 | 2.3494 | 2.8332 | 3.3972 | 4.1491 | 4.775 | 5.3129 | 5.8198 | 6.2079 | 6.6187 | 6.9993 | 9.0519 | 11.0574
Swansea North | Strand Swansea | Primary Substation | 11 | Counterfactual | 0.34035 | 0.4202 | 0.51954 | 0.61899 | 0.73321 | 0.86193 | 1.0099 | 1.2353 | 1.4066 | 1.5839 | 1.7703 | 1.9593 | 2.1725 | 2.3867 | 2.5986 | 2.8019 | 4.0357 | 4.2718 | 0.8106 | 0.97826 | 1.1831 | 1.3884 | 1.6235 | 1.8882 | 2.1918 | 2.6498 | 3.0005 | 3.3627 | 3.7431 | 4.1277 | 4.5602 | 4.9952 | 5.4258 | 5.8382 | 8.3332 | 8.8318
Swansea North | Strand Swansea | Primary Substation | 11 | Electric Engagement | 0.37744 | 0.52718 | 0.77999 | 1.0642 | 1.3287 | 1.619 | 1.9666 | 2.3929 | 2.7677 | 3.0706 | 3.3536 | 3.6291 | 3.7325 | 3.7922 | 3.8535 | 3.9085 | 4.2455 | 4.5394 | 0.90053 | 1.2207 | 1.7418 | 2.3258 | 2.8703 | 3.4671 | 4.1792 | 5.0491 | 5.8166 | 6.4399 | 7.0235 | 7.5911 | 7.8147 | 7.9465 | 8.0807 | 8.2026 | 8.9536 | 9.6067
Swansea North | Strand Swansea | Primary Substation | 11 | Holistic Transition | 0.39551 | 0.53178 | 0.67862 | 0.83666 | 1.0105 | 1.2122 | 1.4407 | 1.7608 | 2.0299 | 2.2989 | 2.5898 | 2.8745 | 3.1593 | 3.4254 | 3.6881 | 3.9175 | 4.3057 | 4.658 | 0.94499 | 1.2453 | 1.5599 | 1.8979 | 2.2679 | 2.6933 | 3.1715 | 3.8337 | 4.3946 | 4.9504 | 5.5495 | 6.1358 | 6.7241 | 7.2744 | 7.8196 | 8.298 | 9.1678 | 9.9561
Swansea North | Strand Swansea | Primary Substation | 11 | Hydrogen Evolution | 0.35826 | 0.46852 | 0.59859 | 0.73968 | 0.89801 | 1.6025 | 1.8162 | 2.1225 | 2.419 | 2.688 | 3.0716 | 3.3419 | 3.6058 | 3.845 | 4.0764 | 4.2745 | 4.6489 | 4.8936 | 0.85133 | 1.0839 | 1.3533 | 1.6459 | 1.9734 | 3.3941 | 3.8329 | 4.4575 | 5.0617 | 5.61 | 6.3868 | 6.9359 | 7.4716 | 7.9575 | 8.4286 | 8.8329 | 9.6241 | 10.1537
Swansea North | Swansea North Local | Primary Substation | 11 | Counterfactual | 0 | 0 | 0 | 5.7735e-05 | 0.00017845 | 0.00046713 | 0.00088177 | 0.0014171 | 0.0019525 | 0.0025088 | 0.0030442 | 0.0034536 | 0.0038577 | 0.0042042 | 0.0045506 | 0.0049547 | 0.0069702 | 0.0089279 | 0 | 0 | 0 | 0.00011547 | 0.0003884 | 0.0010287 | 0.001984 | 0.0032122 | 0.0044403 | 0.0057735 | 0.0070017 | 0.0079149 | 0.0087862 | 0.009542 | 0.010298 | 0.011169 | 0.015704 | 0.020123
Swansea North | Swansea North Local | Primary Substation | 11 | Electric Engagement | 0 | 6.2984e-05 | 0.00017845 | 0.00041989 | 0.00072431 | 0.0014066 | 0.0022149 | 0.0032069 | 0.0042461 | 0.0053484 | 0.0065136 | 0.0076158 | 0.008718 | 0.0095105 | 0.010466 | 0.011484 | 0.016964 | 0.019803 | 0 | 0.00015746 | 0.0003884 | 0.00093426 | 0.0016376 | 0.0031282 | 0.0049337 | 0.0071696 | 0.0095 | 0.011988 | 0.014633 | 0.017121 | 0.019609 | 0.021351 | 0.023419 | 0.025645 | 0.037643 | 0.044393
Swansea North | Swansea North Local | Primary Substation | 11 | Holistic Transition | 0 | 6.2984e-05 | 0.00012072 | 0.0003674 | 0.00067707 | 0.0014224 | 0.0021309 | 0.0031859 | 0.0041254 | 0.0053116 | 0.0062459 | 0.0071224 | 0.0079989 | 0.0086235 | 0.0093058 | 0.010093 | 0.014455 | 0.015835 | 0 | 0.00015746 | 0.00027293 | 0.00086078 | 0.0016061 | 0.0032542 | 0.0048917 | 0.0072851 | 0.0094476 | 0.012198 | 0.014318 | 0.016323 | 0.018328 | 0.019703 | 0.021194 | 0.022895 | 0.032437 | 0.035481
Swansea North | Swansea North Local | Primary Substation | 11 | Hydrogen Evolution | 0 | 5.7735e-05 | 0.00011547 | 0.00028868 | 0.00058785 | 0.001055 | 0.0014644 | 0.0019945 | 0.0027083 | 0.0035533 | 0.0042724 | 0.0048707 | 0.0054638 | 0.0058732 | 0.0063404 | 0.0068075 | 0.0095158 | 0.012466 | 0 | 0.00011547 | 0.00023094 | 0.00057735 | 0.0012387 | 0.0022674 | 0.0031807 | 0.0043669 | 0.0059834 | 0.0079569 | 0.0096155 | 0.011001 | 0.012345 | 0.013258 | 0.014287 | 0.015316 | 0.021488 | 0.028269
Swansea North | Swansea Trading Estate | Primary Substation | 11 | Counterfactual | 0.061299 | 0.074252 | 0.088303 | 0.10387 | 0.12344 | 0.14579 | 0.17041 | 0.20734 | 0.23568 | 0.26645 | 0.29877 | 0.33194 | 0.37093 | 0.40662 | 0.44006 | 0.47761 | 0.63646 | 0.71429 | 0.1419 | 0.16967 | 0.19893 | 0.23129 | 0.27182 | 0.31804 | 0.36884 | 0.44441 | 0.50282 | 0.56616 | 0.63249 | 0.70013 | 0.7793 | 0.85184 | 0.91993 | 0.99621 | 1.3215 | 1.4834
Swansea North | Swansea Trading Estate | Primary Substation | 11 | Electric Engagement | 0.065771 | 0.091442 | 0.12862 | 0.1723 | 0.21297 | 0.25739 | 0.31396 | 0.38053 | 0.4394 | 0.49118 | 0.53849 | 0.58494 | 0.60966 | 0.62809 | 0.64699 | 0.66493 | 0.77233 | 0.83325 | 0.15274 | 0.2088 | 0.28594 | 0.37621 | 0.46053 | 0.55241 | 0.66914 | 0.80599 | 0.92767 | 1.0353 | 1.1342 | 1.2306 | 1.2835 | 1.3232 | 1.3638 | 1.4027 | 1.6396 | 1.7771
Swansea North | Swansea Trading Estate | Primary Substation | 11 | Holistic Transition | 0.06819 | 0.093573 | 0.11735 | 0.14292 | 0.17138 | 0.21323 | 0.25361 | 0.30968 | 0.35413 | 0.40429 | 0.45521 | 0.50211 | 0.5501 | 0.59469 | 0.64314 | 0.68403 | 0.79283 | 0.88268 | 0.15858 | 0.2158 | 0.26715 | 0.32233 | 0.38341 | 0.47139 | 0.55631 | 0.67286 | 0.76608 | 0.87069 | 0.97655 | 1.0744 | 1.1749 | 1.2682 | 1.3696 | 1.4559 | 1.6962 | 1.893
Swansea North | Swansea Trading Estate | Primary Substation | 11 | Hydrogen Evolution | 0.063766 | 0.082818 | 0.10307 | 0.13055 | 0.16083 | 0.19539 | 0.23327 | 0.28644 | 0.34376 | 0.39851 | 0.45086 | 0.49632 | 0.54967 | 0.5888 | 0.63557 | 0.67081 | 0.77707 | 0.86175 | 0.14743 | 0.18831 | 0.23045 | 0.28714 | 0.34959 | 0.42073 | 0.49866 | 0.60711 | 0.72418 | 0.8363 | 0.94339 | 1.0366 | 1.1455 | 1.2258 | 1.3215 | 1.3942 | 1.6192 | 1.7987
Swansea North | Swansea Waterfront | Primary Substation | 11 | Counterfactual | 0.172 | 0.2118 | 0.24416 | 0.28006 | 0.3236 | 0.37286 | 0.42966 | 0.52031 | 0.59383 | 0.68142 | 0.76319 | 0.84612 | 0.93302 | 1.0249 | 1.1122 | 1.1955 | 1.5493 | 1.6323 | 0.36088 | 0.44303 | 0.50998 | 0.58418 | 0.67441 | 0.7764 | 0.89424 | 1.0813 | 1.2359 | 1.4207 | 1.5921 | 1.7641 | 1.9437 | 2.1337 | 2.3141 | 2.4854 | 3.211 | 3.3921
Swansea North | Swansea Waterfront | Primary Substation | 11 | Electric Engagement | 0.18608 | 0.25176 | 0.34318 | 0.45136 | 0.5512 | 0.66682 | 0.81794 | 1.0115 | 1.1853 | 1.3317 | 1.4623 | 1.5922 | 1.6553 | 1.6937 | 1.7285 | 1.7637 | 2.0237 | 2.164 | 0.3949 | 0.53302 | 0.7216 | 0.94514 | 1.1515 | 1.3908 | 1.707 | 2.1124 | 2.4797 | 2.7904 | 3.0671 | 3.3415 | 3.4815 | 3.5659 | 3.6431 | 3.7208 | 4.2804 | 4.5969
Swansea North | Swansea Waterfront | Primary Substation | 11 | Holistic Transition | 0.19259 | 0.25219 | 0.30585 | 0.36714 | 0.43985 | 0.53889 | 0.65435 | 0.8066 | 0.93881 | 1.0693 | 1.2048 | 1.3339 | 1.452 | 1.5626 | 1.6702 | 1.7629 | 2.079 | 2.2152 | 0.41098 | 0.53923 | 0.65468 | 0.7865 | 0.94239 | 1.1571 | 1.4082 | 1.7336 | 2.0186 | 2.2982 | 2.5849 | 2.8554 | 3.1013 | 3.3305 | 3.5542 | 3.7481 | 4.423 | 4.728
Swansea North | Swansea Waterfront | Primary Substation | 11 | Hydrogen Evolution | 0.17878 | 0.23018 | 0.27447 | 0.33137 | 0.3953 | 0.46969 | 0.56753 | 0.71006 | 0.83606 | 0.96398 | 1.0887 | 1.208 | 1.3369 | 1.435 | 1.5237 | 1.6033 | 1.8121 | 1.9239 | 0.37633 | 0.48307 | 0.5751 | 0.69433 | 0.82778 | 0.98297 | 1.1899 | 1.4892 | 1.7569 | 2.0275 | 2.2875 | 2.5367 | 2.806 | 3.007 | 3.1884 | 3.3515 | 3.7931 | 4.0419
Swansea North | Tir John Primary | Primary Substation | 6.6 | Counterfactual | 0.33814 | 0.60078 | 0.60087 | 0.60097 | 0.60127 | 0.60187 | 0.60268 | 0.6039 | 0.60502 | 0.60655 | 0.60777 | 0.60876 | 0.60965 | 0.61054 | 0.61133 | 0.61221 | 0.61828 | 0.62329 | 0.84031 | 1.4968 | 1.497 | 1.4972 | 1.4979 | 1.4992 | 1.5011 | 1.5039 | 1.5065 | 1.5101 | 1.5129 | 1.5151 | 1.517 | 1.5189 | 1.5206 | 1.5225 | 1.5358 | 1.5471
Swansea North | Tir John Primary | Primary Substation | 6.6 | Electric Engagement | 0.60058 | 0.60098 | 0.60177 | 0.60286 | 0.60395 | 0.60535 | 0.60715 | 0.60956 | 0.61197 | 0.61467 | 0.61766 | 0.62025 | 0.62247 | 0.62367 | 0.62496 | 0.62616 | 0.63295 | 0.63895 | 1.4964 | 1.4973 | 1.499 | 1.5014 | 1.5038 | 1.5069 | 1.5109 | 1.5163 | 1.5218 | 1.5278 | 1.5345 | 1.5404 | 1.5455 | 1.5483 | 1.5513 | 1.554 | 1.5701 | 1.5847
Swansea North | Tir John Primary | Primary Substation | 6.6 | Holistic Transition | 0.60068 | 0.60099 | 0.60148 | 0.60259 | 0.6038 | 0.60532 | 0.60734 | 0.60997 | 0.61251 | 0.61565 | 0.61836 | 0.62068 | 0.6228 | 0.62411 | 0.62551 | 0.62689 | 0.63247 | 0.63538 | 1.4966 | 1.4974 | 1.4984 | 1.5009 | 1.5037 | 1.5072 | 1.5118 | 1.5179 | 1.5237 | 1.5309 | 1.537 | 1.5423 | 1.5472 | 1.5501 | 1.5532 | 1.5563 | 1.5695 | 1.5762
Swansea North | Tir John Primary | Primary Substation | 6.6 | Hydrogen Evolution | 0.60058 | 0.60078 | 0.60107 | 0.60175 | 0.60264 | 0.60373 | 0.60503 | 0.60661 | 0.60861 | 0.61122 | 0.61362 | 0.61561 | 0.6175 | 0.6186 | 0.61979 | 0.62088 | 0.62598 | 0.63152 | 1.4964 | 1.4968 | 1.4974 | 1.4988 | 1.5008 | 1.5032 | 1.506 | 1.5095 | 1.5139 | 1.5198 | 1.5251 | 1.5295 | 1.5337 | 1.536 | 1.5386 | 1.541 | 1.5531 | 1.5663
Swansea North | Travellers Rest Primary | Primary Substation | 11 | Counterfactual | 0.27368 | 0.35341 | 0.44284 | 0.54299 | 0.66837 | 0.82011 | 0.99993 | 1.2719 | 1.4899 | 1.7342 | 1.9695 | 2.1951 | 2.4566 | 2.6835 | 2.9023 | 3.1256 | 4.1047 | 4.4413 | 0.63302 | 0.8008 | 0.98659 | 1.1951 | 1.4582 | 1.7777 | 2.1599 | 2.7314 | 3.1969 | 3.723 | 4.2222 | 4.6932 | 5.2344 | 5.702 | 6.1527 | 6.6125 | 8.6621 | 9.4216
Swansea North | Travellers Rest Primary | Primary Substation | 11 | Electric Engagement | 0.31235 | 0.46025 | 0.71242 | 1.0241 | 1.3162 | 1.666 | 2.093 | 2.6149 | 3.0925 | 3.508 | 3.9037 | 4.2847 | 4.5008 | 4.6327 | 4.7669 | 4.9041 | 5.6527 | 6.1288 | 0.72654 | 1.043 | 1.5662 | 2.2192 | 2.8324 | 3.5668 | 4.4621 | 5.5552 | 6.5627 | 7.4479 | 8.2973 | 9.114 | 9.6035 | 9.8999 | 10.2005 | 10.5083 | 12.1951 | 13.3314
Swansea North | Travellers Rest Primary | Primary Substation | 11 | Holistic Transition | 0.33055 | 0.4665 | 0.61052 | 0.78893 | 0.99462 | 1.2718 | 1.5824 | 2.0062 | 2.3774 | 2.795 | 3.1977 | 3.5754 | 3.9424 | 4.2493 | 4.5451 | 4.8103 | 5.5613 | 5.9119 | 0.7717 | 1.0719 | 1.384 | 1.7758 | 2.2266 | 2.8254 | 3.4984 | 4.4069 | 5.2108 | 6.1177 | 6.9791 | 7.7893 | 8.5758 | 9.2237 | 9.8486 | 10.4122 | 12.0915 | 12.8928
Swansea North | Travellers Rest Primary | Primary Substation | 11 | Hydrogen Evolution | 0.29114 | 0.40164 | 0.52403 | 0.68393 | 0.86977 | 1.086 | 1.3313 | 1.673 | 2.0038 | 2.3771 | 2.7338 | 3.0623 | 3.3877 | 3.6476 | 3.9056 | 4.1282 | 4.7187 | 5.2009 | 0.67295 | 0.90673 | 1.1629 | 1.5014 | 1.8952 | 2.3519 | 2.8678 | 3.5785 | 4.2755 | 5.0737 | 5.8264 | 6.5176 | 7.1976 | 7.7359 | 8.2703 | 8.7347 | 10.0497 | 11.1593
Swansea North | Tregaron | Primary Substation | 11 | Counterfactual | 3.6041 | 3.6251 | 3.6553 | 3.6929 | 3.7485 | 3.8489 | 3.9823 | 4.1578 | 4.3205 | 4.5077 | 4.6649 | 4.756 | 4.8444 | 4.9201 | 5.0047 | 2.0036 | 2.6085 | 3.0496 | 8.9825 | 9.0266 | 9.0902 | 9.1708 | 9.2926 | 9.5123 | 9.8117 | 10.2046 | 10.575 | 11.0092 | 11.3652 | 11.5577 | 11.7398 | 11.8906 | 12.0645 | 4.5232 | 5.8702 | 6.8874
Swansea North | Tregaron | Primary Substation | 11 | Electric Engagement | 3.6133 | 3.6559 | 3.7441 | 3.8699 | 4.0016 | 4.2591 | 4.5669 | 4.8445 | 5.1162 | 5.3762 | 5.6281 | 3.2382 | 3.4686 | 3.7215 | 3.9709 | 4.2456 | 5.7107 | 6.434 | 9.0051 | 9.096 | 9.2838 | 9.5591 | 9.8524 | 10.41 | 11.081 | 11.6583 | 12.2246 | 12.7668 | 13.285 | 7.2118 | 7.7126 | 8.2649 | 8.808 | 9.4061 | 12.6116 | 14.3386
Swansea North | Tregaron | Primary Substation | 11 | Holistic Transition | 3.6192 | 3.6584 | 3.7047 | 3.8193 | 3.9641 | 4.2184 | 4.4093 | 4.6567 | 4.864 | 5.0981 | 2.6414 | 2.9685 | 3.2864 | 3.5456 | 3.796 | 4.0531 | 5.2678 | 5.634 | 9.0198 | 9.1065 | 9.2064 | 9.4722 | 9.8086 | 10.3736 | 10.7805 | 11.3125 | 11.7533 | 12.2538 | 6.0184 | 6.7529 | 7.4636 | 8.0237 | 8.5644 | 9.1192 | 11.7868 | 12.605
Swansea North | Tregaron | Primary Substation | 11 | Hydrogen Evolution | 3.608 | 3.6434 | 3.6913 | 3.7601 | 3.8593 | 4.0119 | 4.1689 | 4.3566 | 4.4996 | 4.6788 | 4.8332 | 2.0361 | 2.1701 | 2.2773 | 2.4208 | 2.5656 | 3.3744 | 4.1322 | 8.9915 | 9.0663 | 9.1687 | 9.3183 | 9.5409 | 9.8771 | 10.224 | 10.634 | 10.9394 | 11.3319 | 11.6602 | 4.6144 | 4.8956 | 5.1127 | 5.4222 | 5.7378 | 7.6075 | 9.3631
Swansea North | Trevaughan | Primary Substation | 11 | Counterfactual | 0.6976 | 0.77365 | 0.86607 | 0.97347 | 1.103 | 1.2793 | 1.4895 | 1.8052 | 2.0664 | 2.3569 | 2.6369 | 2.901 | 3.1967 | 3.5085 | 3.799 | 4.0882 | 5.2617 | 5.8283 | 1.5241 | 1.6853 | 1.8781 | 2.1028 | 2.3762 | 2.7499 | 3.2023 | 3.8771 | 4.446 | 5.0858 | 5.6909 | 6.2514 | 6.8715 | 7.527 | 8.1364 | 8.742 | 11.2302 | 12.4951
Swansea North | Trevaughan | Primary Substation | 11 | Electric Engagement | 0.73302 | 0.88237 | 1.1358 | 1.45 | 1.7555 | 2.1846 | 2.7161 | 3.3573 | 3.9603 | 4.5097 | 5.062 | 5.6159 | 5.9954 | 6.291 | 6.602 | 7.0124 | 8.5703 | 9.3138 | 1.61 | 1.9322 | 2.4605 | 3.1208 | 3.7691 | 4.6748 | 5.8079 | 7.1721 | 8.4636 | 9.6496 | 10.8463 | 12.0471 | 12.8972 | 13.5452 | 14.2228 | 15.102 | 18.5109 | 20.2686
Swansea North | Trevaughan | Primary Substation | 11 | Holistic Transition | 0.7559 | 0.89963 | 1.0465 | 1.2558 | 1.498 | 1.8881 | 2.3267 | 2.9299 | 3.4515 | 4.0213 | 4.5711 | 5.0981 | 5.6214 | 6.0792 | 6.5303 | 7.0322 | 8.3701 | 8.8948 | 1.6666 | 1.9881 | 2.3054 | 2.7717 | 3.3115 | 4.1703 | 5.1401 | 6.4609 | 7.612 | 8.8733 | 10.0684 | 11.2143 | 12.3478 | 13.324 | 14.2842 | 15.3432 | 18.2896 | 19.4761
Swansea North | Trevaughan | Primary Substation | 11 | Hydrogen Evolution | 0.71426 | 0.82819 | 0.97124 | 1.1407 | 1.3506 | 1.615 | 1.9445 | 2.3862 | 2.7783 | 3.2229 | 3.6446 | 4.0381 | 4.4229 | 4.7532 | 5.0798 | 5.4458 | 6.332 | 7.1142 | 1.5621 | 1.8046 | 2.1063 | 2.4651 | 2.9157 | 3.4804 | 4.1916 | 5.1323 | 5.9783 | 6.952 | 7.8596 | 8.7036 | 9.5229 | 10.2173 | 10.9033 | 11.6696 | 13.6457 | 15.4309
Swansea North | Tumble | Primary Substation | 11 | Counterfactual | 0.33386 | 0.38876 | 0.45833 | 0.537 | 0.62814 | 0.74038 | 0.86983 | 1.0641 | 1.2173 | 1.3864 | 1.5485 | 1.702 | 1.8661 | 2.0301 | 2.1906 | 2.3514 | 3.0862 | 3.4022 | 0.76424 | 0.87921 | 1.0236 | 1.1871 | 1.3776 | 1.6129 | 1.8874 | 2.2949 | 2.6214 | 2.9853 | 3.3283 | 3.6479 | 3.9854 | 4.3231 | 4.6533 | 4.9839 | 6.52 | 7.2232
Swansea North | Tumble | Primary Substation | 11 | Electric Engagement | 0.36165 | 0.4656 | 0.65362 | 0.88296 | 1.1028 | 1.3798 | 1.7085 | 2.1063 | 2.4727 | 2.7974 | 3.1097 | 3.4006 | 3.5701 | 3.6978 | 3.8286 | 3.9649 | 4.8136 | 5.196 | 0.83134 | 1.0526 | 1.4428 | 1.9212 | 2.383 | 2.9616 | 3.6474 | 4.4768 | 5.2452 | 5.9315 | 6.5953 | 7.2128 | 7.5897 | 7.8682 | 8.1523 | 8.4488 | 10.2994 | 11.1978
Swansea North | Tumble | Primary Substation | 11 | Holistic Transition | 0.37693 | 0.4713 | 0.57904 | 0.71957 | 0.87494 | 1.0896 | 1.3306 | 1.6519 | 1.9348 | 2.2529 | 2.5635 | 2.8707 | 3.1922 | 3.4781 | 3.747 | 3.9704 | 4.6709 | 4.962 | 0.86944 | 1.077 | 1.309 | 1.6177 | 1.9588 | 2.4203 | 2.9406 | 3.6283 | 4.2385 | 4.9272 | 5.5886 | 6.2455 | 6.9337 | 7.538 | 8.1061 | 8.5773 | 10.1129 | 10.7704
Swansea North | Tumble | Primary Substation | 11 | Hydrogen Evolution | 0.34636 | 0.42276 | 0.51681 | 0.62789 | 0.75801 | 0.9136 | 1.09 | 1.3311 | 1.5543 | 1.812 | 2.0606 | 2.2916 | 2.5191 | 2.7317 | 2.9406 | 3.1264 | 3.6305 | 4.0292 | 0.79286 | 0.95372 | 1.1509 | 1.3843 | 1.6601 | 1.9877 | 2.3576 | 2.8574 | 3.3263 | 3.8764 | 4.399 | 4.8828 | 5.3567 | 5.7985 | 6.2329 | 6.6219 | 7.7343 | 8.6388
Swansea North | Uplands Swansea | Primary Substation | 11 | Counterfactual | 0.22231 | 0.33321 | 0.47217 | 0.61565 | 0.77791 | 0.95913 | 1.1651 | 1.4816 | 1.7056 | 1.9442 | 2.1902 | 2.4454 | 2.7316 | 3.0161 | 3.2939 | 3.5795 | 4.7625 | 5.0561 | 0.48881 | 0.72059 | 1.0071 | 1.3032 | 1.6371 | 2.0097 | 2.4321 | 3.0757 | 3.5332 | 4.0197 | 4.5209 | 5.0399 | 5.6204 | 6.1972 | 6.7604 | 7.3402 | 9.7497 | 10.3836
Swansea North | Uplands Swansea | Primary Substation | 11 | Electric Engagement | 0.28155 | 0.49392 | 0.86405 | 1.2578 | 1.6255 | 2.0238 | 2.5006 | 3.0883 | 3.6029 | 4.0179 | 4.4066 | 4.7805 | 4.9173 | 5.0869 | 5.2479 | 5.385 | 5.8309 | 6.2341 | 0.63083 | 1.0824 | 1.8461 | 2.6542 | 3.4102 | 4.2275 | 5.2018 | 6.3981 | 7.4493 | 8.3011 | 9.101 | 9.8703 | 10.1666 | 10.5395 | 10.8941 | 11.1973 | 12.1908 | 13.0841
Swansea North | Uplands Swansea | Primary Substation | 11 | Holistic Transition | 0.30653 | 0.49554 | 0.70884 | 0.91685 | 1.1482 | 1.4082 | 1.71 | 2.1383 | 2.5227 | 2.9865 | 3.4859 | 3.9248 | 4.3135 | 4.6788 | 5.0315 | 5.345 | 5.8555 | 6.3031 | 0.69279 | 1.1061 | 1.563 | 2.007 | 2.4977 | 3.0454 | 3.6759 | 4.5599 | 5.3609 | 6.331 | 7.3713 | 8.2821 | 9.0845 | 9.8385 | 10.57 | 11.2226 | 12.3666 | 13.3727
Swansea North | Uplands Swansea | Primary Substation | 11 | Hydrogen Evolution | 0.24769 | 0.39873 | 0.58023 | 0.77128 | 0.98948 | 1.2399 | 1.5326 | 1.9412 | 2.2756 | 2.6312 | 3.0169 | 3.3923 | 3.7684 | 4.1204 | 4.4406 | 4.7277 | 5.2711 | 5.6207 | 0.54668 | 0.86403 | 1.2405 | 1.6371 | 2.0889 | 2.6066 | 3.2079 | 4.0394 | 4.7213 | 5.4453 | 6.2293 | 6.9924 | 7.7579 | 8.4759 | 9.129 | 9.7158 | 10.8684 | 11.6325
Swansea North | Upper Bank | Primary Substation | 11 | Counterfactual | 0.22275 | 0.28199 | 0.35381 | 0.43088 | 0.52295 | 0.62592 | 0.73908 | 0.91746 | 1.0507 | 1.1902 | 1.3302 | 1.479 | 1.6421 | 1.8005 | 1.951 | 2.114 | 2.8432 | 2.9911 | 0.49822 | 0.62189 | 0.77034 | 0.92969 | 1.1196 | 1.3321 | 1.5659 | 1.9311 | 2.2059 | 2.4936 | 2.7816 | 3.0862 | 3.4186 | 3.7412 | 4.0469 | 4.3795 | 5.8756 | 6.1957
Swansea North | Upper Bank | Primary Substation | 11 | Electric Engagement | 0.24993 | 0.36524 | 0.56304 | 0.80958 | 1.032 | 1.2483 | 1.5061 | 1.8275 | 2.1089 | 2.3428 | 2.5513 | 2.7595 | 2.8288 | 2.9098 | 2.9883 | 3.0527 | 3.2846 | 3.4988 | 0.56391 | 0.80845 | 1.2176 | 1.7284 | 2.1903 | 2.6355 | 3.1645 | 3.8217 | 4.4 | 4.883 | 5.3157 | 5.7471 | 5.9005 | 6.0808 | 6.2555 | 6.4004 | 6.9297 | 7.4166
Swansea North | Upper Bank | Primary Substation | 11 | Holistic Transition | 0.26281 | 0.37451 | 0.50535 | 0.65358 | 0.78603 | 0.93265 | 1.1026 | 1.3433 | 1.5483 | 1.7961 | 2.0559 | 2.2949 | 2.5119 | 2.7118 | 2.9058 | 3.0776 | 3.3567 | 3.5774 | 0.59594 | 0.83899 | 1.1194 | 1.4375 | 1.7194 | 2.0298 | 2.387 | 2.8869 | 3.3164 | 3.8371 | 4.3803 | 4.8779 | 5.3277 | 5.7414 | 6.1446 | 6.5033 | 7.1366 | 7.6415
Swansea North | Upper Bank | Primary Substation | 11 | Hydrogen Evolution | 0.2354 | 0.31796 | 0.41299 | 0.52502 | 0.64957 | 0.7953 | 0.96762 | 1.1932 | 1.3879 | 1.5988 | 1.8199 | 2.0402 | 2.2714 | 2.4847 | 2.6708 | 2.8359 | 3.0929 | 3.2552 | 0.52702 | 0.70006 | 0.89779 | 1.1309 | 1.3906 | 1.6937 | 2.0509 | 2.5116 | 2.9119 | 3.3464 | 3.8005 | 4.2533 | 4.7297 | 5.1702 | 5.5527 | 5.8937 | 6.4453 | 6.8087
Swansea North | Victoria Road | Primary Substation | 11 | Counterfactual | 1.2069 | 1.3512 | 1.4324 | 1.5198 | 1.6233 | 1.7388 | 1.8704 | 2.0837 | 2.2448 | 2.4218 | 2.6108 | 2.7944 | 2.9961 | 3.1864 | 3.3728 | 3.5594 | 4.3574 | 4.5267 | 2.9708 | 3.2664 | 3.4349 | 3.6159 | 3.8298 | 4.0684 | 4.3401 | 4.7763 | 5.1089 | 5.4748 | 5.8645 | 6.2403 | 6.6512 | 7.0378 | 7.4164 | 7.7954 | 9.4236 | 9.7898
Swansea North | Victoria Road | Primary Substation | 11 | Electric Engagement | 1.3175 | 1.4532 | 1.6801 | 1.9427 | 2.1884 | 2.4628 | 2.7983 | 3.2112 | 3.5777 | 3.8775 | 4.1441 | 4.3972 | 4.473 | 4.5228 | 4.5755 | 4.6232 | 4.8803 | 5.0714 | 3.2078 | 3.4967 | 3.9656 | 4.5064 | 5.0139 | 5.5806 | 6.271 | 7.1182 | 7.8732 | 8.4944 | 9.0496 | 9.5742 | 9.7424 | 9.8559 | 9.9747 | 10.0838 | 10.6765 | 11.1226
Swansea North | Victoria Road | Primary Substation | 11 | Holistic Transition | 1.3347 | 1.4566 | 1.5871 | 1.7314 | 1.9036 | 2.1067 | 2.3323 | 2.6459 | 2.9018 | 3.1795 | 3.4554 | 3.7238 | 3.9891 | 4.237 | 4.4679 | 4.6673 | 4.9257 | 5.1512 | 3.2504 | 3.5181 | 3.7988 | 4.1091 | 4.4777 | 4.9084 | 5.3838 | 6.0372 | 6.5738 | 7.1545 | 7.7266 | 8.2839 | 8.8353 | 9.3496 | 9.8293 | 10.2457 | 10.8497 | 11.3693
Swansea North | Victoria Road | Primary Substation | 11 | Hydrogen Evolution | 1.2972 | 1.3971 | 1.5059 | 1.6373 | 1.7867 | 1.9568 | 2.1612 | 2.4536 | 2.7222 | 2.9926 | 3.2493 | 3.4926 | 3.7414 | 3.9607 | 4.173 | 4.3506 | 4.6682 | 4.8536 | 3.1564 | 3.3667 | 3.5935 | 3.8664 | 4.1769 | 4.5294 | 4.9517 | 5.5512 | 6.1052 | 6.6619 | 7.1864 | 7.6829 | 8.1901 | 8.6376 | 9.0709 | 9.4348 | 10.115 | 10.5264
Swansea North | Wern | Primary Substation | 11 | Counterfactual | 0.17868 | 0.21689 | 0.26201 | 0.3136 | 0.36824 | 0.43168 | 0.50434 | 0.60807 | 0.68618 | 0.7711 | 0.85585 | 0.94232 | 1.038 | 1.133 | 1.2254 | 1.3179 | 1.7127 | 1.8034 | 0.42831 | 0.50887 | 0.60268 | 0.7099 | 0.82346 | 0.95547 | 1.1073 | 1.3215 | 1.4847 | 1.6629 | 1.8391 | 2.017 | 2.2124 | 2.4065 | 2.5954 | 2.7842 | 3.5885 | 3.7848
Swansea North | Wern | Primary Substation | 11 | Electric Engagement | 0.19678 | 0.2686 | 0.39238 | 0.53486 | 0.66646 | 0.8092 | 0.97999 | 1.1891 | 1.3741 | 1.5302 | 1.6722 | 1.7977 | 1.8375 | 1.8682 | 1.9 | 1.9283 | 2.1093 | 2.2478 | 0.47194 | 0.62597 | 0.88332 | 1.1791 | 1.4534 | 1.7493 | 2.1024 | 2.5334 | 2.9167 | 3.2423 | 3.5401 | 3.7975 | 3.8819 | 3.9477 | 4.016 | 4.076 | 4.4756 | 4.8019
Swansea North | Wern | Primary Substation | 11 | Holistic Transition | 0.20492 | 0.27609 | 0.35642 | 0.43292 | 0.51326 | 0.61501 | 0.7222 | 0.87206 | 0.9955 | 1.1291 | 1.2626 | 1.3985 | 1.5355 | 1.6635 | 1.7879 | 1.9004 | 2.1232 | 2.2484 | 0.49207 | 0.64887 | 0.82186 | 0.98746 | 1.1606 | 1.3774 | 1.6023 | 1.9133 | 2.1705 | 2.4484 | 2.7215 | 3.0003 | 3.2828 | 3.5464 | 3.8051 | 4.0407 | 4.5425 | 4.8321
Swansea North | Wern | Primary Substation | 11 | Hydrogen Evolution | 0.18751 | 0.24043 | 0.30158 | 0.3731 | 0.4497 | 0.53908 | 0.64307 | 0.78017 | 0.89927 | 1.0299 | 1.1617 | 1.2837 | 1.4038 | 1.5104 | 1.6111 | 1.6954 | 1.8428 | 1.9423 | 0.4484 | 0.5607 | 0.68887 | 0.83883 | 0.99955 | 1.1866 | 1.4033 | 1.6846 | 1.9312 | 2.2036 | 2.476 | 2.7254 | 2.9707 | 3.1874 | 3.3923 | 3.5633 | 3.8764 | 4.0958
Swansea North | West Cross | Primary Substation | 11 | Counterfactual | 0.30338 | 0.36871 | 0.44502 | 0.52947 | 0.62469 | 0.73186 | 0.85102 | 1.0355 | 1.1695 | 1.3108 | 1.459 | 1.6168 | 1.7918 | 1.9736 | 2.152 | 2.3232 | 3.054 | 3.1958 | 0.66898 | 0.80641 | 0.96487 | 1.1399 | 1.3367 | 1.5578 | 1.803 | 2.1785 | 2.4532 | 2.7424 | 3.0454 | 3.3671 | 3.7228 | 4.0926 | 4.4559 | 4.8035 | 6.2902 | 6.5991
Swansea North | West Cross | Primary Substation | 11 | Electric Engagement | 0.34026 | 0.46672 | 0.68407 | 0.93217 | 1.1633 | 1.4141 | 1.7136 | 2.0804 | 2.4044 | 2.6701 | 2.9063 | 3.1437 | 3.2171 | 3.2541 | 3.2906 | 3.3254 | 3.5521 | 3.7663 | 0.75792 | 1.028 | 1.4774 | 1.9884 | 2.4653 | 2.9811 | 3.5943 | 4.3417 | 5.0045 | 5.5509 | 6.0387 | 6.529 | 6.6915 | 6.7767 | 6.8606 | 6.9413 | 7.4648 | 7.9559
Swansea North | West Cross | Primary Substation | 11 | Holistic Transition | 0.35642 | 0.47069 | 0.59614 | 0.72454 | 0.86723 | 1.0295 | 1.2168 | 1.4889 | 1.7259 | 1.9581 | 2.2038 | 2.4514 | 2.7019 | 2.9344 | 3.1585 | 3.357 | 3.6934 | 3.9325 | 0.79818 | 1.0496 | 1.3199 | 1.5954 | 1.8993 | 2.2422 | 2.6348 | 3.1982 | 3.693 | 4.1739 | 4.681 | 5.1921 | 5.7106 | 6.192 | 6.6583 | 7.0731 | 7.8323 | 8.3886
Swansea North | West Cross | Primary Substation | 11 | Hydrogen Evolution | 0.32013 | 0.41141 | 0.5138 | 0.6257 | 0.75204 | 0.89748 | 1.0689 | 1.3175 | 1.5261 | 1.7492 | 1.9795 | 2.2034 | 2.4184 | 2.6163 | 2.8012 | 2.9626 | 3.2164 | 3.3631 | 0.70705 | 0.8997 | 1.1133 | 1.3461 | 1.6083 | 1.909 | 2.2613 | 2.7678 | 3.1951 | 3.6512 | 4.1201 | 4.5756 | 5.0124 | 5.4149 | 5.7919 | 6.1217 | 6.6673 | 6.9988
Swansea North | Westfa | Primary Substation | 11 | Counterfactual | 3.311 | 3.3438 | 3.3849 | 3.4327 | 3.4905 | 3.5679 | 3.6719 | 3.8243 | 3.9501 | 4.0831 | 4.2064 | 4.321 | 4.4431 | 4.5626 | 4.6786 | 4.791 | 5.2849 | 5.5262 | 8.2495 | 8.3184 | 8.4039 | 8.5035 | 8.6249 | 8.7878 | 9.0094 | 9.3358 | 9.6109 | 9.904 | 10.1716 | 10.4164 | 10.6748 | 10.9275 | 11.1725 | 11.408 | 12.4457 | 12.9829
Swansea North | Westfa | Primary Substation | 11 | Electric Engagement | 3.3285 | 3.3923 | 3.5063 | 3.6457 | 3.7805 | 3.9678 | 4.2513 | 4.578 | 4.8813 | 5.1464 | 5.3513 | 5.5362 | 5.6166 | 5.8473 | 5.9441 | 6.0446 | 6.6841 | 6.9694 | 8.2917 | 8.4278 | 8.6644 | 8.9559 | 9.2399 | 9.633 | 10.2506 | 10.9553 | 11.6129 | 12.1904 | 12.6232 | 13.0116 | 13.179 | 13.7257 | 13.9361 | 14.1549 | 15.5516 | 16.222
Swansea North | Westfa | Primary Substation | 11 | Holistic Transition | 3.3383 | 3.3972 | 3.4627 | 3.5515 | 3.6554 | 3.8725 | 4.097 | 4.3566 | 4.6416 | 4.8887 | 5.1225 | 5.3483 | 5.5761 | 5.7799 | 5.9717 | 6.1274 | 6.6264 | 6.8361 | 8.3162 | 8.4461 | 8.5872 | 8.7834 | 9.0128 | 9.5031 | 10.0003 | 10.565 | 11.2148 | 11.7642 | 12.2742 | 12.764 | 13.2537 | 13.686 | 14.0926 | 14.4219 | 15.5189 | 15.9921
Swansea North | Westfa | Primary Substation | 11 | Hydrogen Evolution | 3.319 | 3.3656 | 3.4316 | 3.5058 | 3.5973 | 3.7158 | 3.9143 | 4.1087 | 4.2921 | 4.4944 | 6.252 | 6.4266 | 6.5974 | 6.7456 | 6.8883 | 7.0159 | 7.3843 | 7.6818 | 8.2677 | 8.366 | 8.5049 | 8.6614 | 8.8567 | 9.1086 | 9.549 | 9.9697 | 10.3721 | 10.8189 | 15.1511 | 15.5286 | 15.8953 | 16.2065 | 16.5053 | 16.7738 | 17.5902 | 18.2659
Swansea North | Whitland | Primary Substation | 11 | Counterfactual | 0.23974 | 0.25704 | 0.27737 | 0.30217 | 0.33766 | 0.40125 | 0.48142 | 0.59107 | 0.69158 | 0.81188 | 0.91339 | 0.99377 | 1.0715 | 1.1464 | 1.2179 | 1.2939 | 1.6966 | 1.9823 | 0.5349 | 0.57219 | 0.6154 | 0.66872 | 0.74656 | 0.88561 | 1.0655 | 1.3108 | 1.5396 | 1.8173 | 2.0466 | 2.2236 | 2.3903 | 2.5519 | 2.7059 | 2.8689 | 3.7582 | 4.4121
Swansea North | Whitland | Primary Substation | 11 | Electric Engagement | 0.24741 | 0.2821 | 0.34153 | 0.42448 | 0.51145 | 0.66837 | 0.86615 | 1.0979 | 1.3341 | 1.5715 | 1.8171 | 2.0402 | 2.235 | 2.3809 | 2.5324 | 2.7973 | 3.7089 | 4.1635 | 0.55333 | 0.62962 | 0.75613 | 0.93714 | 1.1298 | 1.4694 | 1.9017 | 2.4096 | 2.9302 | 3.4557 | 4.0005 | 4.4952 | 4.9352 | 5.2545 | 5.5844 | 6.1432 | 8.1353 | 9.2152
Swansea North | Whitland | Primary Substation | 11 | Holistic Transition | 0.25174 | 0.28732 | 0.32038 | 0.38974 | 0.4734 | 0.63922 | 0.82048 | 1.048 | 1.2651 | 1.5217 | 1.7445 | 1.9493 | 2.1513 | 2.3129 | 2.4775 | 2.7394 | 3.5019 | 3.778 | 0.56407 | 0.64537 | 0.71754 | 0.8788 | 1.0738 | 1.4429 | 1.8522 | 2.3648 | 2.8574 | 3.4417 | 3.9377 | 4.3962 | 4.846 | 5.196 | 5.551 | 6.1005 | 7.7736 | 8.3861
Swansea North | Whitland | Primary Substation | 11 | Hydrogen Evolution | 0.2433 | 0.26735 | 0.29761 | 0.3428 | 0.40549 | 0.49649 | 0.60124 | 0.72869 | 0.87806 | 1.0632 | 1.215 | 1.3447 | 1.4743 | 1.5677 | 1.6706 | 1.8162 | 2.2963 | 2.7987 | 0.54297 | 0.59507 | 0.66018 | 0.75787 | 0.89756 | 1.0972 | 1.3297 | 1.6085 | 1.9397 | 2.3609 | 2.7004 | 2.9903 | 3.2745 | 3.4763 | 3.6969 | 4.0045 | 5.0919 | 6.242
Swansea North | Ynys Street | Primary Substation | 11 | Counterfactual | 0.17713 | 0.25468 | 0.34367 | 0.44053 | 0.56482 | 0.70411 | 0.85995 | 1.1028 | 1.2908 | 1.5013 | 1.7095 | 1.9177 | 2.1369 | 2.3438 | 2.5444 | 2.7461 | 3.585 | 3.7896 | 0.39925 | 0.56143 | 0.74568 | 0.94629 | 1.2072 | 1.4974 | 1.8226 | 2.3243 | 2.7172 | 3.1596 | 3.5931 | 4.0226 | 4.4709 | 4.8933 | 5.3026 | 5.7141 | 7.4427 | 7.899
Swansea North | Ynys Street | Primary Substation | 11 | Electric Engagement | 0.21461 | 0.3589 | 0.60642 | 0.92121 | 1.1911 | 1.5081 | 1.8953 | 2.373 | 2.7954 | 3.1445 | 3.4584 | 3.7485 | 3.8647 | 3.9455 | 4.0271 | 4.1088 | 4.5512 | 4.8299 | 0.48991 | 0.79652 | 1.3082 | 1.9709 | 2.531 | 3.1895 | 3.9923 | 4.9808 | 5.8591 | 6.5897 | 7.2503 | 7.8597 | 8.1207 | 8.3021 | 8.4845 | 8.668 | 9.6645 | 10.3251
Swansea North | Ynys Street | Primary Substation | 11 | Holistic Transition | 0.23218 | 0.36272 | 0.52703 | 0.68961 | 0.89324 | 1.1351 | 1.4062 | 1.7677 | 2.0547 | 2.3689 | 2.6856 | 2.9825 | 3.275 | 3.5418 | 3.7907 | 4.0115 | 4.4994 | 4.7442 | 0.53349 | 0.81912 | 1.1791 | 1.5308 | 1.9701 | 2.487 | 3.0653 | 3.8268 | 4.4349 | 5.1013 | 5.7658 | 6.3905 | 7.0055 | 7.5621 | 8.0821 | 8.5458 | 9.6349 | 10.1989
Swansea North | Ynys Street | Primary Substation | 11 | Hydrogen Evolution | 0.19398 | 0.30015 | 0.4176 | 0.58972 | 0.76138 | 0.96315 | 1.1987 | 1.5224 | 1.7987 | 2.0966 | 2.3845 | 2.6555 | 2.9263 | 3.1623 | 3.3881 | 3.5831 | 3.9713 | 4.2427 | 0.43778 | 0.66082 | 0.90556 | 1.2759 | 1.6364 | 2.0589 | 2.5502 | 3.2179 | 3.7916 | 4.4144 | 5.0096 | 5.5685 | 6.1248 | 6.6085 | 7.0713 | 7.4731 | 8.322 | 8.9404
Swansea North | Ynysfeio | Primary Substation | 11 | Counterfactual | 0.18434 | 0.24289 | 0.31361 | 0.38685 | 0.47184 | 0.56863 | 0.67815 | 0.85102 | 0.97949 | 1.1183 | 1.2598 | 1.4048 | 1.5668 | 1.8042 | 2.0461 | 2.2016 | 2.8622 | 3.01 | 0.42993 | 0.55329 | 0.69994 | 0.8518 | 1.0277 | 1.228 | 1.4548 | 1.8091 | 2.0749 | 2.3626 | 2.654 | 2.9507 | 3.2805 | 3.7724 | 4.2745 | 4.5909 | 5.9424 | 6.2637
Swansea North | Ynysfeio | Primary Substation | 11 | Electric Engagement | 0.21243 | 0.32457 | 0.51624 | 0.73603 | 0.94193 | 1.1715 | 1.4488 | 1.786 | 2.0801 | 2.3228 | 2.5392 | 2.7593 | 2.9869 | 3.0384 | 3.0898 | 3.139 | 3.3794 | 3.5422 | 0.49812 | 0.73803 | 1.1339 | 1.5871 | 2.013 | 2.4871 | 3.0578 | 3.7488 | 4.3542 | 4.8563 | 5.3064 | 5.7643 | 6.2659 | 6.3813 | 6.4964 | 6.6072 | 7.1553 | 7.5389
Swansea North | Ynysfeio | Primary Substation | 11 | Holistic Transition | 0.22647 | 0.32801 | 0.43872 | 0.55723 | 0.68991 | 0.85228 | 1.0339 | 1.308 | 1.6588 | 1.8864 | 2.1218 | 2.3496 | 2.5717 | 2.7747 | 2.9656 | 3.1317 | 3.4438 | 3.6106 | 0.53284 | 0.75692 | 0.99452 | 1.2498 | 1.534 | 1.8781 | 2.2612 | 2.8345 | 3.5849 | 4.0611 | 4.5509 | 5.0252 | 5.4877 | 5.9089 | 6.3055 | 6.6524 | 7.3494 | 7.7381
Swansea North | Ynysfeio | Primary Substation | 11 | Hydrogen Evolution | 0.19627 | 0.2783 | 0.37265 | 0.47653 | 0.59556 | 0.73214 | 0.89237 | 1.2109 | 1.4847 | 1.6976 | 1.9141 | 2.1187 | 2.3245 | 2.5041 | 2.677 | 2.8234 | 3.0805 | 3.2299 | 0.45717 | 0.63052 | 0.82686 | 1.0427 | 1.29 | 1.5728 | 1.9033 | 2.568 | 3.141 | 3.5797 | 4.0234 | 4.4418 | 4.8621 | 5.2288 | 5.5819 | 5.8819 | 6.4363 | 6.7719
Upper Boat 132 & 33 | Abertysswg | Primary Substation | 11 | Counterfactual | 0.30511 | 0.36006 | 0.42195 | 0.49028 | 0.57153 | 0.67574 | 0.7916 | 0.967 | 1.1038 | 1.2526 | 1.3998 | 1.5479 | 1.7102 | 1.8707 | 2.0286 | 2.2236 | 3.1851 | 3.4283 | 0.667 | 0.78377 | 0.91242 | 1.0545 | 1.2238 | 1.441 | 1.6847 | 2.0497 | 2.3382 | 2.6543 | 2.9629 | 3.2695 | 3.6022 | 3.9316 | 4.2555 | 4.6585 | 6.6653 | 7.1987
Upper Boat 132 & 33 | Abertysswg | Primary Substation | 11 | Electric Engagement | 0.33785 | 0.44859 | 0.62119 | 0.82693 | 1.0229 | 2.0594 | 2.3551 | 2.7132 | 3.038 | 3.3231 | 3.5917 | 3.8554 | 4.0221 | 4.2379 | 4.4519 | 4.6396 | 5.2887 | 5.6829 | 0.74641 | 0.98693 | 1.3446 | 1.7717 | 2.1809 | 4.2737 | 4.8881 | 5.6311 | 6.3087 | 6.9074 | 7.475 | 8.0304 | 8.397 | 8.8683 | 9.335 | 9.7454 | 11.1573 | 12.0486
Upper Boat 132 & 33 | Abertysswg | Primary Substation | 11 | Holistic Transition | 0.35004 | 0.45043 | 0.54861 | 0.66648 | 0.80027 | 0.99115 | 1.2001 | 1.482 | 2.5455 | 2.9328 | 3.3184 | 3.6453 | 3.9059 | 4.143 | 4.3739 | 4.5829 | 5.1755 | 5.5234 | 0.7767 | 1.0009 | 1.212 | 1.4687 | 1.7592 | 2.1659 | 2.6129 | 3.2095 | 5.3746 | 6.2087 | 7.0322 | 7.7273 | 8.2759 | 8.7701 | 9.2523 | 9.6906 | 10.9851 | 11.7481
Upper Boat 132 & 33 | Abertysswg | Primary Substation | 11 | Hydrogen Evolution | 0.32352 | 0.40932 | 0.4948 | 0.59704 | 0.71622 | 0.86479 | 1.0311 | 1.2633 | 1.4764 | 1.721 | 1.9712 | 2.2307 | 2.5371 | 2.8081 | 3.0382 | 3.2187 | 3.6433 | 4.0019 | 0.70964 | 0.89512 | 1.0737 | 1.2871 | 1.5375 | 1.8481 | 2.1952 | 2.6742 | 3.1184 | 3.6349 | 4.1583 | 4.702 | 5.3458 | 5.9147 | 6.3949 | 6.7721 | 7.6942 | 8.4896
Upper Boat 132 & 33 | Caerphilly | Primary Substation | 11 | Counterfactual | 0.2543 | 0.32797 | 0.41784 | 0.5127 | 0.62418 | 0.74971 | 0.89199 | 1.113 | 1.2789 | 1.4574 | 1.641 | 1.8328 | 2.0492 | 2.2606 | 2.4641 | 2.7143 | 3.8516 | 4.0972 | 0.57159 | 0.72685 | 0.91479 | 1.1114 | 1.342 | 1.6014 | 1.8956 | 2.3481 | 2.6908 | 3.0598 | 3.4375 | 3.8296 | 4.2701 | 4.7005 | 5.1148 | 5.6285 | 7.9763 | 8.5019
Upper Boat 132 & 33 | Caerphilly | Primary Substation | 11 | Electric Engagement | 0.29156 | 0.43534 | 0.68815 | 0.96996 | 1.2355 | 1.5303 | 1.8896 | 2.3245 | 2.7057 | 3.0249 | 3.31 | 3.5928 | 3.7192 | 3.8995 | 4.075 | 4.2252 | 4.6168 | 4.8763 | 0.66178 | 0.96956 | 1.4975 | 2.0789 | 2.6286 | 3.2375 | 3.9772 | 4.8693 | 5.6542 | 6.3146 | 6.9077 | 7.4939 | 7.7715 | 8.1697 | 8.557 | 8.8896 | 9.7718 | 10.3711
Upper Boat 132 & 33 | Caerphilly | Primary Substation | 11 | Holistic Transition | 0.30908 | 0.44023 | 0.59266 | 0.74851 | 0.92285 | 1.1428 | 1.3833 | 1.7154 | 2.0053 | 2.3782 | 2.8297 | 3.21 | 3.5048 | 3.7756 | 4.0433 | 4.2762 | 4.7103 | 5.0125 | 0.70499 | 0.99449 | 1.3265 | 1.662 | 2.0352 | 2.5003 | 3.0074 | 3.6987 | 4.308 | 5.0955 | 6.0513 | 6.8512 | 7.4636 | 8.0251 | 8.5816 | 9.0683 | 10.0421 | 10.7274
Upper Boat 132 & 33 | Caerphilly | Primary Substation | 11 | Hydrogen Evolution | 0.27139 | 0.37721 | 0.50845 | 0.65143 | 0.81337 | 0.99784 | 1.2115 | 1.5163 | 1.7951 | 2.1035 | 2.4551 | 2.8092 | 3.19 | 3.448 | 3.6988 | 3.8929 | 4.2874 | 4.5568 | 0.61062 | 0.83431 | 1.1128 | 1.4097 | 1.7459 | 2.1279 | 2.5687 | 3.192 | 3.7641 | 4.4016 | 5.1311 | 5.8686 | 6.662 | 7.1925 | 7.7069 | 8.105 | 8.9494 | 9.5407
Upper Boat 132 & 33 | Creigiau | Primary Substation | 11 | Counterfactual | 0.54167 | 0.56646 | 0.66619 | 0.69712 | 0.74439 | 0.80486 | 0.87865 | 0.98392 | 1.0685 | 1.1664 | 1.2772 | 1.4018 | 1.5584 | 1.7167 | 1.8817 | 1.99 | 2.4649 | 2.8188 | 1.1427 | 1.1945 | 1.3958 | 1.46 | 1.5603 | 1.69 | 1.8494 | 2.0738 | 2.2552 | 2.4669 | 2.7018 | 2.9618 | 3.2878 | 3.6175 | 3.9618 | 4.1845 | 5.1763 | 5.9364
Upper Boat 132 & 33 | Creigiau | Primary Substation | 11 | Electric Engagement | 0.55297 | 0.66954 | 0.74843 | 0.85553 | 0.96198 | 1.1219 | 1.3094 | 1.5796 | 1.8353 | 2.0693 | 2.3539 | 2.5583 | 2.6443 | 2.7058 | 2.7644 | 2.8213 | 3.3392 | 3.5165 | 1.1704 | 1.4087 | 1.5721 | 1.8004 | 2.0301 | 2.3762 | 2.7792 | 3.3489 | 3.8928 | 4.3943 | 5.0099 | 5.4499 | 5.6418 | 5.7767 | 5.9056 | 6.0318 | 7.1826 | 7.6045
Upper Boat 132 & 33 | Creigiau | Primary Substation | 11 | Holistic Transition | 0.55945 | 0.67301 | 0.73247 | 0.82551 | 0.97333 | 1.1376 | 1.3145 | 1.562 | 1.7647 | 1.9898 | 2.1491 | 2.3288 | 2.5426 | 2.7368 | 2.9088 | 3.0064 | 3.2934 | 3.4093 | 1.1865 | 1.4212 | 1.5524 | 1.7606 | 2.0904 | 2.4543 | 2.8425 | 3.3824 | 3.826 | 4.3159 | 4.6551 | 5.0417 | 5.5037 | 5.9205 | 6.2895 | 6.4968 | 7.135 | 7.4002
Upper Boat 132 & 33 | Creigiau | Primary Substation | 11 | Hydrogen Evolution | 0.54683 | 0.65428 | 0.69104 | 0.76603 | 0.8601 | 0.97319 | 1.1053 | 1.2832 | 1.46 | 1.6577 | 1.8525 | 2.0375 | 2.2166 | 2.3716 | 2.5021 | 2.6229 | 3.0574 | 3.3212 | 1.1548 | 1.3733 | 1.4498 | 1.6129 | 1.8199 | 2.0685 | 2.356 | 2.7286 | 3.102 | 3.5236 | 3.9346 | 4.324 | 4.7 | 5.0228 | 5.2936 | 5.5463 | 6.4985 | 7.0996
Upper Boat 132 & 33 | Energlyn 33kv | Primary Substation | 11 | Counterfactual | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0028868 | 0.0080357 | 0.091988 | 0.091988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0057735 | 0.016827 | 0.19619 | 0.19619
Upper Boat 132 & 33 | Energlyn 33kv | Primary Substation | 11 | Electric Engagement | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7735e-05 | 5.7735e-05 | 5.7735e-05 | 5.7735e-05 | 0.0029445 | 0.013416 | 0.048613 | 0.082257 | 0.10596 | 0.10949 | 0.10949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00011547 | 0.00011547 | 0.00011547 | 0.00011547 | 0.005889 | 0.028343 | 0.10519 | 0.17862 | 0.23076 | 0.2385 | 0.2385
Upper Boat 132 & 33 | Energlyn 33kv | Primary Substation | 11 | Holistic Transition | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0028868 | 0.01298 | 0.050686 | 0.085028 | 0.10372 | 0.10372 | 0.10372 | 0.10372 | 0.10372 | 0.10372 | 0.10372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0057735 | 0.027975 | 0.11035 | 0.1859 | 0.22699 | 0.22699 | 0.22699 | 0.22699 | 0.22699 | 0.22699 | 0.22699
Upper Boat 132 & 33 | Energlyn 33kv | Primary Substation | 11 | Hydrogen Evolution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0028868 | 0.0053956 | 0.0089174 | 0.016024 | 0.03199 | 0.046146 | 0.063188 | 0.077344 | 0.1095 | 0.1095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0057735 | 0.011295 | 0.019032 | 0.034662 | 0.069209 | 0.10035 | 0.13727 | 0.16842 | 0.23858 | 0.23858
Upper Boat 132 & 33 | Energlyn Primary | Bulk Supply Point | 11 | Counterfactual | 0.32729 | 0.40295 | 0.49331 | 0.59266 | 1.3387 | 1.4757 | 1.6322 | 1.8733 | 2.0576 | 2.2571 | 2.4569 | 2.6587 | 2.8809 | 3.1014 | 3.3156 | 3.5761 | 4.7638 | 5.0288 | 0.73039 | 0.88914 | 1.0768 | 1.283 | 3.0988 | 3.3838 | 3.7105 | 4.2086 | 4.5938 | 5.0127 | 5.4283 | 5.8441 | 6.2984 | 6.7494 | 7.1876 | 7.7247 | 10.1952 | 10.7773
Upper Boat 132 & 33 | Energlyn Primary | Bulk Supply Point | 11 | Electric Engagement | 0.35886 | 0.50168 | 0.7511 | 1.0454 | 1.9547 | 2.2804 | 2.6724 | 3.1491 | 3.5734 | 3.9326 | 4.2626 | 4.5818 | 4.738 | 4.9263 | 5.1103 | 5.2755 | 5.8763 | 6.2215 | 0.80867 | 1.1125 | 1.6285 | 2.2373 | 4.3924 | 5.068 | 5.8792 | 6.863 | 7.7431 | 8.4932 | 9.1867 | 9.8557 | 10.2032 | 10.6203 | 11.0271 | 11.3927 | 12.7217 | 13.5272
Upper Boat 132 & 33 | Energlyn Primary | Bulk Supply Point | 11 | Holistic Transition | 0.3772 | 0.50429 | 0.64602 | 0.81039 | 1.6256 | 1.8642 | 2.1319 | 2.4986 | 2.8281 | 3.2573 | 3.6908 | 4.0739 | 4.3998 | 4.6949 | 4.9803 | 5.2354 | 5.8743 | 6.181 | 0.85423 | 1.1328 | 1.4372 | 1.7929 | 3.7669 | 4.2748 | 4.8445 | 5.6153 | 6.3152 | 7.2321 | 8.1512 | 8.9605 | 9.6449 | 10.2603 | 10.8562 | 11.3912 | 12.7979 | 13.4992
Upper Boat 132 & 33 | Energlyn Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 0.3376 | 0.44324 | 0.56513 | 0.70753 | 1.502 | 1.6957 | 1.9203 | 2.2371 | 2.5215 | 2.8644 | 3.2179 | 3.5731 | 3.9281 | 4.1949 | 4.4343 | 4.6394 | 5.1004 | 5.4235 | 0.75462 | 0.97689 | 1.2312 | 1.528 | 3.4468 | 3.8507 | 4.3172 | 4.9682 | 5.5578 | 6.2778 | 7.0157 | 7.758 | 8.4982 | 9.0486 | 9.5408 | 9.9646 | 10.9651 | 11.6949
Upper Boat 132 & 33 | Gas Yard | Primary Substation | 11 | Counterfactual | 0.41693 | 0.50417 | 0.60815 | 0.71726 | 0.84333 | 0.98454 | 1.1455 | 1.4019 | 1.591 | 1.7953 | 2.0034 | 2.2184 | 2.4578 | 2.6963 | 2.928 | 3.1584 | 4.1292 | 4.3315 | 0.99367 | 1.1772 | 1.3925 | 1.6182 | 1.8785 | 2.1701 | 2.5027 | 3.0271 | 3.4171 | 3.8393 | 4.2669 | 4.7062 | 5.193 | 5.6779 | 6.1492 | 6.6174 | 8.6002 | 9.0403
Upper Boat 132 & 33 | Gas Yard | Primary Substation | 11 | Electric Engagement | 0.46068 | 0.62838 | 0.91356 | 1.2407 | 1.5469 | 1.8814 | 2.285 | 2.7801 | 3.2082 | 3.5572 | 3.8675 | 4.1686 | 4.2513 | 4.3055 | 4.359 | 4.4051 | 4.6143 | 4.7918 | 1.0995 | 1.458 | 2.0466 | 2.7203 | 3.3529 | 4.0428 | 4.8724 | 5.886 | 6.766 | 7.4875 | 8.132 | 8.7568 | 8.9366 | 9.0577 | 9.1773 | 9.2811 | 9.7622 | 10.1823
Upper Boat 132 & 33 | Gas Yard | Primary Substation | 11 | Holistic Transition | 0.48111 | 0.63241 | 0.7945 | 0.96869 | 1.1639 | 1.3932 | 1.6545 | 2.0223 | 2.3266 | 2.6542 | 2.9762 | 3.2897 | 3.5965 | 3.88 | 4.1435 | 4.3712 | 4.6587 | 4.8649 | 1.15 | 1.4836 | 1.8312 | 2.2057 | 2.6229 | 3.1087 | 3.6596 | 4.4246 | 5.0624 | 5.7476 | 6.4101 | 7.056 | 7.6892 | 8.2741 | 8.819 | 9.2915 | 9.9436 | 10.4284
Upper Boat 132 & 33 | Gas Yard | Primary Substation | 11 | Hydrogen Evolution | 0.43745 | 0.56092 | 0.70132 | 0.85481 | 1.0297 | 1.2297 | 1.4662 | 1.8091 | 2.1 | 2.4117 | 2.7318 | 3.0379 | 3.3393 | 3.6079 | 3.8606 | 4.0767 | 4.4206 | 4.6023 | 1.0404 | 1.3011 | 1.5929 | 1.9115 | 2.2742 | 2.6878 | 3.1747 | 3.8745 | 4.4713 | 5.1125 | 5.7674 | 6.3929 | 7.0077 | 7.5554 | 8.071 | 8.5134 | 9.2559 | 9.6699
Upper Boat 132 & 33 | Ironbridge | Primary Substation | 11 | Counterfactual | 0.23838 | 0.26575 | 0.2979 | 0.33338 | 0.37816 | 0.42686 | 0.48044 | 0.56276 | 0.62391 | 0.6903 | 0.75776 | 0.82741 | 0.9064 | 0.98325 | 1.0572 | 1.1332 | 1.487 | 1.9809 | 0.56537 | 0.62292 | 0.68962 | 0.76315 | 0.85713 | 0.95836 | 1.0693 | 1.2378 | 1.3642 | 1.5015 | 1.6403 | 1.7825 | 1.9432 | 2.0995 | 2.2498 | 2.4042 | 3.1304 | 4.192
Upper Boat 132 & 33 | Ironbridge | Primary Substation | 11 | Electric Engagement | 0.25452 | 0.30779 | 0.40634 | 0.53063 | 0.63801 | 0.75506 | 0.89574 | 1.0637 | 1.2118 | 1.3363 | 1.4476 | 1.5556 | 1.6048 | 1.642 | 1.6792 | 1.7164 | 2.6486 | 2.7887 | 0.60442 | 0.71815 | 0.92526 | 1.19 | 1.4158 | 1.6613 | 1.9542 | 2.302 | 2.6102 | 2.8716 | 3.1066 | 3.3335 | 3.4446 | 3.5297 | 3.6151 | 3.7004 | 5.77 | 6.0996
Upper Boat 132 & 33 | Ironbridge | Primary Substation | 11 | Holistic Transition | 0.26274 | 0.31148 | 0.37497 | 0.43478 | 0.50101 | 0.58375 | 0.67407 | 0.7985 | 0.90144 | 1.0226 | 1.148 | 1.3762 | 1.7305 | 2.0784 | 2.3839 | 2.4754 | 2.6678 | 2.8069 | 0.62484 | 0.73243 | 0.87317 | 1.0031 | 1.146 | 1.3224 | 1.5142 | 1.7746 | 1.9921 | 2.2482 | 2.5118 | 3.0032 | 3.7738 | 4.5309 | 5.1946 | 5.388 | 5.8242 | 6.1438
Upper Boat 132 & 33 | Ironbridge | Primary Substation | 11 | Hydrogen Evolution | 0.24649 | 0.28524 | 0.33077 | 0.3947 | 0.45645 | 0.52508 | 0.60459 | 0.71778 | 0.82073 | 0.92837 | 1.0381 | 1.1409 | 1.2475 | 1.3566 | 1.4935 | 1.6166 | 2.1514 | 2.484 | 0.58417 | 0.66589 | 0.76172 | 0.89968 | 1.0293 | 1.1722 | 1.3371 | 1.5694 | 1.7815 | 2.0041 | 2.2302 | 2.4419 | 2.6608 | 2.888 | 3.1762 | 3.4369 | 4.6094 | 5.3463
Upper Boat 132 & 33 | Lady Windsor | Primary Substation | 11 | Counterfactual | 0.050109 | 0.066122 | 0.085007 | 0.10572 | 0.1302 | 0.1591 | 0.19346 | 0.2469 | 0.28826 | 0.33453 | 0.37896 | 0.42372 | 0.4721 | 0.52038 | 0.56735 | 0.6139 | 0.83285 | 0.8842 | 0.11508 | 0.14862 | 0.18781 | 0.23087 | 0.28195 | 0.34263 | 0.41548 | 0.5273 | 0.61525 | 0.71441 | 0.80822 | 0.90114 | 1.0005 | 1.0997 | 1.1962 | 1.2917 | 1.7463 | 1.8646
Upper Boat 132 & 33 | Lady Windsor | Primary Substation | 11 | Electric Engagement | 0.059882 | 0.09108 | 0.14646 | 0.21224 | 0.27507 | 0.34722 | 0.43491 | 0.54246 | 0.63923 | 0.72193 | 0.79717 | 0.87133 | 0.90279 | 0.92159 | 0.9403 | 0.95891 | 1.0542 | 1.1328 | 0.13853 | 0.20486 | 0.31956 | 0.4562 | 0.58748 | 0.73841 | 0.9215 | 1.1455 | 1.3484 | 1.5235 | 1.6843 | 1.8419 | 1.9147 | 1.9585 | 2.002 | 2.0455 | 2.2706 | 2.4615
Upper Boat 132 & 33 | Lady Windsor | Primary Substation | 11 | Holistic Transition | 0.063839 | 0.091206 | 0.12139 | 0.15831 | 0.20031 | 0.25127 | 0.31156 | 0.39527 | 0.46714 | 0.54726 | 0.62625 | 0.70644 | 0.78428 | 0.85187 | 0.91474 | 0.9702 | 1.0757 | 1.1242 | 0.14837 | 0.2083 | 0.27311 | 0.35373 | 0.44516 | 0.55523 | 0.68545 | 0.86385 | 1.0186 | 1.1917 | 1.3597 | 1.5299 | 1.6948 | 1.8363 | 1.9682 | 2.0853 | 2.3289 | 2.4449
Upper Boat 132 & 33 | Lady Windsor | Primary Substation | 11 | Hydrogen Evolution | 0.054827 | 0.077801 | 0.1043 | 0.13403 | 0.16948 | 0.21086 | 0.25956 | 0.32943 | 0.39159 | 0.46265 | 0.53252 | 0.59907 | 0.66333 | 0.71902 | 0.77129 | 0.81707 | 0.90942 | 0.97478 | 0.12581 | 0.17415 | 0.22953 | 0.29177 | 0.36652 | 0.45368 | 0.5557 | 0.70033 | 0.83077 | 0.98182 | 1.1283 | 1.2671 | 1.4005 | 1.5152 | 1.6231 | 1.7181 | 1.9266 | 2.083
Upper Boat 132 & 33 | Merthyr East Primary | Bulk Supply Point | 11 | Counterfactual | 0.67252 | 0.76724 | 0.87635 | 0.99544 | 1.1325 | 1.2931 | 1.4738 | 1.7579 | 1.9804 | 2.227 | 2.4807 | 2.7419 | 3.0296 | 3.3122 | 3.5888 | 3.9252 | 5.4466 | 5.7998 | 1.4629 | 1.6639 | 1.8915 | 2.1395 | 2.4248 | 2.7592 | 3.1368 | 3.726 | 4.1958 | 4.7204 | 5.2581 | 5.8059 | 6.4061 | 6.9953 | 7.5716 | 8.2734 | 11.435 | 12.2061
Upper Boat 132 & 33 | Merthyr East Primary | Bulk Supply Point | 11 | Electric Engagement | 0.7138 | 0.89659 | 1.1978 | 1.5518 | 1.8863 | 2.2742 | 2.7617 | 3.3646 | 3.9218 | 4.4215 | 4.8613 | 5.3041 | 5.5293 | 5.8163 | 6.1495 | 6.3897 | 7.1768 | 7.6042 | 1.5627 | 1.956 | 2.5801 | 3.3129 | 4.0084 | 4.8124 | 5.831 | 7.0898 | 8.2678 | 9.3387 | 10.2815 | 11.2291 | 11.7353 | 12.3687 | 13.0929 | 13.624 | 15.3525 | 16.3465
Upper Boat 132 & 33 | Merthyr East Primary | Bulk Supply Point | 11 | Holistic Transition | 0.7351 | 0.90451 | 1.0805 | 1.2778 | 1.5008 | 1.8069 | 2.1583 | 2.6415 | 3.1275 | 3.7775 | 4.4212 | 4.9632 | 5.3867 | 5.7716 | 6.1873 | 6.5098 | 7.3597 | 7.7521 | 1.6154 | 1.9913 | 2.3702 | 2.7974 | 3.278 | 3.9393 | 4.7002 | 5.7343 | 6.7945 | 8.2104 | 9.5994 | 10.7535 | 11.6402 | 12.4417 | 13.3047 | 13.9805 | 15.8418 | 16.7464
Upper Boat 132 & 33 | Merthyr East Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 0.69138 | 0.82639 | 0.97691 | 1.1463 | 1.3404 | 1.568 | 1.8531 | 2.2604 | 2.6497 | 3.1705 | 3.6968 | 4.2365 | 4.7441 | 5.0641 | 5.3856 | 5.6412 | 6.2717 | 6.6636 | 1.5053 | 1.7921 | 2.1067 | 2.4601 | 2.866 | 3.3401 | 3.941 | 4.7914 | 5.6201 | 6.743 | 7.8663 | 9.0207 | 10.1019 | 10.7643 | 11.4243 | 11.9529 | 13.3149 | 14.1978
Upper Boat 132 & 33 | Middle Fan | Primary Substation | 11 | Counterfactual | 0.14675 | 0.19276 | 0.23722 | 0.28699 | 0.34589 | 0.41463 | 0.49755 | 0.62505 | 0.71918 | 0.81724 | 0.91229 | 1.0032 | 1.1027 | 1.1996 | 1.294 | 1.3885 | 1.7664 | 1.8445 | 0.32417 | 0.42481 | 0.51689 | 0.61993 | 0.74191 | 0.88463 | 1.0575 | 1.3209 | 1.5172 | 1.7223 | 1.9194 | 2.1061 | 2.3092 | 2.5067 | 2.6992 | 2.8917 | 3.6693 | 3.8446
Upper Boat 132 & 33 | Middle Fan | Primary Substation | 11 | Electric Engagement | 0.16503 | 0.27045 | 0.38563 | 0.51953 | 0.6461 | 0.79451 | 0.97684 | 1.2121 | 1.4191 | 1.5847 | 1.7322 | 1.8649 | 1.9134 | 1.9451 | 1.977 | 2.0089 | 2.2224 | 2.3277 | 0.36822 | 0.60709 | 0.84483 | 1.121 | 1.3831 | 1.6913 | 2.069 | 2.5568 | 2.9881 | 3.3351 | 3.6455 | 3.924 | 4.0335 | 4.1054 | 4.1777 | 4.25 | 4.7244 | 4.9769
Upper Boat 132 & 33 | Middle Fan | Primary Substation | 11 | Holistic Transition | 0.17351 | 0.27164 | 0.33667 | 0.41412 | 0.50641 | 0.62406 | 0.75987 | 0.95871 | 1.0899 | 1.2325 | 1.3766 | 1.5072 | 1.6343 | 1.7485 | 1.8562 | 1.9509 | 2.18 | 2.2748 | 0.38931 | 0.61662 | 0.75622 | 0.92347 | 1.1222 | 1.3738 | 1.6638 | 2.0848 | 2.362 | 2.6635 | 2.9653 | 3.2396 | 3.5066 | 3.7448 | 3.9698 | 4.1686 | 4.6747 | 4.8959
Upper Boat 132 & 33 | Middle Fan | Primary Substation | 11 | Hydrogen Evolution | 0.1548 | 0.24966 | 0.31662 | 0.39044 | 0.47829 | 0.57761 | 0.69864 | 0.83843 | 0.96095 | 1.0937 | 1.2274 | 1.3518 | 1.4756 | 1.5835 | 1.6872 | 1.7761 | 1.963 | 2.0636 | 0.34255 | 0.5582 | 0.69865 | 0.85305 | 1.0376 | 1.246 | 1.4993 | 1.7857 | 2.0386 | 2.3145 | 2.59 | 2.846 | 3.1 | 3.3206 | 3.533 | 3.7157 | 4.1194 | 4.3502
Upper Boat 132 & 33 | Mill St Tonyrefail | Primary Substation | 11 | Counterfactual | 0.3241 | 0.38327 | 0.46008 | 0.54835 | 0.65485 | 0.77337 | 0.91282 | 1.1193 | 1.2879 | 1.475 | 1.6635 | 1.8894 | 2.1005 | 2.2881 | 2.473 | 2.6314 | 3.3512 | 3.5442 | 0.76274 | 0.88721 | 1.0472 | 1.231 | 1.4532 | 1.701 | 1.9944 | 2.4246 | 2.7806 | 3.1779 | 3.5749 | 4.048 | 4.4852 | 4.8722 | 5.2537 | 5.5782 | 7.0668 | 7.4976
Upper Boat 132 & 33 | Mill St Tonyrefail | Primary Substation | 11 | Electric Engagement | 0.35002 | 0.46143 | 0.6554 | 0.88505 | 1.112 | 1.3886 | 1.7151 | 2.1208 | 2.4975 | 2.8361 | 3.172 | 3.5919 | 3.7675 | 3.8585 | 3.9506 | 4.0444 | 4.5203 | 4.7948 | 0.82667 | 1.0643 | 1.4668 | 1.9436 | 2.4182 | 2.9956 | 3.6753 | 4.5193 | 5.3081 | 6.023 | 6.7374 | 7.6362 | 8.0259 | 8.2266 | 8.4293 | 8.6363 | 9.6915 | 10.3379
Upper Boat 132 & 33 | Mill St Tonyrefail | Primary Substation | 11 | Holistic Transition | 0.36457 | 0.46601 | 0.58246 | 0.72626 | 0.90166 | 1.1171 | 1.3679 | 1.7303 | 2.0889 | 2.4267 | 2.7595 | 3.076 | 3.3465 | 3.5891 | 3.8173 | 4.0221 | 4.4563 | 4.6613 | 0.8627 | 1.0853 | 1.3358 | 1.6483 | 2.0288 | 2.4907 | 3.0289 | 3.8008 | 4.5721 | 5.297 | 6.0035 | 6.6739 | 7.2426 | 7.7481 | 8.224 | 8.6528 | 9.624 | 10.0981
Upper Boat 132 & 33 | Mill St Tonyrefail | Primary Substation | 11 | Hydrogen Evolution | 0.33274 | 0.43033 | 0.55297 | 0.68237 | 0.84265 | 1.0222 | 1.2377 | 1.5437 | 1.8188 | 2.1042 | 2.3847 | 2.6059 | 2.8214 | 3.01 | 3.1884 | 3.3447 | 3.6839 | 3.9337 | 0.78301 | 0.99006 | 1.2489 | 1.5214 | 1.8614 | 2.2409 | 2.6957 | 3.336 | 3.917 | 4.523 | 5.1126 | 5.5713 | 6.0166 | 6.4041 | 6.7711 | 7.0944 | 7.8411 | 8.4128
Upper Boat 132 & 33 | Morlanga | Primary Substation | 11 | Counterfactual | 0.30184 | 0.31244 | 0.32631 | 0.34194 | 0.36629 | 0.40409 | 0.45091 | 0.51372 | 0.56489 | 0.62403 | 0.67605 | 0.72051 | 0.764 | 0.80869 | 0.85128 | 0.89344 | 1.1051 | 1.2253 | 0.70553 | 0.72757 | 0.75649 | 0.78934 | 0.84279 | 0.92656 | 1.0318 | 1.1704 | 1.2847 | 1.4188 | 1.534 | 1.6301 | 1.722 | 1.8166 | 1.9066 | 1.9958 | 2.4566 | 2.7342
Upper Boat 132 & 33 | Morlanga | Primary Substation | 11 | Electric Engagement | 0.30731 | 0.32784 | 0.36863 | 0.43449 | 0.50304 | 0.60137 | 0.70905 | 0.82819 | 0.94358 | 1.0533 | 1.1653 | 1.2671 | 1.3452 | 1.4015 | 1.4588 | 1.5193 | 1.9469 | 2.1432 | 0.7188 | 0.76212 | 0.84733 | 0.99205 | 1.1452 | 1.3624 | 1.5978 | 1.8548 | 2.1059 | 2.3468 | 2.594 | 2.8189 | 2.9978 | 3.1229 | 3.2497 | 3.384 | 4.3344 | 4.8042
Upper Boat 132 & 33 | Morlanga | Primary Substation | 11 | Holistic Transition | 0.31002 | 0.32774 | 0.35858 | 0.40814 | 0.46822 | 0.54779 | 0.62908 | 0.73391 | 0.83213 | 0.94563 | 1.0487 | 1.1452 | 1.3179 | 1.3942 | 1.468 | 1.5395 | 1.8776 | 1.9809 | 0.72553 | 0.7641 | 0.83361 | 0.94906 | 1.0893 | 1.2683 | 1.4499 | 1.6828 | 1.9029 | 2.159 | 2.3866 | 2.6004 | 3.0049 | 3.169 | 3.3279 | 3.4823 | 4.2234 | 4.4573
Upper Boat 132 & 33 | Morlanga | Primary Substation | 11 | Hydrogen Evolution | 0.30421 | 0.31921 | 0.33783 | 0.37327 | 0.42229 | 0.48592 | 0.54922 | 0.61726 | 0.68474 | 0.77211 | 0.84949 | 0.91946 | 0.98328 | 1.0374 | 1.0892 | 1.1383 | 1.3975 | 1.5906 | 0.71096 | 0.74224 | 0.78141 | 0.86133 | 0.97367 | 1.118 | 1.2588 | 1.4045 | 1.5526 | 1.749 | 1.9192 | 2.072 | 2.2101 | 2.3251 | 2.4354 | 2.5411 | 3.1363 | 3.5882
Upper Boat 132 & 33 | Mountain Ash | Primary Substation | 11 | Counterfactual | 0.22074 | 0.29248 | 0.37953 | 0.47089 | 0.58 | 0.70771 | 0.85468 | 1.0786 | 1.2489 | 1.4349 | 1.6195 | 1.808 | 2.0185 | 2.3241 | 2.6343 | 2.8363 | 3.7435 | 3.9777 | 0.50809 | 0.65972 | 0.8407 | 1.0308 | 1.2576 | 1.5246 | 1.8321 | 2.2952 | 2.6515 | 3.042 | 3.4261 | 3.814 | 4.2437 | 4.8785 | 5.5242 | 5.9364 | 7.8056 | 8.3194
Upper Boat 132 & 33 | Mountain Ash | Primary Substation | 11 | Electric Engagement | 0.25952 | 0.39998 | 0.63772 | 0.91235 | 1.1724 | 1.4726 | 1.8337 | 2.272 | 2.6588 | 2.9848 | 3.2758 | 3.5791 | 3.9324 | 4.0098 | 4.0879 | 4.1613 | 4.5482 | 4.8194 | 0.60145 | 0.90279 | 1.3952 | 1.9638 | 2.5045 | 3.1326 | 3.8815 | 4.788 | 5.5921 | 6.2746 | 6.8881 | 7.5258 | 8.309 | 8.4857 | 8.6632 | 8.8308 | 9.7237 | 10.3676
Upper Boat 132 & 33 | Mountain Ash | Primary Substation | 11 | Holistic Transition | 0.27658 | 0.40503 | 0.54285 | 0.69696 | 0.87292 | 1.0986 | 1.3489 | 1.699 | 2.0458 | 2.4236 | 2.8044 | 3.1535 | 3.4601 | 3.7351 | 3.995 | 4.2194 | 4.7002 | 4.9628 | 0.64374 | 0.92824 | 1.2251 | 1.5597 | 1.94 | 2.422 | 2.9562 | 3.694 | 4.4356 | 5.2424 | 6.0492 | 6.7874 | 7.4335 | 8.0099 | 8.5528 | 9.0245 | 10.1045 | 10.708
Upper Boat 132 & 33 | Mountain Ash | Primary Substation | 11 | Hydrogen Evolution | 0.23882 | 0.34464 | 0.46508 | 0.60543 | 0.76743 | 0.96278 | 1.1758 | 1.5426 | 1.8763 | 2.2262 | 2.5722 | 2.8557 | 3.1354 | 3.3683 | 3.606 | 3.8022 | 4.2186 | 4.491 | 0.54912 | 0.77351 | 1.0252 | 1.3176 | 1.6562 | 2.0674 | 2.5103 | 3.274 | 3.9711 | 4.7065 | 5.4291 | 6.0162 | 6.5913 | 7.0699 | 7.5589 | 7.965 | 8.8727 | 9.4884
Upper Boat 132 & 33 | Nantgarw Primary | Bulk Supply Point | 11 | Counterfactual | 0.14987 | 0.18965 | 0.23776 | 0.28744 | 0.35061 | 0.42858 | 0.51363 | 0.63916 | 0.73755 | 0.84701 | 0.9567 | 1.0678 | 1.1946 | 1.3133 | 1.4254 | 1.547 | 2.1105 | 2.3443 | 0.33574 | 0.42046 | 0.52062 | 0.62425 | 0.75624 | 0.91869 | 1.097 | 1.3574 | 1.564 | 1.7948 | 2.0236 | 2.2524 | 2.5115 | 2.7545 | 2.9841 | 3.2326 | 4.3996 | 4.8979
Upper Boat 132 & 33 | Nantgarw Primary | Bulk Supply Point | 11 | Electric Engagement | 0.16785 | 0.24607 | 0.37308 | 0.52442 | 0.66458 | 0.83383 | 1.0426 | 1.289 | 1.5114 | 1.7093 | 1.8926 | 2.074 | 2.1765 | 2.2576 | 2.341 | 2.4189 | 2.8535 | 3.0908 | 0.3791 | 0.54825 | 0.81183 | 1.1276 | 1.4202 | 1.7725 | 2.2066 | 2.718 | 3.1819 | 3.5974 | 3.9849 | 4.3657 | 4.5904 | 4.7689 | 4.9515 | 5.1214 | 6.0784 | 6.6239
Upper Boat 132 & 33 | Nantgarw Primary | Bulk Supply Point | 11 | Holistic Transition | 0.17653 | 0.25169 | 0.33339 | 0.42159 | 0.52089 | 0.67354 | 0.82497 | 1.0292 | 1.1974 | 1.3937 | 1.5908 | 1.7818 | 1.9727 | 2.1443 | 2.3177 | 2.4678 | 2.9055 | 3.1693 | 0.40036 | 0.56832 | 0.74539 | 0.93772 | 1.1533 | 1.4769 | 1.7997 | 2.2302 | 2.5883 | 3.0054 | 3.4205 | 3.8241 | 4.2282 | 4.5897 | 4.9521 | 5.2684 | 6.2288 | 6.81
Upper Boat 132 & 33 | Nantgarw Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 0.15898 | 0.21682 | 0.2842 | 0.37409 | 0.47241 | 0.59008 | 0.71739 | 0.89491 | 1.0821 | 1.2708 | 1.4497 | 1.6071 | 1.7865 | 1.9227 | 2.0801 | 2.203 | 2.5666 | 2.8581 | 0.35629 | 0.47953 | 0.62021 | 0.80823 | 1.0132 | 1.2577 | 1.5224 | 1.8879 | 2.2745 | 2.6683 | 3.039 | 3.3655 | 3.7349 | 4.0172 | 4.343 | 4.5998 | 5.3819 | 6.0157
Upper Boat 132 & 33 | Nantwen | Primary Substation | 11 | Counterfactual | 0.070405 | 0.093211 | 0.12182 | 0.15344 | 0.19098 | 0.24275 | 0.30378 | 0.39489 | 0.46845 | 0.55023 | 0.62765 | 0.69927 | 0.77406 | 0.84934 | 0.92335 | 1.0144 | 1.4408 | 1.5728 | 0.15476 | 0.20245 | 0.2619 | 0.32786 | 0.40677 | 0.51611 | 0.64688 | 0.84013 | 0.99897 | 1.1776 | 1.3435 | 1.4942 | 1.6491 | 1.8053 | 1.9587 | 2.1488 | 3.0525 | 3.3533
Upper Boat 132 & 33 | Nantwen | Primary Substation | 11 | Electric Engagement | 0.082892 | 0.12684 | 0.20775 | 0.30592 | 0.40115 | 0.52988 | 0.68561 | 0.8747 | 1.0505 | 1.2085 | 1.3638 | 1.5086 | 1.6103 | 1.7229 | 1.8351 | 1.9414 | 2.3545 | 2.5636 | 0.18503 | 0.27818 | 0.44614 | 0.65143 | 0.85225 | 1.1223 | 1.4501 | 1.848 | 2.2205 | 2.5584 | 2.8921 | 3.2035 | 3.4315 | 3.6786 | 3.9244 | 4.1572 | 5.0623 | 5.557
Upper Boat 132 & 33 | Nantwen | Primary Substation | 11 | Holistic Transition | 0.088796 | 0.12715 | 0.17051 | 0.22751 | 0.29293 | 0.39351 | 0.50845 | 0.65983 | 0.8108 | 1.0124 | 1.2088 | 1.3742 | 1.5141 | 1.6353 | 1.7518 | 1.8611 | 2.2194 | 2.352 | 0.1997 | 0.28343 | 0.37635 | 0.50223 | 0.64658 | 0.86426 | 1.1145 | 1.4411 | 1.7701 | 2.2116 | 2.6361 | 2.9934 | 3.2936 | 3.549 | 3.7946 | 4.0258 | 4.8129 | 5.113
Upper Boat 132 & 33 | Nantwen | Primary Substation | 11 | Hydrogen Evolution | 0.075811 | 0.10797 | 0.14615 | 0.18974 | 0.2437 | 0.31375 | 0.39574 | 0.5066 | 0.61178 | 0.75668 | 0.90002 | 1.0416 | 1.1771 | 1.2819 | 1.3684 | 1.4477 | 1.6869 | 1.8972 | 0.16718 | 0.23461 | 0.31457 | 0.40628 | 0.52141 | 0.66992 | 0.84395 | 1.0759 | 1.3004 | 1.6156 | 1.923 | 2.226 | 2.5143 | 2.734 | 2.9143 | 3.081 | 3.616 | 4.0993
Upper Boat 132 & 33 | Nelson | Primary Substation | 11 | Counterfactual | 0.31769 | 0.37304 | 0.4402 | 0.51344 | 0.60033 | 0.70244 | 0.82011 | 1.0024 | 1.1417 | 1.2935 | 1.4437 | 1.595 | 1.7606 | 1.9246 | 2.084 | 2.2752 | 3.1479 | 3.3708 | 0.70137 | 0.81782 | 0.95744 | 1.1096 | 1.2904 | 1.5033 | 1.75 | 2.1279 | 2.4204 | 2.7411 | 3.0547 | 3.3668 | 3.7056 | 4.0411 | 4.3675 | 4.7616 | 6.5765 | 7.0659
Upper Boat 132 & 33 | Nelson | Primary Substation | 11 | Electric Engagement | 0.3466 | 0.45489 | 0.64334 | 0.86611 | 1.077 | 1.3191 | 1.6114 | 1.9681 | 2.2851 | 2.5552 | 2.803 | 3.0438 | 3.1684 | 3.3183 | 3.4652 | 3.6995 | 4.0973 | 4.367 | 0.77152 | 1.0025 | 1.3935 | 1.856 | 2.2962 | 2.8006 | 3.408 | 4.1473 | 4.808 | 5.3756 | 5.9 | 6.4079 | 6.6874 | 7.0206 | 7.3471 | 7.8454 | 8.7492 | 9.3863
Upper Boat 132 & 33 | Nelson | Primary Substation | 11 | Holistic Transition | 0.36015 | 0.45713 | 0.56397 | 0.68873 | 0.82951 | 1.0074 | 1.2083 | 1.4836 | 1.736 | 2.0741 | 2.412 | 2.7063 | 2.9547 | 3.1769 | 3.3894 | 3.6829 | 4.1663 | 4.3894 | 0.80511 | 1.0184 | 1.2483 | 1.5194 | 1.8241 | 2.2046 | 2.6341 | 3.2155 | 3.7548 | 4.4812 | 5.2012 | 5.8254 | 6.349 | 6.8135 | 7.2584 | 7.8652 | 8.9359 | 9.4496
Upper Boat 132 & 33 | Nelson | Primary Substation | 11 | Hydrogen Evolution | 0.33072 | 0.41114 | 0.5045 | 0.61372 | 0.73997 | 0.8879 | 1.061 | 1.2999 | 1.5187 | 1.7934 | 2.0742 | 2.3546 | 2.6455 | 2.8376 | 3.0224 | 3.2331 | 3.5893 | 3.8412 | 0.7311 | 0.90053 | 1.0956 | 1.3236 | 1.5882 | 1.8974 | 2.2581 | 2.7499 | 3.2049 | 3.7849 | 4.3739 | 4.9624 | 5.5721 | 5.9675 | 6.3476 | 6.7802 | 7.5623 | 8.1375
Upper Boat 132 & 33 | Pencoed Primary | Bulk Supply Point | 11 | Counterfactual | 0.29046 | 0.33804 | 0.40393 | 0.48237 | 0.57322 | 0.68464 | 0.82041 | 1.0188 | 1.1897 | 1.385 | 1.59 | 1.8489 | 2.073 | 2.2655 | 2.4576 | 2.6056 | 3.3737 | 3.8736 | 0.67585 | 0.77623 | 0.91361 | 1.0773 | 1.2678 | 1.5026 | 1.7916 | 2.2101 | 2.5757 | 2.9972 | 3.4345 | 3.9825 | 4.4514 | 4.8525 | 5.2531 | 5.5598 | 7.1841 | 8.279
Upper Boat 132 & 33 | Pencoed Primary | Bulk Supply Point | 11 | Electric Engagement | 0.31432 | 0.40737 | 0.56821 | 0.76463 | 0.95429 | 1.2125 | 1.5156 | 1.8986 | 2.2677 | 2.6167 | 2.992 | 3.5053 | 3.7602 | 3.8994 | 4.0373 | 4.1503 | 5.1044 | 5.466 | 0.73332 | 0.93249 | 1.2663 | 1.676 | 2.0746 | 2.6176 | 3.2546 | 4.0597 | 4.8418 | 5.5877 | 6.3962 | 7.5074 | 8.0778 | 8.3942 | 8.7063 | 8.9566 | 11.0691 | 11.9197
Upper Boat 132 & 33 | Pencoed Primary | Bulk Supply Point | 11 | Holistic Transition | 0.32964 | 0.41778 | 0.51859 | 0.65616 | 0.82102 | 1.0419 | 1.3053 | 1.6871 | 2.0581 | 2.4562 | 2.8501 | 3.2744 | 3.7109 | 4.1135 | 4.4497 | 4.6513 | 5.2225 | 5.4779 | 0.77063 | 0.96445 | 1.1807 | 1.4813 | 1.8416 | 2.319 | 2.8901 | 3.7127 | 4.5184 | 5.3848 | 6.2321 | 7.1493 | 8.099 | 8.9691 | 9.6857 | 10.1101 | 11.3783 | 11.9628
Upper Boat 132 & 33 | Pencoed Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 0.30191 | 0.39329 | 0.51105 | 0.6347 | 0.78487 | 0.96716 | 1.1877 | 1.4964 | 1.7807 | 2.0949 | 2.4009 | 2.6375 | 2.8414 | 3.0991 | 3.3739 | 3.6167 | 4.1794 | 4.5197 | 0.70161 | 0.8967 | 1.146 | 1.4075 | 1.7283 | 2.1173 | 2.5877 | 3.2404 | 3.8483 | 4.5261 | 5.1795 | 5.6788 | 6.105 | 6.6542 | 7.2468 | 7.772 | 9.022 | 9.804
Upper Boat 132 & 33 | Pentrebach | Primary Substation | 11 | Counterfactual | 0.044582 | 0.064217 | 0.08697 | 0.11165 | 0.14233 | 0.17707 | 0.21822 | 0.2831 | 0.33472 | 0.39139 | 0.44844 | 0.50819 | 0.57944 | 0.65081 | 0.7165 | 0.77092 | 1.0062 | 1.0617 | 0.1017 | 0.14308 | 0.19035 | 0.24164 | 0.3055 | 0.37813 | 0.46462 | 0.59999 | 0.70924 | 0.82976 | 0.94994 | 1.0747 | 1.2228 | 1.3712 | 1.5075 | 1.6194 | 2.1068 | 2.2332
Upper Boat 132 & 33 | Pentrebach | Primary Substation | 11 | Electric Engagement | 0.055116 | 0.093095 | 0.15721 | 0.23261 | 0.30411 | 0.39225 | 0.50731 | 0.64965 | 0.77631 | 0.87841 | 0.96808 | 1.0509 | 1.0809 | 1.1022 | 1.1232 | 1.1429 | 1.2332 | 1.3158 | 0.12708 | 0.20852 | 0.3414 | 0.49779 | 0.6468 | 0.83171 | 1.0751 | 1.3746 | 1.6427 | 1.8601 | 2.052 | 2.2285 | 2.2982 | 2.3477 | 2.3965 | 2.4427 | 2.6581 | 2.8563
Upper Boat 132 & 33 | Pentrebach | Primary Substation | 11 | Holistic Transition | 0.059876 | 0.094224 | 0.13251 | 0.18132 | 0.25413 | 0.33545 | 0.42354 | 0.53294 | 0.61191 | 0.70174 | 0.79099 | 0.87438 | 0.95449 | 1.0254 | 1.0912 | 1.1492 | 1.2684 | 1.3348 | 0.13884 | 0.21477 | 0.2973 | 0.4034 | 0.56152 | 0.73965 | 0.93135 | 1.1657 | 1.3358 | 1.5295 | 1.7196 | 1.8966 | 2.0661 | 2.2151 | 2.3535 | 2.4763 | 2.7501 | 2.9067
Upper Boat 132 & 33 | Pentrebach | Primary Substation | 11 | Hydrogen Evolution | 0.049363 | 0.076809 | 0.10764 | 0.14692 | 0.19333 | 0.24653 | 0.31678 | 0.4085 | 0.48968 | 0.58198 | 0.67315 | 0.76187 | 0.84671 | 0.90856 | 0.96775 | 1.0196 | 1.1225 | 1.194 | 0.11258 | 0.17072 | 0.23519 | 0.31765 | 0.41564 | 0.52787 | 0.6777 | 0.86985 | 1.0417 | 1.2385 | 1.4307 | 1.6174 | 1.7954 | 1.9228 | 2.0449 | 2.1526 | 2.3822 | 2.5499
Upper Boat 132 & 33 | Pontyclun 132/11kV | Bulk Supply Point | 11 | Counterfactual | 8.0264 | 8.0943 | 8.1653 | 8.2433 | 8.3357 | 8.4407 | 8.5605 | 8.7605 | 8.8999 | 9.0521 | 9.2272 | 9.3872 | 9.565 | 9.7639 | 9.935 | 10.1051 | 10.8685 | 11.0787 | 19.8892 | 20.0336 | 20.1813 | 20.3431 | 20.5346 | 20.7524 | 21.0016 | 21.4198 | 21.7095 | 22.0268 | 22.3982 | 22.726 | 23.0882 | 23.5041 | 23.8537 | 24.2 | 25.7766 | 26.2299
Upper Boat 132 & 33 | Pontyclun 132/11kV | Bulk Supply Point | 11 | Electric Engagement | 8.057 | 8.192 | 8.3871 | 8.615 | 8.8297 | 9.0699 | 9.3662 | 9.7655 | 10.0796 | 10.3347 | 10.5962 | 10.8235 | 10.918 | 11.0315 | 11.0964 | 11.1596 | 11.5982 | 11.8135 | 19.9629 | 20.2571 | 20.661 | 21.1321 | 21.5774 | 22.0754 | 22.6879 | 23.5293 | 24.1795 | 24.7072 | 25.2645 | 25.7368 | 25.9412 | 26.2087 | 26.3537 | 26.4957 | 27.5129 | 28.0176
Upper Boat 132 & 33 | Pontyclun 132/11kV | Bulk Supply Point | 11 | Holistic Transition | 8.0711 | 8.1966 | 8.3109 | 8.4396 | 8.584 | 8.7705 | 8.9714 | 9.2839 | 9.511 | 9.757 | 10.0504 | 10.4241 | 10.6673 | 10.9237 | 11.1377 | 11.3214 | 11.7546 | 11.9908 | 19.9977 | 20.2793 | 20.5254 | 20.8039 | 21.1146 | 21.5107 | 21.9368 | 22.6047 | 23.0813 | 23.5972 | 24.2245 | 25.058 | 25.5671 | 26.1155 | 26.5616 | 26.9472 | 27.9227 | 28.4582
Upper Boat 132 & 33 | Pontyclun 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | 8.041 | 8.1473 | 8.2486 | 8.3662 | 8.5005 | 8.6524 | 8.828 | 9.1264 | 9.3678 | 9.6153 | 9.8903 | 10.1118 | 13.9245 | 14.1503 | 14.3521 | 14.5141 | 14.9708 | 15.2092 | 19.9223 | 20.1527 | 20.3642 | 20.6086 | 20.8877 | 21.2027 | 21.5661 | 22.1974 | 22.6951 | 23.2072 | 23.7881 | 24.2436 | 33.6691 | 34.1472 | 34.5601 | 34.8937 | 35.9114 | 36.4384
Upper Boat 132 & 33 | Swansea Road Merthyr | Primary Substation | 11 | Counterfactual | 0.1915 | 0.2219 | 0.2598 | 0.29837 | 0.34354 | 0.39727 | 0.4584 | 0.5534 | 0.62774 | 0.71067 | 0.79267 | 0.87505 | 0.96492 | 1.0534 | 1.14 | 1.2473 | 1.7414 | 1.8703 | 0.45048 | 0.51498 | 0.59366 | 0.674 | 0.76827 | 0.88068 | 1.0094 | 1.2076 | 1.3654 | 1.543 | 1.7167 | 1.8889 | 2.0751 | 2.2585 | 2.4379 | 2.6613 | 3.693 | 3.9768
Upper Boat 132 & 33 | Swansea Road Merthyr | Primary Substation | 11 | Electric Engagement | 0.20535 | 0.26478 | 0.3671 | 0.48522 | 0.59762 | 0.72739 | 0.88673 | 1.0815 | 1.2606 | 1.4185 | 1.5615 | 1.7022 | 1.7809 | 1.8779 | 1.9734 | 2.0572 | 2.2977 | 2.4668 | 0.48408 | 0.61208 | 0.82493 | 1.071 | 1.3067 | 1.578 | 1.9122 | 2.32 | 2.6992 | 3.0373 | 3.3443 | 3.6451 | 3.8228 | 4.0382 | 4.2501 | 4.4367 | 4.9813 | 5.3799
Upper Boat 132 & 33 | Swansea Road Merthyr | Primary Substation | 11 | Holistic Transition | 0.21217 | 0.26712 | 0.32685 | 0.39202 | 0.46584 | 0.56586 | 0.6798 | 0.83639 | 0.99083 | 1.1987 | 1.4032 | 1.5767 | 1.7163 | 1.8411 | 1.96 | 2.0656 | 2.3455 | 2.4839 | 0.50087 | 0.62283 | 0.75116 | 0.89329 | 1.0536 | 1.2697 | 1.5166 | 1.8522 | 2.1883 | 2.6408 | 3.0812 | 3.4518 | 3.7468 | 4.0082 | 4.2577 | 4.4803 | 5.101 | 5.4192
Upper Boat 132 & 33 | Swansea Road Merthyr | Primary Substation | 11 | Hydrogen Evolution | 0.19773 | 0.24119 | 0.29314 | 0.34902 | 0.41412 | 0.49075 | 0.58223 | 0.71231 | 0.83755 | 1.0065 | 1.1755 | 1.3454 | 1.5059 | 1.6095 | 1.7083 | 1.7934 | 1.9983 | 2.1565 | 0.46468 | 0.55701 | 0.6657 | 0.78267 | 0.91963 | 1.0803 | 1.273 | 1.5442 | 1.8099 | 2.1735 | 2.5335 | 2.8958 | 3.2364 | 3.4513 | 3.6554 | 3.8325 | 4.2846 | 4.6446
Upper Boat 132 & 33 | Talbot Green Primary | Bulk Supply Point | 11 | Counterfactual | 0.60745 | 0.76413 | 0.81536 | 0.86272 | 1.391 | 1.4546 | 1.5344 | 1.6507 | 1.739 | 1.8388 | 1.9383 | 2.052 | 2.169 | 2.2866 | 2.3967 | 2.52 | 3.0018 | 3.1365 | 1.334 | 1.6521 | 1.7603 | 1.8586 | 3.1555 | 3.2876 | 3.4568 | 3.6976 | 3.8829 | 4.0925 | 4.2996 | 4.5382 | 4.7799 | 5.0227 | 5.2502 | 5.5095 | 6.499 | 6.7909
Upper Boat 132 & 33 | Talbot Green Primary | Bulk Supply Point | 11 | Electric Engagement | 0.74149 | 1.2955 | 1.4369 | 1.5798 | 1.7142 | 1.8646 | 2.0682 | 2.2996 | 2.5059 | 2.6812 | 2.8456 | 3.0212 | 3.1101 | 3.1487 | 3.187 | 3.245 | 3.4235 | 3.8212 | 1.61 | 2.9672 | 3.2668 | 3.5619 | 3.8409 | 4.1527 | 4.5827 | 5.0631 | 5.4937 | 5.8617 | 6.2076 | 6.5828 | 6.7894 | 6.8766 | 6.963 | 7.1001 | 7.5145 | 8.3598
Upper Boat 132 & 33 | Talbot Green Primary | Bulk Supply Point | 11 | Holistic Transition | 1.2223 | 1.2966 | 1.3855 | 1.4643 | 1.5531 | 1.6639 | 1.8073 | 1.9937 | 2.1453 | 2.3167 | 2.4862 | 2.6681 | 2.8537 | 2.9963 | 3.1316 | 3.27 | 3.4968 | 3.8827 | 2.8117 | 2.9766 | 3.1731 | 3.3435 | 3.5346 | 3.7704 | 4.0827 | 4.4767 | 4.8008 | 5.1654 | 5.5227 | 5.9111 | 6.3106 | 6.6072 | 6.889 | 7.1877 | 7.6988 | 8.509
Upper Boat 132 & 33 | Talbot Green Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 0.73192 | 1.2679 | 1.3488 | 1.4207 | 1.5031 | 1.5976 | 1.7275 | 1.8943 | 2.0463 | 2.2071 | 2.3624 | 2.5259 | 2.6969 | 2.8262 | 2.9479 | 3.0711 | 3.2791 | 3.5416 | 1.5854 | 2.9027 | 3.0779 | 3.2273 | 3.399 | 3.5952 | 3.873 | 4.2179 | 4.5341 | 4.8706 | 5.1924 | 5.538 | 5.9002 | 6.1678 | 6.4169 | 6.6802 | 7.1323 | 7.6922
Upper Boat 132 & 33 | Tonypandy | Primary Substation | 11 | Counterfactual | 0.68875 | 0.78056 | 0.8918 | 1.0117 | 1.1521 | 1.3277 | 1.5115 | 1.7879 | 1.9941 | 2.2151 | 2.4423 | 2.3192 | 2.5914 | 2.8496 | 3.0982 | 3.3502 | 4.5089 | 4.7988 | 1.6381 | 1.8325 | 2.0639 | 2.3132 | 2.6041 | 2.9734 | 3.3542 | 3.9206 | 4.3466 | 4.8034 | 5.2714 | 4.8523 | 5.407 | 5.9322 | 6.4382 | 6.9503 | 9.3141 | 9.9319
Upper Boat 132 & 33 | Tonypandy | Primary Substation | 11 | Electric Engagement | 0.73514 | 0.91524 | 1.2168 | 1.5642 | 1.8896 | 2.3172 | 2.7741 | 3.3344 | 3.8273 | 4.2466 | 4.6218 | 4.639 | 4.7725 | 4.8648 | 4.9576 | 5.0457 | 5.5284 | 5.8169 | 1.7497 | 2.136 | 2.7594 | 3.4754 | 4.1483 | 5.0529 | 5.9935 | 7.1434 | 8.1588 | 9.0258 | 9.8057 | 9.6839 | 9.9749 | 10.179 | 10.3838 | 10.5793 | 11.6558 | 12.3214
Upper Boat 132 & 33 | Tonypandy | Primary Substation | 11 | Holistic Transition | 0.75745 | 0.92356 | 1.103 | 1.2979 | 1.5213 | 1.8135 | 2.1315 | 2.5692 | 2.9186 | 3.302 | 3.7008 | 3.7401 | 4.1503 | 4.5287 | 4.8731 | 5.1706 | 5.8108 | 6.1326 | 1.8049 | 2.1725 | 2.5582 | 2.9776 | 3.4557 | 4.0745 | 4.7456 | 5.6572 | 6.3888 | 7.1883 | 8.0166 | 7.9425 | 8.7998 | 9.5899 | 10.3031 | 10.9221 | 12.3247 | 13.0656
Upper Boat 132 & 33 | Tonypandy | Primary Substation | 11 | Hydrogen Evolution | 0.71102 | 0.85051 | 1.0134 | 1.1974 | 1.4078 | 1.6997 | 1.9707 | 2.3528 | 2.6959 | 3.051 | 3.4111 | 3.3739 | 3.7182 | 4.0117 | 4.3032 | 4.5442 | 5.032 | 5.3019 | 1.6884 | 1.9844 | 2.3248 | 2.7077 | 3.1457 | 3.7733 | 4.3336 | 5.1151 | 5.8192 | 6.5492 | 7.2863 | 7.0409 | 7.743 | 8.3425 | 8.9376 | 9.4316 | 10.4698 | 11.0624
Upper Boat 132 & 33 | Trethomas | Primary Substation | 11 | Counterfactual | 0.23999 | 0.27151 | 0.3095 | 0.35118 | 0.40036 | 0.45767 | 0.52372 | 0.62603 | 0.70444 | 0.78997 | 0.87533 | 0.96236 | 1.0584 | 1.1528 | 1.2448 | 1.3485 | 2.0196 | 2.13 | 0.57657 | 0.64265 | 0.72145 | 0.80789 | 0.91 | 1.0293 | 1.1675 | 1.3792 | 1.5434 | 1.7235 | 1.9014 | 2.0808 | 2.2772 | 2.4704 | 2.6584 | 2.8716 | 4.2767 | 4.5207
Upper Boat 132 & 33 | Trethomas | Primary Substation | 11 | Electric Engagement | 0.25734 | 0.31871 | 0.42563 | 0.55203 | 0.67215 | 0.81007 | 0.97788 | 1.182 | 1.3633 | 1.5172 | 1.6576 | 1.7959 | 1.859 | 1.9386 | 2.0507 | 2.2648 | 2.5028 | 2.649 | 0.61835 | 0.74902 | 0.97017 | 1.2318 | 1.4816 | 1.7682 | 2.116 | 2.5381 | 2.9149 | 3.2371 | 3.5333 | 3.8238 | 3.9654 | 4.1425 | 4.3908 | 4.8639 | 5.4016 | 5.7458
Upper Boat 132 & 33 | Trethomas | Primary Substation | 11 | Holistic Transition | 0.26511 | 0.31989 | 0.38031 | 0.45084 | 0.53076 | 0.6325 | 0.74674 | 0.90398 | 1.0443 | 1.2167 | 1.4135 | 1.6419 | 1.8656 | 2.0596 | 2.1837 | 2.2932 | 2.5383 | 2.6721 | 0.63758 | 0.75778 | 0.88749 | 1.0403 | 1.2128 | 1.4299 | 1.6736 | 2.0048 | 2.3037 | 2.6723 | 3.091 | 3.5791 | 4.057 | 4.469 | 4.7282 | 4.9581 | 5.5056 | 5.8117
Upper Boat 132 & 33 | Trethomas | Primary Substation | 11 | Hydrogen Evolution | 0.24823 | 0.2933 | 0.34515 | 0.40698 | 0.47847 | 0.56141 | 0.65768 | 0.79426 | 0.91808 | 1.0567 | 1.1981 | 1.341 | 1.5013 | 1.6444 | 1.7853 | 1.9106 | 2.2382 | 2.379 | 0.59534 | 0.69021 | 0.7984 | 0.92731 | 1.0769 | 1.25 | 1.4502 | 1.7312 | 1.9881 | 2.2788 | 2.5729 | 2.8708 | 3.2057 | 3.5047 | 3.799 | 4.0628 | 4.7815 | 5.1014
Upper Boat 132 & 33 | Upper Boat Primary | Bulk Supply Point | 11 | Counterfactual | 0.62794 | 0.72387 | 0.84713 | 0.97993 | 1.1347 | 1.3148 | 1.5289 | 1.8597 | 2.1223 | 2.4166 | 2.7354 | 3.0904 | 3.4359 | 3.7495 | 4.0586 | 4.3313 | 5.5129 | 5.7982 | 1.4839 | 1.6849 | 1.9401 | 2.2151 | 2.5356 | 2.9093 | 3.3555 | 4.0386 | 4.5871 | 5.2046 | 5.8706 | 6.6089 | 7.3206 | 7.9645 | 8.5992 | 9.1554 | 11.5893 | 12.2149
Upper Boat 132 & 33 | Upper Boat Primary | Bulk Supply Point | 11 | Electric Engagement | 0.6793 | 0.86441 | 1.1871 | 1.5609 | 1.9135 | 2.3273 | 2.8282 | 3.4554 | 4.0255 | 4.5261 | 5.0352 | 5.5682 | 5.873 | 5.9893 | 6.1047 | 6.2074 | 6.7817 | 7.1066 | 1.608 | 2.0018 | 2.6681 | 3.4397 | 4.1704 | 5.0286 | 6.0648 | 7.3617 | 8.5478 | 9.5995 | 10.6788 | 11.8103 | 12.4874 | 12.7507 | 13.0114 | 13.2423 | 14.5578 | 15.3298
Upper Boat 132 & 33 | Upper Boat Primary | Bulk Supply Point | 11 | Holistic Transition | 0.70258 | 0.8682 | 1.0539 | 1.2672 | 1.5139 | 1.8264 | 2.1918 | 2.7305 | 3.2168 | 3.7413 | 4.2734 | 4.8543 | 5.2601 | 5.626 | 5.9613 | 6.2554 | 6.8142 | 7.1066 | 1.6657 | 2.029 | 2.4271 | 2.8879 | 3.4186 | 4.0847 | 4.8632 | 6.002 | 7.0398 | 8.1592 | 9.2862 | 10.5565 | 11.4109 | 12.1765 | 12.8748 | 13.4904 | 14.7483 | 15.4257
Upper Boat 132 & 33 | Upper Boat Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 0.65187 | 0.80504 | 0.99136 | 1.1911 | 1.4241 | 1.7038 | 2.045 | 2.534 | 2.972 | 3.441 | 3.9113 | 4.2923 | 4.6587 | 4.9811 | 5.2971 | 5.5661 | 6.1192 | 6.4337 | 1.5385 | 1.8618 | 2.2519 | 2.6686 | 3.1566 | 3.7423 | 4.4561 | 5.4717 | 6.3875 | 7.3736 | 8.3554 | 9.1423 | 9.8951 | 10.5579 | 11.2098 | 11.7672 | 12.9889 | 13.7036
Upper Boat 132 & 33 | Wattstown | Primary Substation | 11 | Counterfactual | 0.074184 | 0.11324 | 0.1604 | 0.21075 | 0.26932 | 0.33625 | 0.41368 | 0.53579 | 0.62678 | 0.72556 | 0.82522 | 0.92679 | 1.0398 | 1.1582 | 1.274 | 1.3829 | 1.843 | 1.9429 | 0.16566 | 0.24743 | 0.34511 | 0.4493 | 0.57041 | 0.70888 | 0.86944 | 1.1201 | 1.3087 | 1.514 | 1.7197 | 1.9278 | 2.1581 | 2.3998 | 2.6365 | 2.8582 | 3.8012 | 4.0214
Upper Boat 132 & 33 | Wattstown | Primary Substation | 11 | Electric Engagement | 0.095583 | 0.17071 | 0.30164 | 0.61127 | 0.75456 | 0.91532 | 1.1102 | 1.3491 | 1.5584 | 1.7307 | 1.8865 | 2.0372 | 2.1048 | 2.1422 | 2.1797 | 2.2167 | 2.4026 | 2.5261 | 0.21734 | 0.377 | 0.64728 | 1.3546 | 1.651 | 1.983 | 2.3843 | 2.8747 | 3.3062 | 3.6637 | 3.9886 | 4.3026 | 4.453 | 4.5372 | 4.6213 | 4.7048 | 5.127 | 5.4188
Upper Boat 132 & 33 | Wattstown | Primary Substation | 11 | Holistic Transition | 0.10544 | 0.17176 | 0.24425 | 0.32567 | 0.41758 | 0.53062 | 0.65856 | 0.83901 | 0.99962 | 1.1624 | 1.3296 | 1.4889 | 1.644 | 1.7847 | 1.9166 | 2.0325 | 2.1947 | 2.3059 | 0.2418 | 0.38713 | 0.54279 | 0.71822 | 0.91528 | 1.1552 | 1.4257 | 1.8027 | 2.1417 | 2.4842 | 2.8331 | 3.1656 | 3.4895 | 3.7818 | 4.0561 | 4.2983 | 4.6752 | 4.9343
Upper Boat 132 & 33 | Wattstown | Primary Substation | 11 | Hydrogen Evolution | 0.083763 | 0.1392 | 0.20213 | 0.27327 | 0.35501 | 0.44987 | 0.56219 | 0.72959 | 0.87514 | 1.0257 | 1.1786 | 1.3236 | 1.4676 | 1.5942 | 1.7152 | 1.819 | 2.0048 | 2.113 | 0.18755 | 0.30407 | 0.43509 | 0.58293 | 0.75298 | 0.94968 | 1.1817 | 1.5252 | 1.8258 | 2.1374 | 2.4517 | 2.7491 | 3.0439 | 3.3025 | 3.5499 | 3.763 | 4.1661 | 4.4122
Uskmouth | Caldicot | Primary Substation | 11 | Counterfactual | 0.3376 | 0.38727 | 0.44633 | 0.51165 | 0.59219 | 0.68998 | 0.79933 | 0.96541 | 1.0934 | 1.2324 | 1.3696 | 1.5082 | 1.6608 | 1.8123 | 1.9586 | 2.1094 | 2.7703 | 2.968 | 0.78222 | 0.8865 | 1.0091 | 1.1447 | 1.3121 | 1.5158 | 1.7448 | 2.0887 | 2.3569 | 2.6498 | 2.936 | 3.222 | 3.5346 | 3.8453 | 4.145 | 4.4541 | 5.8225 | 6.2584
Uskmouth | Caldicot | Primary Substation | 11 | Electric Engagement | 0.36492 | 0.4609 | 0.63069 | 0.83419 | 1.0256 | 1.249 | 1.5146 | 1.8298 | 2.1092 | 2.3466 | 2.564 | 2.7755 | 2.8733 | 2.9474 | 3.0218 | 3.0944 | 3.478 | 3.7335 | 0.84831 | 1.0529 | 1.4047 | 1.8267 | 2.2253 | 2.691 | 3.2428 | 3.8948 | 4.476 | 4.9736 | 5.4328 | 5.8784 | 6.0981 | 6.2645 | 6.4311 | 6.5946 | 7.4563 | 8.0536
Uskmouth | Caldicot | Primary Substation | 11 | Holistic Transition | 0.37737 | 0.463 | 0.55764 | 0.66933 | 0.79438 | 0.96043 | 1.144 | 1.3931 | 1.6143 | 1.8593 | 2.1048 | 2.3363 | 2.5583 | 2.7573 | 2.9465 | 3.1135 | 3.5028 | 3.7387 | 0.87931 | 1.0676 | 1.2713 | 1.5137 | 1.784 | 2.1393 | 2.5316 | 3.0574 | 3.5292 | 4.0521 | 4.5707 | 5.0601 | 5.529 | 5.9462 | 6.3433 | 6.6956 | 7.5694 | 8.1072
Uskmouth | Caldicot | Primary Substation | 11 | Hydrogen Evolution | 0.34968 | 0.41993 | 0.49908 | 0.59448 | 0.7105 | 0.85054 | 1.0078 | 1.2293 | 1.4304 | 1.6535 | 1.8749 | 2.0828 | 2.2902 | 2.4647 | 2.6356 | 2.7816 | 3.1364 | 3.3847 | 0.8099 | 0.95792 | 1.1231 | 1.322 | 1.5653 | 1.859 | 2.187 | 2.6442 | 3.0625 | 3.531 | 3.9921 | 4.4242 | 4.8534 | 5.2135 | 5.5659 | 5.869 | 6.6437 | 7.2061
Uskmouth | Chepstow | Primary Substation | 11 | Counterfactual | 0.97506 | 1.0471 | 1.1274 | 1.2164 | 1.3215 | 1.4457 | 1.5831 | 1.7951 | 1.9532 | 2.1237 | 2.2949 | 2.4693 | 2.6633 | 2.8597 | 3.0496 | 3.237 | 4.0363 | 4.2474 | 2.3418 | 2.4932 | 2.6593 | 2.8432 | 3.0604 | 3.3173 | 3.6019 | 4.0369 | 4.3641 | 4.7182 | 5.0711 | 5.4285 | 5.8239 | 6.2246 | 6.6118 | 6.9936 | 8.6342 | 9.0934
Uskmouth | Chepstow | Primary Substation | 11 | Electric Engagement | 1.0092 | 1.1435 | 1.3701 | 1.6391 | 1.89 | 2.1752 | 2.5118 | 2.9144 | 3.2638 | 3.5545 | 3.8175 | 4.0673 | 4.1672 | 4.239 | 4.3097 | 4.4573 | 4.849 | 5.1011 | 2.4249 | 2.7118 | 3.1801 | 3.7355 | 4.2551 | 4.8457 | 5.54 | 6.3663 | 7.0859 | 7.6888 | 8.237 | 8.7567 | 8.9787 | 9.1395 | 9.2976 | 9.6491 | 10.5518 | 11.1386
Uskmouth | Chepstow | Primary Substation | 11 | Holistic Transition | 1.025 | 1.1471 | 1.2721 | 1.4159 | 1.5764 | 1.7766 | 2.0002 | 2.3041 | 2.5696 | 2.8494 | 3.2934 | 3.5644 | 3.9548 | 4.1939 | 4.4177 | 4.6178 | 4.9872 | 5.2385 | 2.464 | 2.7326 | 3.0007 | 3.31 | 3.6535 | 4.0791 | 4.5519 | 5.1864 | 5.7459 | 6.3339 | 7.3257 | 7.8921 | 8.7601 | 9.2579 | 9.7247 | 10.1442 | 10.9808 | 11.5585
Uskmouth | Chepstow | Primary Substation | 11 | Hydrogen Evolution | 0.9909 | 1.0946 | 1.2022 | 1.327 | 1.4748 | 1.651 | 1.8496 | 2.1318 | 2.3769 | 2.6413 | 2.909 | 3.1621 | 3.4144 | 3.6381 | 3.8482 | 4.1097 | 4.5295 | 4.7646 | 2.3785 | 2.598 | 2.8218 | 3.0813 | 3.3893 | 3.7563 | 4.1668 | 4.7452 | 5.2507 | 5.7983 | 6.3489 | 6.8682 | 7.3859 | 7.8441 | 8.2748 | 8.8478 | 9.7791 | 10.3095
Uskmouth | Cwmbran Primary | Bulk Supply Point | 11 | Counterfactual | 0.4541 | 0.54478 | 0.65103 | 0.77067 | 0.9152 | 1.0824 | 1.2743 | 1.5458 | 1.7529 | 1.9689 | 2.1888 | 2.4191 | 2.6737 | 2.9262 | 3.1652 | 3.4203 | 4.5737 | 4.998 | 1.0392 | 1.2312 | 1.4528 | 1.7019 | 2.0018 | 2.3486 | 2.7467 | 3.3044 | 3.7333 | 4.1807 | 4.6342 | 5.1057 | 5.6241 | 6.1392 | 6.6271 | 7.1472 | 9.5151 | 10.4181
Uskmouth | Cwmbran Primary | Bulk Supply Point | 11 | Electric Engagement | 0.4962 | 0.6695 | 0.94992 | 1.2798 | 1.5944 | 1.955 | 2.3975 | 2.939 | 3.4147 | 3.8142 | 4.1681 | 4.5177 | 4.6691 | 4.7858 | 4.9075 | 5.0246 | 5.7319 | 6.1143 | 1.1404 | 1.5126 | 2.0937 | 2.7756 | 3.4283 | 4.1762 | 5.0909 | 6.2075 | 7.1922 | 8.0216 | 8.7599 | 9.4854 | 9.8152 | 10.0745 | 10.343 | 10.6002 | 12.1685 | 13.0359
Uskmouth | Cwmbran Primary | Bulk Supply Point | 11 | Holistic Transition | 0.51582 | 0.67752 | 0.84748 | 1.0398 | 1.2645 | 1.5819 | 1.906 | 2.3318 | 2.6615 | 3.0324 | 3.4168 | 3.807 | 4.2327 | 4.6296 | 5.0024 | 5.3007 | 6.0428 | 6.5077 | 1.189 | 1.5469 | 1.9135 | 2.3282 | 2.8109 | 3.4842 | 4.1711 | 5.0602 | 5.7525 | 6.5279 | 7.3283 | 8.1429 | 9.0366 | 9.8693 | 10.6486 | 11.2732 | 12.8984 | 13.9387
Uskmouth | Cwmbran Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 0.47335 | 0.61408 | 0.77658 | 0.97082 | 1.1959 | 1.4398 | 1.7083 | 2.0663 | 2.4125 | 2.762 | 3.1117 | 3.4355 | 3.7879 | 4.0873 | 4.4098 | 4.6752 | 5.32 | 5.6894 | 1.0827 | 1.382 | 1.7235 | 2.1287 | 2.5992 | 3.1073 | 3.664 | 4.3971 | 5.1073 | 5.8265 | 6.544 | 7.2088 | 7.931 | 8.5482 | 9.2142 | 9.7658 | 11.1445 | 11.9433
Uskmouth | Llantarnam Primary | Bulk Supply Point | 11 | Counterfactual | 1.0749 | 1.2098 | 1.365 | 1.5307 | 1.7439 | 1.9741 | 2.2322 | 2.6316 | 2.9353 | 3.2693 | 3.606 | 3.9523 | 4.3474 | 4.7172 | 5.0713 | 5.4402 | 7.2474 | 8.1783 | 2.5701 | 2.853 | 3.1752 | 3.5191 | 3.9694 | 4.4503 | 4.9889 | 5.8135 | 6.4478 | 7.1479 | 7.8479 | 8.5615 | 9.3715 | 10.1277 | 10.8516 | 11.608 | 15.3747 | 17.3934
Uskmouth | Llantarnam Primary | Bulk Supply Point | 11 | Electric Engagement | 1.1438 | 1.3901 | 1.81 | 2.375 | 2.8531 | 3.3943 | 4.051 | 4.8423 | 5.5396 | 6.1242 | 6.635 | 7.1377 | 7.3632 | 7.5667 | 7.7652 | 7.9104 | 9.4608 | 10.1168 | 2.7364 | 3.2601 | 4.1291 | 5.3272 | 6.3216 | 7.4483 | 8.8116 | 10.4481 | 11.8969 | 13.1196 | 14.1944 | 15.2482 | 15.759 | 16.2341 | 16.6972 | 17.0279 | 20.5379 | 22.0545
Uskmouth | Llantarnam Primary | Bulk Supply Point | 11 | Holistic Transition | 1.1743 | 1.3991 | 1.6929 | 1.9748 | 2.3103 | 2.7168 | 3.1716 | 3.7705 | 4.2743 | 4.8324 | 5.399 | 6.02 | 7.0686 | 7.8563 | 8.5198 | 8.933 | 9.9354 | 10.5818 | 2.812 | 3.3038 | 3.953 | 4.5624 | 5.2855 | 6.1545 | 7.1241 | 8.3833 | 9.452 | 10.6352 | 11.8256 | 13.1431 | 15.4759 | 17.1712 | 18.5801 | 19.4492 | 21.685 | 23.151
Uskmouth | Llantarnam Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 1.1069 | 1.3041 | 1.5186 | 1.8196 | 2.0951 | 2.4168 | 2.7987 | 3.3344 | 3.8229 | 4.3513 | 4.8825 | 5.3819 | 5.8845 | 6.4415 | 7.0332 | 7.544 | 8.7867 | 9.4494 | 2.6433 | 3.0591 | 3.5079 | 4.1615 | 4.7379 | 5.4091 | 6.2033 | 7.3059 | 8.319 | 9.4218 | 10.5228 | 11.5563 | 12.5921 | 13.7658 | 15.0256 | 16.1166 | 18.8675 | 20.3568
Uskmouth | Magor Primary | Bulk Supply Point | 11 | Counterfactual | 4.4104 | 4.4493 | 4.5049 | 4.5779 | 4.6711 | 4.7802 | 4.8951 | 5.0545 | 5.177 | 5.3177 | 5.4884 | 5.644 | 5.7993 | 3.3 | 3.436 | 3.5698 | 4.1668 | 4.4716 | 10.3879 | 10.4732 | 10.5946 | 10.7535 | 10.9595 | 11.1998 | 11.4505 | 11.7955 | 12.0603 | 12.3675 | 12.734 | 13.0611 | 13.3849 | 7.0776 | 7.3607 | 7.6383 | 8.8851 | 9.5449
Uskmouth | Magor Primary | Bulk Supply Point | 11 | Electric Engagement | 4.4377 | 4.533 | 4.6947 | 4.9029 | 5.1266 | 6.159 | 6.438 | 6.8038 | 7.1066 | 7.3873 | 7.6979 | 8.1227 | 8.2471 | 5.7775 | 5.8676 | 6.1172 | 6.6428 | 7.6943 | 10.455 | 10.6714 | 11.0308 | 11.4967 | 12.0057 | 14.1169 | 14.7298 | 15.52 | 16.1669 | 16.7711 | 17.4437 | 18.334 | 18.6111 | 12.4092 | 12.6072 | 13.127 | 14.3202 | 16.5354
Uskmouth | Magor Primary | Bulk Supply Point | 11 | Holistic Transition | 4.4448 | 4.5341 | 4.6583 | 4.8298 | 4.9925 | 5.2096 | 5.4429 | 5.7438 | 5.9785 | 6.2544 | 6.5078 | 6.8815 | 7.1967 | 4.8241 | 4.9896 | 5.2972 | 5.7339 | 6.6927 | 10.4727 | 10.6795 | 10.9676 | 11.3668 | 11.7368 | 12.2268 | 12.7507 | 13.4185 | 13.9324 | 14.5339 | 15.0769 | 15.8491 | 16.5616 | 10.5604 | 10.9089 | 11.5421 | 12.5169 | 14.4944
Uskmouth | Magor Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 4.4296 | 4.5266 | 4.6536 | 4.7997 | 4.9863 | 5.1556 | 5.3549 | 5.627 | 5.8535 | 6.1071 | 6.3374 | 6.6251 | 6.8214 | 4.37 | 4.521 | 4.7327 | 5.1854 | 5.8486 | 10.4345 | 10.6544 | 10.9421 | 11.2776 | 11.7072 | 12.0852 | 12.5301 | 13.1216 | 13.6037 | 14.1493 | 14.6382 | 15.2369 | 15.6498 | 9.4519 | 9.7641 | 10.1984 | 11.2126 | 12.6262
Uskmouth | Newhouse Primary S/S | Primary Substation | 11 | Counterfactual | 0.10636 | 0.12915 | 0.15198 | 0.1758 | 0.20145 | 0.23238 | 0.26762 | 0.3198 | 0.3605 | 0.40565 | 0.44953 | 0.49352 | 0.54192 | 0.59 | 0.63639 | 0.6832 | 0.89772 | 0.96954 | 0.25123 | 0.29988 | 0.34843 | 0.39937 | 0.45284 | 0.51754 | 0.5917 | 0.70029 | 0.78619 | 0.88196 | 0.97395 | 1.065 | 1.1643 | 1.2631 | 1.3584 | 1.4545 | 1.8995 | 2.0576
Uskmouth | Newhouse Primary S/S | Primary Substation | 11 | Electric Engagement | 0.11515 | 0.15518 | 0.22064 | 0.29915 | 0.36164 | 0.4328 | 0.51768 | 0.61845 | 0.70839 | 0.7861 | 0.85783 | 0.92836 | 0.96309 | 0.98754 | 1.0123 | 1.0368 | 1.1646 | 1.2569 | 0.27237 | 0.36018 | 0.50011 | 0.66856 | 0.79923 | 0.94799 | 1.1248 | 1.334 | 1.5218 | 1.6855 | 1.8377 | 1.9868 | 2.0648 | 2.1196 | 2.175 | 2.23 | 2.5194 | 2.7353
Uskmouth | Newhouse Primary S/S | Primary Substation | 11 | Holistic Transition | 0.11885 | 0.1586 | 0.19981 | 0.24811 | 0.2889 | 0.34337 | 0.40375 | 0.48505 | 0.55683 | 0.63527 | 0.71317 | 0.78925 | 0.8637 | 0.92939 | 0.9926 | 1.0488 | 1.164 | 1.2457 | 0.28154 | 0.37054 | 0.46232 | 0.57129 | 0.65967 | 0.77627 | 0.90569 | 1.0779 | 1.2315 | 1.3995 | 1.5644 | 1.7255 | 1.883 | 2.0208 | 2.1535 | 2.2723 | 2.5358 | 2.721
Uskmouth | Newhouse Primary S/S | Primary Substation | 11 | Hydrogen Evolution | 0.11085 | 0.14609 | 0.18275 | 0.22603 | 0.2635 | 0.30903 | 0.35938 | 0.42973 | 0.4962 | 0.56766 | 0.63722 | 0.70164 | 0.7676 | 0.82256 | 0.87744 | 0.92408 | 1.0421 | 1.1348 | 0.2615 | 0.33873 | 0.41928 | 0.51472 | 0.59347 | 0.68918 | 0.79447 | 0.93998 | 1.0787 | 1.2294 | 1.3746 | 1.5087 | 1.6454 | 1.759 | 1.8723 | 1.9693 | 2.2291 | 2.4388
Uskmouth | Newport East Primary | Bulk Supply Point | 11 | Counterfactual | 0.6479 | 0.84513 | 1.0804 | 1.3508 | 1.6675 | 2.0138 | 2.403 | 2.9897 | 3.4321 | 3.8904 | 4.3516 | 4.8412 | 5.3772 | 5.9072 | 6.4215 | 6.9441 | 9.4309 | 10.359 | 1.4208 | 1.8368 | 2.3254 | 2.8858 | 3.5407 | 4.2558 | 5.0588 | 6.2572 | 7.1676 | 8.1088 | 9.0536 | 10.0539 | 11.144 | 12.222 | 13.2681 | 14.3316 | 19.4351 | 21.4171
Uskmouth | Newport East Primary | Bulk Supply Point | 11 | Electric Engagement | 0.74483 | 1.1208 | 1.7458 | 2.5012 | 3.2271 | 4.0159 | 4.9651 | 6.0988 | 7.0767 | 7.8788 | 8.5544 | 9.2213 | 9.4578 | 9.6473 | 9.833 | 9.9917 | 11.1442 | 11.9843 | 1.6552 | 2.4606 | 3.7533 | 5.3129 | 6.8181 | 8.4514 | 10.4093 | 12.735 | 14.7464 | 16.4021 | 17.7985 | 19.1736 | 19.693 | 20.1224 | 20.5428 | 20.9012 | 23.5035 | 25.4028
Uskmouth | Newport East Primary | Bulk Supply Point | 11 | Holistic Transition | 0.78986 | 1.141 | 1.5252 | 1.9744 | 2.4846 | 3.0716 | 3.7152 | 4.5498 | 5.2266 | 5.9542 | 6.7215 | 7.528 | 8.3479 | 9.1169 | 9.8314 | 10.4379 | 11.8131 | 12.8266 | 1.7664 | 2.5411 | 3.3675 | 4.3314 | 5.4219 | 6.6675 | 8.0249 | 9.7565 | 11.1685 | 12.6807 | 14.2716 | 15.9509 | 17.666 | 19.2764 | 20.7686 | 22.0396 | 25.107 | 27.4041
Uskmouth | Newport East Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 0.69307 | 0.97472 | 1.3263 | 1.7214 | 2.1794 | 2.6734 | 3.2358 | 4.0194 | 4.6864 | 5.3759 | 6.0963 | 6.8004 | 7.5105 | 8.1696 | 8.82 | 9.3775 | 10.7178 | 11.5191 | 1.5238 | 2.1201 | 2.8566 | 3.6805 | 4.6364 | 5.663 | 6.8257 | 8.4285 | 9.7948 | 11.205 | 12.6768 | 14.1172 | 15.5692 | 16.9271 | 18.2725 | 19.4301 | 22.3217 | 24.0818
Uskmouth | Newport South Primary | Bulk Supply Point | 11 | Counterfactual | 0.38777 | 0.40045 | 0.41415 | 0.43366 | 0.47179 | 0.52361 | 0.58061 | 0.64827 | 0.71156 | 0.78341 | 0.85616 | 0.92621 | 0.97177 | 1.0107 | 1.0451 | 1.098 | 1.4675 | 1.6224 | 0.82539 | 0.85305 | 0.88193 | 0.92304 | 1.0084 | 1.1269 | 1.2571 | 1.4095 | 1.5546 | 1.7196 | 1.8861 | 2.0451 | 2.1388 | 2.2194 | 2.2909 | 2.4039 | 3.2444 | 3.5727
Uskmouth | Newport South Primary | Bulk Supply Point | 11 | Electric Engagement | 0.39047 | 0.41527 | 0.44741 | 0.53555 | 0.63461 | 0.75554 | 0.88739 | 1.0281 | 1.1633 | 1.2958 | 1.4116 | 1.4758 | 1.5531 | 1.682 | 1.837 | 1.917 | 2.4124 | 2.5473 | 0.83177 | 0.88706 | 0.95472 | 1.1593 | 1.3923 | 1.6768 | 1.9814 | 2.3051 | 2.6184 | 2.9264 | 3.1952 | 3.3341 | 3.5115 | 3.8212 | 4.1956 | 4.3833 | 5.4261 | 5.7374
Uskmouth | Newport South Primary | Bulk Supply Point | 11 | Holistic Transition | 0.39229 | 0.41938 | 0.47914 | 0.56181 | 0.66285 | 0.79364 | 0.91765 | 1.0567 | 1.1785 | 1.3156 | 1.3854 | 1.4765 | 1.6286 | 1.7973 | 1.893 | 1.9446 | 2.4674 | 2.6271 | 0.83595 | 0.89812 | 1.0395 | 1.236 | 1.4765 | 1.7792 | 2.0692 | 2.3905 | 2.6766 | 2.9955 | 3.1461 | 3.3536 | 3.7137 | 4.1172 | 4.3333 | 4.4446 | 5.5362 | 5.8808
Uskmouth | Newport South Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 0.38984 | 0.40829 | 0.43687 | 0.52588 | 0.63103 | 0.74875 | 0.85885 | 0.98287 | 1.1288 | 1.272 | 1.3914 | 1.4459 | 1.5195 | 1.608 | 1.7732 | 1.9331 | 2.2789 | 2.4757 | 0.82981 | 0.87006 | 0.93064 | 1.1352 | 1.3806 | 1.6561 | 1.9128 | 2.197 | 2.5266 | 2.8538 | 3.1252 | 3.2411 | 3.3948 | 3.5997 | 3.9863 | 4.3696 | 5.098 | 5.5245
Uskmouth | Newport West Primary | Bulk Supply Point | 11 | Counterfactual | 4.7346 | 4.8431 | 4.9531 | 5.0768 | 5.2242 | 5.0818 | 5.2742 | 5.5685 | 5.7855 | 6.0189 | 6.2567 | 6.5024 | 6.776 | 7.0451 | 7.3023 | 7.6009 | 9.0626 | 9.4674 | 11.4925 | 11.7201 | 11.9477 | 12.2035 | 12.5086 | 12.0772 | 12.4745 | 13.0762 | 13.5234 | 14.0048 | 14.4929 | 14.9951 | 15.5513 | 16.0985 | 16.6218 | 17.235 | 20.3456 | 21.2036
Uskmouth | Newport West Primary | Bulk Supply Point | 11 | Electric Engagement | 4.7806 | 4.9704 | 5.2773 | 5.6442 | 5.9919 | 6.0584 | 6.6416 | 7.2012 | 7.915 | 8.3142 | 8.6771 | 8.9996 | 9.1446 | 9.3697 | 9.6357 | 9.7757 | 10.672 | 11.0938 | 11.6039 | 12.0081 | 12.6417 | 13.4004 | 14.1216 | 14.123 | 15.3192 | 16.468 | 17.9246 | 18.751 | 19.4971 | 20.1597 | 20.4864 | 21.0256 | 21.6669 | 21.9953 | 23.8823 | 24.8273
Uskmouth | Newport West Primary | Bulk Supply Point | 11 | Holistic Transition | 4.8022 | 4.9809 | 5.1555 | 5.3557 | 5.5847 | 5.5615 | 5.9944 | 6.4139 | 6.9773 | 7.335 | 7.7414 | 8.1503 | 8.6499 | 9.1648 | 9.5307 | 9.8082 | 10.9572 | 11.4757 | 11.6572 | 12.0487 | 12.425 | 12.8557 | 13.345 | 13.1755 | 14.077 | 14.9497 | 16.1039 | 16.8462 | 17.6821 | 18.5472 | 19.6439 | 20.7903 | 21.5719 | 22.15 | 24.5694 | 25.7248
Uskmouth | Newport West Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 4.7559 | 4.9086 | 5.0611 | 5.2541 | 5.4749 | 5.4064 | 5.6802 | 6.0651 | 6.4392 | 6.8024 | 7.3765 | 7.7316 | 8.0967 | 9.7409 | 10.2142 | 10.6618 | 11.5145 | 11.9722 | 11.5412 | 11.8635 | 12.181 | 12.5843 | 13.0452 | 12.7684 | 13.3334 | 14.1193 | 14.8847 | 15.6309 | 16.7969 | 17.5248 | 18.272 | 22.2421 | 23.2858 | 24.2895 | 26.0819 | 27.0823
Uskmouth | Panteg Primary | Bulk Supply Point | 11 | Counterfactual | 0.54512 | 0.72984 | 0.84383 | 0.97044 | 1.1204 | 1.2935 | 1.4929 | 1.7963 | 2.0273 | 2.2801 | 2.5328 | 2.7845 | 3.0624 | 3.3394 | 3.6075 | 3.8862 | 5.1417 | 5.8991 | 1.2866 | 1.6656 | 1.9019 | 2.1645 | 2.4755 | 2.8352 | 3.2513 | 3.8776 | 4.3598 | 4.8899 | 5.4148 | 5.9326 | 6.4997 | 7.0662 | 7.6144 | 8.1847 | 10.7883 | 12.4207
Uskmouth | Panteg Primary | Bulk Supply Point | 11 | Electric Engagement | 0.67729 | 0.8621 | 1.1758 | 1.5471 | 1.9012 | 2.2931 | 2.7694 | 3.3509 | 3.8633 | 4.2887 | 4.6786 | 5.0317 | 5.1782 | 5.2851 | 5.3963 | 5.5025 | 6.655 | 7.0696 | 1.5704 | 1.9639 | 2.6127 | 3.3806 | 4.1165 | 4.9307 | 5.9174 | 7.1188 | 8.1829 | 9.0726 | 9.893 | 10.6272 | 10.9501 | 11.1891 | 11.4365 | 11.6663 | 14.2212 | 15.1912
Uskmouth | Panteg Primary | Bulk Supply Point | 11 | Holistic Transition | 0.69932 | 0.865 | 1.043 | 1.2483 | 1.4827 | 1.7809 | 2.1107 | 2.5583 | 2.9245 | 3.3107 | 3.7117 | 4.148 | 4.742 | 5.3039 | 5.78 | 6.0662 | 6.6832 | 7.076 | 1.625 | 1.9885 | 2.3708 | 2.8147 | 3.3196 | 3.9557 | 4.6582 | 5.5994 | 6.3721 | 7.1782 | 8.011 | 8.9256 | 10.1917 | 11.3878 | 12.3973 | 12.9963 | 14.3979 | 15.2927
Uskmouth | Panteg Primary | Bulk Supply Point | 11 | Hydrogen Evolution | 0.65128 | 0.78532 | 0.9469 | 1.1348 | 1.356 | 1.6045 | 1.8884 | 2.2879 | 2.6511 | 3.0461 | 3.4352 | 3.7997 | 4.1824 | 4.626 | 5.0808 | 5.4625 | 6.2895 | 6.6596 | 1.5047 | 1.7865 | 2.1241 | 2.5154 | 2.9781 | 3.4964 | 4.0857 | 4.9067 | 5.6581 | 6.4817 | 7.2868 | 8.04 | 8.8276 | 9.7631 | 10.7216 | 11.5298 | 13.332 | 14.1686
Uskmouth | Pontypool North Primary | Primary Substation | 11 | Counterfactual | 0.57387 | 0.59578 | 0.62045 | 0.6476 | 0.68311 | 0.72523 | 0.77334 | 0.84389 | 0.90058 | 0.9644 | 1.027 | 1.0891 | 1.1604 | 1.2266 | 1.2878 | 1.3585 | 1.6941 | 1.9268 | 1.2734 | 1.3201 | 1.3717 | 1.4285 | 1.5026 | 1.5909 | 1.6923 | 1.8395 | 1.9593 | 2.0949 | 2.2264 | 2.3547 | 2.5008 | 2.6368 | 2.7625 | 2.9082 | 3.6178 | 4.1161
Uskmouth | Pontypool North Primary | Primary Substation | 11 | Electric Engagement | 0.58288 | 0.62542 | 0.69257 | 0.77368 | 0.85157 | 0.93933 | 1.0517 | 1.1812 | 1.2982 | 1.4038 | 1.5011 | 1.5969 | 1.6611 | 1.7223 | 1.7836 | 1.8264 | 2.3323 | 2.4778 | 1.2952 | 1.3876 | 1.5274 | 1.6965 | 1.8599 | 2.0443 | 2.2796 | 2.55 | 2.7962 | 3.0199 | 3.2278 | 3.4308 | 3.5748 | 3.7161 | 3.8567 | 3.9519 | 5.0878 | 5.4244
Uskmouth | Pontypool North Primary | Primary Substation | 11 | Holistic Transition | 0.58767 | 0.62907 | 0.66999 | 0.71937 | 0.77423 | 0.85936 | 0.94306 | 1.0548 | 1.1497 | 1.2618 | 1.3704 | 1.5046 | 1.7866 | 1.9549 | 2.0995 | 2.1752 | 2.4305 | 2.5981 | 1.3069 | 1.3997 | 1.4884 | 1.5967 | 1.7165 | 1.898 | 2.0777 | 2.3147 | 2.5188 | 2.7589 | 2.9894 | 3.2805 | 3.9306 | 4.2996 | 4.6095 | 4.7707 | 5.3343 | 5.7016
Uskmouth | Pontypool North Primary | Primary Substation | 11 | Hydrogen Evolution | 0.57822 | 0.60907 | 0.6428 | 0.69249 | 0.74961 | 0.81605 | 0.88932 | 0.98977 | 1.1028 | 1.2169 | 1.3224 | 1.411 | 1.5163 | 1.6018 | 1.7136 | 1.801 | 2.1593 | 2.4416 | 1.2833 | 1.3492 | 1.4198 | 1.5229 | 1.6422 | 1.7809 | 1.934 | 2.1418 | 2.3759 | 2.6154 | 2.8353 | 3.0207 | 3.2386 | 3.4211 | 3.6611 | 3.8508 | 4.6448 | 5.2615
Uskmouth | Ringland Newport | Primary Substation | 11 | Counterfactual | 0.66292 | 0.79831 | 1.0093 | 1.1687 | 1.3449 | 1.5256 | 1.7146 | 1.9815 | 2.1955 | 2.428 | 2.6619 | 2.9121 | 3.2229 | 3.5363 | 3.8443 | 4.1524 | 5.1246 | 5.3655 | 1.5379 | 1.8222 | 2.2548 | 2.5856 | 2.952 | 3.3281 | 3.7214 | 4.2714 | 4.7169 | 5.2021 | 5.6886 | 6.2075 | 6.8523 | 7.5027 | 8.1419 | 8.7814 | 10.7867 | 11.3126
Uskmouth | Ringland Newport | Primary Substation | 11 | Electric Engagement | 0.70917 | 1.0031 | 1.3175 | 1.6787 | 2.0211 | 2.3682 | 2.7559 | 3.233 | 3.6647 | 4.0346 | 4.3881 | 4.7724 | 4.9901 | 5.2188 | 5.4083 | 5.597 | 6.0397 | 6.3641 | 1.6488 | 2.2664 | 2.9229 | 3.6775 | 4.3959 | 5.1202 | 5.9233 | 6.9091 | 7.806 | 8.5805 | 9.326 | 10.1397 | 10.6216 | 11.1405 | 11.5609 | 11.9801 | 12.9795 | 13.7253
Uskmouth | Ringland Newport | Primary Substation | 11 | Holistic Transition | 0.72683 | 1.0083 | 1.2293 | 1.4645 | 1.7068 | 1.9756 | 2.268 | 2.6898 | 3.133 | 3.5188 | 3.9147 | 4.3007 | 4.6813 | 5.0362 | 5.371 | 5.678 | 6.0975 | 6.4333 | 1.6927 | 2.2916 | 2.7691 | 3.2765 | 3.7978 | 4.3734 | 4.9965 | 5.8878 | 6.86 | 7.6794 | 8.5159 | 9.3323 | 10.138 | 10.8879 | 11.5967 | 12.2493 | 13.2054 | 13.971
Uskmouth | Ringland Newport | Primary Substation | 11 | Hydrogen Evolution | 0.68175 | 0.93574 | 1.1208 | 1.3356 | 1.581 | 1.8414 | 2.1415 | 2.5303 | 2.8785 | 3.2476 | 3.6165 | 3.9772 | 4.3331 | 4.7013 | 5.0158 | 5.302 | 5.7216 | 6.0194 | 1.5815 | 2.1121 | 2.5031 | 2.9585 | 3.48 | 4.0312 | 4.6639 | 5.4744 | 6.2052 | 6.9812 | 7.7523 | 8.5062 | 9.2496 | 10.0353 | 10.6936 | 11.2955 | 12.2073 | 12.8768
Uskmouth | Rogerstone | Primary Substation | 11 | Counterfactual | 1.065 | 1.1804 | 1.3206 | 1.4732 | 1.6508 | 1.8582 | 2.0947 | 2.4665 | 2.7446 | 3.0449 | 3.3481 | 3.6547 | 3.9916 | 4.3279 | 4.6566 | 4.9924 | 6.4547 | 6.7783 | 2.5019 | 2.7425 | 3.032 | 3.3471 | 3.7135 | 4.1416 | 4.6308 | 5.3927 | 5.9677 | 6.5903 | 7.2148 | 7.8416 | 8.5265 | 9.21 | 9.8784 | 10.5621 | 13.5642 | 14.2686
Uskmouth | Rogerstone | Primary Substation | 11 | Electric Engagement | 1.1275 | 1.3482 | 1.7395 | 2.2 | 2.6392 | 3.1352 | 3.7337 | 4.4455 | 5.0656 | 5.5737 | 6.0217 | 6.45 | 6.5783 | 6.7137 | 6.8854 | 7.0064 | 7.5802 | 8.0541 | 2.6532 | 3.1201 | 3.9267 | 4.8751 | 5.7835 | 6.8085 | 8.0413 | 9.4979 | 10.771 | 11.8198 | 12.7471 | 13.632 | 13.9063 | 14.2083 | 14.583 | 14.8509 | 16.1346 | 17.2311
Uskmouth | Rogerstone | Primary Substation | 11 | Holistic Transition | 1.156 | 1.3477 | 1.5622 | 1.8069 | 2.0842 | 2.4278 | 2.8117 | 3.3327 | 3.777 | 4.2717 | 4.7535 | 5.228 | 5.8183 | 6.237 | 6.6602 | 7.0102 | 7.7116 | 8.1909 | 2.724 | 3.1418 | 3.6013 | 4.1271 | 4.72 | 5.4485 | 6.2565 | 7.3388 | 8.2689 | 9.3043 | 10.2936 | 11.2803 | 12.566 | 13.4358 | 14.3108 | 15.04 | 16.5706 | 17.6652
Uskmouth | Rogerstone | Primary Substation | 11 | Hydrogen Evolution | 1.0929 | 1.2551 | 1.4409 | 1.6509 | 1.8931 | 2.1807 | 2.5201 | 3.0047 | 3.4189 | 3.8658 | 4.33 | 4.7879 | 5.2517 | 5.6406 | 6.0283 | 6.3463 | 6.8849 | 7.3228 | 2.5658 | 2.9054 | 3.2915 | 3.7272 | 4.2301 | 4.8262 | 5.5266 | 6.5175 | 7.368 | 8.2891 | 9.241 | 10.1813 | 11.134 | 11.9295 | 12.724 | 13.3773 | 14.5141 | 15.4997
Uskmouth | St Arvans | Primary Substation | 11 | Counterfactual | 0.11847 | 0.13103 | 0.14626 | 0.16366 | 0.18479 | 0.21044 | 0.23909 | 0.2836 | 0.31754 | 0.35378 | 0.39017 | 0.42666 | 0.46685 | 0.5068 | 0.54564 | 0.58464 | 0.7468 | 0.80759 | 0.28047 | 0.30681 | 0.33825 | 0.37418 | 0.41787 | 0.47096 | 0.53052 | 0.62216 | 0.69277 | 0.7685 | 0.8439 | 0.91889 | 1.0009 | 1.0825 | 1.1618 | 1.2414 | 1.5751 | 1.7055
Uskmouth | St Arvans | Primary Substation | 11 | Electric Engagement | 0.12374 | 0.14859 | 0.19216 | 0.24497 | 0.29434 | 0.3544 | 0.4251 | 0.50914 | 0.58391 | 0.64878 | 0.70899 | 0.76507 | 0.79324 | 0.81448 | 0.83629 | 0.85753 | 0.96782 | 1.029 | 0.29348 | 0.3465 | 0.43641 | 0.54549 | 0.64789 | 0.77226 | 0.91813 | 1.0907 | 1.2449 | 1.3795 | 1.505 | 1.6219 | 1.6832 | 1.7292 | 1.7763 | 1.8223 | 2.0621 | 2.2033
Uskmouth | St Arvans | Primary Substation | 11 | Holistic Transition | 0.1265 | 0.14867 | 0.17277 | 0.20148 | 0.23347 | 0.27787 | 0.32694 | 0.39296 | 0.4507 | 0.5136 | 0.57722 | 0.63462 | 0.69006 | 0.73998 | 0.78705 | 0.82922 | 0.92894 | 0.9879 | 0.30037 | 0.34917 | 0.40078 | 0.46262 | 0.53121 | 0.6253 | 0.72901 | 0.86711 | 0.98869 | 1.121 | 1.2537 | 1.3739 | 1.49 | 1.594 | 1.6921 | 1.7803 | 1.9999 | 2.1327
Uskmouth | St Arvans | Primary Substation | 11 | Hydrogen Evolution | 0.12056 | 0.13902 | 0.1596 | 0.18485 | 0.2152 | 0.25276 | 0.29505 | 0.35492 | 0.40761 | 0.46597 | 0.52387 | 0.57852 | 0.63118 | 0.6771 | 0.72125 | 0.7588 | 0.84732 | 0.9115 | 0.2854 | 0.32426 | 0.36696 | 0.41937 | 0.48275 | 0.56088 | 0.64833 | 0.77116 | 0.87985 | 1.001 | 1.1203 | 1.2329 | 1.341 | 1.4352 | 1.5257 | 1.6029 | 1.7937 | 1.9363
Uskmouth | Sudbrook Primary | Primary Substation | 11 | Counterfactual | 0.33003 | 0.35223 | 0.37926 | 0.41231 | 0.44 | 0.46748 | 0.49842 | 0.54171 | 0.57733 | 0.61727 | 0.65651 | 0.69341 | 0.73539 | 0.77421 | 0.81045 | 0.85119 | 1.036 | 1.1416 | 0.81084 | 0.85851 | 0.9151 | 0.98413 | 1.0421 | 1.0997 | 1.1653 | 1.2562 | 1.3322 | 1.4179 | 1.5009 | 1.5777 | 1.6639 | 1.7441 | 1.8189 | 1.9027 | 2.2897 | 2.5162
Uskmouth | Sudbrook Primary | Primary Substation | 11 | Electric Engagement | 0.33533 | 0.3693 | 0.41602 | 0.47851 | 0.55592 | 0.61618 | 0.691 | 0.77628 | 0.8565 | 0.93222 | 1.0064 | 1.0769 | 1.1293 | 1.1716 | 1.2159 | 1.2611 | 1.5187 | 1.6324 | 0.82376 | 0.89914 | 0.99738 | 1.1293 | 1.295 | 1.4214 | 1.5782 | 1.757 | 1.9262 | 2.0869 | 2.2451 | 2.3947 | 2.5089 | 2.5996 | 2.6942 | 2.791 | 3.3463 | 3.6068
Uskmouth | Sudbrook Primary | Primary Substation | 11 | Holistic Transition | 0.33757 | 0.37617 | 0.4152 | 0.46558 | 0.50661 | 0.56586 | 0.62409 | 0.69918 | 0.76567 | 0.8434 | 0.91856 | 0.98646 | 1.0544 | 1.1147 | 1.1795 | 1.2374 | 1.4631 | 1.582 | 0.82926 | 0.91635 | 1.0008 | 1.1108 | 1.2009 | 1.3267 | 1.4518 | 1.6118 | 1.755 | 1.9223 | 2.0822 | 2.2273 | 2.3723 | 2.4996 | 2.6356 | 2.758 | 3.2453 | 3.5028
Uskmouth | Sudbrook Primary | Primary Substation | 11 | Hydrogen Evolution | 0.33316 | 0.36632 | 0.40185 | 0.452 | 0.49411 | 0.53622 | 0.58092 | 0.64067 | 0.70966 | 0.78011 | 0.8441 | 0.89756 | 0.96079 | 1.0055 | 1.0603 | 1.1032 | 1.2749 | 1.4268 | 0.8182 | 0.89127 | 0.96691 | 1.073 | 1.1622 | 1.2505 | 1.3443 | 1.4685 | 1.6124 | 1.7619 | 1.8965 | 2.0092 | 2.1407 | 2.2341 | 2.3475 | 2.4376 | 2.8083 | 3.1384