## Introduction
Data Dictionary
Column Heading | Description
Associated GSP | Name of the upstream Grid Supply Point (GSP) which supplies the substation. Note that some GSPs which run in parallel are reported as groups.
Substation | Name of the substation for which the generation and demand headroom figures have been calculated.
Supply Level | Identifier for whether the substation is a Primary or a Bulk Supply Point. The definition is supplied in the 'NDP 2026 Introduction & Methodology Report'.
Voltage Level (kV) | Voltage of the lower voltage side of the transformation at the substation.
Scenario | Identifier for one of the four Distribution Future Energy Scenarios (DFES) the headroom figures refer to. Holistic Transition was chosen as the best view scenario for the NDP 2026.
Units | The units used to define the headroom available at each substation under each scenario and all of the years reported on (see below).
2024 | Defines the year snapshot for the headroom calculation, where the year refers to the end of the fiscal year.
2025
2026
2027
2028
2029
2030
2031
2032
2033
2034
2035
2036
2037
2038
2039
2040
2045
2050
South West
Network Headroom Report 2026
May 2026
v1.0
How to use this workbook
The 'Demand Headroom' and 'Generation Headroom' sheets contain data as described by the data dictionary below. Cells highlighted in red indicate zero headroom, which is defined as the point at which adding demand or generation at a given substation would cause a thermal overload to occur on an related asset in the network. The impact of some high-certainty medium-term reinforcement schemes on the network has been included from the year 2030. This may be observed as a step change increase in the available headroom from the year 2030.
The 'Fault Level Contribution' sheet contains the total make and break contribution (kA) from the demand and generation expected to connect at each primary substation for each year and scenario under the DFES forecasts. The existing maximum prospective fault levels under normal system running conditions and the make and break switchgear ratings at bussing points can be taken from the LTDS Table 4.
In the context of the NHR, zero headroom does not necessarily mean a prospective customer would not be able to connect. This data should not be used to make connections decisions as it is intended to provide a view of the capacity of the network against the DFES scenarios rather than a view of the contractually available capacity. Prospective customers should follow the regular connections application process to gain an accurate assessment of the headroom available for their connection.
Summary
This Network Headroom Report (NHR) workbook provides a view of the capacity to connect additional demand and generation to NGED's South West network, in line with the load growth forecasted across the four Distribution Future Energy Scenarios (DFES) out to 2050. The DFES 2024 publication was used as the basis for this NHR to align with the forecasts used for the Network Development Reports.
The NHR forms one part of the wider Network Development Plan (NDP), and it is recommended to view this report alongside the NDP Introduction & Methodology Report and the Network Development Reports which are presented as an interactive map on the Network Opportunity and Development Map (NODM).

## Demand Headroom
Associated GSP | Substation | Supply Level | Voltage Level (kV) | Scenario | Units | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050
Abham 132 kV | Ashburton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Ashburton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Ashburton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Ashburton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Barton. | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.4 | 9.3 | 9.1 | 8.9 | 8.7 | 8.5 | 8 | 7.7 | 7.1 | 6.7 | 6.2 | 5.6 | 4.8 | 4.1 | 3.3 | 2.6 | 1.9 | 0 | 0
Abham 132 kV | Barton. | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.4 | 9 | 8.6 | 7.9 | 7.4 | 6.7 | 5.9 | 4.7 | 3.2 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Barton. | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.4 | 9.1 | 8.8 | 8.4 | 8.1 | 7.7 | 7.2 | 6.4 | 5.4 | 4.5 | 3.4 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Barton. | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.4 | 9.1 | 8.8 | 8.4 | 8 | 7.5 | 6.9 | 6.1 | 5.2 | 4.2 | 3.1 | 1.9 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Blackawton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 2.3 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Blackawton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Blackawton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Blackawton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Bovey Tracey | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 4 | 3.8 | 3.6 | 3.5 | 2.8 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Bovey Tracey | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 2.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Bovey Tracey | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3.7 | 3.2 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Bovey Tracey | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 3.4 | 2.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Bradley Lane | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10 | 5.6 | 5.4 | 5.2 | 4.8 | 4.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Bradley Lane | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10 | 5.3 | 5 | 4.4 | 3.8 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Bradley Lane | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10 | 5.4 | 5.2 | 4.9 | 4.5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Bradley Lane | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10 | 5.4 | 5.1 | 4.6 | 4.1 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Buckfastleigh | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Buckfastleigh | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Buckfastleigh | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Buckfastleigh | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Chudleigh Knighton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 4.6 | 4.2 | 3.9 | 3.7 | 2.9 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Chudleigh Knighton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 2.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Chudleigh Knighton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 4 | 3.2 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Chudleigh Knighton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 3.5 | 2.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Churston | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.1 | 3 | 2.9 | 2.8 | 2.5 | 2.2 | 1.6 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Churston | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.1 | 2.8 | 2.5 | 2.2 | 1.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Churston | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.1 | 2.9 | 2.6 | 2.4 | 2.1 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Churston | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.1 | 2.9 | 2.7 | 2.4 | 2 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Colley End | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.9 | 7.7 | 7.5 | 7.3 | 6.9 | 6.7 | 6.1 | 5.7 | 5.1 | 4.7 | 4.1 | 3.4 | 2.5 | 1.6 | 0.8 | 0 | 0 | 0 | 0
Abham 132 kV | Colley End | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.9 | 7.4 | 6.9 | 6.2 | 5.4 | 4.7 | 3.7 | 2.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Colley End | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.9 | 7.5 | 7.2 | 6.9 | 6.4 | 6 | 5.3 | 4.3 | 3 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Colley End | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.9 | 7.5 | 7.1 | 6.7 | 6.1 | 5.7 | 4.8 | 4 | 2.9 | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Dartmouth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 2.3 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Dartmouth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Dartmouth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Dartmouth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Dawlish | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Dawlish | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Dawlish | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Dawlish | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Higher Woodway | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Higher Woodway | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Higher Woodway | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Higher Woodway | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Hollicombe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.5 | 2.4 | 2.4 | 2.3 | 2 | 1.7 | 1.3 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Hollicombe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.5 | 2.3 | 2 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Hollicombe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.5 | 2.3 | 2.2 | 1.9 | 1.6 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Hollicombe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.5 | 2.3 | 2.2 | 1.9 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Ivybridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 1.8 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Ivybridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Ivybridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Ivybridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Kingsbridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.2 | 3.9 | 3.7 | 3.6 | 3.4 | 3.1 | 2.8 | 2.6 | 2.1 | 1.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Kingsbridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.2 | 3.7 | 3.4 | 2.9 | 2.3 | 1.7 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Kingsbridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.2 | 3.9 | 3.6 | 3.3 | 2.9 | 2.5 | 2.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Kingsbridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.2 | 3.8 | 3.5 | 3.2 | 2.7 | 2.2 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Langage | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.5 | 12.4 | 6.2 | 6.2 | 6.2 | 5.9 | 5.8 | 5.5 | 5.2 | 4.9 | 4.7 | 4.4 | 4 | 3.8 | 3.5 | 3.3 | 3.1 | 1.8 | 0.8
Abham 132 kV | Langage | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.5 | 12.3 | 5.9 | 5.8 | 5.4 | 5 | 4.7 | 4.2 | 3.6 | 3.1 | 2.6 | 2.1 | 1.7 | 1.3 | 0.9 | 0.5 | 0 | 0 | 0
Abham 132 kV | Langage | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.5 | 12.3 | 6 | 5.8 | 5.6 | 5.4 | 5.2 | 4.8 | 4.4 | 4 | 3.7 | 3.3 | 2.7 | 2.2 | 1.8 | 1.4 | 1 | 0 | 0
Abham 132 kV | Langage | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.5 | 12.3 | 6 | 5.9 | 5.6 | 5.3 | 5 | 4.6 | 4.1 | 3.8 | 3.4 | 2.9 | 2.5 | 2.1 | 1.8 | 1.5 | 1.3 | 0.8 | 0.6
Abham 132 kV | Lawes Bridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 6.9 | 6.5 | 5.8 | 5 | 3.9 | 2.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Lawes Bridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 6.5 | 5.7 | 4.5 | 2.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Lawes Bridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 6.6 | 5.9 | 4.7 | 3.3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Lawes Bridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 6.6 | 6 | 4.9 | 3.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Laywell Brixham | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 1.6 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Laywell Brixham | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Laywell Brixham | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Laywell Brixham | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Linketty Lane | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11 | 10.9 | 10.7 | 10.5 | 10.3 | 10.1 | 9.7 | 9.5 | 9 | 8.8 | 8.4 | 8 | 7.5 | 6.9 | 6.3 | 5.7 | 4.8 | 0 | 0
Abham 132 kV | Linketty Lane | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11 | 10.6 | 10.2 | 9.6 | 9.2 | 8.7 | 8 | 7 | 5.8 | 4.6 | 3.7 | 2.8 | 2 | 0.8 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Linketty Lane | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11 | 10.6 | 10.4 | 10 | 9.7 | 9.4 | 8.9 | 8.3 | 7.5 | 6.8 | 6.1 | 5.2 | 4.3 | 3.3 | 2.3 | 1.4 | 0 | 0 | 0
Abham 132 kV | Linketty Lane | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11 | 10.6 | 10.4 | 9.9 | 9.5 | 9.1 | 8.5 | 7.8 | 7 | 6.2 | 5.3 | 3.9 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Marldon | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 3.2 | 3.2 | 3.2 | 3.1 | 3.1 | 3 | 2.9 | 2.8 | 2.2 | 1.6 | 0 | 0
Abham 132 kV | Marldon | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 3 | 2.9 | 2.4 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Marldon | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 3.1 | 3 | 3 | 2.6 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Marldon | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 3.1 | 3 | 2.9 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Modbury | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 1.8 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Modbury | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Modbury | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Modbury | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Newton Abbot Bsp (Forde Road) | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 27.8 | 23.6 | 22.9 | 0 | 0 | 0 | 9.8 | 8.3 | 5.6 | 4.1 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Newton Abbot Bsp (Forde Road) | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 27.8 | 22.5 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Newton Abbot Bsp (Forde Road) | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 27.8 | 23 | 13.4 | 0 | 0 | 0 | 5.9 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Newton Abbot Bsp (Forde Road) | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 27.8 | 22.8 | 11.8 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Newton Abbot Main | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 16.1 | 15.7 | 14.9 | 14.3 | 13.7 | 12.8 | 11.5 | 10.5 | 9.5 | 8.5 | 7.5 | 2 | 0
Abham 132 kV | Newton Abbot Main | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 13.7 | 12.1 | 10.4 | 8.8 | 7.5 | 6.1 | 4.9 | 3.8 | 2.6 | 1.1 | 0 | 0 | 0
Abham 132 kV | Newton Abbot Main | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 15.1 | 14 | 12.8 | 11.6 | 10.2 | 8.6 | 6.9 | 5.3 | 3.8 | 1.9 | 0 | 0 | 0
Abham 132 kV | Newton Abbot Main | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 13.4 | 12.1 | 10.9 | 9.7 | 8.2 | 6.7 | 5.3 | 4 | 2.6 | 1.6 | 0 | 0
Abham 132 kV | Newton Ferrers | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 1.4 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Newton Ferrers | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Newton Ferrers | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Newton Ferrers | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Paignton 33/11kv S/S | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.8 | 10.7 | 10.6 | 10.5 | 10.2 | 9.9 | 9.3 | 8.8 | 8.2 | 7.8 | 7.4 | 7 | 6.6 | 6.1 | 5.6 | 5.3 | 4.9 | 2.8 | 1.1
Abham 132 kV | Paignton 33/11kv S/S | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.8 | 10.5 | 10.2 | 9.9 | 9.3 | 8.5 | 7.5 | 6.5 | 5.6 | 4.9 | 4.2 | 3.1 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Paignton 33/11kv S/S | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.8 | 10.6 | 10.3 | 9.9 | 9.4 | 8.8 | 7.9 | 7.1 | 6.2 | 5.6 | 5 | 4.1 | 3.1 | 2 | 1.2 | 0 | 0 | 0 | 0
Abham 132 kV | Paignton 33/11kv S/S | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.8 | 10.5 | 10.4 | 10.1 | 9.5 | 8.9 | 7.9 | 7.1 | 6.4 | 5.8 | 5.1 | 4.3 | 3.6 | 2.9 | 2.3 | 1.8 | 1.4 | 0 | 0
Abham 132 kV | Paignton Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 41.2 | 40.1 | 35.6 | 0 | 0 | 0 | 19.2 | 16.3 | 11 | 8 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Paignton Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 41.2 | 38.9 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Paignton Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 41.2 | 39.3 | 11.8 | 0 | 0 | 0 | 11.6 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Paignton Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 41.2 | 39.2 | 10.4 | 0 | 0 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Plympton Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 7.1 | 5.7 | 0 | 0 | 0 | 0 | 24.1 | 23.1 | 21.6 | 20.6 | 19.5 | 17.8 | 15.7 | 13.6 | 11.8 | 10.2 | 8 | 0 | 0
Abham 132 kV | Plympton Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 7.1 | 5 | 0 | 0 | 0 | 0 | 19.1 | 16.3 | 12.8 | 9.3 | 6.8 | 3.9 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Plympton Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 7.1 | 5.2 | 0 | 0 | 0 | 0 | 21.9 | 20 | 17.5 | 15.2 | 12.6 | 9.7 | 6.4 | 3.2 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Plympton Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 7.1 | 5.1 | 0 | 0 | 0 | 0 | 20.4 | 18.4 | 15.9 | 13 | 10.4 | 6.9 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Salcombe 340038 | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.6 | 2.5 | 2.5 | 2.5 | 2.4 | 2.4 | 2.3 | 2.2 | 2.1 | 2 | 1.9 | 1.7 | 1.4 | 1.2 | 0.9 | 0.6 | 0 | 0 | 0
Abham 132 kV | Salcombe 340038 | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.6 | 2.4 | 2.4 | 2.2 | 2.1 | 1.9 | 1.8 | 1.4 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Salcombe 340038 | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.6 | 2.5 | 2.5 | 2.4 | 2.4 | 2.3 | 2.2 | 2 | 1.7 | 1.4 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Salcombe 340038 | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.6 | 2.5 | 2.4 | 2.3 | 2.2 | 2.1 | 2 | 1.8 | 1.5 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | South Brent | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.7 | 1.6 | 1.6 | 1.5 | 1.5 | 1.4 | 2.7 | 2.4 | 1.9 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | South Brent | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.7 | 1.5 | 1.5 | 1.4 | 1.2 | 1.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | South Brent | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.7 | 1.6 | 1.5 | 1.5 | 1.4 | 1.4 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | South Brent | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.7 | 1.6 | 1.5 | 1.4 | 1.3 | 1.2 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Stokenham | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 2.2 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Stokenham | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Stokenham | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Stokenham | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Teignmouth Gasworks | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 6.4 | 6.2 | 6 | 5.9 | 5.4 | 3.7 | 2.3 | 1 | 0 | 0 | 0 | 0
Abham 132 kV | Teignmouth Gasworks | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 5.7 | 4 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Teignmouth Gasworks | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 6 | 5.2 | 3.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Teignmouth Gasworks | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 6.1 | 5.7 | 4.2 | 2.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Torquay Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 57.8 | 56.7 | 35.4 | 0 | 0 | 0 | 46.3 | 44.2 | 41.3 | 38.9 | 36.6 | 34 | 31.1 | 28.2 | 25.4 | 23 | 20.3 | 6.4 | 0
Abham 132 kV | Torquay Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 57.8 | 46.1 | 3.1 | 0 | 0 | 0 | 36.8 | 30.9 | 24.7 | 19 | 14.4 | 8.1 | 3 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Torquay Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 57.8 | 49.8 | 11.7 | 0 | 0 | 0 | 41.5 | 37.7 | 32.9 | 29 | 25 | 18.8 | 12.1 | 5.7 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Torquay Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 57.8 | 48.8 | 10.3 | 0 | 0 | 0 | 40.4 | 36.4 | 31.8 | 27.9 | 23.9 | 19.1 | 15.1 | 11.2 | 7.5 | 4 | 1.3 | 0 | 0
Abham 132 kV | Torwood | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.7 | 5.7 | 5.6 | 5.6 | 5.6 | 5.5 | 5.1 | 5 | 4.9 | 4.7 | 4.6 | 4.3 | 4 | 3.8 | 3.5 | 3.2 | 3 | 1.5 | 0
Abham 132 kV | Torwood | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.7 | 5.5 | 5.3 | 5.1 | 4.8 | 4.5 | 4.1 | 3.5 | 2.9 | 2.3 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Torwood | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.7 | 5.6 | 5.5 | 5.3 | 5.2 | 5.2 | 4.8 | 4.7 | 4.3 | 4 | 3.5 | 2.8 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Torwood | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.7 | 5.6 | 5.5 | 5.3 | 5.2 | 5 | 4.6 | 4.3 | 4 | 3.7 | 3.3 | 2.7 | 2.3 | 1.8 | 1.5 | 1.1 | 0.9 | 0 | 0
Abham 132 kV | Torycombe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.9 | 7.9 | 7.9 | 8 | 8 | 8 | 10.6 | 10.6 | 10.5 | 10.5 | 10.5 | 10.4 | 10.3 | 10.2 | 10.1 | 10.1 | 10 | 9.6 | 9.3
Abham 132 kV | Torycombe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.8 | 10.3 | 10.2 | 10.1 | 10.1 | 10.1 | 10 | 9.9 | 9.8 | 9.8 | 9.7 | 9.6 | 9.4 | 9.2
Abham 132 kV | Torycombe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.3 | 10.2 | 10.1 | 10 | 9.8 | 9.8 | 9.4 | 9.1
Abham 132 kV | Torycombe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.8 | 10.4 | 10.3 | 10.2 | 10.2 | 10.2 | 10 | 9.9 | 9.8 | 9.7 | 9.5 | 9.5 | 9.2 | 9
Abham 132 kV | Totnes | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 7.3 | 6.8 | 6.2 | 5.8 | 5.4 | 4.9 | 4.2 | 3.5 | 2.8 | 2.2 | 1.6 | 0 | 0
Abham 132 kV | Totnes | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 4.6 | 3.5 | 2.5 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Totnes | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 5.6 | 4.5 | 3.6 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Totnes | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5.2 | 4.3 | 3.3 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Totnes Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 47 | 46.9 | 34.9 | 0 | 0 | 0 | 56.6 | 54.9 | 52.6 | 51 | 49.1 | 46.2 | 42.5 | 39.4 | 36.5 | 34.1 | 31.5 | 19 | 0
Abham 132 kV | Totnes Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 47 | 45.5 | 3.1 | 0 | 0 | 0 | 51.7 | 48.1 | 43.7 | 38.9 | 35.3 | 31.4 | 27.4 | 23.7 | 20.1 | 16.5 | 0 | 0 | 0
Abham 132 kV | Totnes Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 47 | 46.9 | 11.5 | 0 | 0 | 0 | 54.6 | 51.6 | 47.9 | 44.4 | 39.7 | 35.1 | 30.7 | 26.2 | 22 | 17.6 | 0 | 0 | 0
Abham 132 kV | Totnes Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 47 | 46.9 | 10.1 | 0 | 0 | 0 | 53.1 | 50.1 | 46.6 | 42 | 37.6 | 32.8 | 28.4 | 23.9 | 19.9 | 15.9 | 12.9 | 0 | 0
Abham 132 kV | Upton Valley | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9 | 8.9 | 8.6 | 8.3 | 8.1 | 7.6 | 7 | 6.6 | 6 | 5.5 | 5.1 | 4.5 | 3.9 | 3.2 | 2.6 | 2 | 1.4 | 0 | 0
Abham 132 kV | Upton Valley | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9 | 8.6 | 7.7 | 7 | 6.5 | 5.6 | 4.5 | 3.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Upton Valley | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9 | 8.7 | 8 | 7.6 | 7.3 | 6.7 | 6.1 | 5.2 | 4.2 | 3.1 | 2.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Upton Valley | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9 | 8.6 | 8.2 | 7.6 | 7.2 | 6.5 | 5.6 | 4.9 | 3.8 | 2.8 | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Ashwater | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.1 | 3 | 3 | 3 | 3 | 2.9 | 4.2 | 4.1 | 4 | 4 | 3.8 | 3.2 | 2.5 | 0.6 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Ashwater | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.1 | 3 | 3 | 3 | 2.8 | 2.7 | 3.9 | 3.1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Ashwater | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.1 | 3 | 3 | 3 | 2.9 | 2.8 | 4 | 3.9 | 3.5 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Ashwater | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.1 | 3 | 3 | 3 | 2.9 | 2.8 | 4 | 3.8 | 2.9 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Barnstaple Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 6.1 | 3.3 | 2.1 | 0.6 | 0 | 0 | 4.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Barnstaple Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 6.1 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Barnstaple Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 6.1 | 2.7 | 1.2 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Barnstaple Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 6.1 | 2.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Barnstaple Quay | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Barnstaple Quay | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Barnstaple Quay | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Barnstaple Quay | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Bideford Main | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Bideford Main | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Bideford Main | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Bideford Main | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Bratton Fleming | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.9 | 3.9 | 3.9 | 3.8 | 3.8 | 2.9 | 2.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Bratton Fleming | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.9 | 3.9 | 3.8 | 3.7 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Bratton Fleming | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.9 | 3.9 | 3.8 | 3.8 | 3.7 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Bratton Fleming | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.9 | 3.9 | 3.8 | 3.7 | 3.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Braunton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Braunton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Braunton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Braunton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Clovelly | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.5 | 1.4 | 1.4 | 1.3 | 1.3 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Clovelly | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.5 | 1.4 | 1.3 | 1.2 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Clovelly | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.5 | 1.4 | 1.4 | 1.3 | 1.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Clovelly | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.5 | 1.4 | 1.3 | 1.3 | 1.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | East Curry | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.7 | 5.4 | 5 | 4.8 | 4.4 | 3.8 | 3.2 | 2.9 | 2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | East Curry | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.7 | 5.1 | 4.6 | 3.9 | 3.1 | 2.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | East Curry | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.7 | 5.3 | 4.9 | 4.5 | 4 | 3.3 | 2.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | East Curry | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.7 | 5.2 | 4.8 | 4.3 | 3.5 | 2.5 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | East Yelland Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 10.1 | 4.4 | 3.1 | 1.6 | 0 | 0 | 13.7 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | East Yelland Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 10.1 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | East Yelland Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 10.1 | 3.7 | 2 | 0 | 0 | 0 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | East Yelland Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 10.1 | 3.5 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Fremington | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Fremington | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Fremington | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Fremington | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Georgeham | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Georgeham | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Georgeham | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Georgeham | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Great Torrington | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Great Torrington | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Great Torrington | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Great Torrington | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Hatherleigh | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Hatherleigh | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Hatherleigh | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Hatherleigh | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Heddon Cross | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 3.7 | 3.6 | 3.6 | 3.6 | 3.6 | 3.5 | 2.8 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Heddon Cross | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 3.6 | 3.6 | 3.6 | 3.5 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Heddon Cross | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 3.7 | 3.6 | 3.6 | 3.6 | 3.5 | 3.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Heddon Cross | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 3.7 | 3.6 | 3.6 | 3.5 | 3.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Holsworthy | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.9 | 3.4 | 3.2 | 2.9 | 2.5 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Holsworthy | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.9 | 3.2 | 2.9 | 2.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Holsworthy | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.9 | 3.3 | 3.2 | 2.6 | 2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Holsworthy | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.9 | 3.3 | 3 | 2.6 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Ilfracombe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Ilfracombe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Ilfracombe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Ilfracombe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Launceston | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Launceston | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Launceston | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Launceston | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Lynton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Lynton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.7 | 2.7 | 2.7 | 2.6 | 2.6 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Lynton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.6 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Lynton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.7 | 2.7 | 2.7 | 2.7 | 2.6 | 2.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Middle Barlington | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Middle Barlington | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Middle Barlington | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Middle Barlington | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Mortonhampstead | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2 | 1.9 | 1.9 | 1.9 | 1.8 | 1.8 | 1.6 | 1.6 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Mortonhampstead | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2 | 1.9 | 1.8 | 1.8 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Mortonhampstead | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2 | 1.9 | 1.9 | 1.9 | 1.8 | 1.8 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Mortonhampstead | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2 | 1.9 | 1.9 | 1.8 | 1.7 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Morwenstow | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.1 | 7.7 | 7.4 | 7.1 | 6.7 | 6.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Morwenstow | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.1 | 7.5 | 7 | 6.4 | 5.3 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Morwenstow | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.1 | 7.7 | 7.3 | 6.8 | 6.2 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Morwenstow | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.1 | 7.6 | 7.2 | 6.7 | 5.7 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | North Tawton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.3 | 2.4 | 2.4 | 2.4 | 2.4 | 2.5 | 1.6 | 1.6 | 1.4 | 1.3 | 1.2 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | North Tawton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.3 | 2.4 | 2.3 | 2.2 | 2.2 | 2.2 | 1.2 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | North Tawton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.3 | 2.4 | 2.4 | 2.5 | 2.5 | 2.5 | 1.6 | 1.5 | 1.2 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | North Tawton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.3 | 2.4 | 2.4 | 2.3 | 2.4 | 2.4 | 1.4 | 1.2 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | North Tawton Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 2.4 | 2.4 | 2.4 | 2.5 | 2.4 | 1.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | North Tawton Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 2.4 | 2.4 | 2.3 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | North Tawton Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 2.4 | 2.4 | 2.4 | 2.5 | 1.8 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | North Tawton Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 2.4 | 2.4 | 2.4 | 2.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Northam | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.7 | 11.6 | 11.4 | 11.2 | 11.1 | 10.9 | 10.6 | 10.3 | 9.9 | 9.5 | 9.2 | 9 | 8.6 | 8.3 | 7.9 | 7.5 | 7.2 | 5.2 | 3.8
Alverdiscott 132 kV | Northam | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.7 | 11.5 | 11.2 | 10.9 | 10.5 | 10.1 | 9.5 | 8.6 | 7.9 | 7.4 | 7 | 6.6 | 6.2 | 5.8 | 5.4 | 5 | 4.7 | 3.1 | 1.8
Alverdiscott 132 kV | Northam | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.7 | 11.5 | 11.4 | 11.1 | 10.8 | 10.5 | 10.1 | 9.5 | 8.9 | 8.5 | 8.1 | 7.6 | 7 | 6.4 | 5.9 | 5.3 | 4.9 | 3.2 | 2.1
Alverdiscott 132 kV | Northam | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.7 | 11.5 | 11.3 | 11 | 10.7 | 10.4 | 9.9 | 9.2 | 8.6 | 8.2 | 7.8 | 7.3 | 6.8 | 6.4 | 5.9 | 5.4 | 5.1 | 3.7 | 3.2
Alverdiscott 132 kV | Okehampton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.9 | 2.6 | 2.5 | 2.3 | 2 | 1.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Okehampton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.9 | 2.5 | 2.2 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Okehampton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.9 | 2.6 | 2.4 | 2 | 1.6 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Okehampton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.9 | 2.6 | 2.3 | 2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Park Lane SWEB | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Park Lane SWEB | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Park Lane SWEB | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Park Lane SWEB | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Pyworthy Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 49.2 | 48.2 | 47.6 | 46.8 | 45 | 41.9 | 39.2 | 36.2 | 32.9 | 30.7 | 27.7 | 24.2 | 20.3 | 15.9 | 11.7 | 7.8 | 2.4 | 0 | 0
Alverdiscott 132 kV | Pyworthy Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 49.2 | 47.7 | 46.6 | 43.8 | 39.2 | 34.5 | 30.4 | 24.5 | 17.3 | 11.5 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Pyworthy Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 49.2 | 48 | 47.4 | 45.3 | 42.5 | 39.6 | 36.1 | 31.2 | 25.3 | 18.8 | 13.2 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Pyworthy Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 49.2 | 47.9 | 47.1 | 45.1 | 40.8 | 36.7 | 32.7 | 27.8 | 21.9 | 15.2 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Rock Park | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.6 | 10.4 | 10.2 | 9.9 | 9.3 | 8.6 | 4.3 | 2.8 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Rock Park | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.6 | 10.2 | 9.8 | 9.2 | 8.4 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Rock Park | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.6 | 10.3 | 10 | 9.6 | 9 | 8.2 | 3.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Rock Park | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.6 | 10.2 | 9.9 | 9.4 | 8.7 | 7.8 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Roundswell | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.5 | 8.3 | 8 | 7.9 | 7.6 | 7.4 | 7.2 | 7 | 6.7 | 6.5 | 6.2 | 5.9 | 5.3 | 4.4 | 3.4 | 2.4 | 1.7 | 0 | 0
Alverdiscott 132 kV | Roundswell | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.5 | 8.1 | 7.7 | 7.3 | 6.8 | 6.3 | 6 | 5.3 | 4.4 | 3.3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Roundswell | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.5 | 8.1 | 7.8 | 7.5 | 7.1 | 6.7 | 6.4 | 5.8 | 5 | 4.4 | 3.7 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Roundswell | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.5 | 8.1 | 7.8 | 7.5 | 7 | 6.6 | 6.3 | 5.8 | 5.1 | 4.3 | 3.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Shebbear | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.5 | 2.4 | 2.4 | 2.4 | 2.3 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Shebbear | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.5 | 2.4 | 2.3 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Shebbear | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.5 | 2.4 | 2.4 | 2.4 | 1.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Shebbear | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.5 | 2.4 | 2.4 | 2.3 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | South Molton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.6 | 4.4 | 4.3 | 4.2 | 4.1 | 3.9 | 3.6 | 3.2 | 2.9 | 2.6 | 2.3 | 2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | South Molton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.6 | 4.3 | 4.1 | 3.8 | 3.6 | 3.2 | 2.6 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | South Molton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.6 | 4.4 | 4.3 | 4.1 | 4 | 3.7 | 3.1 | 2.4 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | South Molton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.6 | 4.4 | 4.2 | 4 | 3.7 | 3.3 | 2.8 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Stratton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.2 | 7.8 | 7.5 | 7.2 | 6.8 | 6.2 | 5.1 | 4.5 | 3.7 | 3.1 | 2.5 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Stratton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.2 | 7.6 | 7.1 | 6.4 | 5.3 | 4.4 | 2.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Stratton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.2 | 7.7 | 7.4 | 6.9 | 6.3 | 5.7 | 4.4 | 3.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Stratton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.2 | 7.7 | 7.3 | 6.8 | 5.8 | 5 | 3.6 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Tinkers Cross | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Tinkers Cross | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Tinkers Cross | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Tinkers Cross | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Whiddon Down | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.1 | 2 | 2 | 2 | 1.9 | 1.9 | 1.6 | 1.6 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Whiddon Down | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.1 | 2 | 1.9 | 1.8 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Whiddon Down | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.1 | 2 | 2 | 1.9 | 1.9 | 1.8 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Whiddon Down | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.1 | 2 | 2 | 1.9 | 1.8 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Axminster | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7 | 6.6 | 6.4 | 6.1 | 5.6 | 4.9 | 4.2 | 3.3 | 2.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Axminster | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7 | 6.3 | 5.8 | 5 | 4 | 2.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Axminster | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7 | 6.4 | 6.2 | 5.7 | 5 | 4.2 | 3.2 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Axminster | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7 | 6.4 | 6 | 5.5 | 4.6 | 3.6 | 2.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Beaminster | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.7 | 5.6 | 5.5 | 5.3 | 5.1 | 4.9 | 4.8 | 4.7 | 4.4 | 4.3 | 4.1 | 3.8 | 3.5 | 3.1 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Beaminster | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.7 | 5.5 | 5.4 | 5 | 4.7 | 4.5 | 4.2 | 3.8 | 3.3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Beaminster | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.7 | 5.6 | 5.5 | 5.2 | 5.1 | 4.9 | 4.7 | 4.4 | 4 | 3.6 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Beaminster | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.7 | 5.6 | 5.4 | 5.1 | 4.9 | 4.7 | 4.4 | 4.1 | 3.8 | 3.3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Bridport | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.7 | 5.5 | 5.2 | 4.8 | 4 | 3.2 | 1.3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Bridport | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.7 | 5.2 | 4.7 | 3.9 | 2.9 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Bridport | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.7 | 5.3 | 5 | 4.5 | 3.7 | 2.9 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Bridport | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.7 | 5.3 | 4.9 | 4.2 | 3.2 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Chard | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.3 | 6.1 | 5.8 | 5.7 | 5.1 | 4.2 | 2.9 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Chard | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.3 | 5.9 | 5.4 | 4.7 | 3.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Chard | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.3 | 6 | 5.6 | 4.9 | 4 | 3.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Chard | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.3 | 6 | 5.5 | 4.9 | 3.7 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Coker | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.3 | 3.3 | 3.2 | 3.1 | 3 | 2.9 | 2.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Coker | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.3 | 3.2 | 3.1 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Coker | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.3 | 3.3 | 3.2 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Coker | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.3 | 3.3 | 2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Colyford | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.4 | 6 | 5.9 | 5.6 | 5.2 | 4.7 | 3.9 | 3.2 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Colyford | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.4 | 5.8 | 5.3 | 4.6 | 3.8 | 2.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Colyford | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.4 | 5.9 | 5.7 | 5.3 | 4.7 | 4.1 | 3.1 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Colyford | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.4 | 5.9 | 5.6 | 5.1 | 4.3 | 3.5 | 2.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Crewkerne | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.4 | 7.1 | 6.8 | 6.7 | 6.1 | 5.3 | 4 | 3.3 | 2.5 | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Crewkerne | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.4 | 6.9 | 6.3 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Crewkerne | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.4 | 7 | 6.6 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Crewkerne | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.4 | 7 | 2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Dowlish Ford | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.4 | 5.1 | 4.7 | 4.5 | 4 | 3 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Dowlish Ford | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.4 | 4.9 | 4.2 | 3.4 | 2.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Dowlish Ford | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.4 | 5 | 4.5 | 3.8 | 2.8 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Dowlish Ford | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.4 | 5 | 4.4 | 3.7 | 2.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | East Chinnock Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 3.7 | 3.7 | 3.6 | 3.6 | 3.6 | 2.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | East Chinnock Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 3.7 | 3.6 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | East Chinnock Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 3.7 | 3.7 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | East Chinnock Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 3.7 | 2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Martock | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.1 | 3.1 | 3 | 3 | 3 | 2.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Martock | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.1 | 3 | 2.9 | 2.8 | 2.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Martock | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.1 | 3 | 3 | 2.9 | 2.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Martock | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.1 | 3 | 3 | 2.9 | 2.4 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Montacute | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 4 | 3.9 | 3.9 | 3.7 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Montacute | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 3.8 | 3.6 | 3.3 | 2.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Montacute | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 3.9 | 3.8 | 3.2 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Montacute | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 3.9 | 3.7 | 3.5 | 2.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Penn Cross | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 6.2 | 6 | 5.8 | 5.3 | 4.8 | 4.1 | 3.4 | 2.4 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Penn Cross | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 5.9 | 5.5 | 4.8 | 3.9 | 2.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Penn Cross | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 6.1 | 5.8 | 5.4 | 4.9 | 4.2 | 3.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Penn Cross | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 6 | 5.7 | 5.2 | 4.4 | 3.6 | 2.6 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Waterlake Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.9 | 4.6 | 4.3 | 4.1 | 3.6 | 2.7 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Waterlake Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.9 | 4.4 | 3.8 | 3.1 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Waterlake Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.9 | 4.5 | 4.1 | 3.5 | 2.6 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Waterlake Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.9 | 4.5 | 4 | 3.4 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Woodcote Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 24.9 | 24 | 23.1 | 22.3 | 20.5 | 18.2 | 15.8 | 13.6 | 10.5 | 7.9 | 4.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Woodcote Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 24.9 | 23.2 | 21.4 | 18.8 | 10.7 | 6.6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Woodcote Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 24.9 | 23.6 | 22.4 | 16 | 13.5 | 10.7 | 8 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Woodcote Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 24.9 | 23.4 | 17.3 | 15.3 | 12.1 | 8.8 | 5.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bath Road Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 4.6 | 4.1 | 3.4 | 3.4 | 3.4 | 3 | 2.6 | 2.2 | 1.9 | 1.5 | 0.6 | 0 | 0
Bridgwater 132 kV | Bath Road Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 2.9 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bath Road Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 4.4 | 3.6 | 2.8 | 2.6 | 2.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bath Road Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 3.3 | 2.4 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bridgwater Grid Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 25.4 | 20.1 | 17.6 | 14.8 | 11.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bridgwater Grid Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 25.4 | 17.8 | 13.1 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bridgwater Grid Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 25.4 | 18.8 | 15.5 | 11.2 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bridgwater Grid Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 25.4 | 18.5 | 14.8 | 9.9 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bridgwater Local | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 6.5 | 6 | 5.5 | 5 | 4.5 | 4 | 3.6 | 3.1 | 2.8 | 2.5 | 2.1 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bridgwater Local | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 6.2 | 5.5 | 4.5 | 3.8 | 2.9 | 2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bridgwater Local | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 6.3 | 5.6 | 4.9 | 4.2 | 3.6 | 2.9 | 2.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bridgwater Local | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 6.3 | 5.6 | 5 | 4.3 | 3.6 | 2.9 | 2.2 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Burnham | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Burnham | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Burnham | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Burnham | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Colley Lane | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.4 | 4.5 | 4.3 | 4.2 | 4 | 3.7 | 3.2 | 2.9 | 2.4 | 2.2 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Colley Lane | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.4 | 4.2 | 3.9 | 3.3 | 2.8 | 2.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Colley Lane | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.4 | 4.3 | 4.1 | 3.8 | 3.5 | 3.1 | 2.4 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Colley Lane | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.4 | 4.3 | 4.1 | 3.7 | 3.2 | 2.8 | 2.1 | 1.4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Creech St Michael | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8 | 7.8 | 7.8 | 7.7 | 7.6 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Creech St Michael | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8 | 7.7 | 7.6 | 7.3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Creech St Michael | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8 | 7.8 | 7.7 | 7.5 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Creech St Michael | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8 | 7.8 | 7.7 | 7.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Curry Mallet | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.6 | 3.5 | 3.5 | 3.5 | 3.4 | 3.4 | 3.3 | 3.3 | 3.2 | 3.1 | 3 | 2.9 | 2.8 | 2.6 | 2.4 | 2.3 | 2.1 | 1.4 | 0.6
Bridgwater 132 kV | Curry Mallet | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.6 | 3.5 | 3.5 | 3.4 | 3.3 | 3.2 | 3.1 | 2.9 | 2.7 | 2.5 | 2.3 | 2.1 | 1.9 | 1.7 | 1.5 | 1.3 | 1.1 | 0.7 | 0
Bridgwater 132 kV | Curry Mallet | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.6 | 3.5 | 3.5 | 3.5 | 3.4 | 3.4 | 3.3 | 3.1 | 2.9 | 2.7 | 2.5 | 2.3 | 2 | 1.8 | 1.6 | 1.3 | 1.1 | 0.6 | 0
Bridgwater 132 kV | Curry Mallet | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.6 | 3.5 | 3.5 | 3.4 | 3.4 | 3.3 | 3.2 | 3.1 | 2.9 | 2.7 | 2.4 | 2.2 | 1.9 | 1.6 | 1.4 | 1.2 | 1 | 0.6 | 0
Bridgwater 132 kV | Edgarley | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.5 | 2.2 | 2 | 1.7 | 1.1 | 0 | 6.8 | 6.7 | 6.6 | 6.4 | 6.2 | 6 | 5.7 | 5.5 | 5.3 | 5.1 | 4.9 | 3.7 | 0.8
Bridgwater 132 kV | Edgarley | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.5 | 1.9 | 1.4 | 0 | 0 | 0 | 6.4 | 6.1 | 5.8 | 5.3 | 4.9 | 4.7 | 4.5 | 4.3 | 4 | 3.5 | 2.7 | 0 | 0
Bridgwater 132 kV | Edgarley | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.5 | 2 | 1.7 | 1.2 | 0 | 0 | 6.7 | 6.4 | 6 | 5.8 | 5.6 | 5.3 | 5 | 4.7 | 4.3 | 3.9 | 2.8 | 0 | 0
Bridgwater 132 kV | Edgarley | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.5 | 2 | 1.6 | 1 | 0 | 0 | 6.5 | 6.4 | 6.1 | 5.7 | 5.4 | 5.1 | 4.8 | 4.5 | 4.2 | 3.9 | 3.1 | 0.6 | 0
Bridgwater 132 kV | Martock | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2 | 1.6 | 1.4 | 1.1 | 0.5 | 0 | 1.5 | 1.3 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Martock | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2 | 1.3 | 0.7 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Martock | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2 | 1.4 | 1.1 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Martock | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2 | 1.4 | 1 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Millfield | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.6 | 2.2 | 2 | 1.7 | 1.2 | 0 | 4.5 | 3.9 | 3.2 | 2.7 | 2.2 | 1.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Millfield | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.6 | 1.9 | 1.4 | 0 | 0 | 0 | 2.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Millfield | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.6 | 2.1 | 1.8 | 0.9 | 0 | 0 | 3.8 | 2.8 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Millfield | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.6 | 2 | 1.6 | 0.7 | 0 | 0 | 3.1 | 2.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Nether Stowey | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.5 | 6.4 | 6.4 | 6.3 | 6.2 | 6.2 | 6.2 | 6.1 | 6 | 5.8 | 5.7 | 5.6 | 5.3 | 5.1 | 4.8 | 4.5 | 4.3 | 1.3 | 0
Bridgwater 132 kV | Nether Stowey | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.5 | 6.3 | 6.2 | 6.1 | 5.9 | 5.8 | 5.8 | 5.5 | 5.2 | 4.8 | 4.6 | 4.3 | 3.4 | 2.1 | 1 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Nether Stowey | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.5 | 6.4 | 6.3 | 6.2 | 6.2 | 6.1 | 6.2 | 6 | 5.8 | 5.6 | 5.4 | 5.1 | 4.7 | 4.3 | 3.1 | 1.5 | 0 | 0 | 0
Bridgwater 132 kV | Nether Stowey | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.5 | 6.4 | 6.3 | 6.2 | 6.1 | 6 | 5.9 | 5.8 | 5.5 | 5.3 | 5.1 | 4.8 | 4.4 | 3.5 | 2 | 1 | 0 | 0 | 0
Bridgwater 132 kV | North Street Langport | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.3 | 7.2 | 7.1 | 7.1 | 7 | 6.8 | 6.1 | 5.9 | 5.6 | 5.4 | 5.1 | 4.8 | 4.4 | 3.9 | 3.5 | 3.1 | 2.7 | 0.9 | 0
Bridgwater 132 kV | North Street Langport | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.3 | 7.1 | 7 | 6.8 | 6.5 | 6.1 | 5.3 | 4.8 | 4.3 | 3.6 | 3.1 | 2.6 | 2.2 | 1.8 | 1.4 | 1.1 | 0.7 | 0 | 0
Bridgwater 132 kV | North Street Langport | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.3 | 7.2 | 7.1 | 7 | 6.8 | 6.6 | 5.9 | 5.4 | 4.8 | 4.4 | 3.9 | 3.4 | 2.8 | 2.3 | 1.8 | 1.3 | 0.8 | 0 | 0
Bridgwater 132 kV | North Street Langport | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.3 | 7.1 | 7.1 | 6.9 | 6.7 | 6.4 | 5.6 | 5.3 | 4.9 | 4.4 | 3.9 | 3.3 | 2.7 | 2.1 | 1.5 | 1 | 0.6 | 0 | 0
Bridgwater 132 kV | Shapwick | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.2 | 2.2 | 2.1 | 2.1 | 2 | 1.9 | 1.8 | 1.7 | 1.5 | 1.4 | 1.3 | 1.2 | 0.9 | 0.7 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Shapwick | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.2 | 2.1 | 2 | 0.6 | 0 | 0 | 1.4 | 1.1 | 0.8 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Shapwick | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.2 | 2.1 | 2.1 | 2 | 0 | 0 | 1.7 | 1.6 | 1.4 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Shapwick | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.2 | 2.1 | 2.1 | 2 | 0 | 0 | 1.6 | 1.4 | 1.1 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Somerton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.2 | 1.7 | 1.5 | 1.2 | 0.6 | 0 | 5.1 | 4.8 | 4.4 | 4.1 | 3.7 | 3.3 | 2.7 | 2.1 | 1.4 | 0.9 | 0 | 0 | 0
Bridgwater 132 kV | Somerton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.2 | 1.4 | 0.8 | 0 | 0 | 0 | 3.8 | 3.1 | 2.3 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Somerton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.2 | 1.6 | 1.2 | 0 | 0 | 0 | 4.3 | 3.5 | 2.6 | 2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Somerton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.2 | 1.5 | 1.1 | 0 | 0 | 0 | 4.2 | 3.5 | 2.8 | 2.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Street Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 6.6 | 5.7 | 5.2 | 4.5 | 3 | 1.3 | 13.1 | 11.5 | 9.4 | 7.8 | 5.8 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Street Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 6.6 | 4.7 | 3.1 | 0 | 0 | 0 | 6.6 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Street Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 6.6 | 5.2 | 4.4 | 2.2 | 0 | 0 | 10.5 | 6.8 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Street Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 6.6 | 5 | 3.9 | 2 | 0 | 0 | 8.7 | 5.7 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Watchfield | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Watchfield | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Watchfield | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Watchfield | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Wedmore | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.4 | 2.1 | 1.9 | 1.6 | 1.1 | 0 | 3.1 | 3 | 3 | 2.9 | 2.8 | 2.8 | 2.6 | 2.5 | 2.4 | 2.2 | 2.1 | 1.4 | 0.8
Bridgwater 132 kV | Wedmore | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.4 | 1.8 | 1.4 | 0 | 0 | 0 | 2.9 | 2.8 | 2.6 | 2.4 | 2.3 | 2.1 | 2 | 1.9 | 1.7 | 1.6 | 1.4 | 0 | 0
Bridgwater 132 kV | Wedmore | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.4 | 2 | 1.7 | 1.2 | 0 | 0 | 3.1 | 3 | 2.9 | 2.8 | 2.6 | 2.5 | 2.3 | 2.1 | 1.9 | 1.7 | 1.6 | 0 | 0
Bridgwater 132 kV | Wedmore | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.4 | 1.9 | 1.6 | 0.9 | 0 | 0 | 3 | 2.9 | 2.8 | 2.7 | 2.5 | 2.4 | 2.2 | 2 | 1.8 | 1.6 | 1.4 | 0.6 | 0
Bridgwater 132 kV | Wells | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5 | 4.8 | 4.7 | 4.1 | 2.7 | 1.2 | 3.6 | 3.2 | 2.8 | 2.5 | 2.1 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Wells | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5 | 4.2 | 2.8 | 0 | 0 | 0 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Wells | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5 | 4.7 | 4 | 2 | 0 | 0 | 3 | 2.2 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Wells | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5 | 4.6 | 3.6 | 1.8 | 0 | 0 | 2.5 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Athelstan Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.4 | 5.2 | 5.2 | 5 | 4.8 | 4.6 | 4.5 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Athelstan Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.4 | 5 | 4.7 | 4.4 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Athelstan Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.4 | 5 | 4.9 | 4.7 | 4.5 | 1.6 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Athelstan Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.4 | 5 | 4.8 | 4.5 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Bridge Mills | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 3.5 | 3.3 | 3.1 | 2.6 | 1.9 | 6.4 | 6.3 | 6.1 | 4.7 | 3.3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Bridge Mills | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 3.4 | 3 | 2.5 | 1.7 | 0.6 | 5.9 | 5.2 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Bridge Mills | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 3.5 | 3.2 | 2.9 | 2.3 | 1.4 | 6.2 | 5.9 | 4.4 | 2.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Bridge Mills | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 3.4 | 3.1 | 2.7 | 1.9 | 0.9 | 6 | 5.7 | 3.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Budleigh Salterton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.5 | 4.5 | 4.4 | 4.4 | 4.3 | 4.2 | 4.1 | 4 | 3.8 | 3.7 | 3.6 | 3.4 | 3.2 | 2.9 | 1.5 | 0 | 0 | 0 | 0
Exeter 132 kV | Budleigh Salterton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.5 | 4.4 | 4.3 | 4.2 | 4.1 | 3.9 | 3.7 | 3.4 | 3.1 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Budleigh Salterton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.5 | 4.4 | 4.4 | 4.3 | 4.2 | 4.1 | 4 | 3.8 | 3.5 | 3.3 | 2.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Budleigh Salterton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.5 | 4.4 | 4.4 | 4.3 | 4.2 | 4.1 | 3.9 | 3.7 | 3.4 | 3.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Burlescombe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Burlescombe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.1 | 1 | 1 | 1 | 1 | 0 | 0.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Burlescombe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Burlescombe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.1 | 1 | 1 | 1 | 1 | 0.7 | 0.8 | 0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Clyst Honiton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.5 | 1.2 | 0.9 | 0.5 | 0 | 0 | 10.7 | 7.8 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Clyst Honiton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.5 | 1.1 | 0.7 | 0 | 0 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Clyst Honiton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.5 | 1.2 | 0.8 | 0 | 0 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Clyst Honiton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.5 | 1.1 | 0.7 | 0 | 0 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Core Hill | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.1 | 0.8 | 0.8 | 0.6 | 0 | 0 | 3 | 2.2 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Core Hill | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Core Hill | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.1 | 0.7 | 0.6 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Core Hill | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.1 | 0.7 | 0.5 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Countess Wear | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.1 | 8 | 7.9 | 7.7 | 7.7 | 7.4 | 7.1 | 6.8 | 6.6 | 6.3 | 6.1 | 5.8 | 5.4 | 5 | 4.6 | 4.3 | 3.8 | 2.1 | 1.1
Exeter 132 kV | Countess Wear | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.1 | 7.9 | 7.7 | 7.5 | 6.9 | 6.4 | 6 | 5.5 | 4.9 | 4.4 | 4 | 3.6 | 2.8 | 2.2 | 1.9 | 1.6 | 1.3 | 0 | 0
Exeter 132 kV | Countess Wear | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.1 | 7.9 | 7.8 | 7.2 | 6.9 | 6.6 | 6.3 | 5.9 | 5.5 | 5.1 | 4.8 | 4.3 | 3.8 | 3.3 | 2.9 | 2.2 | 1.7 | 0.5 | 0
Exeter 132 kV | Countess Wear | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.1 | 7.9 | 7.7 | 7.5 | 7.2 | 6.8 | 6.5 | 6.1 | 5.7 | 5.3 | 4.9 | 4.4 | 3.9 | 3.2 | 2.5 | 2.2 | 1.9 | 1.1 | 0.8
Exeter 132 kV | Cowley Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.7 | 7.5 | 7.3 | 7.1 | 6.9 | 6.7 | 6 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Cowley Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.7 | 7.1 | 6.7 | 6.3 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Cowley Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.7 | 7.2 | 6.8 | 6.5 | 6.1 | 1.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Cowley Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.7 | 7.1 | 6.8 | 6.4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Crediton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.4 | 5 | 4.7 | 4.3 | 3.7 | 2.8 | 2.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Crediton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.4 | 4.8 | 4.3 | 3.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Crediton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.4 | 5 | 4.6 | 4.2 | 3.4 | 0.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Crediton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.4 | 4.9 | 4.5 | 3.9 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Cullompton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.6 | 3.4 | 3.1 | 2.6 | 1.9 | 6.4 | 5.3 | 4.1 | 3.1 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Cullompton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3.5 | 3.1 | 2.5 | 1.8 | 0.6 | 5 | 3.4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Cullompton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.5 | 3.3 | 2.9 | 2.3 | 1.4 | 5.9 | 4.5 | 2.9 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Cullompton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.5 | 3.2 | 2.8 | 2 | 0.9 | 5.2 | 3.8 | 2.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Dunkeswell 33/11kv | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.4 | 3.3 | 3.1 | 3 | 2.7 | 2.2 | 3.2 | 3.2 | 3.1 | 3 | 2.9 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Dunkeswell 33/11kv | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.4 | 3 | 2.6 | 2 | 1.2 | 0 | 2.9 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Dunkeswell 33/11kv | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.4 | 3.2 | 2.9 | 2.5 | 2 | 1.4 | 2.9 | 2.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Dunkeswell 33/11kv | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.4 | 3.1 | 2.8 | 2.4 | 1.6 | 0.8 | 2.9 | 2.7 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | East Budleigh | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 3.6 | 3.6 | 3.5 | 3.4 | 3.4 | 3.3 | 3.2 | 3.1 | 3 | 2.9 | 2.8 | 2.6 | 2.4 | 1.5 | 0 | 0 | 0 | 0
Exeter 132 kV | East Budleigh | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 3.6 | 3.5 | 3.4 | 3.3 | 3.2 | 3 | 2.8 | 2.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | East Budleigh | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 3.6 | 3.6 | 3.5 | 3.4 | 3.3 | 3.2 | 3.1 | 2.9 | 2.7 | 2.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | East Budleigh | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 3.6 | 3.6 | 3.5 | 3.4 | 3.3 | 3.1 | 3 | 2.8 | 2.6 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter City Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 14.5 | 5.4 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter City Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 14.5 | 3.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter City Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 14.5 | 4.2 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter City Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 14.5 | 4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter Main Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 37.4 | 33 | 31.9 | 30.5 | 29 | 26.8 | 22.5 | 20 | 16.9 | 14.4 | 11.5 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter Main Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 37.4 | 31.9 | 29.7 | 26.8 | 23.3 | 19.1 | 13.5 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter Main Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 37.4 | 32.3 | 30.7 | 28.3 | 25.8 | 22.7 | 17.8 | 13.4 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter Main Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 37.4 | 32.1 | 30.3 | 28.2 | 25.1 | 21.5 | 16 | 11.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter Science Park | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.1 | 16 | 15.9 | 15.8 | 15.8 | 15.1 | 5.9 | 5.3 | 4.6 | 4 | 3.7 | 3.6 | 3.5 | 3.5 | 3.4 | 3.4 | 3.4 | 0 | 0
Exeter 132 kV | Exeter Science Park | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.1 | 16 | 15.9 | 15.8 | 14.6 | 13.6 | 4.1 | 3.3 | 2.9 | 3 | 3.1 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter Science Park | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.1 | 16 | 15.9 | 15.1 | 14.3 | 13.6 | 4.3 | 3.6 | 3.1 | 3.1 | 3.2 | 3.1 | 3.1 | 2.3 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter Science Park | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.1 | 16 | 15.8 | 15.7 | 14.7 | 13.8 | 4.5 | 3.7 | 3.2 | 3.2 | 3.2 | 3.2 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exminster | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exminster | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exminster | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exminster | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exmouth Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 13.3 | 12.7 | 12.1 | 11.5 | 10.6 | 9.4 | 7.7 | 6.2 | 4.2 | 2.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exmouth Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 13.3 | 12.1 | 10.9 | 9.4 | 0 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exmouth Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 13.3 | 12.3 | 11.6 | 10.6 | 0 | 0 | 5.9 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exmouth Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 13.3 | 12.2 | 11.3 | 10.2 | 0 | 0 | 4.4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exmouth Works | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2 | 1.8 | 1.7 | 1.5 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exmouth Works | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2 | 1.7 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exmouth Works | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2 | 1.7 | 1.6 | 1.3 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exmouth Works | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2 | 1.7 | 1.5 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Folly Bridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.5 | 3.3 | 3.2 | 3 | 2.5 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Folly Bridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.5 | 3.2 | 3 | 2.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Folly Bridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.5 | 3.3 | 3.2 | 2.9 | 2.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Folly Bridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.5 | 3.3 | 3.1 | 2.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Haven Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.4 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Haven Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Haven Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Haven Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Heavitree | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2.8 | 2.5 | 2.2 | 2 | 1.6 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Heavitree | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Heavitree | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 1.9 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Heavitree | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Hemyock | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.3 | 3.2 | 3 | 2.9 | 2.6 | 2.1 | 6.1 | 5.4 | 4.5 | 3.8 | 3.1 | 2.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Hemyock | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.3 | 2.9 | 2.5 | 2 | 1.1 | 0 | 3.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Hemyock | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.3 | 3.1 | 2.8 | 2.4 | 1.9 | 1.3 | 4.9 | 3.6 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Hemyock | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.3 | 3 | 2.7 | 2.3 | 1.6 | 0.8 | 4.2 | 2.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Hill Barton Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.2 | 0.9 | 0.9 | 0.7 | 0.6 | 0 | 3.9 | 2.9 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Hill Barton Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.2 | 0.7 | 0.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Hill Barton Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.2 | 0.8 | 0.7 | 0 | 0 | 0 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Hill Barton Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.2 | 0.8 | 0.6 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Honiton Heathfield | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.5 | 3.3 | 3.2 | 3.1 | 2.8 | 2.5 | 2.3 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Honiton Heathfield | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.5 | 3.1 | 2.8 | 2.4 | 1.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Honiton Heathfield | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.5 | 3.2 | 3 | 2.8 | 2.4 | 1.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Honiton Heathfield | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.5 | 3.2 | 3 | 2.6 | 2.1 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Lapford | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.7 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Lapford | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.7 | 1.6 | 1.6 | 1.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Lapford | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.7 | 1.6 | 1.6 | 1.6 | 1.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Lapford | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.7 | 1.6 | 1.6 | 1.6 | 1.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Marsh Barton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.2 | 13 | 12.8 | 12.4 | 12.1 | 8 | 10.8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Marsh Barton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.2 | 12.8 | 12.4 | 11.4 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Marsh Barton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.2 | 12.8 | 12.4 | 11.5 | 9.7 | 1.7 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Marsh Barton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.2 | 12.8 | 12.5 | 11.9 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Marsh Green | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 1.2 | 0.9 | 0.6 | 0 | 0 | 6.2 | 4.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Marsh Green | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 1.2 | 0.7 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Marsh Green | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 1.2 | 0.8 | 0 | 0 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Marsh Green | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 1.2 | 0.8 | 0 | 0 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Newton Poppleford | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.5 | 2.4 | 2.4 | 2.4 | 2.3 | 2.3 | 2 | 1.9 | 1.7 | 1.6 | 1.5 | 1.4 | 1.2 | 1.1 | 0.9 | 0 | 0 | 0 | 0
Exeter 132 kV | Newton Poppleford | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.5 | 2.4 | 2.4 | 2.3 | 2.2 | 2 | 1.7 | 1.4 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Newton Poppleford | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.5 | 2.4 | 2.4 | 2.3 | 2.3 | 2.2 | 1.8 | 1.6 | 1.4 | 1.2 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Newton Poppleford | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.5 | 2.4 | 2.4 | 2.3 | 2.2 | 2.1 | 1.8 | 1.6 | 1.4 | 1.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Newton St Cyres | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.9 | 2.9 | 2.9 | 2.8 | 2.8 | 2.8 | 2.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Newton St Cyres | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.9 | 2.8 | 2.8 | 2.7 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Newton St Cyres | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.9 | 2.9 | 2.8 | 2.8 | 2.8 | 0.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Newton St Cyres | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.9 | 2.9 | 2.8 | 2.8 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Offwell | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Offwell | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Offwell | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Offwell | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Ottery St Mary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.9 | 7.8 | 7.8 | 7.6 | 7.5 | 6.7 | 6.2 | 4.5 | 2.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Ottery St Mary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.9 | 7.7 | 7.6 | 6.8 | 4.9 | 2.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Ottery St Mary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.9 | 7.8 | 7.7 | 7.5 | 6.1 | 4.2 | 3.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Ottery St Mary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.9 | 7.8 | 7.6 | 7.4 | 5.8 | 3.7 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Pinhoe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 1.7 | 1.2 | 0.7 | 0 | 0 | 5.8 | 5.4 | 4.8 | 4.4 | 4.1 | 3.6 | 3 | 2.3 | 1.6 | 1 | 0 | 0 | 0
Exeter 132 kV | Pinhoe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 1.4 | 0.7 | 0 | 0 | 0 | 4 | 2.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Pinhoe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 1.5 | 0.9 | 0 | 0 | 0 | 5.2 | 4.4 | 3.5 | 2.8 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Pinhoe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 1.5 | 0.8 | 0 | 0 | 0 | 4.6 | 3.8 | 2.8 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Sidmouth Town | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.1 | 1.5 | 1.4 | 1.1 | 0.8 | 0 | 3 | 2.2 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Sidmouth Town | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.1 | 1.2 | 0.8 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Sidmouth Town | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.1 | 1.3 | 1 | 0 | 0 | 0 | 1.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Sidmouth Town | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.1 | 1.3 | 1 | 0.6 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Sowton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.6 | 9.5 | 9.5 | 9.4 | 9.3 | 9.2 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 8.9 | 8.8 | 8.7 | 8.6 | 8.5 | 8.1 | 6.3 | 4.6
Exeter 132 kV | Sowton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.6 | 9.4 | 9.2 | 8.9 | 8.8 | 8.5 | 8.3 | 8 | 7.7 | 7.4 | 7.1 | 6.4 | 5.5 | 4.5 | 3.7 | 2.9 | 2 | 0 | 0
Exeter 132 kV | Sowton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.6 | 9.4 | 9.3 | 9 | 8.8 | 8.7 | 8.5 | 8.3 | 8.2 | 8 | 7.8 | 7.2 | 6.5 | 5.7 | 5 | 4.2 | 3.4 | 0 | 0
Exeter 132 kV | Sowton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.6 | 9.4 | 9.3 | 9.1 | 8.9 | 8.7 | 8.5 | 8.4 | 8.2 | 8.1 | 7.9 | 7.4 | 6.6 | 5.8 | 5 | 4.3 | 3.8 | 2.2 | 1.4
Exeter 132 kV | Sowton B | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.9 | 15.9 | 15.9 | 16 | 16.1 | 16.1 | 16.2 | 16.3 | 16.4 | 16.4 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 8.8 | 0 | 0
Exeter 132 kV | Sowton B | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.9 | 15.9 | 15.9 | 16 | 16.1 | 16.1 | 16.2 | 16.3 | 16.4 | 16.4 | 15.2 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Sowton B | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.9 | 15.9 | 15.9 | 16 | 16.1 | 16.1 | 16.2 | 16.3 | 16.4 | 16.4 | 16.5 | 16.5 | 11.1 | 2.6 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Sowton B | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.9 | 15.9 | 15.9 | 16 | 16.1 | 16.1 | 16.2 | 16.3 | 16.4 | 16.4 | 16.5 | 13.2 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Sowton Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 35.4 | 28.5 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Sowton Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 35.4 | 24.2 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Sowton Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 35.4 | 25.7 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Sowton Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 35.4 | 25.1 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | St Thomas | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.8 | 11.7 | 11.6 | 11.4 | 11.1 | 10.7 | 10.2 | 10 | 9.6 | 9.3 | 9 | 8.6 | 8 | 7.5 | 6.9 | 6.4 | 5.9 | 0 | 0
Exeter 132 kV | St Thomas | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.8 | 11.5 | 11.2 | 10.7 | 10.2 | 9.5 | 8.7 | 7.8 | 6.8 | 5.7 | 5 | 4.2 | 3.7 | 3.1 | 2.5 | 1.9 | 1.4 | 0 | 0
Exeter 132 kV | St Thomas | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.8 | 11.6 | 11.4 | 11 | 10.7 | 10.3 | 9.8 | 9.3 | 8.5 | 8 | 7.3 | 6.5 | 5.7 | 4.8 | 4 | 3.2 | 2.5 | 0 | 0
Exeter 132 kV | St Thomas | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.8 | 11.5 | 11.4 | 11 | 10.5 | 10 | 9.4 | 8.7 | 7.9 | 7.2 | 6.5 | 5.6 | 4.8 | 4.1 | 0.9 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Junction | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.8 | 9.7 | 9.4 | 9 | 8.6 | 8.2 | 7.2 | 6.3 | 5.5 | 5.1 | 4.7 | 4.2 | 3.4 | 2.5 | 1.6 | 1 | 0 | 0 | 0
Exeter 132 kV | Tiverton Junction | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.8 | 9.6 | 9.2 | 8.6 | 8 | 7.3 | 6.2 | 5.2 | 4.2 | 2.9 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Junction | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.8 | 9.6 | 9.3 | 8.8 | 8.3 | 7.9 | 7 | 5.9 | 4.8 | 3.9 | 3.2 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Junction | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.8 | 9.6 | 9.3 | 8.7 | 8.1 | 7.5 | 6.3 | 5.3 | 4.3 | 3.3 | 2.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Moorhayes | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.6 | 3.3 | 3.2 | 3.2 | 3 | 2.7 | 2.2 | 1.8 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Moorhayes | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.6 | 3.1 | 2.7 | 2.2 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Moorhayes | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.6 | 3.2 | 3 | 2.7 | 2.5 | 2.1 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Moorhayes | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.6 | 3.2 | 2.9 | 2.6 | 2.1 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton South | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.6 | 3.4 | 3.2 | 3.2 | 3 | 2.7 | 2.3 | 1.8 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton South | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.6 | 3.1 | 2.7 | 2.3 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton South | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.6 | 3.2 | 3 | 2.7 | 2.5 | 2.1 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton South | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.6 | 3.2 | 2.9 | 2.6 | 2.1 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Topsham | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1 | 0.8 | 0.7 | 0.6 | 0 | 0 | 8 | 7.8 | 7.6 | 7.5 | 7.3 | 7.1 | 6.8 | 6.6 | 6.3 | 6.1 | 5.7 | 3.9 | 1.6
Exeter 132 kV | Topsham | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1 | 0.8 | 0.5 | 0 | 0 | 0 | 7.5 | 7.1 | 6.7 | 6.2 | 5.9 | 5.6 | 5.2 | 4.8 | 4.5 | 3.9 | 3.2 | 0.8 | 0
Exeter 132 kV | Topsham | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1 | 0.8 | 0.6 | 0 | 0 | 0 | 7.8 | 7.6 | 7.2 | 7 | 6.7 | 6.3 | 5.9 | 5.5 | 4.9 | 3.8 | 3 | 0 | 0
Exeter 132 kV | Topsham | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1 | 0.8 | 0.6 | 0 | 0 | 0 | 7.6 | 7.3 | 7 | 6.6 | 6.3 | 6 | 5.6 | 5.1 | 4.5 | 3.9 | 3.3 | 1.3 | 0
Exeter 132 kV | Witheridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.7 | 1.7 | 1.6 | 1.5 | 1.4 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Witheridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.7 | 1.7 | 1.5 | 1.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Witheridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.7 | 1.7 | 1.6 | 1.5 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Witheridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.7 | 1.7 | 1.6 | 1.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Withycombe Raleigh | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.7 | 8.5 | 8.4 | 8.2 | 7.9 | 7.3 | 6.4 | 5.8 | 5 | 4.4 | 3.8 | 3.1 | 2 | 0.7 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Withycombe Raleigh | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.7 | 8.3 | 7.9 | 7.4 | 6.5 | 5.6 | 4.3 | 2.9 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Withycombe Raleigh | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.7 | 8.4 | 8.2 | 7.7 | 7.1 | 6.5 | 5.5 | 4.4 | 3 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Withycombe Raleigh | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.7 | 8.3 | 8.1 | 7.7 | 6.9 | 6.2 | 5 | 3.9 | 2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Woodbury | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 6.2 | 6.1 | 5.7 | 5.4 | 5.1 | 4.7 | 4.1 | 3.6 | 3 | 2.6 | 1.9 | 0 | 0
Exeter 132 kV | Woodbury | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 5.3 | 4.6 | 3.8 | 2.9 | 2.3 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Woodbury | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 6 | 5.5 | 4.8 | 4.2 | 3.5 | 2.7 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Woodbury | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 5.6 | 5 | 4.3 | 3.6 | 2.9 | 2.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Blackpool | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.4 | 8.1 | 7.6 | 7.2 | 6.9 | 6.6 | 6.3 | 6 | 5.5 | 5.2 | 4.5 | 3.7 | 2.9 | 2.1 | 1.3 | 0.7 | 0 | 0 | 0
Indian Queens 132 kV | Blackpool | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.4 | 7.9 | 7.2 | 6.5 | 6 | 5.4 | 4.9 | 3.9 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Blackpool | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.4 | 8 | 7.4 | 7 | 6.6 | 6.3 | 5.9 | 5.3 | 4.5 | 3.2 | 2.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Blackpool | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.4 | 7.9 | 7.4 | 6.8 | 6.3 | 5.9 | 5.4 | 4.8 | 3.7 | 2.7 | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Bodmin | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 1.4 | 1.3 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Bodmin | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Bodmin | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 1.3 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Bodmin | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 1.2 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Bugle | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.5 | 2.3 | 2.4 | 2.4 | 2.4 | 2.3 | 2 | 1.9 | 1.9 | 1.8 | 1.8 | 1.6 | 1.3 | 1 | 0.7 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Bugle | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.5 | 2.3 | 2.3 | 2.2 | 2 | 1.8 | 1.4 | 1.2 | 1 | 0.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Bugle | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.5 | 2.3 | 2.4 | 2.3 | 2.3 | 2.3 | 1.9 | 1.8 | 1.8 | 1.6 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Bugle | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.5 | 2.3 | 2.3 | 2.3 | 2.2 | 2 | 1.6 | 1.5 | 1.3 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Callywith | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 1.4 | 1.3 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Callywith | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 1.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Callywith | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 1.2 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Callywith | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 1.2 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Carn Brea | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.4 | 1.1 | 5.4 | 5.3 | 5.2 | 5.1 | 4.8 | 4.6 | 4.2 | 4 | 3.7 | 3.3 | 2.7 | 2.1 | 1.5 | 1 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Carn Brea | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.4 | 0.9 | 5.1 | 4.8 | 4.5 | 4.2 | 3.6 | 2.9 | 2.1 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Carn Brea | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.4 | 1 | 5.3 | 5.1 | 5 | 4.8 | 4.4 | 3.9 | 3.2 | 2.5 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Carn Brea | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.4 | 1 | 5.2 | 5 | 4.7 | 4.5 | 4 | 3.4 | 2.7 | 2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Holmans | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.1 | 6.7 | 6.3 | 6 | 5.6 | 5.3 | 5 | 4.5 | 3.9 | 3.5 | 2.9 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Holmans | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.1 | 6.5 | 5.9 | 5.1 | 4.5 | 3.8 | 3.1 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Holmans | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.1 | 6.6 | 6.2 | 5.8 | 5.4 | 5 | 4.5 | 3.6 | 2.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Holmans | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.1 | 6.5 | 6 | 5.5 | 4.9 | 4.3 | 3.7 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Treswithian | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 4.5 | 3.8 | 3.4 | 2.9 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Treswithian | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Treswithian | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 3.5 | 2.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Treswithian | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Constantine 33kv | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.6 | 3.2 | 3 | 2.7 | 2.5 | 2.1 | 2.6 | 2.3 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Constantine 33kv | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.6 | 3 | 2.6 | 2 | 1.4 | 0.6 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Constantine 33kv | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.6 | 3.2 | 2.9 | 2.7 | 2.4 | 1.9 | 2.3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Constantine 33kv | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.6 | 3.1 | 2.8 | 2.4 | 1.8 | 1.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Davidstow | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Davidstow | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Davidstow | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Davidstow | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Delabole | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Delabole | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Delabole | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Delabole | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Devoran | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.6 | 1.5 | 1.5 | 1.4 | 1.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Devoran | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.6 | 1.5 | 1.4 | 1.2 | 1.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Devoran | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.6 | 1.5 | 1.5 | 1.4 | 1.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Devoran | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.6 | 1.5 | 1.4 | 1.3 | 1.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Drinnick. | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.9 | 3.8 | 3.9 | 3.9 | 3.9 | 4 | 4 | 4 | 4 | 4 | 4 | 3.9 | 3.8 | 3.7 | 3.5 | 3.5 | 3.4 | 2.9 | 2.2
Indian Queens 132 kV | Drinnick. | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.9 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.7 | 3.6 | 3.5 | 3.4 | 3.3 | 3.2 | 3.1 | 3 | 2.9 | 2.8 | 2.3 | 1.8
Indian Queens 132 kV | Drinnick. | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.9 | 3.8 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.8 | 3.7 | 3.7 | 3.5 | 3.4 | 3.2 | 3.1 | 3 | 2.9 | 2.2 | 1.5
Indian Queens 132 kV | Drinnick. | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.9 | 3.8 | 3.8 | 3.9 | 3.9 | 3.9 | 3.9 | 3.8 | 3.7 | 3.6 | 3.5 | 3.4 | 3.2 | 3 | 2.9 | 2.8 | 2.6 | 2 | 1.4
Indian Queens 132 kV | Falmouth Bickland Hl | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Falmouth Bickland Hl | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Falmouth Bickland Hl | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Falmouth Bickland Hl | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Falmouth Docks | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Falmouth Docks | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Falmouth Docks | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Falmouth Docks | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fowey | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.6 | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fowey | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fowey | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.6 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fowey | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fraddon | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.2 | 13.1 | 12.8 | 10.2 | 10.1 | 9.9 | 11.1 | 10.9 | 10.5 | 10.3 | 10 | 9.6 | 9.1 | 8.6 | 8.1 | 7.6 | 7 | 4.5 | 2.1
Indian Queens 132 kV | Fraddon | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.2 | 13 | 10 | 9.8 | 9.4 | 8.9 | 9.8 | 9.2 | 8.5 | 7.8 | 7.2 | 6.6 | 5.9 | 5.4 | 4.9 | 4.3 | 3.9 | 2.6 | 1.7
Indian Queens 132 kV | Fraddon | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.2 | 13 | 10.1 | 9.9 | 9.6 | 9.3 | 10.2 | 9.7 | 9.1 | 8.6 | 7.9 | 7.2 | 6.5 | 5.8 | 5.2 | 4.5 | 3.9 | 2.1 | 0.8
Indian Queens 132 kV | Fraddon | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.2 | 13 | 10.1 | 9.9 | 9.5 | 9.1 | 10.1 | 9.6 | 8.9 | 8 | 7.3 | 6.5 | 5.7 | 4.9 | 4.2 | 3.5 | 3 | 1.6 | 0
Indian Queens 132 kV | Fraddon Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fraddon Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fraddon Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fraddon Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Geevor | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Geevor | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Geevor | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Geevor | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Hayle | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.1 | 4.2 | 3 | 1.7 | 0.5 | 0 | 4.7 | 4 | 3.4 | 3.1 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Hayle | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.1 | 3.6 | 1.7 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Hayle | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.1 | 3.9 | 2.5 | 1.1 | 0 | 0 | 4.3 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Hayle | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.1 | 3.8 | 2.2 | 0 | 0 | 0 | 3.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Hayle Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Hayle Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Hayle Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Hayle Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Helston | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.4 | 3 | 2.7 | 2.4 | 2.1 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Helston | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.4 | 2.8 | 2.3 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Helston | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.4 | 2.9 | 2.6 | 2.2 | 1.9 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Helston | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.4 | 2.9 | 2.5 | 1.9 | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Isles Of Scilly | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Isles Of Scilly | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Isles Of Scilly | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Isles Of Scilly | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Laneast | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Laneast | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Laneast | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Laneast | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Lanner | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.9 | 0 | 0 | 0 | 0 | 0 | 4.3 | 4.1 | 3.8 | 3.6 | 3.3 | 3 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Lanner | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.9 | 0 | 0 | 0 | 0 | 0 | 3.4 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Lanner | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.9 | 0 | 0 | 0 | 0 | 0 | 4.1 | 3.7 | 3.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Lanner | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.9 | 0 | 0 | 0 | 0 | 0 | 3.8 | 3.4 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Lostwithiel | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Lostwithiel | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Lostwithiel | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Lostwithiel | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Marazion | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Marazion | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Marazion | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Marazion | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mevagissey | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.1 | 7.8 | 7.4 | 7 | 6.7 | 6.4 | 6.1 | 5.8 | 5.3 | 5 | 4.3 | 3.6 | 2.8 | 2 | 1.3 | 0.6 | 0 | 0 | 0
Indian Queens 132 kV | Mevagissey | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.1 | 7.6 | 7 | 6.3 | 5.8 | 5.3 | 4.7 | 3.8 | 2.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mevagissey | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.1 | 7.7 | 7.2 | 6.8 | 6.4 | 6.1 | 5.6 | 5.1 | 4.4 | 3.1 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mevagissey | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.1 | 7.7 | 7.1 | 6.6 | 6.1 | 5.7 | 5.2 | 4.6 | 3.5 | 2.6 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mousehole | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mousehole | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mousehole | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mousehole | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mullion | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.6 | 3.2 | 3 | 2.7 | 2.5 | 2.1 | 2.6 | 2.4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mullion | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.6 | 3 | 2.6 | 2 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mullion | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.6 | 3.2 | 3 | 2.7 | 2.4 | 2 | 2.4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mullion | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.6 | 3.1 | 2.8 | 2.4 | 1.8 | 1.2 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newlyn | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newlyn | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newlyn | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newlyn | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newquay Trencreek Ln | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newquay Trencreek Ln | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newquay Trencreek Ln | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newquay Trencreek Ln | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newquay Trevemper | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newquay Trevemper | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newquay Trevemper | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newquay Trevemper | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Padstow | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.2 | 3.9 | 3.7 | 1.7 | 1.3 | 0.8 | 5 | 4.8 | 4.5 | 4.3 | 2.7 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Padstow | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.2 | 3.7 | 1.4 | 0.8 | 0 | 0 | 4 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Padstow | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.2 | 3.8 | 1.8 | 1.5 | 1.1 | 0 | 4.8 | 4.3 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Padstow | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.2 | 3.8 | 1.6 | 1.2 | 0.6 | 0 | 4.5 | 4 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Par Harbour | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.5 | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Par Harbour | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Par Harbour | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Par Harbour | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Penryn | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5.9 | 5.7 | 4.9 | 3.8 | 2.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Penryn | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Penryn | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 5.8 | 4.8 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Penryn | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 3.9 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Penzance Causewayhead | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Penzance Causewayhead | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Penzance Causewayhead | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Penzance Causewayhead | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Penzance Heamoor | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Penzance Heamoor | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Penzance Heamoor | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Penzance Heamoor | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Perranporth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.6 | 2.4 | 2.3 | 2.1 | 2.1 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Perranporth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.6 | 2.3 | 2.1 | 1.7 | 1.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Perranporth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.6 | 2.4 | 2.4 | 2.2 | 2.1 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Perranporth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.6 | 2.3 | 2.3 | 2 | 1.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Polzeath | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.6 | 3.4 | 3.2 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Polzeath | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.6 | 3.3 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Polzeath | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.6 | 3.3 | 1.3 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Polzeath | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.6 | 3.3 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Probus 33 | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Probus 33 | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Probus 33 | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Probus 33 | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Rame Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Rame Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Rame Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Rame Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Redruth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7 | 6.8 | 6.4 | 6.1 | 5.9 | 5.3 | 4.6 | 4.1 | 3.6 | 3.2 | 2.6 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Redruth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7 | 6.6 | 6 | 5.5 | 4.6 | 3.8 | 2.8 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Redruth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7 | 6.7 | 6.3 | 5.7 | 5.3 | 4.8 | 3.8 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Redruth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7 | 6.7 | 6.2 | 5.7 | 4.9 | 4.2 | 3.2 | 2.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Roseland | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Roseland | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Roseland | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Roseland | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Sawles Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8 | 7.7 | 7.3 | 6.9 | 6.6 | 6.3 | 6 | 5.7 | 5.2 | 4.9 | 4.2 | 3.5 | 2.7 | 1.9 | 1.3 | 0.6 | 0 | 0 | 0
Indian Queens 132 kV | Sawles Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8 | 7.5 | 6.9 | 6.2 | 5.7 | 5.2 | 4.6 | 3.7 | 2.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Sawles Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8 | 7.6 | 7.1 | 6.7 | 6.3 | 6 | 5.5 | 5 | 4.3 | 3 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Sawles Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8 | 7.6 | 7 | 6.5 | 6.1 | 5.7 | 5.1 | 4.5 | 3.4 | 2.5 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Agnes | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.9 | 2.7 | 2.6 | 2.4 | 2.3 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Agnes | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.9 | 2.6 | 2.4 | 2 | 1.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Agnes | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.9 | 2.7 | 2.6 | 2.4 | 2.3 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Agnes | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.9 | 2.6 | 2.5 | 2.2 | 2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Austell | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.4 | 10.2 | 9.7 | 9.3 | 8.9 | 8.4 | 7.3 | 6.7 | 5.9 | 5.3 | 4.3 | 3.4 | 2.4 | 1.6 | 0.8 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Austell | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.4 | 9.9 | 9.1 | 8.4 | 7.6 | 6.8 | 5.4 | 3.8 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Austell | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.4 | 10 | 9.3 | 8.8 | 8.3 | 7.7 | 6.5 | 5.4 | 4.1 | 2.4 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Austell | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.4 | 10 | 9.4 | 8.7 | 8.1 | 7.4 | 6.1 | 5.1 | 3.5 | 2.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Austell Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Austell Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Austell Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Austell Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Buryan | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Buryan | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Buryan | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Buryan | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Columb Major | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.9 | 4.8 | 4.8 | 4.8 | 4.8 | 4.7 | 4.7 | 4.6 | 4.5 | 4.4 | 2.8 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Columb Major | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.9 | 4.7 | 4.6 | 4.5 | 4.4 | 4.3 | 4.1 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Columb Major | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.9 | 4.8 | 4.7 | 4.6 | 4.6 | 4.5 | 4.4 | 4.2 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Columb Major | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.9 | 4.8 | 4.7 | 4.6 | 4.5 | 4.4 | 4.2 | 4 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Ives | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Ives | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Ives | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Ives | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Keverne | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 3.3 | 3 | 2.8 | 2.5 | 2.2 | 2.7 | 2.4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Keverne | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 3.1 | 2.6 | 2 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Keverne | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 3.3 | 3 | 2.7 | 2.4 | 2 | 2.4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Keverne | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 3.2 | 2.9 | 2.4 | 1.9 | 1.3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Mawgan | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.8 | 5.6 | 5.4 | 5.2 | 4.9 | 4.6 | 4.4 | 4.1 | 3.9 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Mawgan | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.8 | 5.6 | 5.3 | 5 | 4.7 | 4.3 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Mawgan | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.8 | 5.6 | 5.4 | 5.2 | 4.9 | 4.6 | 4.4 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Mawgan | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.8 | 5.6 | 5.3 | 5 | 4.7 | 4.4 | 4.1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Tudy | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.2 | 9.2 | 9.1 | 9 | 9 | 8.9 | 9 | 8.9 | 8.7 | 8.6 | 8.5 | 8.3 | 8.1 | 7.9 | 7.7 | 7.5 | 7.3 | 6.3 | 5.3
Indian Queens 132 kV | St Tudy | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.2 | 9.1 | 9 | 8.9 | 8.8 | 8.7 | 8.6 | 8.4 | 8.1 | 7.8 | 7.6 | 7.3 | 7 | 6.8 | 6.5 | 6.3 | 6.1 | 5.7 | 5.4
Indian Queens 132 kV | St Tudy | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.2 | 9.2 | 9.1 | 9 | 8.9 | 8.8 | 8.8 | 8.6 | 8.4 | 8.1 | 7.9 | 7.6 | 7.3 | 7 | 6.7 | 6.4 | 6.2 | 5.5 | 4.9
Indian Queens 132 kV | St Tudy | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.2 | 9.2 | 9.1 | 9 | 8.9 | 8.8 | 8.7 | 8.5 | 8.3 | 7.9 | 7.6 | 7.2 | 6.9 | 6.5 | 6.2 | 5.9 | 5.6 | 5.1 | 4.6
Indian Queens 132 kV | St Tudy Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 11.9 | 10.5 | 8.5 | 7.1 | 5.5 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Tudy Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Tudy Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 10.3 | 7.7 | 4.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Tudy Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.3 | 5.7 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Trebal | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.6 | 5.6 | 5.6 | 5.7 | 5.8 | 5.8 | 5.9 | 6 | 6.1 | 6.1 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6
Indian Queens 132 kV | Trebal | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.6 | 5.6 | 5.6 | 5.7 | 5.8 | 5.8 | 5.9 | 6 | 6.1 | 6.1 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 5.9
Indian Queens 132 kV | Trebal | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.6 | 5.6 | 5.6 | 5.7 | 5.8 | 5.8 | 5.9 | 6 | 6.1 | 6.1 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.1 | 5.1
Indian Queens 132 kV | Trebal | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.6 | 5.6 | 5.6 | 5.7 | 5.8 | 5.8 | 5.9 | 6 | 6.1 | 6.1 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 5.7 | 4.9
Indian Queens 132 kV | Truro Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 32.5 | 31.8 | 31.4 | 30.7 | 30 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 32.5 | 31.2 | 30.2 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 32.5 | 31.5 | 30.9 | 29.6 | 28.3 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 32.5 | 31.4 | 30.6 | 29.3 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Shortlanesend | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.3 | 6.9 | 6.6 | 6.2 | 5.6 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Shortlanesend | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.3 | 6.5 | 5.7 | 4.7 | 3.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Shortlanesend | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.3 | 6.6 | 6.1 | 5.2 | 4.1 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Shortlanesend | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.3 | 6.6 | 5.9 | 5.1 | 3.7 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Treyew Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 7 | 6.6 | 6.3 | 5.8 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Treyew Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 6.7 | 6.1 | 5.4 | 3.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Treyew Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 6.8 | 6.4 | 5.8 | 4.7 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Treyew Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 6.7 | 6.3 | 5.6 | 4.2 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Twelveheads. | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 6.5 | 6.5 | 6.5 | 6.4 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Twelveheads. | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 6.5 | 6.4 | 6.3 | 5.5 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Twelveheads. | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 6.5 | 6.5 | 6.4 | 6.3 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Twelveheads. | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 6.5 | 6.5 | 6.4 | 5.9 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Wadebridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.5 | 3.3 | 3.1 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Wadebridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.5 | 3.2 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Wadebridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.5 | 3.2 | 1.3 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Wadebridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.5 | 3.2 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Wheal Reeth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.3 | 2.2 | 2.2 | 2.1 | 2 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Wheal Reeth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.3 | 2.2 | 2.1 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Wheal Reeth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.3 | 2.2 | 2.2 | 2.1 | 1.8 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Wheal Reeth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.3 | 2.2 | 2.2 | 1.9 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Abbeywood Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.2 | 7.8 | 7.3 | 7.1 | 6.9 | 6.5 | 7.5 | 7.6 | 7.7 | 7.8 | 7.8 | 7.7 | 7.5 | 7.3 | 7.2 | 7 | 6.9 | 6.1 | 5.4
Iron Acton 132 kV | Abbeywood Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.2 | 7.7 | 6.4 | 5.7 | 4.9 | 4.2 | 7.5 | 7.3 | 6.9 | 6.6 | 6.4 | 6.1 | 5.8 | 5.5 | 5.3 | 5 | 4.4 | 0.9 | 0
Iron Acton 132 kV | Abbeywood Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.2 | 7.7 | 6.6 | 5.8 | 5.2 | 4.7 | 7.5 | 7.4 | 7.2 | 7 | 6.8 | 6.6 | 6.3 | 6 | 5.7 | 5.4 | 5.2 | 1.8 | 0
Iron Acton 132 kV | Abbeywood Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.2 | 7.7 | 6.8 | 6.2 | 5.7 | 5.2 | 7.5 | 7.5 | 7.3 | 7.1 | 6.9 | 6.6 | 6.3 | 6.1 | 5.9 | 5.7 | 5.5 | 5 | 4.8
Iron Acton 132 kV | Almondsbury | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8 | 7.9 | 7.5 | 7.1 | 6.6 | 6.1 | 5.6 | 5.4 | 5.2 | 5.1 | 5 | 4.7 | 4.3 | 3.9 | 3.5 | 3.1 | 2.7 | 0 | 0
Iron Acton 132 kV | Almondsbury | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8 | 7.8 | 7.1 | 6.5 | 5.8 | 5 | 4.2 | 3.4 | 2.8 | 2.3 | 1.8 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Almondsbury | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8 | 7.8 | 7.2 | 6.7 | 6.1 | 5.3 | 4.4 | 3.9 | 3.3 | 2.9 | 2.4 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Almondsbury | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8 | 7.8 | 7.3 | 6.7 | 6.1 | 5.4 | 4.5 | 4 | 3.4 | 2.9 | 2.4 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Bedminster | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 7.5 | 6.2 | 5.3 | 4.5 | 3.4 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Bedminster | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Bedminster | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Bedminster | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 6.1 | 4.4 | 2.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Bishopsworth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9 | 8.8 | 8.7 | 8.6 | 8.4 | 8.2 | 7.7 | 7.4 | 7 | 6.7 | 6.3 | 5.8 | 5.1 | 4.4 | 3.6 | 2.9 | 2.2 | 0 | 0
Iron Acton 132 kV | Bishopsworth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9 | 8.6 | 8.1 | 7.7 | 7.2 | 6.5 | 5.8 | 4.8 | 3.6 | 2.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Bishopsworth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9 | 8.6 | 8.3 | 8 | 7.6 | 7.3 | 6.7 | 6 | 5 | 4.2 | 3.3 | 2.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Bishopsworth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9 | 8.6 | 8.4 | 8.1 | 7.6 | 7.1 | 6.5 | 5.7 | 4.8 | 3.9 | 3 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Bower Ashton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.4 | 1.9 | 1.2 | 0.7 | 0 | 0 | 7 | 6.7 | 6.3 | 6 | 5.6 | 5.2 | 4.7 | 4.2 | 3.7 | 3.3 | 2.8 | 0 | 0
Iron Acton 132 kV | Bower Ashton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.4 | 1.4 | 0 | 0 | 0 | 0 | 5.4 | 4.5 | 3.4 | 2.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Bower Ashton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.4 | 1.6 | 0 | 0 | 0 | 0 | 5.8 | 5.3 | 4.6 | 3.9 | 3.2 | 2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Bower Ashton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.4 | 1.5 | 0.6 | 0 | 0 | 0 | 5.9 | 5.3 | 4.5 | 3.8 | 3.1 | 2.2 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Bradley Stoke | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.9 | 8.8 | 8.6 | 8.4 | 8.2 | 8.2 | 8 | 7.9 | 7.7 | 7.5 | 7.3 | 6.9 | 6.3 | 5.8 | 5.2 | 4.7 | 4.1 | 1 | 0
Iron Acton 132 kV | Bradley Stoke | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.9 | 8.6 | 8.2 | 7.8 | 7.4 | 7.1 | 6.8 | 6.2 | 5.5 | 4.6 | 3.9 | 3 | 2.2 | 1.4 | 0.5 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Bradley Stoke | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.9 | 8.6 | 8.3 | 7.9 | 7.6 | 7.4 | 7.1 | 6.7 | 6 | 5.4 | 4.7 | 3.9 | 2.8 | 1.8 | 0.8 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Bradley Stoke | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.9 | 8.6 | 8.3 | 8 | 7.7 | 7.5 | 7.3 | 6.8 | 6.3 | 5.7 | 5.1 | 4.4 | 3.7 | 3 | 2.4 | 1.7 | 1.2 | 0 | 0
Iron Acton 132 kV | Bradley Stoke Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 34.1 | 33.6 | 32.7 | 32.1 | 31.5 | 31 | 27.1 | 26.6 | 25.9 | 25.6 | 25.1 | 24 | 22.6 | 21.2 | 19.7 | 18.4 | 17 | 9.2 | 1.6
Iron Acton 132 kV | Bradley Stoke Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 34.1 | 33.1 | 31.7 | 30.6 | 29.6 | 28.4 | 23.6 | 21.6 | 19.7 | 17.7 | 16 | 13.8 | 11.7 | 9.3 | 7.2 | 5.1 | 3.1 | 0 | 0
Iron Acton 132 kV | Bradley Stoke Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 34.1 | 33.2 | 31.9 | 31 | 30.1 | 29.1 | 24.8 | 23.4 | 21.7 | 20.4 | 18.8 | 16.5 | 13.9 | 11.5 | 9 | 6.5 | 4.3 | 0 | 0
Iron Acton 132 kV | Bradley Stoke Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 34.1 | 33.2 | 32 | 31.2 | 30.2 | 29.3 | 24.6 | 23.2 | 21.6 | 20.2 | 18.7 | 16.6 | 14.7 | 12.8 | 11 | 9.3 | 7.8 | 1.7 | 0
Iron Acton 132 kV | Broadweir Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.5 | 11.3 | 11.4 | 11.5 | 11.6 | 11.5 | 2.1 | 1.9 | 1.6 | 1.3 | 1.1 | 1 | 1 | 1 | 0.9 | 0.9 | 0.9 | 0.7 | 0.6
Iron Acton 132 kV | Broadweir Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.5 | 11.3 | 11.4 | 11.5 | 11.3 | 11 | 1.4 | 1 | 0.8 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 0
Iron Acton 132 kV | Broadweir Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.5 | 11.3 | 11.4 | 11.4 | 11.2 | 10.9 | 1.5 | 1.2 | 0.8 | 0.8 | 0.9 | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0
Iron Acton 132 kV | Broadweir Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.5 | 11.3 | 11.4 | 11.5 | 11.4 | 11.1 | 1.6 | 1.2 | 0.9 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.5 | 0.5 | 0 | 0 | 0
Iron Acton 132 kV | Clifton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.6 | 17.4 | 16.9 | 16.4 | 15.9 | 15.3 | 14.5 | 14 | 13.2 | 12.6 | 11.9 | 11 | 10.3 | 9.5 | 8.7 | 7.9 | 7.1 | 2.9 | 0
Iron Acton 132 kV | Clifton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.6 | 16.8 | 15.9 | 14.3 | 13.1 | 11.9 | 10.5 | 8.4 | 5.8 | 3.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Clifton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.6 | 16.9 | 16.1 | 14.9 | 14 | 13.2 | 11.9 | 10.6 | 8.6 | 6.8 | 5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Clifton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.6 | 16.9 | 16.1 | 15.2 | 14.4 | 13.4 | 12.2 | 11 | 9.5 | 8.2 | 6.8 | 4.8 | 3.2 | 1.7 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Cotham Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.7 | 10.7 | 10.9 | 11 | 11.2 | 11.3 | 11.2 | 11.4 | 11.5 | 11.7 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8
Iron Acton 132 kV | Cotham Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.7 | 10.7 | 10.9 | 11 | 11.2 | 11.3 | 11.2 | 11.4 | 11.5 | 11.7 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8
Iron Acton 132 kV | Cotham Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.7 | 10.7 | 10.9 | 11 | 11.2 | 11.3 | 11.2 | 11.4 | 11.5 | 11.7 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8
Iron Acton 132 kV | Cotham Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.7 | 10.7 | 10.9 | 11 | 11.2 | 11.3 | 11.2 | 11.4 | 11.5 | 11.7 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8
Iron Acton 132 kV | Cribbs Causeway | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.5 | 9.4 | 9.3 | 9.4 | 9.6 | 9.7 | 6.5 | 6.3 | 6.3 | 6.3 | 6.2 | 6 | 5.7 | 5.4 | 5.2 | 4.9 | 4.7 | 3.2 | 1.6
Iron Acton 132 kV | Cribbs Causeway | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.5 | 9.4 | 9.2 | 9.3 | 9.4 | 9.5 | 6.2 | 5.9 | 5.7 | 5.4 | 5.2 | 4.7 | 4.4 | 3.9 | 3.5 | 3.1 | 2.7 | 0.6 | 0
Iron Acton 132 kV | Cribbs Causeway | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.5 | 9.4 | 9.2 | 9.3 | 9.5 | 9.6 | 6.7 | 6.5 | 6.4 | 6.3 | 6 | 5.6 | 5.1 | 4.8 | 4.3 | 3.9 | 3.5 | 1.4 | 0
Iron Acton 132 kV | Cribbs Causeway | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.5 | 9.4 | 9.3 | 9.4 | 9.5 | 9.6 | 6.2 | 6 | 5.8 | 5.7 | 5.5 | 5.1 | 4.8 | 4.5 | 4.2 | 4 | 3.6 | 2.1 | 0.6
Iron Acton 132 kV | Eastville | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.8 | 8.4 | 8.3 | 8.2 | 7.8 | 7.6 | 7.6 | 7.2 | 6.6 | 6.2 | 5.7 | 5 | 4.1 | 3.2 | 2.3 | 1.6 | 0.7 | 0 | 0
Iron Acton 132 kV | Eastville | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.8 | 8.1 | 7.7 | 7.1 | 6.6 | 6 | 5.5 | 4.1 | 2.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Eastville | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.8 | 8.2 | 8 | 7.8 | 7.6 | 7.3 | 7 | 6.1 | 4.9 | 3.8 | 2.6 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Eastville | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.8 | 8.2 | 7.9 | 7.5 | 7 | 6.6 | 6.2 | 5.2 | 4 | 2.6 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Emersons Green | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.7 | 9.9 | 9 | 8.2 | 8 | 7.8 | 7.9 | 8 | 8 | 8.1 | 8.1 | 6.5 | 3.8 | 1.1 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Emersons Green | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.7 | 9.9 | 8.9 | 8.1 | 7.9 | 7.6 | 6.3 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Emersons Green | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.7 | 9.9 | 8.9 | 8.2 | 7.9 | 7.7 | 7.8 | 5.8 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Emersons Green | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.7 | 9.9 | 8.9 | 8.1 | 7.9 | 7.7 | 7.8 | 6.1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Feeder Rd 11kv | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 41.2 | 40.1 | 38.7 | 37.7 | 36.7 | 35.2 | 33.5 | 31.7 | 29.8 | 28.3 | 26.6 | 17.2 | 10.1
Iron Acton 132 kV | Feeder Rd 11kv | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 28.2 | 24.2 | 19.9 | 16.1 | 13.1 | 9.9 | 7.7 | 5.4 | 3.2 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Feeder Rd 11kv | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 31.5 | 29.3 | 26.8 | 24.8 | 22.4 | 19.5 | 16.4 | 13.3 | 10.3 | 6.5 | 2.8 | 0 | 0
Iron Acton 132 kV | Feeder Rd 11kv | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 36.9 | 34.5 | 31.7 | 29 | 26.2 | 22.8 | 20.3 | 17.7 | 15.4 | 13.3 | 11.8 | 7.2 | 5.7
Iron Acton 132 kV | Feeder Road 33kv | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 52.5 | 36.4 | 27.1 | 19.2 | 14.5 | 28.7 | 96.5 | 94.3 | 91.2 | 89 | 86.6 | 83.8 | 80.1 | 75.9 | 68 | 59.4 | 50.6 | 3.8 | 0
Iron Acton 132 kV | Feeder Road 33kv | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 52.5 | 26.7 | 0 | 0 | 0 | 0 | 81.2 | 71.6 | 53.3 | 35.5 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Feeder Road 33kv | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 52.5 | 28.5 | 5.6 | 0 | 0 | 0 | 86.5 | 82.3 | 76.9 | 67.1 | 54.5 | 34.2 | 11 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Feeder Road 33kv | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 52.5 | 28.8 | 19.1 | 6.7 | 0 | 0 | 89.5 | 84.9 | 79.6 | 73.5 | 60.9 | 45.3 | 31.1 | 17.2 | 4.2 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Feeder Road B | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.3 | 4.2 | 2.4 | 2.3 | 2.3
Iron Acton 132 kV | Feeder Road B | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.3 | 2.2 | 2.1 | 1.9 | 1.6
Iron Acton 132 kV | Feeder Road B | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.3 | 2.2 | 2.2 | 1.9 | 1.8
Iron Acton 132 kV | Feeder Road B | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.3 | 2.4 | 2.2 | 2 | 1.8
Iron Acton 132 kV | Filton Dc | Primary Substation | 11 | Counterfactual | Headroom (MW) | 23.1 | 15.9 | 13.7 | 12.9 | 12.4 | 11.8 | 14.2 | 13.7 | 12.9 | 12.3 | 11.7 | 10.9 | 9.8 | 8.7 | 6.9 | 4.9 | 2.7 | 0 | 0
Iron Acton 132 kV | Filton Dc | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 23.1 | 15.1 | 7.7 | 5.2 | 4 | 2.2 | 6.3 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Filton Dc | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 23.1 | 15.3 | 8 | 5.5 | 4.6 | 3.5 | 7.9 | 5.6 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Filton Dc | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 23.1 | 15.2 | 12.7 | 11.3 | 10.4 | 9.3 | 12.1 | 10.9 | 9.4 | 7.9 | 5.3 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Hewlett Packard | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 6.7 | 6.2 | 5.6 | 5 | 4.2 | 3.3 | 2.9 | 2.5 | 2.1 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Hewlett Packard | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 6.3 | 5.5 | 4.6 | 3.9 | 2.9 | 1.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Hewlett Packard | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 6.3 | 5.4 | 4.6 | 3.7 | 2.7 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Hewlett Packard | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.3 | 5.6 | 4.8 | 4 | 3.1 | 1.9 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Keynsham West | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.8 | 14.7 | 14.6 | 14.6 | 14.5 | 14.4 | 14.3 | 14.1 | 13.8 | 13.7 | 13.4 | 13.2 | 12.8 | 12.4 | 11.9 | 11.5 | 11.2 | 9.4 | 7.9
Iron Acton 132 kV | Keynsham West | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.8 | 14.6 | 14.3 | 14.1 | 13.9 | 13.6 | 13.3 | 12.8 | 12.1 | 11.5 | 11 | 10.4 | 9.9 | 9.4 | 8.9 | 8.3 | 7.8 | 5.9 | 4.5
Iron Acton 132 kV | Keynsham West | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.8 | 14.6 | 14.6 | 14.5 | 14.4 | 14.3 | 14 | 13.6 | 13.2 | 12.9 | 12.5 | 12 | 11.3 | 10.7 | 10.1 | 9.5 | 9 | 7.1 | 5.9
Iron Acton 132 kV | Keynsham West | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.8 | 14.6 | 14.5 | 14.3 | 14.2 | 14 | 13.8 | 13.4 | 12.9 | 12.4 | 11.9 | 11.3 | 10.7 | 10.1 | 9.6 | 9.1 | 8.8 | 7.4 | 6.8
Iron Acton 132 kV | Lockleaze | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.7 | 8.4 | 8.1 | 7.9 | 7.5 | 7.1 | 6.5 | 6.1 | 5.5 | 5.1 | 4.7 | 4.1 | 3.3 | 2.6 | 1.9 | 1.2 | 0.5 | 0 | 0
Iron Acton 132 kV | Lockleaze | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.7 | 8.1 | 7.5 | 6.9 | 5.4 | 4.6 | 3.9 | 2.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Lockleaze | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.7 | 8.2 | 7.7 | 7 | 5.9 | 5.4 | 4.8 | 4.1 | 3.1 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Lockleaze | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.7 | 8.2 | 7.7 | 7.2 | 6.5 | 5.9 | 5.1 | 4.2 | 3.3 | 2.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Lockleaze Bsp 132kv | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 4.2 | 0 | 0 | 0 | 0 | 0 | 107.3 | 105.6 | 103.4 | 101.8 | 100.1 | 97.2 | 89.8 | 82.4 | 75.1 | 68.4 | 61.1 | 22.3 | 0
Iron Acton 132 kV | Lockleaze Bsp 132kv | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 4.2 | 0 | 0 | 0 | 0 | 0 | 89.9 | 77.8 | 63.4 | 49.3 | 37.6 | 23.3 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Lockleaze Bsp 132kv | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 4.2 | 0 | 0 | 0 | 0 | 0 | 97.1 | 88.8 | 77.9 | 68 | 57.2 | 43 | 27.2 | 12.2 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Lockleaze Bsp 132kv | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 4.2 | 0 | 0 | 0 | 0 | 0 | 101.2 | 97.3 | 87.5 | 77.8 | 68 | 55.8 | 45.5 | 35.2 | 25.4 | 16.3 | 8.6 | 0 | 0
Iron Acton 132 kV | Mangotsfield | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.3 | 6 | 5.9 | 5.7 | 5.4 | 5 | 4.8 | 4.4 | 3.9 | 3.5 | 3 | 2.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Mangotsfield | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.3 | 5.7 | 5.1 | 4.4 | 3.7 | 3 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Mangotsfield | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.3 | 5.8 | 5.2 | 4.8 | 4.2 | 3.7 | 3.2 | 2.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Mangotsfield | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.3 | 5.8 | 5.4 | 4.9 | 4.4 | 3.8 | 3.2 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Patchway Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.4 | 5.3 | 5.3 | 4.9 | 4.6 | 4 | 5.3 | 5.3 | 5.1 | 5 | 4.9 | 4.7 | 4.3 | 4 | 3.6 | 3.3 | 3 | 1.1 | 0
Iron Acton 132 kV | Patchway Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.4 | 5.2 | 4.6 | 3.9 | 3.2 | 2.2 | 4.7 | 4.4 | 4 | 3.5 | 3.2 | 2.7 | 2.2 | 1.6 | 1.2 | 0.6 | 0 | 0 | 0
Iron Acton 132 kV | Patchway Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.4 | 5.2 | 4.7 | 4 | 3.4 | 2.5 | 4.8 | 4.4 | 3.9 | 3.5 | 3 | 2.4 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Patchway Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.4 | 5.2 | 4.9 | 4.2 | 3.6 | 2.8 | 5 | 4.8 | 4.4 | 4.1 | 3.8 | 3.4 | 3 | 2.5 | 2.1 | 1.8 | 1.4 | 0 | 0
Iron Acton 132 kV | Seabank Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 65 | 58.2 | 54.8 | 50.8 | 47.1 | 43.6 | 43.3 | 40.4 | 37.6 | 35.2 | 35.8 | 35.8 | 36 | 36.1 | 36.2 | 36.4 | 36.5 | 37.1 | 36.4
Iron Acton 132 kV | Seabank Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 65 | 58 | 54.3 | 50.3 | 46.3 | 42.6 | 42 | 38.7 | 35.6 | 32.8 | 33.1 | 32.8 | 32.7 | 32.5 | 32.3 | 30.8 | 26.6 | 7.8 | 0
Iron Acton 132 kV | Seabank Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 65 | 58.1 | 54.4 | 50.4 | 46.6 | 42.9 | 42.4 | 39.3 | 36.5 | 33.9 | 34.5 | 34.4 | 34.4 | 34.5 | 34.5 | 34.6 | 32.4 | 12.4 | 0
Iron Acton 132 kV | Seabank Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 65 | 58.1 | 54.4 | 50.5 | 46.7 | 43.1 | 42.6 | 39.4 | 36.5 | 34 | 34.4 | 34.3 | 34.4 | 34.5 | 34.7 | 34.8 | 35 | 33.1 | 26.5
Iron Acton 132 kV | St Pauls Bsp 11kv | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 12.3 | 11.4 | 9.5 | 7 | 5.6 | 3.7 | 10.1 | 9 | 8.1 | 7.5 | 6.9 | 5.7 | 4.9 | 4 | 3.2 | 2.5 | 1.5 | 0 | 0
Iron Acton 132 kV | St Pauls Bsp 11kv | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 12.3 | 10.6 | 8.2 | 2 | 0 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | St Pauls Bsp 11kv | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 12.3 | 10.8 | 8.7 | 1.8 | 0 | 0 | 4.1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | St Pauls Bsp 11kv | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 12.3 | 10.7 | 8.5 | 5.6 | 2.9 | 0 | 6.5 | 4.3 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Western Approach | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.4 | 10.4 | 7.1 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Western Approach | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.4 | 10.2 | 6.6 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Western Approach | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.4 | 10.2 | 6.7 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Western Approach | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.4 | 10.2 | 6.8 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Whitchurch | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.5 | 8.7 | 7.9 | 6.8 | 6.1 | 5.2 | 4.1 | 3.1 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Whitchurch | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.5 | 8.2 | 6.5 | 3.3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Whitchurch | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.5 | 8.4 | 6.9 | 3.6 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Whitchurch | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.5 | 8.3 | 7.2 | 5.6 | 4.3 | 3.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Winterbourne | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.2 | 3.8 | 3.2 | 2.9 | 2.7 | 2.4 | 1.7 | 1.2 | 0.8 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Winterbourne | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.2 | 3.6 | 2.8 | 2.3 | 1.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Winterbourne | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.2 | 3.7 | 3 | 2.5 | 2.2 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Winterbourne | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.2 | 3.7 | 3 | 2.5 | 2.1 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Woodland Way | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.5 | 3.7 | 3 | 2.4 | 1.4 | 0 | 16.5 | 15 | 12.6 | 10.9 | 9 | 6.5 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Woodland Way | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.5 | 2.6 | 0.9 | 0 | 0 | 0 | 8.1 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Woodland Way | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.5 | 3 | 1.7 | 0.6 | 0 | 0 | 12.6 | 8.8 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Woodland Way | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.5 | 2.8 | 1.6 | 0 | 0 | 0 | 10.9 | 7.1 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Adelaide Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.5 | 5.4 | 5.1 | 4.4 | 4 | 3.9 | 3 | 2.4 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Adelaide Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.5 | 5.2 | 4.9 | 2.4 | 1.9 | 1.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Adelaide Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.5 | 5.3 | 4.9 | 2.7 | 2.4 | 2.3 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Adelaide Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.5 | 5.3 | 5 | 4.2 | 3.7 | 3.5 | 2.3 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Alexandra Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.4 | 1.9 | 0.9 | 0 | 0 | 0 | 2.7 | 2.1 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Alexandra Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Alexandra Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.4 | 1.5 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Alexandra Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.4 | 1.4 | 0 | 0 | 0 | 0 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Alma Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.5 | 10.4 | 10.3 | 10.2 | 10.1 | 9.9 | 9.9 | 9.7 | 9.3 | 9 | 8.7 | 8.3 | 7.7 | 7.1 | 6.4 | 5.7 | 5.1 | 1.5 | 0
Landulph 132 kV | Alma Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.5 | 10.1 | 9.9 | 9.5 | 9.1 | 8.7 | 8.4 | 7.5 | 6.4 | 5.4 | 4.5 | 3.7 | 2.9 | 2 | 1.1 | 0 | 0 | 0 | 0
Landulph 132 kV | Alma Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.5 | 10.2 | 10.1 | 9.9 | 9.8 | 9.6 | 9.5 | 9 | 8.2 | 7.5 | 6.8 | 5.9 | 4.8 | 3.6 | 2.4 | 1.3 | 0 | 0 | 0
Landulph 132 kV | Alma Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.5 | 10.2 | 10 | 9.7 | 9.4 | 9.1 | 8.9 | 8.2 | 7.4 | 6.7 | 5.9 | 5 | 4 | 3 | 2 | 1.1 | 0 | 0 | 0
Landulph 132 kV | Armada Street | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.6 | 8.5 | 8.4 | 8.3 | 8.1 | 8 | 7.6 | 7.3 | 7 | 6.8 | 6.6 | 6.1 | 5.8 | 5.4 | 4.9 | 4.6 | 4.2 | 2.1 | 0
Landulph 132 kV | Armada Street | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.6 | 8.2 | 7.9 | 7.5 | 7.1 | 6.7 | 6.1 | 5.2 | 4.2 | 3.2 | 2.4 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Armada Street | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.6 | 8.3 | 8.1 | 7.9 | 7.6 | 7.4 | 6.8 | 6.5 | 5.9 | 5.4 | 4.8 | 4 | 3.2 | 2.5 | 1.7 | 1.1 | 0 | 0 | 0
Landulph 132 kV | Armada Street | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.6 | 8.2 | 8 | 7.7 | 7.4 | 7.1 | 6.4 | 6 | 5.4 | 4.8 | 4.2 | 3.3 | 2.8 | 2.2 | 1.7 | 1.2 | 0.6 | 0 | 0
Landulph 132 kV | Buckwell Street | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.6 | 9.5 | 9.5 | 9.1 | 8.5 | 7.5 | 9.4 | 9.2 | 9 | 8.9 | 9 | 8.7 | 8.6 | 8.6 | 8.5 | 8.5 | 8.5 | 8.4 | 8.2
Landulph 132 kV | Buckwell Street | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.6 | 9.2 | 6.3 | 5 | 2.5 | 0 | 8.5 | 8 | 7.5 | 7 | 6.8 | 5.8 | 4.8 | 3.9 | 3 | 2.2 | 1.3 | 0 | 0
Landulph 132 kV | Buckwell Street | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.6 | 9.4 | 7.6 | 7.9 | 6.4 | 5 | 9 | 8.7 | 8.4 | 8.1 | 8.1 | 7 | 6 | 5.1 | 4.1 | 3.2 | 2.5 | 0 | 0
Landulph 132 kV | Buckwell Street | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.6 | 9.5 | 7.2 | 5.6 | 3.9 | 1.9 | 9.1 | 8.9 | 8.6 | 8.4 | 8.4 | 7.9 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 6.5 | 5.8
Landulph 132 kV | Callington | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Callington | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Callington | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Callington | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Eggbuckland | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 6.3 | 6.1 | 5.9 | 5.7 | 5.5 | 5.2 | 4.8 | 4.4 | 3.9 | 3.5 | 3.1 | 0.7 | 0
Landulph 132 kV | Eggbuckland | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 4.4 | 3.6 | 2.9 | 2.2 | 1.6 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Eggbuckland | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 5.7 | 5.3 | 4.8 | 4.3 | 3.8 | 3.2 | 2.5 | 1.7 | 1 | 0 | 0 | 0 | 0
Landulph 132 kV | Eggbuckland | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 5 | 4.5 | 4 | 3.5 | 2.8 | 2.2 | 1.6 | 1.1 | 0.5 | 0 | 0 | 0
Landulph 132 kV | Elim Terrace | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 5.2 | 5 | 4.9 | 4.8 | 4.6 | 4.2 | 3.8 | 3.4 | 3 | 2.6 | 0 | 0
Landulph 132 kV | Elim Terrace | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 4 | 3.3 | 2.7 | 2.3 | 1.8 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Elim Terrace | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 4.9 | 4.4 | 4 | 3.6 | 3.1 | 2.4 | 1.7 | 1 | 0 | 0 | 0 | 0
Landulph 132 kV | Elim Terrace | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 4.5 | 4 | 3.6 | 3.2 | 2.6 | 2.1 | 1.5 | 0.9 | 0 | 0 | 0 | 0
Landulph 132 kV | Ernesettle B & S | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.3 | 4.3 | 4.3 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
Landulph 132 kV | Ernesettle B & S | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.3 | 4.3 | 4.3 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 0 | 0
Landulph 132 kV | Ernesettle B & S | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.3 | 4.3 | 4.3 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 0 | 0
Landulph 132 kV | Ernesettle B & S | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.3 | 4.3 | 4.3 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.3
Landulph 132 kV | Ernesettle Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 11.2 | 10.3 | 9.2 | 8.2 | 7.2 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Ernesettle Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 11.2 | 9.1 | 6.7 | 4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Ernesettle Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 11.2 | 9.4 | 7.4 | 5.2 | 3.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Ernesettle Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 11.2 | 9.3 | 7.4 | 5.4 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Gunnislake | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Gunnislake | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Gunnislake | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Gunnislake | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Ivybridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 1.8 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Ivybridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Ivybridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Ivybridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Landulph Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Landulph Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Landulph Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Landulph Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Langage | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.5 | 12.4 | 6.2 | 6.2 | 6.2 | 5.9 | 5.8 | 5.5 | 5.2 | 4.9 | 4.7 | 4.4 | 4 | 3.8 | 3.5 | 3.3 | 3.1 | 1.8 | 0.8
Landulph 132 kV | Langage | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.5 | 12.3 | 5.9 | 5.8 | 5.4 | 5 | 4.7 | 4.2 | 3.6 | 3.1 | 2.6 | 2.1 | 1.7 | 1.3 | 0.9 | 0.5 | 0 | 0 | 0
Landulph 132 kV | Langage | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.5 | 12.3 | 6 | 5.8 | 5.6 | 5.4 | 5.2 | 4.8 | 4.4 | 4 | 3.7 | 3.3 | 2.7 | 2.2 | 1.8 | 1.4 | 1 | 0 | 0
Landulph 132 kV | Langage | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.5 | 12.3 | 6 | 5.9 | 5.6 | 5.3 | 5 | 4.6 | 4.1 | 3.8 | 3.4 | 2.9 | 2.5 | 2.1 | 1.8 | 1.5 | 1.3 | 0.8 | 0.6
Landulph 132 kV | Lanreath | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Lanreath | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Lanreath | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Lanreath | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Lifton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Lifton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Lifton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Lifton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Linketty Lane | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11 | 10.9 | 10.7 | 10.5 | 10.3 | 10.1 | 9.7 | 9.5 | 9 | 8.8 | 8.4 | 8 | 7.5 | 6.9 | 6.3 | 5.7 | 4.8 | 0 | 0
Landulph 132 kV | Linketty Lane | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11 | 10.6 | 10.2 | 9.6 | 9.2 | 8.7 | 8 | 7 | 5.8 | 4.6 | 3.7 | 2.8 | 2 | 0.8 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Linketty Lane | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11 | 10.6 | 10.4 | 10 | 9.7 | 9.4 | 8.9 | 8.3 | 7.5 | 6.8 | 6.1 | 5.2 | 4.3 | 3.3 | 2.3 | 1.4 | 0 | 0 | 0
Landulph 132 kV | Linketty Lane | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11 | 10.6 | 10.4 | 9.9 | 9.5 | 9.1 | 8.5 | 7.8 | 7 | 6.2 | 5.3 | 3.9 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Liskeard | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Liskeard | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Liskeard | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Liskeard | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Longbridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.7 | 6.6 | 6.6 | 6.3 | 6 | 5.8 | 5.4 | 5.1 | 4.7 | 4.5 | 4.2 | 3.8 | 3.5 | 3.1 | 2.8 | 2.5 | 2.1 | 0 | 0
Landulph 132 kV | Longbridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.7 | 6.5 | 6.2 | 5.6 | 5.1 | 4.5 | 3.9 | 3.1 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Longbridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.7 | 6.5 | 6.3 | 5.7 | 5.3 | 4.9 | 4.4 | 3.8 | 3.1 | 2.5 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Longbridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.7 | 6.5 | 6.3 | 5.9 | 5.5 | 5.1 | 4.6 | 4 | 3.4 | 2.8 | 2.3 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Looe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Looe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Looe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Looe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Merrivale | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.8 | 0.6 | 0.5 | 0 | 0 | 0 | 4.9 | 4 | 2.8 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Merrivale | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Merrivale | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Merrivale | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Milehouse Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 34.4 | 25.1 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Milehouse Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 34.4 | 20.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Milehouse Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 34.4 | 22.1 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Milehouse Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 34.4 | 21.6 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Modbury | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 1.8 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Modbury | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Modbury | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Modbury | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Newport Street | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.6 | 5.5 | 5 | 4.5 | 4.2 | 3.9 | 25.1 | 24.6 | 23.9 | 23.5 | 23.1 | 22.7 | 22.3 | 21.8 | 21.4 | 21.1 | 20.7 | 12.4 | 10
Landulph 132 kV | Newport Street | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.6 | 5.3 | 0 | 0 | 0 | 0 | 12.9 | 4.3 | 2.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Newport Street | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.6 | 5.4 | 0 | 0 | 0 | 0 | 13.9 | 5.7 | 4.4 | 3.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Newport Street | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.6 | 5.4 | 0 | 0 | 0 | 0 | 16.2 | 15.4 | 12.6 | 11.9 | 9.4 | 8.1 | 7.4 | 6.7 | 6 | 5.3 | 4.8 | 3 | 2
Landulph 132 kV | Newton Ferrers | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 1.4 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Newton Ferrers | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Newton Ferrers | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Newton Ferrers | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.1 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Old Laira Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 10.7 | 10.6 | 10.4 | 10.2 | 10.1 | 9.8 | 9.5 | 9.2 | 8.9 | 8.6 | 8.3 | 6.4 | 2.9
Landulph 132 kV | Old Laira Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 9.2 | 8.6 | 8 | 7.5 | 7.1 | 6.7 | 6.4 | 6 | 5.7 | 4.7 | 0 | 0
Landulph 132 kV | Old Laira Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 10.3 | 10 | 9.6 | 9.3 | 8.9 | 8.4 | 7.9 | 7.4 | 6.8 | 6.4 | 6 | 0 | 0
Landulph 132 kV | Old Laira Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 10.1 | 9.8 | 9.4 | 9 | 8.5 | 8 | 7.6 | 7.2 | 6.8 | 6.5 | 6.2 | 3.6 | 2.5
Landulph 132 kV | Pensilva | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Pensilva | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Pensilva | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Pensilva | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Plymouth 33 (New) | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 6.7 | 6 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Plymouth 33 (New) | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 6.7 | 5.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Plymouth 33 (New) | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 6.7 | 5.4 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Plymouth 33 (New) | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 6.7 | 5.3 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Plymstock South | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 3.1 | 2.3 | 1.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Plymstock South | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Plymstock South | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Plymstock South | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Prince Rock | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.2 | 10.2 | 10.2 | 10.2 | 9.4 | 9.3 | 8.7 | 8.6 | 8.4 | 8.2 | 8.1 | 8 | 7.9 | 7.7 | 7.6 | 7.5 | 7.3 | 6.5 | 5.7
Landulph 132 kV | Prince Rock | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.2 | 10 | 9.9 | 9.7 | 6.6 | 6.4 | 5.7 | 5.3 | 4.8 | 4.4 | 4 | 3.7 | 3.4 | 3.1 | 2.8 | 2.1 | 1.1 | 0 | 0
Landulph 132 kV | Prince Rock | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.2 | 10.1 | 10 | 9.8 | 6.8 | 6.7 | 6.1 | 5.9 | 5.6 | 5.4 | 5.1 | 4.8 | 4.5 | 4.1 | 3.8 | 3 | 2.1 | 0 | 0
Landulph 132 kV | Prince Rock | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.2 | 10.1 | 10 | 9.9 | 9.1 | 9 | 8.2 | 8 | 7.6 | 7.2 | 6.9 | 6.6 | 6.3 | 6.1 | 5.9 | 5.7 | 5.5 | 4.5 | 3.9
Landulph 132 kV | Saltash Dunheved Rd | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.3 | 10.8 | 10.4 | 9.6 | 9 | 8.3 | 5.1 | 4.3 | 3.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Saltash Dunheved Rd | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.3 | 10.3 | 9.1 | 7.9 | 6.7 | 4.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Saltash Dunheved Rd | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.3 | 10.6 | 9.7 | 9.1 | 8.3 | 7.3 | 4.4 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Saltash Dunheved Rd | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 10.5 | 9.5 | 8.6 | 7.5 | 6.3 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Saltash Whity Cross | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 3.7 | 3.4 | 3.2 | 2.9 | 2.6 | 2.3 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Saltash Whity Cross | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 3.6 | 3.3 | 2.9 | 2.6 | 2.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Saltash Whity Cross | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 3.6 | 3.4 | 3.1 | 2.8 | 2.5 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Saltash Whity Cross | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 3.6 | 3.3 | 3 | 2.7 | 2.3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Southway | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.5 | 6.4 | 6.4 | 6.4 | 6.4 | 6.2 | 5.8 | 5.5 | 5.2 | 5 | 4.8 | 4.3 | 3.8 | 3.3 | 2.9 | 2.4 | 2 | 0 | 0
Landulph 132 kV | Southway | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.5 | 6.2 | 6 | 5.8 | 5.6 | 5.3 | 4.6 | 3.9 | 3.1 | 2.4 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Southway | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.5 | 6.2 | 6 | 5.9 | 5.7 | 5.4 | 4.7 | 4.3 | 3.8 | 3.3 | 2.8 | 2.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Southway | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.5 | 6.2 | 6.1 | 5.9 | 5.8 | 5.4 | 4.8 | 4.3 | 3.8 | 3.2 | 2.7 | 2 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | St Germans Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | St Germans Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | St Germans Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | St Germans Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | St Levan Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.4 | 13.3 | 12.9 | 12.6 | 12.3 | 12.1 | 11.9 | 11.8 | 11.5 | 11.4 | 11.2 | 11 | 10.5 | 10.1 | 9.7 | 9.4 | 9.1 | 7.1 | 5.6
Landulph 132 kV | St Levan Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.4 | 13.2 | 12.6 | 12 | 11.5 | 11.1 | 10.8 | 10.1 | 9.4 | 8.7 | 8.1 | 7.3 | 6.5 | 5.8 | 5 | 4.4 | 3.6 | 0 | 0
Landulph 132 kV | St Levan Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.4 | 13.3 | 12.6 | 12.3 | 11.9 | 11.4 | 11.1 | 10.7 | 10.2 | 9.7 | 9.2 | 8.4 | 7.3 | 6.4 | 5.3 | 4.3 | 3.5 | 0 | 0
Landulph 132 kV | St Levan Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.4 | 13.2 | 12.7 | 12.3 | 12 | 11.6 | 11.4 | 11 | 10.5 | 10 | 9.5 | 8.9 | 8.3 | 7.7 | 7.1 | 6.7 | 6.3 | 5 | 4.6
Landulph 132 kV | St Neot | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | St Neot | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | St Neot | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | St Neot | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Stentaway | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 3.2 | 2.4 | 1.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Stentaway | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Stentaway | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Stentaway | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Tavistock | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Tavistock | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Tavistock | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Tavistock | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torpoint Antony | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 5.2 | 5.2 | 5.2 | 5.2 | 5.1 | 3.6 | 2.7 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torpoint Antony | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 5.2 | 5.1 | 5 | 4.9 | 4.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torpoint Antony | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 5.2 | 5.2 | 5.2 | 5.2 | 5.1 | 3.2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torpoint Antony | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 5.2 | 5.2 | 5.1 | 5 | 4.9 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torpoint Town | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.3 | 2.2 | 2.2 | 2.1 | 2.1 | 2 | 1.9 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torpoint Town | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.3 | 2.1 | 2 | 1.9 | 1.7 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torpoint Town | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.3 | 2.2 | 2.1 | 2 | 1.9 | 1.8 | 1.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torpoint Town | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.3 | 2.2 | 2.1 | 2 | 1.8 | 1.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torycombe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.9 | 7.9 | 7.9 | 8 | 8 | 8 | 10.6 | 10.6 | 10.5 | 10.5 | 10.5 | 10.4 | 10.3 | 10.2 | 10.1 | 10.1 | 10 | 9.6 | 9.3
Landulph 132 kV | Torycombe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.8 | 10.3 | 10.2 | 10.1 | 10.1 | 10.1 | 10 | 9.9 | 9.8 | 9.8 | 9.7 | 9.6 | 9.4 | 9.2
Landulph 132 kV | Torycombe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.3 | 10.2 | 10.1 | 10 | 9.8 | 9.8 | 9.4 | 9.1
Landulph 132 kV | Torycombe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.8 | 10.4 | 10.3 | 10.2 | 10.2 | 10.2 | 10 | 9.9 | 9.8 | 9.7 | 9.5 | 9.5 | 9.2 | 9
Landulph 132 kV | Weston Mill | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.6 | 4.5 | 4.4 | 4.2 | 3.7 | 3.3 | 3.2 | 3 | 2.7 | 2.5 | 2.3 | 2 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Weston Mill | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.6 | 4.3 | 4 | 3.5 | 2.8 | 2.1 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Weston Mill | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.6 | 4.3 | 4.1 | 3.8 | 3.3 | 2.8 | 2.7 | 2.2 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Weston Mill | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.6 | 4.3 | 4.1 | 3.7 | 3 | 2.5 | 2.2 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Yelverton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.1 | 2.6 | 1.3 | 0 | 0 | 0 | 3.3 | 3.1 | 2.9 | 2.7 | 2.5 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Yelverton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.1 | 1.7 | 0 | 0 | 0 | 0 | 2.6 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Yelverton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.1 | 2 | 0 | 0 | 0 | 0 | 3.1 | 2.8 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Yelverton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.1 | 1.9 | 0 | 0 | 0 | 0 | 2.9 | 2.5 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Bath (Dolemeads) 132 | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 25.9 | 18 | 16.5 | 15.4 | 11.2 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Bath (Dolemeads) 132 | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 25.9 | 15.8 | 12.6 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Bath (Dolemeads) 132 | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 25.9 | 16.3 | 13.6 | 11 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Bath (Dolemeads) 132 | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 25.9 | 16.6 | 14.1 | 10.8 | 6 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Batheaston | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.2 | 9.1 | 9 | 8.9 | 8.8 | 8.7 | 8 | 7.8 | 7.4 | 7.1 | 6.8 | 6.4 | 5.9 | 5.2 | 4.6 | 4 | 3.5 | 0 | 0
Melksham 132 kV | Batheaston | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.2 | 8.9 | 8.5 | 8.1 | 7.7 | 7.1 | 6.1 | 5.2 | 4.1 | 3.1 | 2.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Batheaston | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.2 | 9 | 8.8 | 8.5 | 8.3 | 8 | 7.3 | 6.8 | 6.1 | 5.4 | 4.7 | 3.6 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Batheaston | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.2 | 8.9 | 8.7 | 8.5 | 8.2 | 7.9 | 7.1 | 6.5 | 5.7 | 5 | 4.3 | 3.3 | 2.4 | 1.6 | 0.8 | 0 | 0 | 0 | 0
Melksham 132 kV | Combe Park | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 11.1 | 5.7 | 5.4 | 5.1 | 3.3 | 2.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Combe Park | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 11.1 | 5.3 | 4.4 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Combe Park | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 11.1 | 5.4 | 4.5 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Combe Park | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 11.1 | 5.4 | 4.7 | 4.1 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Dorchester St - New | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 6.2 | 6 | 5.7 | 5.5 | 4.9 | 4.5 | 3.5 | 2.9 | 2.7 | 2.6 | 2.5 | 2.1 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Dorchester St - New | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 6.2 | 5.4 | 5 | 4.3 | 3.8 | 3.1 | 2.1 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Dorchester St - New | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 6.2 | 5.5 | 5.1 | 4.6 | 4 | 3.5 | 2.6 | 2 | 1.7 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Dorchester St - New | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 6.2 | 5.7 | 5.3 | 4.7 | 4.1 | 3.5 | 2.4 | 1.7 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Entry Hill | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 9.2 | 2.8 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Entry Hill | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 9.2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Entry Hill | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 9.2 | 2.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Entry Hill | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 9.2 | 2.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Oldfield Park | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Oldfield Park | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Oldfield Park | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Oldfield Park | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Park Street | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 1.6 | 1.5 | 1.4 | 1.3 | 1 | 0.9 | 10.9 | 10.8 | 10.5 | 10.3 | 10.1 | 9.7 | 9.4 | 9.1 | 8.7 | 8.4 | 8.2 | 6.6 | 5.2
Melksham 132 kV | Park Street | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 1.6 | 1.3 | 1.1 | 0.7 | 0 | 0 | 9.7 | 9 | 8.2 | 7.2 | 6.5 | 5.5 | 4.6 | 3.8 | 3 | 2 | 1.2 | 0 | 0
Melksham 132 kV | Park Street | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 1.6 | 1.4 | 1.3 | 1.2 | 0.8 | 0.7 | 10.8 | 10.3 | 9.7 | 9.1 | 8.5 | 7.5 | 6.4 | 5.3 | 4.3 | 3.4 | 2.5 | 0 | 0
Melksham 132 kV | Park Street | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 1.6 | 1.4 | 1.3 | 1 | 0.6 | 0 | 10.4 | 10 | 9.5 | 9 | 8.4 | 7.6 | 7.1 | 6.6 | 6.2 | 5.8 | 5.5 | 4.5 | 3.7
Melksham 132 kV | Twerton | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 10.8 | 5.4 | 5.1 | 4.8 | 3.1 | 2.4 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Twerton | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 10.8 | 5 | 4.2 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Twerton | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 10.8 | 5.1 | 4.3 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melksham 132 kV | Twerton | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 10.8 | 5.1 | 4.4 | 3.9 | 1.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Axbridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 1.2 | 1.1 | 0.9 | 0.8 | 0.7 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Axbridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Axbridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 1.1 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Axbridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Blagdon 33/11kv S/S | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.6 | 8.5 | 8.5 | 8.5 | 8.5 | 7.7 | 4.7 | 1.4 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Blagdon 33/11kv S/S | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.4 | 5.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Blagdon 33/11kv S/S | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 8.5 | 5.4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Blagdon 33/11kv S/S | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.4 | 8 | 4.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Bournville | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.5 | 7.3 | 7.1 | 6.9 | 6.7 | 6.5 | 6.1 | 5.8 | 5.3 | 4.9 | 4.5 | 3.9 | 3.1 | 2.3 | 1.5 | 0.8 | 0 | 0 | 0
Sandford 132 kV | Bournville | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.5 | 7 | 6.6 | 6.1 | 5.6 | 5 | 4.3 | 3.2 | 1.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Bournville | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.5 | 7.1 | 6.8 | 6.5 | 6.2 | 5.8 | 5.2 | 4.4 | 3.4 | 2.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Bournville | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.5 | 7.1 | 6.7 | 6.4 | 6 | 5.5 | 4.9 | 4.1 | 3.2 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Cheddar | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 1.2 | 1.1 | 0.9 | 0.8 | 0.7 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Cheddar | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Cheddar | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 1.1 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Cheddar | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Chew Stoke | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Chew Stoke | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Chew Stoke | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Chew Stoke | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Churchill Bsp 132kv | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Churchill Bsp 132kv | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Churchill Bsp 132kv | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Churchill Bsp 132kv | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Churchill Gate 33/11 | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.2 | 1.2 | 1.1 | 1 | 0.8 | 0.7 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Churchill Gate 33/11 | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.2 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Churchill Gate 33/11 | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.2 | 1.1 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Churchill Gate 33/11 | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.2 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Compton Martin 33/11kv S/S | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Compton Martin 33/11kv S/S | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Compton Martin 33/11kv S/S | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Compton Martin 33/11kv S/S | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Congresbury | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Congresbury | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Congresbury | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Congresbury | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | East Brent | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.6 | 0.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | East Brent | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | East Brent | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | East Brent | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Lypstone Farm | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.2 | 2.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Lypstone Farm | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.2 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Lypstone Farm | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.2 | 2.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Lypstone Farm | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.2 | 2.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Nailsea | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Nailsea | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Nailsea | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Nailsea | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Weston Bsp 132kv | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 3.1 | 2.2 | 0 | 0 | 0 | 0 | 32.9 | 31 | 28.4 | 26.7 | 24.7 | 22.1 | 18.4 | 13 | 7.2 | 1.6 | 0 | 0 | 0
Sandford 132 kV | Weston Bsp 132kv | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 3.1 | 0.9 | 0 | 0 | 0 | 0 | 24.1 | 18.5 | 12.2 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Weston Bsp 132kv | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 3.1 | 1.3 | 0 | 0 | 0 | 0 | 30.1 | 26.2 | 21.5 | 17.3 | 12.5 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Weston Bsp 132kv | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 3.1 | 1.2 | 0 | 0 | 0 | 0 | 27 | 23.1 | 18.6 | 13.9 | 8.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Weston Central | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.2 | 11 | 10.9 | 10.7 | 10.5 | 10.2 | 9.8 | 9.5 | 9 | 8.7 | 8.3 | 7.9 | 7.4 | 6.8 | 6.3 | 5.8 | 5.3 | 0 | 0
Sandford 132 kV | Weston Central | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.2 | 10.8 | 10.3 | 9.9 | 9.4 | 8.9 | 8.1 | 7.2 | 6 | 5 | 4.1 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Weston Central | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.2 | 10.9 | 10.6 | 10.4 | 10.1 | 9.7 | 9.2 | 8.6 | 7.9 | 7.2 | 6.5 | 5.7 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Weston Central | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.2 | 10.8 | 10.6 | 10.3 | 9.9 | 9.5 | 8.8 | 8.2 | 7.4 | 6.6 | 5.8 | 4.9 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Weston Locking Rd | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8 | 7.7 | 6.3 | 4.9 | 3.9 | 3.2 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Weston Locking Rd | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8 | 7.3 | 5.4 | 3.1 | 2.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Weston Locking Rd | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8 | 7.4 | 5.8 | 4.3 | 3.4 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Weston Locking Rd | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8 | 7.4 | 5.6 | 3.5 | 2.5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Westwick | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.8 | 3.8 | 3.1 | 2.4 | 2.4 | 2.3 | 1.9 | 1.8 | 1.7 | 1.6 | 1.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Westwick | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.8 | 3.7 | 3 | 2.2 | 2.1 | 1.9 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Westwick | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.8 | 3.7 | 3.1 | 2.4 | 2.4 | 2.3 | 1.9 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Westwick | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.8 | 3.7 | 3 | 2.2 | 2.1 | 2 | 1.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Winscombe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 1.2 | 1.1 | 0.9 | 0.8 | 0.7 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Winscombe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Winscombe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 1.1 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Winscombe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Avonmouth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Avonmouth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Avonmouth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Avonmouth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Avonmouth Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 17.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Avonmouth Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Avonmouth Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Avonmouth Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Cairns Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.6 | 2.2 | 1.9 | 1.8 | 1.6 | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Cairns Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.6 | 1.8 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Cairns Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.6 | 1.9 | 1.5 | 1.2 | 0.9 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Cairns Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.6 | 1.9 | 1.5 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Chewton Mendip | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.8 | 1.7 | 1.7 | 1.7 | 1.6 | 1.5 | 1.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Chewton Mendip | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.8 | 1.7 | 1.6 | 1.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Chewton Mendip | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.8 | 1.7 | 1.7 | 1.5 | 1.4 | 1.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Chewton Mendip | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.8 | 1.7 | 1.6 | 1.6 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Clevedon | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 3.8 | 3.7 | 3.6 | 3.4 | 3.1 | 2.3 | 1.8 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Clevedon | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 3.6 | 3.3 | 2.8 | 2.2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Clevedon | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 3.7 | 3.5 | 3.4 | 3 | 2.6 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Clevedon | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 3.7 | 3.4 | 3.1 | 2.6 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Dinder | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Dinder | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.6 | 1.6 | 1.5 | 1.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Dinder | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Dinder | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.6 | 1.6 | 1.6 | 1.5 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Easton-In-Gordano | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.3 | 9.3 | 9.2 | 9.2 | 9.1 | 9 | 8.9 | 8.8 | 8.6 | 8.5 | 8.3 | 8.2 | 7.9 | 7.6 | 7.4 | 7.2 | 6.7 | 4.3 | 2.3
Seabank 132 kV | Easton-In-Gordano | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.3 | 9.2 | 9.1 | 9 | 8.8 | 8.6 | 8.4 | 8.1 | 7.7 | 7.3 | 7 | 6.7 | 6.4 | 6 | 5.6 | 5.3 | 5 | 4.1 | 3.5
Seabank 132 kV | Easton-In-Gordano | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.3 | 9.2 | 9.2 | 9.1 | 9 | 8.9 | 8.7 | 8.5 | 8.2 | 7.9 | 7.6 | 7.3 | 6.9 | 6.5 | 6.2 | 5.8 | 5.5 | 4.5 | 3.9
Seabank 132 kV | Easton-In-Gordano | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.3 | 9.2 | 9.1 | 9 | 8.9 | 8.8 | 8.6 | 8.3 | 8 | 7.7 | 7.4 | 6.9 | 6 | 5.2 | 4.5 | 3.8 | 3.2 | 1.6 | 1.3
Seabank 132 kV | Evercreech | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Evercreech | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Evercreech | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Evercreech | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Foxhills | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Foxhills | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Foxhills | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Foxhills | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Gas Lane | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9 | 8.9 | 8.8 | 8.7 | 8.6 | 8.4 | 7.5 | 7.3 | 6.9 | 6.6 | 6.3 | 5.8 | 5.3 | 4.7 | 4.1 | 3.6 | 3 | 0 | 0
Seabank 132 kV | Gas Lane | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9 | 8.7 | 8.5 | 8.1 | 7.8 | 7.3 | 6.2 | 5.4 | 4.5 | 3.5 | 2.8 | 2 | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Gas Lane | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9 | 8.8 | 8.6 | 8.5 | 8.3 | 8 | 7.1 | 6.5 | 5.8 | 5.2 | 4.5 | 3.7 | 2.8 | 2 | 1.1 | 0 | 0 | 0 | 0
Seabank 132 kV | Gas Lane | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9 | 8.7 | 8.6 | 8.4 | 8 | 7.7 | 6.7 | 6.1 | 5.5 | 4.7 | 4 | 3.2 | 2.4 | 1.6 | 0.9 | 0 | 0 | 0 | 0
Seabank 132 kV | High Littleton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 6.7 | 6.7 | 6.7 | 6.6 | 6.6 | 6.5 | 6.4 | 6.1 | 5.9 | 5.7 | 5.4 | 5 | 3.5 | 1.8 | 0 | 0 | 0 | 0
Seabank 132 kV | High Littleton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 6.6 | 6.6 | 6.4 | 6.3 | 6.1 | 5.9 | 5.4 | 4.1 | 2.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | High Littleton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 6.7 | 6.6 | 6.6 | 6.5 | 6.5 | 6.2 | 5.9 | 5.4 | 4.5 | 3.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | High Littleton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.7 | 6.6 | 6.5 | 6.4 | 6.3 | 6.1 | 5.8 | 5.3 | 4 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Keynsham East | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.6 | 3.5 | 3.3 | 3.2 | 2.9 | 2.6 | 2.4 | 2.1 | 1.9 | 1.7 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Keynsham East | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3.4 | 3.1 | 2.8 | 2.3 | 1.9 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Keynsham East | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.5 | 3.3 | 3 | 2.7 | 2.4 | 2 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Keynsham East | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.5 | 3.3 | 2.9 | 2.6 | 2.2 | 1.6 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Kingsweston | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.7 | 6 | 5.9 | 5.7 | 5.4 | 4.9 | 3.9 | 3.2 | 2.5 | 2.1 | 1.8 | 1.5 | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Kingsweston | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.7 | 5.8 | 5.5 | 5.1 | 4.3 | 3.3 | 1.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Kingsweston | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.7 | 5.8 | 5.5 | 4.8 | 4.1 | 3.3 | 2.1 | 1.3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Kingsweston | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.7 | 5.8 | 5.6 | 5.3 | 4.6 | 3.7 | 2.3 | 1.3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Midsomer Norton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.8 | 4.6 | 4.4 | 4.3 | 4.1 | 3.9 | 3.2 | 2.9 | 2.3 | 1.9 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Midsomer Norton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.8 | 4.4 | 4 | 3.4 | 3.1 | 2.7 | 1.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Midsomer Norton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.8 | 4.4 | 4.2 | 4 | 3.7 | 3.5 | 2.7 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Midsomer Norton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.8 | 4.4 | 4.1 | 3.7 | 3.4 | 3.1 | 2.2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Newbury | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Newbury | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Newbury | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Newbury | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Paulton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.5 | 3.5 | 3.4 | 3.4 | 3.2 | 3.2 | 3.2 | 2.9 | 2.6 | 2.5 | 2.3 | 2.2 | 1.9 | 1.6 | 1.3 | 0 | 0 | 0 | 0
Seabank 132 kV | Paulton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.5 | 3.4 | 3.3 | 3.1 | 3 | 2.8 | 2.7 | 2.3 | 1.7 | 1.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Paulton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.5 | 3.4 | 3.4 | 3.3 | 3.1 | 3.1 | 3 | 2.6 | 2.1 | 1.8 | 1.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Paulton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.5 | 3.4 | 3.4 | 3.2 | 3 | 2.9 | 2.9 | 2.5 | 2 | 1.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Peasedown | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2 | 2 | 1.9 | 1.9 | 1.7 | 1.6 | 1.4 | 1.3 | 1.1 | 1 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Peasedown | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2 | 1.9 | 1.8 | 1.6 | 1.3 | 1.1 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Peasedown | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2 | 2 | 1.9 | 1.7 | 1.5 | 1.4 | 1.3 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Peasedown | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2 | 1.9 | 1.8 | 1.7 | 1.4 | 1.3 | 1.1 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Portishead Ashlands | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.4 | 6.3 | 6.2 | 6.2 | 6.2 | 6.1 | 6 | 5.9 | 5.7 | 5.6 | 5.5 | 5.3 | 5 | 4.7 | 4.3 | 4.1 | 3.8 | 2.5 | 1.5
Seabank 132 kV | Portishead Ashlands | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.4 | 6.2 | 6 | 5.9 | 5.7 | 5.4 | 5.2 | 4.9 | 4.4 | 3.9 | 3.5 | 3 | 2.7 | 2.4 | 2 | 1.7 | 1.3 | 0 | 0
Seabank 132 kV | Portishead Ashlands | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.4 | 6.2 | 6.1 | 5.9 | 5.9 | 5.7 | 5.4 | 5.2 | 4.8 | 4.5 | 4.1 | 3.6 | 3.1 | 2.5 | 2 | 1.6 | 1.2 | 0 | 0
Seabank 132 kV | Portishead Ashlands | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.4 | 6.2 | 6.1 | 6.1 | 6 | 5.8 | 5.6 | 5.4 | 5.1 | 4.8 | 4.4 | 4 | 3.6 | 3.2 | 2.8 | 2.5 | 2.3 | 1.4 | 1
Seabank 132 kV | Portishead New Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 15.9 | 15.3 | 15.1 | 15 | 14.5 | 13.9 | 10.8 | 9.9 | 8.5 | 7.4 | 6.3 | 4.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Portishead New Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 15.9 | 14.6 | 13.8 | 12.7 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Portishead New Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 15.9 | 14.9 | 14.4 | 13.9 | 13.2 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Portishead New Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 15.9 | 14.8 | 14.3 | 13.6 | 12.5 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Radstock Bsp 132kv | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 21.8 | 20.6 | 20.1 | 19.6 | 18.3 | 16.6 | 11.9 | 9.1 | 5.8 | 3.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Radstock Bsp 132kv | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 21.8 | 19.6 | 18 | 15.5 | 12.2 | 8.5 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Radstock Bsp 132kv | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 21.8 | 20.1 | 19.1 | 17.2 | 14.8 | 12.9 | 7.5 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Radstock Bsp 132kv | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 21.8 | 19.9 | 18.7 | 16.8 | 13.9 | 10.9 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Shepton Mallet | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Shepton Mallet | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Shepton Mallet | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Shepton Mallet | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Stoke Bishop | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.2 | 11.1 | 11.1 | 11.1 | 11 | 11 | 10.9 | 10.8 | 10.6 | 10.4 | 10.3 | 10 | 9.5 | 9.1 | 8.6 | 8.2 | 7.8 | 5.2 | 3.2
Seabank 132 kV | Stoke Bishop | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.2 | 11 | 10.7 | 10.5 | 10.3 | 10.1 | 9.8 | 9.2 | 8.5 | 7.8 | 7.1 | 6.5 | 6 | 5.4 | 4.9 | 4.3 | 3.8 | 1.8 | 1.9
Seabank 132 kV | Stoke Bishop | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.2 | 11 | 10.8 | 10.7 | 10.7 | 10.5 | 10.3 | 9.9 | 9.4 | 8.9 | 8.3 | 7.6 | 6.8 | 6.1 | 5.4 | 4.7 | 4.1 | 2.2 | 1.6
Seabank 132 kV | Stoke Bishop | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.2 | 11 | 10.9 | 10.8 | 10.6 | 10.5 | 10.3 | 9.9 | 9.4 | 8.9 | 8.4 | 7.7 | 7.1 | 6.6 | 6 | 5.5 | 5.1 | 4.1 | 3.9
Seabank 132 kV | Weston-In-Gordano | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.6 | 0.5 | 0 | 0 | 0 | 0 | 3.3 | 2.8 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Weston-In-Gordano | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.6 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Weston-In-Gordano | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.6 | 0 | 0 | 0 | 0 | 0 | 2.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Weston-In-Gordano | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.6 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Alcombe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.4 | 4.2 | 4 | 3.9 | 3.6 | 3.2 | 6.1 | 5.7 | 4.6 | 3.8 | 3.1 | 1.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Alcombe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.4 | 3.9 | 3.6 | 3 | 2.4 | 1.7 | 4.4 | 3.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Alcombe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.4 | 4.1 | 3.9 | 3.7 | 3.3 | 2.8 | 5.6 | 4.8 | 3.4 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Alcombe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.4 | 4 | 3.8 | 3.4 | 2.9 | 2.3 | 5 | 4.2 | 2.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Bowhays Cross | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.1 | 6.9 | 6.7 | 6.5 | 6.2 | 5.8 | 5.3 | 4.5 | 3.5 | 2.7 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Bowhays Cross | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.1 | 6.8 | 6.5 | 6.1 | 5.6 | 4.8 | 3.7 | 2.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Bowhays Cross | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.1 | 6.9 | 6.7 | 6.4 | 6 | 5.4 | 4.7 | 3.9 | 2.8 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Bowhays Cross | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.1 | 6.9 | 6.6 | 6.3 | 5.8 | 5.1 | 4.1 | 3.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Bowhays Cross Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 35.5 | 35 | 34.6 | 34.2 | 33.4 | 32.4 | 32.3 | 30.7 | 28.3 | 26.3 | 24.5 | 21.4 | 17.9 | 15.7 | 13.7 | 11.9 | 9.9 | 0 | 0
Taunton 132 kV | Bowhays Cross Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 35.5 | 34.6 | 33.8 | 32.6 | 31.1 | 29.2 | 28 | 25.2 | 20.3 | 14.9 | 12 | 9.1 | 6.6 | 4.1 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Bowhays Cross Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 35.5 | 34.8 | 34.4 | 33.7 | 32.7 | 31.5 | 30.8 | 28.7 | 25.6 | 21.9 | 16.5 | 12.6 | 9.3 | 6.1 | 3.4 | 0 | 0 | 0 | 0
Taunton 132 kV | Bowhays Cross Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 35.5 | 34.7 | 34.2 | 33.3 | 32 | 30.5 | 29.3 | 27 | 23.5 | 18.3 | 14.3 | 10.9 | 7.7 | 4.6 | 1.9 | 0 | 0 | 0 | 0
Taunton 132 kV | Culmhead | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.5 | 5.8 | 4.8 | 4 | 3.2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Culmhead | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.5 | 5.4 | 3.9 | 2.6 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Culmhead | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.5 | 5.5 | 4.1 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Culmhead | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.5 | 5.4 | 4.2 | 3.1 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Exebridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.7 | 8.6 | 8.6 | 8.5 | 8.5 | 8.4 | 8.4 | 8.3 | 8.2 | 8.1 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 6.8 | 4.7 | 2.5
Taunton 132 kV | Exebridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.7 | 8.6 | 8.5 | 8.4 | 8.3 | 8.2 | 8 | 7.8 | 7.5 | 7.2 | 6.9 | 6.5 | 6.1 | 5.6 | 5 | 4.4 | 3.9 | 2.5 | 1.4
Taunton 132 kV | Exebridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.7 | 8.6 | 8.6 | 8.6 | 8.5 | 8.5 | 8.3 | 8.1 | 7.8 | 7.5 | 7.2 | 6.9 | 6.5 | 6.1 | 5.4 | 4.7 | 4.1 | 2.1 | 0.7
Taunton 132 kV | Exebridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.7 | 8.6 | 8.6 | 8.5 | 8.4 | 8.3 | 8.2 | 8 | 7.6 | 7.3 | 6.9 | 6.5 | 6.1 | 5.5 | 4.8 | 4 | 3.5 | 2.1 | 1
Taunton 132 kV | Holford | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.6 | 4.5 | 4.5 | 4.5 | 4.5 | 4.4 | 4.5 | 4.4 | 4.4 | 4.3 | 4.3 | 4.2 | 4.2 | 4.1 | 4 | 4 | 3.9 | 1.3 | 0
Taunton 132 kV | Holford | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.6 | 4.5 | 4.5 | 4.5 | 4.4 | 4.4 | 4.3 | 4.2 | 4.1 | 4 | 4 | 3.9 | 3.4 | 2.2 | 1 | 0 | 0 | 0 | 0
Taunton 132 kV | Holford | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.6 | 4.5 | 4.5 | 4.5 | 4.5 | 4.4 | 4.4 | 4.3 | 4.3 | 4.2 | 4.1 | 4 | 3.9 | 3.8 | 3.1 | 1.6 | 0 | 0 | 0
Taunton 132 kV | Holford | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.6 | 4.5 | 4.5 | 4.5 | 4.4 | 4.4 | 4.4 | 4.3 | 4.2 | 4.1 | 4 | 3.9 | 3.8 | 3.5 | 2 | 1 | 0 | 0 | 0
Taunton 132 kV | Luckwell Bridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 3.6 | 3.4 | 3.3 | 3 | 2.7 | 3.5 | 3.4 | 3.3 | 3.2 | 3.1 | 3 | 2.8 | 2.6 | 2.4 | 2.3 | 2.1 | 1.1 | 0
Taunton 132 kV | Luckwell Bridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 3.4 | 3 | 2.6 | 2.1 | 1.4 | 3.2 | 3 | 2.7 | 2.4 | 2.2 | 2 | 1.7 | 1.5 | 1.4 | 1.2 | 1 | 0.8 | 0.6
Taunton 132 kV | Luckwell Bridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 3.5 | 3.3 | 3.1 | 2.8 | 2.4 | 3.4 | 3.2 | 3 | 2.8 | 2.6 | 2.3 | 2.1 | 1.8 | 1.6 | 1.4 | 1.3 | 0.8 | 0
Taunton 132 kV | Luckwell Bridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 3.4 | 3.2 | 2.9 | 2.5 | 2 | 3.3 | 3.1 | 2.8 | 2.6 | 2.3 | 2 | 1.7 | 1.4 | 1.1 | 0.8 | 0.6 | 0 | 0
Taunton 132 kV | Lydeard St Lawrence Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.3 | 3.3 | 3.2 | 3.2 | 3.2 | 3.1 | 3.2 | 3.1 | 3 | 3 | 2.9 | 2.8 | 2.6 | 2.4 | 2.2 | 2 | 1.8 | 0.8 | 0
Taunton 132 kV | Lydeard St Lawrence Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.3 | 3.2 | 3.2 | 3.1 | 3 | 2.9 | 2.9 | 2.7 | 2.4 | 2.1 | 1.8 | 1.5 | 1.2 | 0.9 | 0.7 | 0 | 0 | 0 | 0
Taunton 132 kV | Lydeard St Lawrence Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.3 | 3.3 | 3.2 | 3.2 | 3.1 | 3.1 | 3 | 2.8 | 2.6 | 2.4 | 2.1 | 1.7 | 1.4 | 1.1 | 0.8 | 0.5 | 0 | 0 | 0
Taunton 132 kV | Lydeard St Lawrence Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.3 | 3.3 | 3.2 | 3.2 | 3.1 | 3 | 3 | 2.8 | 2.6 | 2.3 | 2 | 1.6 | 1.3 | 0.9 | 0.6 | 0 | 0 | 0 | 0
Taunton 132 kV | Periton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.9 | 3.7 | 3.6 | 3.4 | 3.1 | 2.8 | 5.6 | 5.3 | 4.3 | 3.5 | 2.8 | 1.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Periton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.9 | 3.5 | 3.2 | 2.7 | 2.1 | 1.5 | 4.1 | 3.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Periton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.9 | 3.6 | 3.4 | 3.2 | 2.9 | 2.5 | 5.2 | 4.4 | 3.1 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Periton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.9 | 3.6 | 3.3 | 3 | 2.5 | 2 | 4.6 | 3.9 | 2.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Priorswood | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.8 | 3.7 | 3.5 | 3.3 | 1.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Priorswood | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.6 | 3.2 | 2.7 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Priorswood | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.7 | 3.4 | 3.1 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Priorswood | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.7 | 3.4 | 2.9 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Staplegrove | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.7 | 7.5 | 7.3 | 7.2 | 6.8 | 6.2 | 5.2 | 3.7 | 2.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Staplegrove | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.7 | 7.2 | 6.9 | 6.2 | 5.3 | 3.8 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Staplegrove | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.7 | 7.3 | 7.1 | 6.6 | 5.6 | 4.8 | 3.5 | 2.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Staplegrove | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.7 | 7.3 | 7.1 | 6.6 | 5.4 | 4.3 | 2.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Taunton Local | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.1 | 4.9 | 4.6 | 4.3 | 4 | 3.6 | 3.4 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Taunton Local | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.1 | 4.5 | 3.8 | 2.9 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Taunton Local | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.1 | 4.6 | 4.1 | 3.4 | 2.6 | 1.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Taunton Local | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.1 | 4.5 | 4 | 3.4 | 2.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Taunton Main Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 89.6 | 86.6 | 85 | 83.6 | 81.8 | 79.2 | 72 | 66.2 | 59.8 | 53.6 | 47.9 | 42.2 | 36.2 | 30.4 | 25 | 19.9 | 14 | 0 | 0
Taunton 132 kV | Taunton Main Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 89.6 | 85.2 | 82.3 | 78.7 | 73.9 | 67.3 | 57.5 | 48.2 | 37.7 | 27 | 18.1 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Taunton Main Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 89.6 | 85.7 | 83.4 | 80.7 | 76.7 | 72.5 | 63.9 | 56.8 | 48.1 | 40 | 31.7 | 21.6 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Taunton Main Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 89.6 | 85.5 | 83.3 | 80.6 | 75.8 | 70.6 | 61.2 | 54.1 | 45.5 | 36.5 | 27.8 | 18.5 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Trull | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.5 | 5.8 | 4.8 | 4 | 3.2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Trull | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.5 | 5.4 | 3.9 | 2.6 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Trull | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.5 | 5.5 | 4.1 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Trull | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.5 | 5.4 | 4.2 | 3.1 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wellington Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.5 | 2.5 | 2.5 | 2.5 | 2.4 | 2.4 | 2.3 | 2.3 | 2 | 1.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wellington Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.5 | 2.4 | 2.4 | 2.3 | 2.2 | 2.1 | 2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wellington Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.5 | 2.4 | 2.4 | 2.4 | 2.4 | 2.3 | 2.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wellington Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.5 | 2.4 | 2.4 | 2.4 | 2.3 | 2.2 | 2.1 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wellington Town | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.9 | 6.7 | 6.6 | 6.3 | 6 | 5.5 | 4.6 | 3.9 | 2.9 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wellington Town | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.9 | 6.5 | 6.2 | 5.6 | 4.7 | 3.7 | 2.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wellington Town | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.9 | 6.6 | 6.4 | 5.9 | 5.3 | 4.7 | 3.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wellington Town | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.9 | 6.6 | 6.3 | 5.9 | 5.1 | 4.2 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wiveliscombe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7 | 6.9 | 6.8 | 6.8 | 6.5 | 6.4 | 6.1 | 5.8 | 5.4 | 5.2 | 4.9 | 4.5 | 4.1 | 3.6 | 3.2 | 2.7 | 2.2 | 0 | 0
Taunton 132 kV | Wiveliscombe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7 | 6.8 | 6.7 | 6.4 | 6 | 5.6 | 5.2 | 4.6 | 3.8 | 3.1 | 2.4 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wiveliscombe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7 | 6.9 | 6.8 | 6.7 | 6.4 | 6.2 | 5.8 | 5.4 | 4.7 | 4.1 | 3.4 | 2.6 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wiveliscombe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7 | 6.8 | 6.8 | 6.6 | 6.2 | 5.9 | 5.5 | 5 | 4.3 | 3.6 | 2.8 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0

## Generation Headroom
Associated GSP | Substation | Supply Level | Voltage Level (kV) | Scenario | Units | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050
Abham 132 kV | Ashburton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Ashburton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Ashburton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Ashburton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Barton. | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.4 | 10.2 | 10.1 | 10 | 9.9 | 9.7 | 9.4 | 9.3 | 9.2 | 9.2 | 7.1 | 7.1 | 7 | 7 | 7 | 6.9 | 6.8 | 6.3 | 5.5
Abham 132 kV | Barton. | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.4 | 10 | 9.7 | 9.5 | 9.3 | 9.2 | 7.1 | 6.9 | 6.7 | 6.4 | 6 | 5.6 | 5.2 | 4.8 | 4.4 | 3.9 | 3.5 | 1.2 | 0
Abham 132 kV | Barton. | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.4 | 9.8 | 9.5 | 9.3 | 7 | 6.8 | 6.5 | 6 | 5.5 | 4.9 | 4.3 | 3.9 | 3.5 | 3 | 2.7 | 2.3 | 1.9 | 0 | 0
Abham 132 kV | Barton. | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.4 | 10.2 | 10 | 9.8 | 9.7 | 9.5 | 9.2 | 9.1 | 7.1 | 7 | 6.8 | 6.6 | 6.5 | 6.3 | 6.1 | 6 | 5.7 | 4.3 | 2.9
Abham 132 kV | Blackawton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.8 | 2.8 | 2.7 | 2.6 | 2.5 | 2.4 | 4 | 3.8 | 3.5 | 3.3 | 3 | 2.7 | 2.6 | 2.5 | 2.4 | 2.3 | 2.1 | 1.3 | 0
Abham 132 kV | Blackawton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.8 | 2.7 | 2.6 | 2.3 | 1.9 | 1.6 | 3 | 2.6 | 2.2 | 1.7 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Blackawton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.8 | 2.7 | 2.5 | 2.1 | 1.7 | 1.3 | 2.6 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Blackawton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.8 | 2.8 | 2.7 | 2.6 | 2.4 | 2.3 | 3.8 | 3.5 | 3.2 | 2.8 | 2.4 | 2 | 1.8 | 1.5 | 1.3 | 1 | 0 | 0 | 0
Abham 132 kV | Bovey Tracey | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.6 | 1.6 | 1.4 | 1.2 | 0.9 | 2.5 | 6.4 | 5.6 | 4.7 | 5.3 | 4.2 | 6.6 | 5.8 | 5.4 | 5 | 4.7 | 4.4 | 1.8 | 0
Abham 132 kV | Bovey Tracey | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.6 | 1.5 | 1.2 | 0 | 0 | 0 | 2.4 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Bovey Tracey | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.6 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Bovey Tracey | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.6 | 1.5 | 1.4 | 1.1 | 0 | 0.8 | 5.3 | 4.3 | 3.3 | 3 | 1.2 | 3.1 | 2.2 | 1.5 | 0.7 | 0 | 0 | 0 | 0
Abham 132 kV | Bradley Lane | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.9 | 2.7 | 2.5 | 2.2 | 2 | 1.7 | 10.1 | 9.8 | 9.4 | 9 | 8.6 | 8.4 | 6.9 | 6.5 | 6.2 | 6 | 5.8 | 4.7 | 3.4
Abham 132 kV | Bradley Lane | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.9 | 2.4 | 2 | 1.4 | 0.8 | 0 | 8.2 | 7.5 | 7 | 4 | 2.9 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Bradley Lane | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.9 | 2.2 | 1.7 | 0.9 | 0 | 0 | 7.1 | 6.1 | 5.1 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Bradley Lane | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.9 | 2.6 | 2.3 | 2 | 1.6 | 1.1 | 9.3 | 8.7 | 8.2 | 6.3 | 4.3 | 3.6 | 3 | 2.6 | 2.1 | 1.8 | 0 | 0 | 0
Abham 132 kV | Buckfastleigh | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Buckfastleigh | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Buckfastleigh | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Buckfastleigh | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Chudleigh Knighton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.6 | 1.6 | 1.4 | 1.2 | 0.9 | 2.5 | 6.4 | 5.6 | 4.7 | 5.3 | 4.2 | 6.6 | 5.8 | 5.4 | 5 | 4.7 | 4.3 | 1.7 | 0
Abham 132 kV | Chudleigh Knighton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.6 | 1.5 | 1.2 | 0 | 0 | 0 | 2.4 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Chudleigh Knighton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.6 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Chudleigh Knighton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.6 | 1.5 | 1.4 | 1.1 | 0 | 0.8 | 5.3 | 4.3 | 3.3 | 3 | 1.2 | 3.1 | 2.2 | 1.5 | 0.7 | 0 | 0 | 0 | 0
Abham 132 kV | Churston | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.1 | 9.7 | 9.6 | 9.6 | 9.5 | 9.4 | 9.8 | 9.8 | 6.3 | 6.2 | 6.2 | 6.2 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 5.9 | 5.6
Abham 132 kV | Churston | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.1 | 9.6 | 9.5 | 9.4 | 9.3 | 6.7 | 6.2 | 6 | 5.8 | 5.6 | 5.3 | 5.2 | 5 | 4.8 | 4.6 | 4.4 | 4.2 | 3.1 | 2.1
Abham 132 kV | Churston | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.1 | 9.5 | 9.4 | 9.3 | 6.7 | 6.6 | 6 | 5.7 | 5.3 | 4.9 | 4.6 | 4.4 | 4.2 | 4 | 3.8 | 3.6 | 3.4 | 2.2 | 1.1
Abham 132 kV | Churston | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.1 | 9.7 | 9.6 | 9.5 | 9.4 | 9.3 | 6.3 | 6.2 | 6.1 | 5.9 | 5.7 | 5.6 | 5.6 | 5.5 | 5.4 | 5.3 | 5.2 | 4.6 | 3.9
Abham 132 kV | Colley End | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.1 | 18 | 17.8 | 17.6 | 17.4 | 17.2 | 17.1 | 16.9 | 16.7 | 16.5 | 16.3 | 16.2 | 16 | 15.9 | 15.8 | 15.7 | 15.6 | 14.1 | 13.6
Abham 132 kV | Colley End | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.1 | 17.7 | 17.2 | 16.9 | 16.4 | 16.1 | 15.8 | 15.5 | 15.5 | 14.1 | 13.9 | 13.5 | 13.1 | 12.6 | 12.2 | 11.8 | 11.4 | 9.5 | 7.6
Abham 132 kV | Colley End | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.1 | 17.5 | 16.8 | 16.3 | 15.8 | 15.4 | 14.2 | 13.7 | 13.2 | 12.7 | 12.1 | 11.6 | 11.2 | 10.8 | 10.4 | 10 | 9.6 | 7.2 | 4.9
Abham 132 kV | Colley End | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.1 | 17.9 | 17.6 | 17.4 | 17 | 16.8 | 16.5 | 16.2 | 16 | 15.8 | 15.5 | 15.5 | 14.2 | 14.1 | 14 | 13.9 | 13.6 | 12.3 | 11
Abham 132 kV | Dartmouth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.9 | 7.8 | 7.6 | 7.4 | 7.2 | 6.9 | 7.7 | 7.3 | 6.9 | 6.4 | 5.9 | 5.6 | 5.3 | 5.2 | 5 | 4.8 | 4.6 | 3.4 | 1.9
Abham 132 kV | Dartmouth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.9 | 7.6 | 7.2 | 6.6 | 5.9 | 5.3 | 5.6 | 4.8 | 4.1 | 3.3 | 2.5 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Dartmouth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.9 | 7.5 | 6.9 | 6.2 | 5.4 | 4.6 | 4.7 | 3.7 | 2.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Dartmouth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.9 | 7.7 | 7.4 | 7.1 | 6.8 | 6.3 | 6.9 | 6.3 | 5.8 | 5.1 | 4.4 | 4 | 3.5 | 3.2 | 2.8 | 2.4 | 1.5 | 0 | 0
Abham 132 kV | Dawlish | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.4 | 3.1 | 2.7 | 2.1 | 1.4 | 2.4 | 12.8 | 12 | 11.2 | 10.3 | 9.3 | 8.7 | 7.8 | 7.4 | 7.1 | 6.8 | 6.4 | 3.6 | 0.6
Abham 132 kV | Dawlish | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.4 | 2.7 | 1.9 | 0 | 0 | 0 | 8.5 | 7.1 | 5.9 | 4 | 2.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Dawlish | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.4 | 2.5 | 1.4 | 0 | 0 | 0 | 6.4 | 4.3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Dawlish | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.4 | 3 | 2.4 | 1.5 | 0 | 0.8 | 11.3 | 10.3 | 9.4 | 7.8 | 5.8 | 4.7 | 4 | 3.4 | 2.7 | 1.9 | 0 | 0 | 0
Abham 132 kV | Higher Woodway | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 4.8 | 4.1 | 3.2 | 2.2 | 2.9 | 8.3 | 7.7 | 7.6 | 7.6 | 7.5 | 7.4 | 7.3 | 7.3 | 7.1 | 6.8 | 6.4 | 3.6 | 0.6
Abham 132 kV | Higher Woodway | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 4 | 2.6 | 0 | 0 | 0 | 7.2 | 7 | 5.9 | 4 | 2.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Higher Woodway | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 3.5 | 1.7 | 0 | 0 | 0 | 6.4 | 4.3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Higher Woodway | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 4.5 | 3.6 | 2.3 | 0.7 | 0.8 | 7.6 | 7.5 | 7.4 | 7.3 | 5.8 | 4.7 | 4 | 3.4 | 2.7 | 1.9 | 0 | 0 | 0
Abham 132 kV | Hollicombe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.6 | 9.6 | 9.5 | 9.4 | 9.3 | 9.2 | 9.1 | 9 | 8.9 | 8.8 | 8.7 | 8.6 | 8.6 | 8.5 | 8.5 | 8.5 | 8.4 | 7.4 | 7.3
Abham 132 kV | Hollicombe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.6 | 9.4 | 9.2 | 9 | 8.8 | 8.6 | 8.4 | 7.5 | 7.5 | 7.4 | 7.3 | 7.2 | 7.1 | 7 | 6.8 | 6.6 | 6.4 | 5.5 | 4.6
Abham 132 kV | Hollicombe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.6 | 9.3 | 9 | 8.7 | 8.5 | 7.4 | 7.4 | 7.2 | 7.1 | 6.9 | 6.7 | 6.5 | 6.3 | 6.1 | 6 | 5.8 | 5.6 | 4.4 | 3.3
Abham 132 kV | Hollicombe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.6 | 9.5 | 9.4 | 9.2 | 9.1 | 8.9 | 8.7 | 8.6 | 8.5 | 8.4 | 8.4 | 7.5 | 7.5 | 7.4 | 7.4 | 7.4 | 7.3 | 6.8 | 6.2
Abham 132 kV | Ivybridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.1 | 4.9 | 4.7 | 4.3 | 3.9 | 3.4 | 6.5 | 5.9 | 5.1 | 4.4 | 3.4 | 2.9 | 2.4 | 2.2 | 1.9 | 1.7 | 1.5 | 0 | 0
Abham 132 kV | Ivybridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.1 | 4.6 | 4.1 | 2.9 | 1.7 | 0.5 | 2.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Ivybridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.1 | 4.4 | 3.8 | 2.3 | 0.9 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Ivybridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.1 | 4.8 | 4.5 | 3.9 | 3.3 | 2.6 | 5.5 | 4.5 | 3.4 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Kingsbridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Kingsbridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Kingsbridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Kingsbridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Langage | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 1.7 | 1.6 | 1.4 | 1.2 | 1.1 | 1 | 1 | 0.9 | 0.9 | 0.9 | 0.7 | 0
Abham 132 kV | Langage | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Langage | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Langage | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 1 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Lawes Bridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.1 | 14.9 | 14.8 | 10.6 | 10.5 | 10.3 | 10.1 | 9.8 | 9.4 | 8.9 | 8.2 | 7.8 | 7.6 | 7.4 | 7.3 | 7.2 | 7 | 6.3 | 5.4
Abham 132 kV | Lawes Bridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.1 | 10.7 | 10.6 | 10.2 | 9.5 | 8.4 | 6.9 | 5.3 | 4.1 | 3.4 | 2.7 | 2.2 | 1.7 | 1.1 | 0.6 | 0 | 0 | 0 | 0
Abham 132 kV | Lawes Bridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.1 | 10.7 | 10.4 | 9.8 | 8.8 | 7.5 | 6 | 4.5 | 3 | 1.9 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Lawes Bridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.1 | 10.7 | 10.7 | 10.5 | 10 | 9.1 | 7.9 | 6.5 | 5.1 | 4.4 | 3.8 | 3.4 | 3 | 2.7 | 2.5 | 2.2 | 1.9 | 0 | 0
Abham 132 kV | Laywell Brixham | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.3 | 13.1 | 12.7 | 12.3 | 12 | 11.6 | 13.8 | 13.6 | 13.5 | 13.4 | 13.3 | 13.2 | 13.2 | 13.2 | 13.1 | 13.1 | 12.1 | 11.4 | 9.2
Abham 132 kV | Laywell Brixham | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.3 | 12.6 | 11.8 | 11 | 10 | 9 | 12.1 | 12 | 11.9 | 11.1 | 10 | 9 | 7.9 | 6.8 | 5.8 | 4.7 | 3.1 | 0 | 0
Abham 132 kV | Laywell Brixham | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.3 | 12.4 | 11.3 | 10.1 | 8.9 | 7.6 | 11.7 | 11.1 | 9.5 | 8.1 | 6.7 | 4.6 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Laywell Brixham | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.3 | 12.9 | 12.4 | 11.9 | 11.3 | 10.6 | 13.4 | 13.2 | 13.1 | 12.1 | 12 | 12 | 11.6 | 11.1 | 10.7 | 10.1 | 9.1 | 4.2 | 0.9
Abham 132 kV | Linketty Lane | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.2 | 4.1 | 3.9 | 3.8 | 3.6 | 3.5 | 3 | 2.8 | 2.6 | 2.4 | 2.1 | 2 | 1.9 | 1.8 | 1.7 | 1.6 | 1.6 | 0.9 | 0
Abham 132 kV | Linketty Lane | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.2 | 3.9 | 3.5 | 3.1 | 2.8 | 2.4 | 1.8 | 1.5 | 1.2 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Linketty Lane | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.2 | 3.7 | 3.3 | 2.7 | 2.3 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Linketty Lane | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.2 | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 2.7 | 2.5 | 2.2 | 2 | 1.7 | 1.5 | 1.4 | 1.2 | 1.1 | 0.9 | 0.7 | 0 | 0
Abham 132 kV | Marldon | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.9 | 3.7 | 3.4 | 3 | 2.6 | 4.2 | 4.1 | 4 | 3.9 | 3.8 | 3.7 | 3.6 | 3.6 | 3.5 | 3.5 | 3.5 | 3 | 0.6
Abham 132 kV | Marldon | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.7 | 3.3 | 2.2 | 1.1 | 0 | 3.8 | 3.6 | 3.5 | 3.3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Marldon | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.6 | 3.1 | 1.7 | 0 | 0 | 3.6 | 3.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Marldon | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.8 | 3.6 | 3.2 | 2.7 | 1.9 | 4.1 | 4 | 3.9 | 3.7 | 3.5 | 3.4 | 3.1 | 2.5 | 1.8 | 1.2 | 0 | 0 | 0
Abham 132 kV | Modbury | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.1 | 4.9 | 4.7 | 4.3 | 3.9 | 3.4 | 5.3 | 4.9 | 4.4 | 4 | 3.5 | 2.9 | 2.5 | 2.2 | 1.9 | 1.7 | 1.5 | 0 | 0
Abham 132 kV | Modbury | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.1 | 4.6 | 4.1 | 2.9 | 1.7 | 0.5 | 2.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Modbury | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.1 | 4.4 | 3.8 | 2.3 | 0.9 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Modbury | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.1 | 4.8 | 4.5 | 3.9 | 3.3 | 2.6 | 4.6 | 4.1 | 3.4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Newton Abbot Bsp (Forde Road) | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 26.7 | 25.8 | 24.7 | 23.2 | 21.6 | 21.6 | 46.1 | 43.8 | 41.4 | 40.5 | 37.8 | 39.4 | 35.5 | 34.4 | 38.2 | 37.4 | 36.8 | 26.3 | 17.3
Abham 132 kV | Newton Abbot Bsp (Forde Road) | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 26.7 | 24.5 | 22.1 | 17.6 | 12.7 | 9.7 | 36 | 32.3 | 29.5 | 23.7 | 18.5 | 16.8 | 10 | 5.1 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Newton Abbot Bsp (Forde Road) | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 26.7 | 23.7 | 20.6 | 14.9 | 8.8 | 4.1 | 28.8 | 22.7 | 15.3 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Newton Abbot Bsp (Forde Road) | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 26.7 | 25.4 | 23.8 | 21.8 | 19.1 | 17.9 | 42.6 | 40 | 37.6 | 33.8 | 28 | 30 | 25.1 | 24.2 | 15 | 12.6 | 7 | 0 | 0
Abham 132 kV | Newton Abbot Main | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.5 | 16.4 | 16.3 | 16.1 | 15.9 | 15.8 | 24.4 | 24 | 23.5 | 22.8 | 21.9 | 21.3 | 20.8 | 20.6 | 20.3 | 20.1 | 19.8 | 17.7 | 15.3
Abham 132 kV | Newton Abbot Main | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.5 | 16.2 | 16 | 12.7 | 10.6 | 9.8 | 21.5 | 20 | 18.8 | 17.5 | 16.4 | 15.1 | 13.9 | 12.7 | 11.6 | 10.4 | 9.1 | 3.7 | 0
Abham 132 kV | Newton Abbot Main | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.5 | 16.1 | 15.8 | 10.8 | 10 | 8.7 | 19.8 | 17.8 | 15.5 | 13.6 | 11.6 | 10.5 | 9.5 | 8.6 | 8 | 7.2 | 6.4 | 1.8 | 0
Abham 132 kV | Newton Abbot Main | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.5 | 16.4 | 16.2 | 16 | 15.8 | 10.7 | 23.5 | 22.5 | 21.5 | 20.3 | 19.1 | 18.2 | 17.5 | 17 | 16.4 | 15.9 | 15.2 | 11.1 | 6.7
Abham 132 kV | Newton Ferrers | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5 | 4.8 | 4.6 | 4.2 | 3.8 | 3.4 | 5.3 | 5.3 | 5 | 4.2 | 3.3 | 2.8 | 2.4 | 2.1 | 1.9 | 1.6 | 1.4 | 0 | 0
Abham 132 kV | Newton Ferrers | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5 | 4.6 | 4.1 | 2.9 | 1.7 | 0.5 | 2.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Newton Ferrers | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5 | 4.4 | 3.8 | 2.3 | 0.9 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Newton Ferrers | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5 | 4.8 | 4.4 | 3.9 | 3.2 | 2.5 | 5.3 | 4.3 | 3.3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Paignton 33/11kv S/S | Primary Substation | 11 | Counterfactual | Headroom (MW) | 22.8 | 22.7 | 22.6 | 22.5 | 22.4 | 22.3 | 22.1 | 21.9 | 21.8 | 19.5 | 19.2 | 19 | 18.9 | 18.8 | 18.7 | 18.6 | 18.6 | 18.1 | 17.4
Abham 132 kV | Paignton 33/11kv S/S | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 22.8 | 22.5 | 22.4 | 22.1 | 21.8 | 19.3 | 18.5 | 17.4 | 16.9 | 16.5 | 16 | 15.5 | 15.1 | 14.7 | 14.3 | 14 | 13.6 | 11.9 | 10.5
Abham 132 kV | Paignton 33/11kv S/S | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 22.8 | 22.5 | 22.2 | 21.9 | 19.4 | 18.9 | 18.1 | 17 | 16 | 15.2 | 14.7 | 14.2 | 13.8 | 13.4 | 13.1 | 12.8 | 12.5 | 11 | 9.9
Abham 132 kV | Paignton 33/11kv S/S | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 22.8 | 22.6 | 22.5 | 22.3 | 22 | 21.7 | 19.2 | 18.3 | 17.5 | 17.2 | 16.7 | 16.4 | 16.1 | 15.9 | 15.7 | 15.5 | 15.3 | 14.1 | 13.1
Abham 132 kV | Paignton Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 9.8 | 8.6 | 7.6 | 6.7 | 5.6 | 4.6 | 58.2 | 56.9 | 55.7 | 54.2 | 52.6 | 51.6 | 51 | 50.4 | 49.8 | 49.3 | 48.8 | 44.8 | 33.6
Abham 132 kV | Paignton Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 9.8 | 7.3 | 5.2 | 2.9 | 0 | 0 | 50 | 47 | 44.7 | 42 | 38 | 34.1 | 19.4 | 9.9 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Paignton Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 9.8 | 6.5 | 3.7 | 0.6 | 0 | 0 | 46.1 | 41.8 | 29.7 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Paignton Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 9.8 | 8.2 | 6.8 | 5.4 | 3.5 | 1.3 | 53.8 | 51.4 | 49.2 | 47.5 | 45.5 | 44.1 | 42.7 | 41.5 | 29.1 | 24.5 | 13.6 | 0 | 0
Abham 132 kV | Plympton Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 5.6 | 5.2 | 4.7 | 0.9 | 0 | 0 | 31.6 | 30.4 | 29.1 | 27.8 | 26.2 | 25.3 | 24.6 | 24.1 | 23.7 | 23.3 | 22.9 | 19.8 | 15.9
Abham 132 kV | Plympton Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 5.6 | 4.6 | 0 | 0 | 0 | 0 | 24.8 | 22.5 | 20.4 | 17.9 | 15.7 | 13.6 | 11.6 | 8.7 | 6.6 | 4.5 | 1 | 0 | 0
Abham 132 kV | Plympton Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 5.6 | 1.1 | 0 | 0 | 0 | 0 | 21.6 | 18.3 | 12.7 | 8.6 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Plympton Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 5.6 | 5 | 1.2 | 0 | 0 | 0 | 29.2 | 27.6 | 25.9 | 23.9 | 21.7 | 20.4 | 19.4 | 17.6 | 16.6 | 15.8 | 13.3 | 5.2 | 0
Abham 132 kV | Salcombe 340038 | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2 | 1.9 | 1.8 | 1.7 | 1.6 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Salcombe 340038 | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2 | 1.8 | 1.6 | 1.3 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Salcombe 340038 | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2 | 1.8 | 1.4 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Salcombe 340038 | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2 | 1.9 | 1.8 | 1.6 | 1.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | South Brent | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 7.9 | 7.1 | 6.3 | 5.4 | 4.3 | 3.5 | 3.1 | 2.8 | 2.5 | 2.2 | 1.9 | 0 | 0
Abham 132 kV | South Brent | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 2.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | South Brent | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | South Brent | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 6 | 5 | 3.7 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Stokenham | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.4 | 2.4 | 2.4 | 2.3 | 2.3 | 2.2 | 2.5 | 2.5 | 2.4 | 2.3 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 2 | 2 | 1.3 | 0
Abham 132 kV | Stokenham | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.4 | 2.4 | 2.2 | 2.1 | 1.9 | 1.6 | 2.2 | 2 | 1.9 | 1.7 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Stokenham | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.4 | 2.3 | 2.2 | 2 | 1.7 | 1.3 | 2 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Stokenham | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.4 | 2.4 | 2.3 | 2.2 | 2.2 | 2.1 | 2.4 | 2.3 | 2.3 | 2.1 | 2 | 1.9 | 1.8 | 1.5 | 1.3 | 1 | 0 | 0 | 0
Abham 132 kV | Teignmouth Gasworks | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 4.8 | 4.1 | 3.2 | 2.2 | 2.9 | 12 | 12 | 11.9 | 11.8 | 11.7 | 11.6 | 11.6 | 11.5 | 11.5 | 11.4 | 11.3 | 10.7 | 9.5
Abham 132 kV | Teignmouth Gasworks | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 4 | 2.6 | 0 | 0 | 0 | 11.5 | 11.3 | 11.1 | 10.8 | 10.6 | 10.1 | 8.8 | 7.6 | 6.3 | 4.9 | 0 | 0 | 0
Abham 132 kV | Teignmouth Gasworks | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 3.5 | 1.7 | 0 | 0 | 0 | 11 | 10.6 | 10.1 | 8.4 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Teignmouth Gasworks | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 4.5 | 3.6 | 2.3 | 0.7 | 0.8 | 12 | 11.9 | 11.7 | 11.6 | 11.4 | 11.2 | 11.1 | 11 | 10.9 | 10.8 | 10 | 4.8 | 0
Abham 132 kV | Torquay Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 32 | 31.7 | 31.2 | 28.4 | 27.7 | 27 | 24.7 | 23.9 | 23.1 | 22.1 | 20.9 | 20.1 | 19.7 | 19.4 | 19.1 | 18.7 | 18.4 | 15.9 | 12.6
Abham 132 kV | Torquay Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 32 | 28.8 | 27.4 | 25.7 | 23.8 | 21.5 | 18.6 | 16.3 | 14.3 | 12.5 | 10.8 | 9.4 | 7.7 | 6.1 | 4.4 | 2.9 | 0 | 0 | 0
Abham 132 kV | Torquay Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 32 | 28.3 | 26.2 | 23.9 | 21.5 | 18.6 | 15.7 | 12.6 | 9.6 | 7 | 4.6 | 2.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Torquay Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 32 | 29.2 | 28.5 | 27.5 | 26.1 | 24.2 | 21.1 | 19.1 | 17.2 | 15.9 | 14.7 | 13.7 | 12.9 | 12.1 | 11.3 | 10.7 | 9.6 | 4.1 | 0
Abham 132 kV | Torwood | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.6 | 10.1 | 10 | 9.9 | 9.9 | 9.8 | 9.7 | 9.6 | 9.6 | 9.5 | 9.5 | 9.5 | 9.2 | 8.8
Abham 132 kV | Torwood | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.7 | 10.7 | 10.6 | 10.5 | 10.3 | 10.1 | 9.5 | 9.4 | 9.3 | 9.2 | 9 | 8.9 | 8.8 | 8.7 | 8.6 | 7.2 | 7.2 | 6.6 | 5.9
Abham 132 kV | Torwood | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.7 | 10.7 | 10.5 | 10.2 | 10 | 9.7 | 9.1 | 8.9 | 8.8 | 8.7 | 7.2 | 7.2 | 7.2 | 7.1 | 7 | 6.8 | 6.7 | 5.7 | 4.7
Abham 132 kV | Torwood | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.7 | 10.7 | 10.7 | 10.7 | 10.5 | 10.4 | 9.9 | 9.7 | 9.6 | 9.5 | 9.4 | 9.3 | 9.2 | 9.2 | 9.1 | 9 | 8.9 | 7.2 | 7.1
Abham 132 kV | Torycombe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 4.5 | 4.2 | 3.9 | 3.6 | 3.3 | 3.2 | 3.1 | 3.1 | 3 | 2.9 | 2.3 | 1.6
Abham 132 kV | Torycombe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 3.3 | 2.9 | 2.6 | 2.3 | 1.9 | 1.6 | 1.4 | 1.1 | 0.8 | 0.5 | 0 | 1.2
Abham 132 kV | Torycombe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 2.7 | 2 | 1.5 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0.5
Abham 132 kV | Torycombe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 4.2 | 3.9 | 3.6 | 3.1 | 2.9 | 2.7 | 2.6 | 2.5 | 2.3 | 2.2 | 1.1 | 2.7
Abham 132 kV | Totnes | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.9 | 3.7 | 3.4 | 3 | 2.6 | 10.9 | 10.2 | 9.3 | 8.5 | 7.4 | 6.7 | 6.3 | 6 | 5.7 | 5.4 | 5.2 | 3 | 0.6
Abham 132 kV | Totnes | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.7 | 3.3 | 2.2 | 1.1 | 0 | 7.3 | 5.9 | 4.6 | 3.3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Totnes | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.5 | 3.1 | 1.7 | 0 | 0 | 5.7 | 3.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Totnes | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.8 | 3.6 | 3.2 | 2.6 | 1.9 | 9.8 | 8.8 | 7.7 | 6.4 | 4.9 | 3.9 | 3.1 | 2.5 | 1.8 | 1.2 | 0 | 0 | 0
Abham 132 kV | Totnes Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 16.1 | 15.7 | 15 | 13.9 | 12.7 | 11.3 | 43.1 | 40.9 | 38.6 | 36.1 | 33.1 | 30.8 | 28.8 | 27.6 | 26.5 | 25.5 | 24.5 | 17.2 | 8.8
Abham 132 kV | Totnes Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 16.1 | 15 | 13.6 | 9.9 | 5.7 | 0 | 33.1 | 29.1 | 24.8 | 18.7 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Totnes Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 16.1 | 14.5 | 12.7 | 8.2 | 3.2 | 0 | 28.2 | 21 | 12.6 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Abham 132 kV | Totnes Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 16.1 | 15.5 | 14.6 | 13.1 | 11.3 | 9.1 | 40.2 | 37.3 | 34.4 | 29.9 | 23.9 | 20.2 | 17.2 | 14.8 | 10.5 | 7 | 1.3 | 0 | 0
Abham 132 kV | Upton Valley | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18 | 18 | 17.9 | 17.9 | 17.7 | 17.5 | 17.1 | 16.9 | 16.8 | 16.6 | 16.4 | 16.3 | 16.2 | 16.2 | 16.1 | 16 | 15.9 | 15.4 | 14.5
Abham 132 kV | Upton Valley | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18 | 18 | 17.5 | 17.2 | 16.9 | 16.5 | 15.9 | 15.6 | 15.4 | 15.2 | 14.6 | 14.5 | 14.2 | 13.9 | 13.5 | 13.2 | 12.9 | 11.2 | 9.6
Abham 132 kV | Upton Valley | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18 | 17.8 | 17.2 | 16.7 | 16.3 | 15.8 | 15.2 | 14.5 | 14.1 | 13.7 | 13.3 | 13 | 12.7 | 12.3 | 12 | 11.7 | 11.3 | 9.2 | 7.1
Abham 132 kV | Upton Valley | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18 | 18 | 17.9 | 17.6 | 17.4 | 17.1 | 16.5 | 16.3 | 16.1 | 15.9 | 15.7 | 15.6 | 15.4 | 15.3 | 15.2 | 15.2 | 14.7 | 13.7 | 12.6
Alverdiscott 132 kV | Ashwater | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.9 | 3.9 | 3.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Ashwater | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.9 | 3.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Ashwater | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.9 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Ashwater | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.9 | 3.9 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Barnstaple Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Barnstaple Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Barnstaple Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Barnstaple Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Barnstaple Quay | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 2.8 | 2.5 | 2.1 | 1.7 | 1.3 | 9.2 | 8.9 | 8.5 | 8.2 | 7.8 | 7.5 | 7.4 | 6.1 | 2.1 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Barnstaple Quay | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 2.5 | 1.8 | 0.7 | 0 | 0 | 7.3 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Barnstaple Quay | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 2.3 | 1.4 | 0 | 0 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Barnstaple Quay | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 2.7 | 2.2 | 1.7 | 1.1 | 0 | 8.5 | 8.1 | 7.7 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Bideford Main | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Bideford Main | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Bideford Main | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Bideford Main | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Bratton Fleming | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.8 | 3.7 | 3.6 | 3.5 | 3.4 | 3.3 | 3.2 | 3 | 2.8 | 2.7 | 2.6 | 2.5 | 2.4 | 2.3 | 2.3 | 2.2 | 1.6 | 0
Alverdiscott 132 kV | Bratton Fleming | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3.7 | 3.5 | 3.3 | 3.1 | 2.9 | 2.6 | 2.4 | 2.1 | 1.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Bratton Fleming | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.7 | 3.4 | 3.1 | 2.9 | 2.2 | 2.2 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Bratton Fleming | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.8 | 3.6 | 3.5 | 3.4 | 3.3 | 3.1 | 3 | 2.8 | 2.5 | 2.3 | 2.1 | 2 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Braunton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 7.2 | 7.1 | 7 | 6.9 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Braunton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 7.1 | 6.9 | 6.6 | 6.1 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Braunton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 7 | 6.7 | 6.2 | 4.4 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Braunton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 7.2 | 7 | 6.9 | 6.7 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Clovelly | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.1 | 2 | 2 | 1.9 | 1.8 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Clovelly | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.1 | 2 | 1.8 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Clovelly | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.1 | 1.9 | 1.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Clovelly | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.1 | 2 | 1.9 | 1.8 | 1.8 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | East Curry | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.9 | 3.6 | 3.1 | 2.6 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | East Curry | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.6 | 3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | East Curry | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.4 | 2.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | East Curry | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.8 | 3.4 | 2.8 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | East Yelland Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 8.5 | 7.7 | 6.3 | 4.4 | 2.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | East Yelland Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 8.5 | 6.1 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | East Yelland Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 8.5 | 5.2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | East Yelland Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 8.5 | 7.1 | 5.1 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Fremington | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Fremington | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Fremington | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Fremington | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Georgeham | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.5 | 4.5 | 4.4 | 4.3 | 4.2 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Georgeham | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.5 | 4.4 | 4.1 | 4 | 3.9 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Georgeham | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.5 | 4.3 | 4 | 3.8 | 3.7 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Georgeham | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.5 | 4.4 | 4.3 | 4.2 | 4.1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Great Torrington | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Great Torrington | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Great Torrington | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Great Torrington | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Hatherleigh | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Hatherleigh | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Hatherleigh | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Hatherleigh | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Heddon Cross | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Heddon Cross | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Heddon Cross | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Heddon Cross | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Holsworthy | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Holsworthy | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Holsworthy | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Holsworthy | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Ilfracombe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.1 | 6.9 | 6.6 | 6.4 | 6.2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Ilfracombe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.1 | 6.6 | 5.9 | 5.4 | 5 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Ilfracombe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.1 | 6.4 | 5.5 | 4.8 | 4.2 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Ilfracombe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.1 | 6.8 | 6.3 | 6 | 5.7 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Launceston | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.9 | 1.8 | 1.6 | 1.5 | 1.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Launceston | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.9 | 1.6 | 1.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Launceston | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.9 | 1.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Launceston | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.9 | 1.7 | 1.5 | 1.3 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Lynton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.8 | 3.7 | 3.6 | 3.6 | 3.5 | 3.4 | 3.2 | 3.1 | 2.9 | 2.7 | 2.6 | 2.5 | 2.4 | 2.4 | 2.3 | 2.2 | 1.7 | 0
Alverdiscott 132 kV | Lynton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3.7 | 3.5 | 3.3 | 3.1 | 2.9 | 2.7 | 2.4 | 2.1 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Lynton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.7 | 3.4 | 3.1 | 2.9 | 2.2 | 2.3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Lynton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.8 | 3.7 | 3.6 | 3.5 | 3.3 | 3.2 | 3 | 2.8 | 2.6 | 2.4 | 2.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Middle Barlington | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Middle Barlington | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Middle Barlington | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Middle Barlington | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Mortonhampstead | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Mortonhampstead | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Mortonhampstead | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Mortonhampstead | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Morwenstow | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.6 | 1.6 | 1.6 | 1.5 | 1.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Morwenstow | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.6 | 1.6 | 1.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Morwenstow | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.6 | 1.5 | 1.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Morwenstow | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.6 | 1.6 | 1.5 | 1.5 | 1.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | North Tawton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | North Tawton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | North Tawton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | North Tawton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | North Tawton Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | North Tawton Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | North Tawton Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | North Tawton Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Northam | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9 | 8.9 | 8.9 | 8.8 | 8.8 | 8.8 | 8.7 | 7.7 | 7.6 | 7.5 | 7.4 | 7.3 | 7.3 | 7.3 | 7.2 | 7.2 | 7.2 | 6.9 | 6.4
Alverdiscott 132 kV | Northam | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9 | 8.8 | 8.7 | 7.6 | 7.5 | 7.3 | 7 | 6.5 | 6 | 5.9 | 5.8 | 5.6 | 5.5 | 5.3 | 5.1 | 5 | 4.8 | 3.8 | 2.9
Alverdiscott 132 kV | Northam | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9 | 8.8 | 7.7 | 7.5 | 7.3 | 6.9 | 6.5 | 6 | 5.5 | 5.2 | 5 | 4.9 | 4.7 | 4.5 | 4.4 | 4.2 | 4 | 2.9 | 1.9
Alverdiscott 132 kV | Northam | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9 | 8.9 | 8.8 | 8.8 | 7.6 | 7.6 | 7.4 | 7 | 6.5 | 6.4 | 6.3 | 6.2 | 6.2 | 6.1 | 6.1 | 6 | 5.9 | 5.2 | 4.6
Alverdiscott 132 kV | Okehampton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Okehampton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Okehampton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Okehampton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Park Lane SWEB | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.1 | 7.1 | 7 | 6.7 | 6.4 | 6 | 4.8 | 4 | 3.2 | 2.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Park Lane SWEB | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.1 | 6.9 | 6.7 | 5.7 | 4.5 | 3.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Park Lane SWEB | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.1 | 6.9 | 6.5 | 5.4 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Park Lane SWEB | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.1 | 7 | 6.9 | 6.5 | 5.8 | 4.9 | 2.9 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Pyworthy Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 13.8 | 12.1 | 11 | 9.1 | 7 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Pyworthy Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 13.8 | 10.5 | 8.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Pyworthy Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 13.8 | 10.3 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Pyworthy Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 13.8 | 11.8 | 10.2 | 7.7 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Rock Park | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.9 | 9.8 | 9.7 | 9.5 | 9.4 | 9.4 | 7 | 6.8 | 6.6 | 6.2 | 5.7 | 5.4 | 5.2 | 4.8 | 2.1 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Rock Park | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.9 | 9.6 | 9.4 | 7.1 | 6.7 | 6 | 5.2 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Rock Park | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.9 | 9.5 | 9.3 | 6.9 | 6.3 | 5.3 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Rock Park | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.9 | 9.7 | 9.6 | 9.4 | 7 | 6.8 | 6.3 | 5.7 | 5.1 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Roundswell | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.9 | 12.8 | 12.7 | 12.5 | 12.3 | 12 | 11.6 | 11.2 | 10.8 | 10.3 | 9.7 | 9.3 | 9.1 | 6.2 | 2.1 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Roundswell | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.9 | 12.7 | 12.4 | 11.6 | 10.9 | 10.2 | 9.4 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Roundswell | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.9 | 12.6 | 12.2 | 11.3 | 10.4 | 9.4 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Roundswell | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.9 | 12.8 | 12.5 | 12.2 | 11.9 | 11.5 | 10.9 | 10.4 | 9.9 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Shebbear | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Shebbear | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Shebbear | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Shebbear | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | South Molton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | South Molton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | South Molton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | South Molton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Stratton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.5 | 7.3 | 6.9 | 6.5 | 6.1 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Stratton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.5 | 6.9 | 6.1 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Stratton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.5 | 6.7 | 5.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Stratton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.5 | 7.2 | 6.6 | 6.1 | 5.3 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Tinkers Cross | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Tinkers Cross | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Tinkers Cross | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Tinkers Cross | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Whiddon Down | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Whiddon Down | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Whiddon Down | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alverdiscott 132 kV | Whiddon Down | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Axminster | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.8 | 1.5 | 1.3 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Axminster | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.8 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Axminster | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Axminster | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.8 | 1.4 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Beaminster | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.4 | 6.8 | 6.7 | 5.3 | 3.9 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Beaminster | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.4 | 6.2 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Beaminster | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.4 | 5.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Beaminster | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.4 | 6.8 | 5.6 | 3.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Bridport | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.8 | 14.8 | 14.7 | 14.5 | 14.4 | 14.2 | 13.9 | 13.7 | 13.4 | 13.2 | 13 | 12.8 | 12.7 | 12.6 | 12.6 | 12.5 | 12.4 | 11.9 | 11.2
Axminster 132 kV | Bridport | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.8 | 14.7 | 14.3 | 13.9 | 13.4 | 12.8 | 12.1 | 11.4 | 10.9 | 10.6 | 10.3 | 9.8 | 9.4 | 9 | 8.7 | 8.4 | 8 | 0 | 0
Axminster 132 kV | Bridport | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.8 | 14.5 | 14 | 13.5 | 12.8 | 12.1 | 11.2 | 10.4 | 9.8 | 9.2 | 8.8 | 8.2 | 7.8 | 5 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Bridport | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.8 | 14.7 | 14.6 | 14.3 | 13.9 | 13.4 | 12.8 | 12.2 | 11.7 | 11.5 | 11.2 | 10.9 | 10.8 | 10.6 | 10.5 | 10.4 | 10.2 | 9.1 | 2.2
Axminster 132 kV | Chard | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Chard | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Chard | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Chard | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Coker | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.2 | 4.1 | 3.8 | 3.2 | 2.6 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Coker | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.2 | 3.7 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Coker | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.2 | 3.6 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Coker | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.2 | 4 | 3.5 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Colyford | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.7 | 2.1 | 1.8 | 1.4 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Colyford | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.7 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Colyford | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Colyford | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.7 | 2 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Crewkerne | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.4 | 4.2 | 3.9 | 3.4 | 2.7 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Crewkerne | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.4 | 3.9 | 3.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Crewkerne | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.4 | 3.7 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Crewkerne | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.4 | 4.1 | 3.6 | 2.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Dowlish Ford | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.2 | 3.5 | 3.3 | 3.1 | 2.9 | 2.7 | 1.7 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Dowlish Ford | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.2 | 3.3 | 2.9 | 2.3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Dowlish Ford | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.2 | 3.2 | 2.6 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Dowlish Ford | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.2 | 3.4 | 3.1 | 2.8 | 2.3 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | East Chinnock Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 4.1 | 3.8 | 3.3 | 2.6 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | East Chinnock Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 3.8 | 3.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | East Chinnock Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 3.6 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | East Chinnock Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 4 | 3.5 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Martock | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.5 | 9.8 | 9.1 | 9.1 | 9.1 | 9.1 | 6.3 | 6.2 | 6 | 5.9 | 5.7 | 5.5 | 5.4 | 5.3 | 5.2 | 4.8 | 4.4 | 1.5 | 0
Axminster 132 kV | Martock | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.5 | 9.1 | 9.1 | 9 | 8.9 | 8.7 | 5.4 | 3.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Martock | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.5 | 9.1 | 9.1 | 8.9 | 8.8 | 5.4 | 4.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Martock | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.5 | 9.8 | 9.1 | 9.1 | 9.1 | 9 | 6 | 5.8 | 5.7 | 4.4 | 2.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Montacute | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.4 | 11.3 | 11.3 | 11.2 | 11.1 | 11.1 | 11 | 9.5 | 9.4 | 9.2 | 7.8 | 6.7 | 6.1 | 5.7 | 5.3 | 4.9 | 4.5 | 1.5 | 0
Axminster 132 kV | Montacute | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.4 | 11.3 | 11.1 | 11 | 9.4 | 8.8 | 6.2 | 3.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Montacute | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.4 | 11.3 | 11.1 | 10.9 | 9.2 | 7.4 | 4.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Montacute | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.4 | 11.3 | 11.2 | 11.1 | 10.9 | 9.2 | 8.3 | 7.4 | 6 | 4.4 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Penn Cross | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1 | 1 | 0.9 | 0.8 | 0.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Penn Cross | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Penn Cross | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Penn Cross | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1 | 0.9 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Waterlake Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.8 | 1.7 | 1.5 | 1.3 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Waterlake Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.8 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Waterlake Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.8 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Waterlake Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.8 | 1.6 | 1.3 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Woodcote Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 7.2 | 6.3 | 5.5 | 4.6 | 3.4 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Woodcote Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 7.2 | 5.3 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Woodcote Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 7.2 | 4.7 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Axminster 132 kV | Woodcote Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 7.2 | 6 | 4.7 | 3.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bath Road Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.8 | 5.4 | 4.8 | 4.1 | 3.2 | 2.2 | 11.4 | 10.7 | 9.9 | 9.4 | 8.8 | 8.4 | 10.6 | 10.5 | 10 | 9.9 | 9.5 | 9.2 | 7.8
Bridgwater 132 kV | Bath Road Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.8 | 5 | 1.7 | 0 | 0 | 0 | 5.1 | 1.9 | 0.6 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bath Road Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.8 | 4.8 | 1.4 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bath Road Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.8 | 5.1 | 3.9 | 0 | 0 | 0 | 7.1 | 4.8 | 2.1 | 1 | 0 | 0 | 2.8 | 2.2 | 2.3 | 1.7 | 1 | 0 | 0
Bridgwater 132 kV | Bridgwater Grid Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 19.3 | 15.8 | 13.1 | 9 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bridgwater Grid Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 19.3 | 13.5 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bridgwater Grid Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 19.3 | 12.2 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bridgwater Grid Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 19.3 | 14.9 | 10.3 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bridgwater Local | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.7 | 7.6 | 7.4 | 7.1 | 6.9 | 6.6 | 6.3 | 6 | 5.7 | 5.4 | 5 | 4.8 | 4.6 | 4.5 | 4.4 | 4.3 | 4.1 | 3.2 | 2.1
Bridgwater 132 kV | Bridgwater Local | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.7 | 7.3 | 6.8 | 6.2 | 5.5 | 4.8 | 4.3 | 3.7 | 3.3 | 2.8 | 2.4 | 1.9 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bridgwater Local | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.7 | 7.2 | 6.6 | 5.8 | 5 | 4 | 3.2 | 2.4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Bridgwater Local | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.7 | 7.5 | 7.1 | 6.8 | 6.3 | 5.8 | 5.4 | 5 | 4.6 | 4.2 | 3.7 | 3.4 | 3.2 | 3 | 2 | 1.7 | 1.4 | 0 | 0
Bridgwater 132 kV | Burnham | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Burnham | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Burnham | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Burnham | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Colley Lane | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Colley Lane | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Colley Lane | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Colley Lane | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Creech St Michael | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.9 | 4.1 | 3.9 | 3.7 | 3.4 | 3 | 2.7 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Creech St Michael | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.9 | 4 | 3.6 | 2.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Creech St Michael | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.9 | 3.9 | 3.3 | 2.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Creech St Michael | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.9 | 4.1 | 3.8 | 3.5 | 2.9 | 2.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Curry Mallet | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 2.9 | 2.9 | 2.8 | 2.7 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Curry Mallet | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 2.9 | 2.7 | 2.4 | 2.1 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Curry Mallet | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 2.9 | 2.6 | 2.2 | 1.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Curry Mallet | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 2.9 | 2.8 | 2.7 | 2.6 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Edgarley | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Edgarley | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Edgarley | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Edgarley | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Martock | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Martock | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Martock | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Martock | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Millfield | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 11.3 | 10.8 | 10.2 | 9.7 | 9 | 8.8 | 8.5 | 8.3 | 8.1 | 7.8 | 7.3 | 5.8 | 4.2
Bridgwater 132 kV | Millfield | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.3 | 7.5 | 6.8 | 5.5 | 4.7 | 3.9 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Millfield | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 7.1 | 5.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Millfield | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.3 | 8.6 | 7.7 | 6.7 | 6.3 | 5.5 | 3 | 2.6 | 2.2 | 1.7 | 0 | 0
Bridgwater 132 kV | Nether Stowey | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Nether Stowey | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Nether Stowey | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Nether Stowey | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | North Street Langport | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.3 | 4.1 | 3.8 | 3.2 | 2.5 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | North Street Langport | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.3 | 3.7 | 2.9 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | North Street Langport | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.3 | 3.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | North Street Langport | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.3 | 4 | 3.5 | 2.9 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Shapwick | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Shapwick | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Shapwick | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Shapwick | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Somerton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Somerton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Somerton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Somerton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Street Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 17.7 | 15 | 12.2 | 9.6 | 6.2 | 3.6 | 3.4 | 2.3 | 0.8 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Street Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Street Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Street Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 7 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Watchfield | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Watchfield | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Watchfield | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Watchfield | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Wedmore | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Wedmore | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Wedmore | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Wedmore | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Wells | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.3 | 9.3 | 9.1 | 8.8 | 8.3 | 7.9 | 7.7 | 7.5 | 7.3 | 7.1 | 6.9 | 5.4 | 3.6
Bridgwater 132 kV | Wells | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.1 | 7.3 | 6.6 | 5.6 | 4.6 | 3.7 | 2.8 | 1.8 | 0.8 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Wells | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 5.3 | 3.6 | 2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgwater 132 kV | Wells | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.2 | 8.9 | 8.5 | 7.8 | 6.9 | 6.3 | 5.8 | 5.3 | 4.8 | 4.3 | 3.8 | 0 | 0
Exeter 132 kV | Athelstan Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.9 | 10.9 | 10.8 | 10.8 | 10.8 | 10.7 | 10.2 | 10.2 | 9.9 | 9.8 | 9.7 | 9.7 | 9.6 | 9.6 | 9.6 | 9.6 | 9.5 | 9.4 | 9
Exeter 132 kV | Athelstan Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.9 | 10.9 | 10.8 | 10.6 | 10.3 | 10.1 | 9.4 | 9.3 | 9.1 | 9 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Athelstan Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.9 | 10.9 | 10.7 | 10.3 | 10.1 | 9.8 | 9 | 8.8 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Athelstan Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.9 | 10.9 | 10.8 | 10.8 | 10.8 | 10.5 | 9.8 | 9.6 | 9.5 | 9.4 | 9.3 | 9.3 | 9.3 | 1.5 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Bridge Mills | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.9 | 7.7 | 7.5 | 7.1 | 6.6 | 5.9 | 9 | 8.6 | 8.1 | 7.5 | 6.2 | 4.9 | 4 | 3 | 2.3 | 1.6 | 1.3 | 0 | 0
Exeter 132 kV | Bridge Mills | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.9 | 7.5 | 7 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Bridge Mills | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.9 | 7.4 | 6.7 | 5 | 3.1 | 0.7 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Bridge Mills | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.9 | 7.6 | 7.3 | 6.7 | 5.9 | 4.7 | 8.6 | 7.7 | 5.4 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Budleigh Salterton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.8 | 2.3 | 2.2 | 2.1 | 2 | 1.9 | 1.2 | 1.3 | 1.3 | 1.4 | 1.3 | 1.1 | 1 | 1 | 0.9 | 0.8 | 0.7 | 0 | 0
Exeter 132 kV | Budleigh Salterton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.8 | 2.1 | 1.9 | 1.7 | 1.4 | 1.2 | 0.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Budleigh Salterton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.8 | 2 | 1.7 | 1.4 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Budleigh Salterton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.8 | 2.2 | 2.1 | 2 | 1.8 | 1.6 | 1.3 | 1.2 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Burlescombe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Burlescombe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Burlescombe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Burlescombe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Clyst Honiton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.2 | 7.9 | 7.3 | 6.2 | 4.1 | 2.4 | 1.6 | 1.5 | 1.4 | 1 | 0 | 0 | 0
Exeter 132 kV | Clyst Honiton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Clyst Honiton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Clyst Honiton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Core Hill | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.9 | 4.8 | 4.6 | 4.5 | 4.4 | 4.3 | 10.2 | 10.3 | 10.3 | 10.1 | 9.9 | 9.7 | 9.6 | 9.6 | 9.5 | 9.5 | 9.5 | 9 | 8.6
Exeter 132 kV | Core Hill | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.9 | 4.6 | 4.3 | 4 | 3.6 | 3 | 8.7 | 8.1 | 7.6 | 7.3 | 7.1 | 7 | 7 | 6.7 | 5.9 | 3 | 0 | 0 | 0
Exeter 132 kV | Core Hill | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.9 | 4.5 | 4.1 | 3.7 | 3.2 | 2.6 | 8.5 | 7.9 | 7.4 | 7.3 | 5.7 | 2.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Core Hill | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.9 | 4.8 | 4.5 | 4.4 | 4 | 3.6 | 9.1 | 8.6 | 8 | 7.8 | 7.6 | 7.5 | 7.6 | 7.6 | 7.5 | 7.7 | 6 | 0 | 0
Exeter 132 kV | Countess Wear | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.3 | 9.2 | 9.2 | 9.1 | 9 | 8.9 | 8.6 | 8.5 | 8.4 | 8.2 | 8.1 | 7.9 | 7.8 | 7.7 | 7.6 | 7.5 | 7.2 | 6.9 | 6.7
Exeter 132 kV | Countess Wear | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.3 | 9.2 | 9 | 8.8 | 8.4 | 8 | 7.5 | 7.2 | 7 | 6.7 | 6.5 | 6.2 | 5.5 | 5.3 | 5.2 | 5.1 | 5 | 4.4 | 3.8
Exeter 132 kV | Countess Wear | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.3 | 9.1 | 8.9 | 8.5 | 8.1 | 7.7 | 7.2 | 6.9 | 6.5 | 6.2 | 5.9 | 5.7 | 5.5 | 5 | 4.7 | 4.7 | 4.6 | 4 | 3.4
Exeter 132 kV | Countess Wear | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.3 | 9.2 | 9.1 | 8.9 | 8.7 | 8.5 | 8.1 | 7.8 | 7.6 | 7.4 | 7.1 | 7 | 6.5 | 6.1 | 6 | 5.8 | 5.7 | 5.3 | 4.8
Exeter 132 kV | Cowley Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 21.3 | 20.9 | 20.8 | 20.7 | 20.6 | 20.4 | 20.3 | 20.1 | 20 | 19.8 | 19.5 | 19.3 | 19.1 | 19 | 18.9 | 18.8 | 18.7 | 18.3 | 10.1
Exeter 132 kV | Cowley Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 21.3 | 20.8 | 20.6 | 20.4 | 20.1 | 19.8 | 19.6 | 19.3 | 19.1 | 18.6 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Cowley Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 21.3 | 20.7 | 20.5 | 20.1 | 19.8 | 19.5 | 19.1 | 18.7 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Cowley Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 21.3 | 20.9 | 20.8 | 20.6 | 20.5 | 20.3 | 20.1 | 19.9 | 19.7 | 19.3 | 18.9 | 18.6 | 9.8 | 1.5 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Crediton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.1 | 14.7 | 14.3 | 13.7 | 13 | 12.2 | 10.8 | 9.4 | 8.1 | 6.7 | 5.1 | 3.9 | 3.1 | 2.5 | 1.9 | 1.2 | 0.7 | 0 | 0
Exeter 132 kV | Crediton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.1 | 14.3 | 13.4 | 11.2 | 8.9 | 6.5 | 3.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Crediton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.1 | 14.1 | 12.8 | 10.3 | 7.6 | 4.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Crediton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.1 | 14.6 | 14 | 13.1 | 12 | 10.6 | 8.5 | 6.6 | 5 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Cullompton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.3 | 7.1 | 6.9 | 6.6 | 6.2 | 5.7 | 8.3 | 7.4 | 6.3 | 5.3 | 4.1 | 3.2 | 2.6 | 2 | 1.5 | 1.1 | 0.8 | 0 | 0
Exeter 132 kV | Cullompton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.3 | 6.9 | 6.5 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Cullompton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.3 | 6.8 | 6.3 | 5 | 3.1 | 0.7 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Cullompton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.3 | 7.1 | 6.8 | 6.3 | 5.6 | 4.6 | 6.5 | 5.1 | 3.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Dunkeswell 33/11kv | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Dunkeswell 33/11kv | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Dunkeswell 33/11kv | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Dunkeswell 33/11kv | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | East Budleigh | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 2.3 | 2.2 | 2.1 | 2 | 1.9 | 1.5 | 1.4 | 1.4 | 1.3 | 1.2 | 1.2 | 1.1 | 1 | 0.9 | 0.8 | 0.7 | 0 | 0
Exeter 132 kV | East Budleigh | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 2.1 | 1.9 | 1.7 | 1.4 | 1.2 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | East Budleigh | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 2 | 1.7 | 1.4 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | East Budleigh | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 2.2 | 2.1 | 2 | 1.8 | 1.6 | 1.3 | 1.2 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter City Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter City Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter City Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter City Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter Main Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 23.3 | 11.1 | 9.1 | 6.9 | 4.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter Main Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 23.3 | 7.8 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter Main Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 23.3 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter Main Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 23.3 | 10 | 7 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter Science Park | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.3 | 6 | 6 | 6 | 5.9 | 5.9 | 3.6 | 3.5 | 3.4 | 3.1 | 2.8 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.6
Exeter 132 kV | Exeter Science Park | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.3 | 6 | 5.9 | 5.8 | 5.3 | 4.8 | 1.8 | 1.1 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exeter Science Park | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.3 | 6 | 5.9 | 5.6 | 5.2 | 4.8 | 1.9 | 1.3 | 0.9 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0
Exeter 132 kV | Exeter Science Park | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.3 | 6 | 5.9 | 5.8 | 5.4 | 4.9 | 2 | 1.4 | 0.8 | 0.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exminster | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5 | 4.9 | 4.9 | 4.1 | 4 | 3.8 | 3.4 | 2.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exminster | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5 | 4.9 | 4.1 | 3.6 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exminster | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5 | 4.9 | 4 | 3.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exminster | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5 | 4.9 | 4.1 | 3.9 | 3.5 | 2.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exmouth Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 9.2 | 1.1 | 0.6 | 0 | 0 | 0 | 23.2 | 22.5 | 21.9 | 21.2 | 20.4 | 19.8 | 19.4 | 19 | 18.6 | 18.1 | 17.3 | 14.8 | 12.1
Exeter 132 kV | Exmouth Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 9.2 | 0 | 0 | 0 | 0 | 0 | 18.9 | 17.5 | 16.3 | 15.1 | 13.6 | 12.2 | 10.1 | 8.7 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exmouth Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 9.2 | 0 | 0 | 0 | 0 | 0 | 16.4 | 14.5 | 12.6 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Exmouth Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 9.2 | 0.8 | 0 | 0 | 0 | 0 | 21 | 19.8 | 18.7 | 17.6 | 16.3 | 15.3 | 14.2 | 12.9 | 12.1 | 11.3 | 8.1 | 0 | 0
Exeter 132 kV | Exmouth Works | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.9 | 10.8 | 10.7 | 10.6 | 10.4 | 10.3 | 10.2 | 10 | 9.9 | 9.7 | 9.6 | 9.4 | 9.3 | 9.2 | 9.1 | 9 | 8.8 | 8.3 | 7.6
Exeter 132 kV | Exmouth Works | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.9 | 10.6 | 10.3 | 10.1 | 9.8 | 9.5 | 9.2 | 8.8 | 8.5 | 8.3 | 8 | 7.7 | 7.4 | 7.1 | 6.8 | 6.4 | 6.1 | 4.6 | 3.2
Exeter 132 kV | Exmouth Works | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.9 | 10.5 | 10.1 | 9.7 | 9.3 | 8.8 | 8.5 | 8 | 7.6 | 7.2 | 6.8 | 6.5 | 6.2 | 5.8 | 5.5 | 5.2 | 4.8 | 2.9 | 1.1
Exeter 132 kV | Exmouth Works | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.9 | 10.8 | 10.6 | 10.4 | 10.2 | 9.9 | 9.7 | 9.4 | 9.1 | 8.8 | 8.6 | 8.4 | 8.3 | 8.1 | 7.9 | 7.7 | 7.5 | 6.4 | 5.3
Exeter 132 kV | Folly Bridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.1 | 3 | 2.8 | 2.5 | 2.1 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Folly Bridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.1 | 2.8 | 2.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Folly Bridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.1 | 2.7 | 2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Folly Bridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.1 | 2.9 | 2.6 | 2.2 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Haven Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.8 | 5.6 | 5.4 | 5.2 | 5 | 4.8 | 4.4 | 4.2 | 4 | 3.9 | 3.4 | 3 | 2.7 | 2.3 | 2 | 1.7 | 1.5 | 0 | 0
Exeter 132 kV | Haven Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.8 | 5.4 | 4.9 | 4.5 | 4.1 | 3.7 | 3 | 2.6 | 2.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Haven Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.8 | 5.3 | 4.6 | 4.1 | 3.6 | 3 | 2.2 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Haven Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.8 | 5.6 | 5.2 | 4.9 | 4.6 | 4.2 | 3.7 | 3.3 | 3 | 2.3 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Heavitree | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.2 | 14.1 | 14 | 14 | 13.9 | 13.9 | 14.1 | 14.1 | 14.1 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 10.9 | 10.9 | 10.8
Exeter 132 kV | Heavitree | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.2 | 13.9 | 13.8 | 13.8 | 13.7 | 13.7 | 11 | 10.9 | 10.9 | 10.8 | 10.8 | 10.7 | 10.7 | 10.6 | 10.5 | 10.5 | 10.4 | 9.8 | 8.9
Exeter 132 kV | Heavitree | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.2 | 13.9 | 13.7 | 13.7 | 11.2 | 11.1 | 10.9 | 10.7 | 10.6 | 10.5 | 10.4 | 10.3 | 10.2 | 10.1 | 10 | 9.9 | 9.7 | 8.7 | 7.5
Exeter 132 kV | Heavitree | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.2 | 14 | 14 | 13.9 | 13.8 | 13.8 | 14 | 14 | 14 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.8 | 10.4
Exeter 132 kV | Hemyock | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Hemyock | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Hemyock | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Hemyock | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Hill Barton Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 3.7 | 3.7 | 3.6 | 3.6 | 3.5 | 3.6 | 3.5 | 3.4 | 3.3 | 3.1 | 3 | 2.9 | 2.9 | 2.9 | 2.8 | 2.8 | 2.5 | 2.2
Exeter 132 kV | Hill Barton Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 3.7 | 3.6 | 3.5 | 3.2 | 3 | 2.9 | 2.7 | 2.5 | 2.3 | 2.1 | 1.9 | 1.8 | 1.6 | 1.5 | 1.4 | 1.2 | 0 | 0
Exeter 132 kV | Hill Barton Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 3.7 | 3.6 | 3.4 | 3.2 | 2.7 | 2.8 | 2.5 | 2.2 | 2 | 1.8 | 1.7 | 1.6 | 1.4 | 1.4 | 1.3 | 1.2 | 0 | 0
Exeter 132 kV | Hill Barton Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 3.7 | 3.7 | 3.6 | 3.5 | 3.3 | 3.4 | 3.2 | 3.1 | 2.9 | 2.7 | 2.6 | 2.5 | 2.5 | 2.4 | 2.4 | 2.3 | 1.8 | 1.1
Exeter 132 kV | Honiton Heathfield | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.3 | 11 | 10.9 | 10.7 | 10.5 | 10.2 | 9.9 | 9.5 | 9.2 | 8.8 | 8.3 | 8 | 7.8 | 7.6 | 7.4 | 7 | 6 | 6.3 | 5.1
Exeter 132 kV | Honiton Heathfield | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.3 | 10.8 | 10.5 | 10 | 9.4 | 8.8 | 8.1 | 7.4 | 6.8 | 6.2 | 5.5 | 4.5 | 1.8 | 2.1 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Honiton Heathfield | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.3 | 10.7 | 10.3 | 9.6 | 8.9 | 8 | 7.1 | 6.1 | 5 | 4 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Honiton Heathfield | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 10.9 | 10.7 | 10.5 | 10.2 | 9.7 | 9.2 | 8.7 | 8.2 | 7.6 | 6.8 | 6.3 | 4.3 | 2.5 | 3.5 | 2.9 | 2.3 | 0 | 0
Exeter 132 kV | Lapford | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.6 | 2.6 | 2.5 | 2.4 | 2.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Lapford | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.6 | 2.5 | 2.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Lapford | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.6 | 2.5 | 2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Lapford | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.6 | 2.5 | 2.4 | 2.3 | 1.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Marsh Barton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Marsh Barton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Marsh Barton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Marsh Barton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Marsh Green | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Marsh Green | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Marsh Green | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Marsh Green | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Newton Poppleford | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.5 | 2.3 | 2.2 | 2.1 | 2 | 1.9 | 1.5 | 1.4 | 1.4 | 1.3 | 1.2 | 1.2 | 1.1 | 1 | 0.9 | 0.8 | 0.7 | 0 | 0
Exeter 132 kV | Newton Poppleford | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.5 | 2.1 | 1.9 | 1.7 | 1.4 | 1.2 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Newton Poppleford | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.5 | 2 | 1.7 | 1.4 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Newton Poppleford | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.5 | 2.2 | 2.1 | 2 | 1.8 | 1.6 | 1.4 | 1.2 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Newton St Cyres | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 5.2 | 5.2 | 5.1 | 5 | 4.8 | 4.5 | 4.2 | 3.9 | 3.5 | 3.1 | 2.7 | 2.6 | 2.4 | 1.9 | 1.3 | 0.7 | 0 | 0
Exeter 132 kV | Newton St Cyres | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 5.2 | 5.1 | 4.7 | 4.2 | 3.7 | 3.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Newton St Cyres | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 5.2 | 5.1 | 4.5 | 3.9 | 3.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Newton St Cyres | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 5.2 | 5.2 | 5.1 | 4.9 | 4.6 | 4.2 | 3.9 | 3.5 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Offwell | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.5 | 4.4 | 4.4 | 4.3 | 4.3 | 4.2 | 9.8 | 9.7 | 9.7 | 9.6 | 9.6 | 9.5 | 9.5 | 9.5 | 9.5 | 9.4 | 9.4 | 9.3 | 9.1
Exeter 132 kV | Offwell | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.5 | 4.4 | 4.3 | 4.2 | 4.1 | 4 | 9.5 | 9.4 | 9.3 | 9.2 | 9.1 | 8.8 | 4 | 3 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Offwell | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.5 | 4.3 | 4.2 | 4.1 | 4 | 3.9 | 9.3 | 9.2 | 9 | 5.3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Offwell | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.5 | 4.4 | 4.4 | 4.3 | 4.2 | 4.2 | 9.7 | 9.6 | 9.5 | 9.4 | 9.3 | 9.2 | 9.2 | 8.2 | 8.3 | 7.2 | 5.7 | 0 | 0
Exeter 132 kV | Ottery St Mary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.6 | 10.5 | 10.4 | 10.3 | 10.3 | 9.9 | 9.7 | 9.4 | 9.1 | 8.8 | 8.4 | 8.2 | 8 | 7.9 | 7.7 | 7.5 | 7.3 | 6.6 | 5.6
Exeter 132 kV | Ottery St Mary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.6 | 10.4 | 10.3 | 9.8 | 9.3 | 8.9 | 8.4 | 7.9 | 7.4 | 6.9 | 6.3 | 5.7 | 4 | 3 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Ottery St Mary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.6 | 10.3 | 10 | 9.5 | 9 | 8.3 | 7.6 | 6.8 | 5.9 | 5.1 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Ottery St Mary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.6 | 10.5 | 10.4 | 10.3 | 9.9 | 9.6 | 9.3 | 8.9 | 8.5 | 8 | 7.4 | 7 | 6.3 | 5.8 | 5.9 | 5.6 | 5.3 | 0 | 0
Exeter 132 kV | Pinhoe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.1 | 9.9 | 9.8 | 9.6 | 9.5 | 9.4 | 17.2 | 17.1 | 17.1 | 15.1 | 15 | 15 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.6 | 14.1
Exeter 132 kV | Pinhoe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.1 | 9.7 | 9.4 | 9.2 | 7 | 6.7 | 14.5 | 14.2 | 13.9 | 13.7 | 13.4 | 13.2 | 13 | 12.7 | 12.5 | 12.2 | 12 | 10.6 | 9
Exeter 132 kV | Pinhoe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.1 | 9.6 | 9.2 | 7 | 6.7 | 6.2 | 13.9 | 13.4 | 13 | 12.6 | 12.2 | 11.9 | 11.7 | 11.5 | 11.2 | 11 | 10.7 | 9 | 7.3
Exeter 132 kV | Pinhoe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.1 | 9.8 | 9.6 | 9.3 | 9.2 | 7 | 15 | 14.8 | 14.5 | 14.3 | 14.1 | 14 | 14 | 13.9 | 13.9 | 13.8 | 13.7 | 12.9 | 11.8
Exeter 132 kV | Sidmouth Town | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.9 | 8.7 | 8.5 | 8.2 | 8 | 7.8 | 8 | 7.9 | 7.9 | 7.8 | 7.6 | 7.6 | 7.5 | 7.4 | 7.4 | 7.3 | 7.3 | 6.9 | 6.5
Exeter 132 kV | Sidmouth Town | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.9 | 8.4 | 7.9 | 7.4 | 6.6 | 5.5 | 7.1 | 6.7 | 6.5 | 6.3 | 6.1 | 6 | 6 | 5.7 | 5.3 | 1.6 | 0 | 0 | 0
Exeter 132 kV | Sidmouth Town | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.9 | 8.3 | 7.5 | 6.8 | 5.9 | 4.7 | 6.7 | 6.4 | 6.1 | 6.1 | 5.9 | 2.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Sidmouth Town | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.9 | 8.7 | 8.3 | 7.9 | 7.3 | 6.5 | 7.4 | 7.1 | 6.9 | 6.7 | 6.6 | 6.5 | 6.6 | 6.6 | 6.5 | 6.5 | 6.2 | 0 | 0
Exeter 132 kV | Sowton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 24.4 | 24.4 | 24.3 | 24.2 | 24.1 | 24 | 23.9 | 23.9 | 23.8 | 23.7 | 23.6 | 23.6 | 23.6 | 23.6 | 23.6 | 23.6 | 23.5 | 23.5 | 23.4
Exeter 132 kV | Sowton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 24.4 | 24.3 | 24.2 | 24 | 23.9 | 23.8 | 23.6 | 23.5 | 23.4 | 23.4 | 23.3 | 23.2 | 23.1 | 23 | 23 | 23 | 23 | 22.7 | 22.5
Exeter 132 kV | Sowton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 24.4 | 24.3 | 24.1 | 24 | 23.8 | 23.7 | 23.5 | 23.4 | 23.3 | 23.2 | 23.1 | 23.1 | 23.1 | 22.9 | 22.8 | 22.8 | 22.5 | 22.4 | 20.8
Exeter 132 kV | Sowton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 24.4 | 24.3 | 24.2 | 24.1 | 24 | 23.8 | 23.7 | 23.6 | 23.5 | 23.5 | 23.4 | 23.4 | 23.3 | 23.2 | 23.2 | 23.2 | 23.2 | 22.9 | 22.8
Exeter 132 kV | Sowton B | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5 | 5 | 5 | 4.9 | 4.9 | 4.9 | 4.9 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
Exeter 132 kV | Sowton B | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5 | 5 | 5 | 4.9 | 4.9 | 4.9 | 4.9 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 24.9 | 24.9 | 24.9 | 24.9
Exeter 132 kV | Sowton B | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5 | 5 | 5 | 4.9 | 4.9 | 4.9 | 4.9 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 24.9 | 24.9 | 24.9 | 24.9
Exeter 132 kV | Sowton B | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5 | 5 | 5 | 4.9 | 4.9 | 4.9 | 4.9 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 24.9 | 24.9 | 24.9 | 24.9
Exeter 132 kV | Sowton Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Sowton Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Sowton Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Sowton Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | St Thomas | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.6 | 9.5 | 9.4 | 9.3 | 9.3 | 7.1 | 6.9 | 6.5 | 6.1 | 5.6 | 5 | 4.5 | 4.3 | 4.1 | 3.9 | 3.7 | 3.6 | 2.1 | 0
Exeter 132 kV | St Thomas | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.6 | 9.3 | 9.3 | 7 | 6.4 | 5.5 | 4.6 | 3.8 | 3 | 2.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | St Thomas | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.6 | 9.3 | 7.2 | 6.7 | 5.8 | 4.6 | 3.4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | St Thomas | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.6 | 9.4 | 9.3 | 9.2 | 7.1 | 6.8 | 6.3 | 5.7 | 5.1 | 4.3 | 3.4 | 2.8 | 2.4 | 2 | 1.6 | 1 | 0 | 0 | 0
Exeter 132 kV | Tiverton Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 11 | 10.3 | 9.5 | 8.1 | 6.5 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 11 | 9.5 | 7.7 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 11 | 9 | 6.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 11 | 10.1 | 8.8 | 6.9 | 4.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Junction | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.6 | 10.4 | 10.2 | 9.9 | 9.5 | 9.1 | 8.4 | 7.6 | 6.7 | 5.9 | 5 | 4.3 | 3.8 | 3.4 | 3 | 2.7 | 2.5 | 0.6 | 0
Exeter 132 kV | Tiverton Junction | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.6 | 10.2 | 9.8 | 8.6 | 7.3 | 6 | 4.3 | 2.8 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Junction | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.6 | 10.2 | 9.7 | 8.2 | 6.8 | 5.1 | 3.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Junction | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.6 | 10.3 | 10 | 9.5 | 8.8 | 8.1 | 6.8 | 5.6 | 4.4 | 3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Moorhayes | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.4 | 7.4 | 7.2 | 7 | 6.7 | 6.4 | 5.8 | 5.2 | 4.6 | 3.9 | 3.2 | 2.6 | 2.3 | 2 | 1.7 | 1.5 | 1.2 | 0 | 0
Exeter 132 kV | Tiverton Moorhayes | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.4 | 7.2 | 6.9 | 6.1 | 5.2 | 4.4 | 3.3 | 2.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Moorhayes | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.4 | 7.1 | 6.8 | 5.7 | 4.7 | 3.5 | 2.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton Moorhayes | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.4 | 7.3 | 7.1 | 6.9 | 6.5 | 6.1 | 5.2 | 4.5 | 3.8 | 2.8 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton South | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.4 | 11.3 | 11 | 10.6 | 10.2 | 9.8 | 8.8 | 8 | 7.2 | 6.3 | 5.3 | 4.6 | 4.1 | 3.7 | 3.2 | 2.8 | 2.4 | 0 | 0
Exeter 132 kV | Tiverton South | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.4 | 11 | 10.4 | 9.3 | 8 | 6.8 | 5.2 | 3.9 | 2.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton South | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.4 | 10.8 | 10 | 8.5 | 7.1 | 5.4 | 3.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Tiverton South | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.4 | 11.2 | 10.8 | 10.4 | 9.8 | 9.1 | 7.9 | 7 | 6 | 4.7 | 3 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Topsham | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.4 | 3.3 | 3.2 | 3.1 | 3 | 5.1 | 4.9 | 4.6 | 4.3 | 3.9 | 3.7 | 3.5 | 3.4 | 3.3 | 3.2 | 3 | 2.2 | 1.3
Exeter 132 kV | Topsham | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3.3 | 3 | 2.8 | 2.6 | 2.4 | 3.5 | 3 | 2.5 | 2 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Topsham | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.2 | 3 | 2.7 | 2.4 | 2.1 | 2.7 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Topsham | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.3 | 3.2 | 3 | 2.8 | 2.7 | 4.3 | 3.9 | 3.5 | 3.1 | 2.5 | 2.2 | 1.9 | 1.5 | 1.3 | 1.1 | 0 | 0 | 0
Exeter 132 kV | Witheridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Witheridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Witheridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Witheridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Withycombe Raleigh | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.1 | 17 | 16.8 | 16.7 | 16.6 | 16.5 | 16.4 | 16 | 15.9 | 15.7 | 15.5 | 15.4 | 15.3 | 15.1 | 15 | 14.8 | 14.3 | 13.5 | 12.7
Exeter 132 kV | Withycombe Raleigh | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.1 | 16.7 | 16.4 | 15.9 | 15.7 | 15.3 | 14.9 | 14.5 | 14.1 | 13.8 | 13.1 | 12.6 | 11.5 | 11 | 10.5 | 10 | 9.6 | 7.7 | 5.9
Exeter 132 kV | Withycombe Raleigh | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.1 | 16.5 | 15.9 | 15.6 | 15.2 | 14.7 | 14.1 | 13.5 | 13 | 12.5 | 11.9 | 11.3 | 10.7 | 9.7 | 8.9 | 8.5 | 8.2 | 5.8 | 3.6
Exeter 132 kV | Withycombe Raleigh | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.1 | 16.9 | 16.7 | 16.5 | 16.3 | 15.8 | 15.5 | 15.1 | 14.7 | 14.4 | 13.9 | 13.6 | 13 | 12.2 | 11.9 | 11.6 | 11.4 | 10 | 8.6
Exeter 132 kV | Woodbury | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.3 | 6.2 | 6.2 | 6.2 | 6.2 | 5 | 6.8 | 6.6 | 6.4 | 6.2 | 5.9 | 5.8 | 5.6 | 5.5 | 5.5 | 5.4 | 5.3 | 4.7 | 3.9
Exeter 132 kV | Woodbury | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.3 | 6.2 | 5.1 | 5 | 4.8 | 4.6 | 5.8 | 5.5 | 5.1 | 4.7 | 4.2 | 3.7 | 3 | 2.6 | 2.1 | 1.6 | 0 | 0 | 0
Exeter 132 kV | Woodbury | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.3 | 6.2 | 5.1 | 4.9 | 4.6 | 4.1 | 5.3 | 4.6 | 3.8 | 3 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exeter 132 kV | Woodbury | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.3 | 6.2 | 6.2 | 5.1 | 5 | 4.9 | 6.4 | 6.1 | 5.8 | 5.5 | 5.1 | 4.9 | 4.5 | 4.2 | 4 | 3.7 | 1.8 | 0 | 0
Indian Queens 132 kV | Blackpool | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 4 | 4 | 3.9 | 3.9 | 3.8 | 3.9 | 3.8 | 3.6 | 3.4 | 3.2 | 2.9 | 2.7 | 2.6 | 2.4 | 2.3 | 2.1 | 1.1 | 0
Indian Queens 132 kV | Blackpool | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 4 | 3.9 | 3.8 | 3.6 | 3.3 | 2.6 | 2.1 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Blackpool | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.9 | 3.9 | 3.7 | 3.2 | 2.5 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Blackpool | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 4 | 4 | 3.9 | 3.8 | 3.8 | 3.7 | 3.3 | 3.1 | 2.3 | 1.7 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Bodmin | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 5.1 | 4.9 | 4.5 | 4 | 3.5 | 2.8 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Bodmin | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 4.9 | 4.4 | 3.2 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Bodmin | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 4.7 | 4.1 | 2.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Bodmin | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 5 | 4.7 | 4.2 | 3.4 | 2.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Bugle | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Bugle | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Bugle | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Bugle | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Callywith | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 5.1 | 4.9 | 4.5 | 4.1 | 3.5 | 2.8 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Callywith | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 4.9 | 4.4 | 3.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Callywith | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 4.7 | 4.1 | 2.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Callywith | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 5.1 | 4.8 | 4.2 | 3.4 | 2.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 23.8 | 22.1 | 21.5 | 20.6 | 19.8 | 18.9 | 67.7 | 66.3 | 59.8 | 52.5 | 43 | 35.7 | 28.3 | 23.3 | 15.3 | 11.6 | 7.9 | 0 | 0
Indian Queens 132 kV | Camborne Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 23.8 | 21.3 | 19.8 | 17.5 | 15.1 | 12.8 | 30.9 | 16.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 23.8 | 20.9 | 18.9 | 15.9 | 12.8 | 3.2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 23.8 | 21.8 | 20.8 | 19.6 | 18.3 | 16.8 | 57.3 | 46.6 | 36 | 21.5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Carn Brea | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.7 | 17.6 | 17.4 | 17.2 | 16.9 | 16.7 | 16.5 | 16 | 15.5 | 15.1 | 14.6 | 14.3 | 14 | 13.9 | 13.7 | 13.5 | 13.4 | 12.2 | 10.8
Indian Queens 132 kV | Camborne Carn Brea | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.7 | 17.3 | 17 | 16.5 | 15.5 | 15 | 14.5 | 13.8 | 13.1 | 7.9 | 7.2 | 6.5 | 5.8 | 5.1 | 4.4 | 3.6 | 2.9 | 0 | 0
Indian Queens 132 kV | Camborne Carn Brea | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.7 | 17.2 | 16.8 | 15.7 | 15 | 14.1 | 13.3 | 12.1 | 10.8 | 5.2 | 4.1 | 3.4 | 2.7 | 2.1 | 1.6 | 1 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Carn Brea | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.7 | 17.5 | 17.2 | 16.9 | 16.6 | 16.5 | 15.8 | 15.2 | 14.7 | 14 | 13.3 | 12.9 | 12.5 | 12.1 | 11.8 | 11.4 | 11 | 8.5 | 6.4
Indian Queens 132 kV | Camborne Holmans | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.8 | 13.4 | 13.2 | 12.8 | 12.5 | 12.1 | 11.3 | 10.7 | 10.1 | 9.4 | 8.6 | 8.1 | 7.7 | 7.4 | 7.2 | 6.9 | 6.6 | 4.6 | 2.4
Indian Queens 132 kV | Camborne Holmans | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.8 | 13.1 | 12.5 | 11.5 | 10.5 | 9.6 | 8.2 | 7.1 | 6.1 | 5 | 3.9 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Holmans | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.8 | 12.9 | 12.2 | 10.8 | 9.5 | 8.1 | 6.2 | 4.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Holmans | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.8 | 13.3 | 12.9 | 12.4 | 11.9 | 11.3 | 10.3 | 9.5 | 8.7 | 7.7 | 6.5 | 5.8 | 5.1 | 3.8 | 3.2 | 1.7 | 1 | 0 | 0
Indian Queens 132 kV | Camborne Treswithian | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.7 | 4.4 | 4.4 | 4.2 | 4.1 | 3.9 | 9.3 | 9 | 8.7 | 8.4 | 8 | 7.8 | 7.6 | 7.5 | 7.2 | 7 | 6.7 | 4.7 | 2.5
Indian Queens 132 kV | Camborne Treswithian | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.7 | 4.3 | 4.2 | 3.8 | 3.4 | 3 | 8.1 | 7.2 | 6.1 | 5.1 | 3.9 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Treswithian | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.7 | 4.3 | 4.1 | 3.5 | 3 | 2.3 | 6.3 | 4.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Camborne Treswithian | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.7 | 4.4 | 4.3 | 4.2 | 4 | 3.8 | 9 | 8.7 | 8.3 | 7.8 | 6.6 | 5.8 | 5.2 | 3.9 | 3.3 | 1.7 | 1 | 0 | 0
Indian Queens 132 kV | Constantine 33kv | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Constantine 33kv | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Constantine 33kv | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Constantine 33kv | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Davidstow | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.4 | 3.4 | 3.3 | 3.1 | 2.7 | 1.9 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Davidstow | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.4 | 3.3 | 3.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Davidstow | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.4 | 3.3 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Davidstow | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.4 | 3.3 | 3.3 | 3 | 2.1 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Delabole | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.4 | 4.2 | 4 | 3.4 | 2.7 | 2 | 2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Delabole | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.4 | 4 | 3.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Delabole | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.4 | 3.9 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Delabole | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.4 | 4.2 | 3.8 | 3.1 | 2.2 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Devoran | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Devoran | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Devoran | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Devoran | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Drinnick. | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Drinnick. | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Drinnick. | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Drinnick. | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Falmouth Bickland Hl | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.6 | 15.3 | 15 | 14.7 | 14.4 | 14.1 | 17 | 16.7 | 16.4 | 16.1 | 15.9 | 15.6 | 15.4 | 15.3 | 15.1 | 15 | 14.9 | 14 | 12.9
Indian Queens 132 kV | Falmouth Bickland Hl | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.6 | 14.9 | 14.2 | 13.5 | 12.9 | 12.2 | 14 | 13.4 | 12.8 | 11.4 | 10.9 | 10.5 | 10 | 9.5 | 8.9 | 8.4 | 7.9 | 4.7 | 0
Indian Queens 132 kV | Falmouth Bickland Hl | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.6 | 14.7 | 13.7 | 12.8 | 11.9 | 11 | 13.8 | 13.1 | 12.4 | 10.6 | 9.9 | 9.4 | 8.5 | 7.9 | 7.6 | 6.9 | 6.3 | 0 | 0
Indian Queens 132 kV | Falmouth Bickland Hl | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.6 | 15.2 | 14.7 | 14.2 | 13.8 | 13.3 | 16.1 | 15.6 | 15.3 | 14.1 | 13.7 | 13.5 | 13.3 | 13 | 12.8 | 12.5 | 12.2 | 10.4 | 8.8
Indian Queens 132 kV | Falmouth Docks | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.4 | 8.9 | 8.9 | 8.8 | 8.8 | 8.7 | 8.7 | 7.8 | 7.8 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 8.9 | 8.9 | 8.9 | 8.8 | 7.8
Indian Queens 132 kV | Falmouth Docks | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.4 | 8.9 | 8.7 | 8.6 | 8.4 | 7.9 | 7.7 | 7.6 | 7.6 | 7.5 | 7.4 | 7.3 | 7.2 | 7.1 | 7.7 | 7.6 | 7.5 | 4.7 | 0
Indian Queens 132 kV | Falmouth Docks | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.4 | 8.8 | 8.6 | 8.3 | 7.6 | 6.9 | 7.5 | 7.3 | 7.2 | 7.1 | 6.9 | 6.8 | 6.7 | 6.6 | 7.3 | 7.1 | 7 | 0 | 0
Indian Queens 132 kV | Falmouth Docks | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.4 | 8.9 | 8.8 | 8.8 | 8.7 | 8.7 | 7.8 | 7.8 | 7.7 | 7.7 | 7.6 | 7.6 | 7.6 | 7.5 | 8.8 | 8.7 | 8.7 | 7.7 | 7.4
Indian Queens 132 kV | Fowey | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 4.1 | 4 | 4 | 3.9 | 3.8 | 3.7 | 3.7 | 3.2 | 2.6 | 2 | 0 | 0
Indian Queens 132 kV | Fowey | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fowey | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fowey | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 4 | 3.9 | 3.8 | 2.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fraddon | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.2 | 8.2 | 8.1 | 8.1 | 7.8 | 7.3 | 6.1 | 5.3 | 4.3 | 3.3 | 2.2 | 1.3 | 0.9 | 0.6 | 0.9 | 0.6 | 0 | 0 | 0
Indian Queens 132 kV | Fraddon | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.2 | 8.1 | 8.2 | 6.9 | 5.6 | 4.3 | 2.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fraddon | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.2 | 8 | 8 | 6.4 | 4.7 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fraddon | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.2 | 8.1 | 8.3 | 8 | 7.4 | 6.7 | 5.2 | 4.1 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fraddon Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fraddon Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fraddon Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Fraddon Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Geevor | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.9 | 9.9 | 9.7 | 9.6 | 9.5 | 9.4 | 9.6 | 9.4 | 9.2 | 9 | 8.7 | 8.5 | 8.3 | 8.2 | 9.6 | 9.5 | 9.5 | 8.6 | 7.2
Indian Queens 132 kV | Geevor | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.9 | 9.7 | 9.4 | 9.1 | 8.8 | 8.5 | 4.2 | 3.6 | 3.2 | 2.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Geevor | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.9 | 9.6 | 9.2 | 8.8 | 8.4 | 7.8 | 3.1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Geevor | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.9 | 9.8 | 9.6 | 9.5 | 9.3 | 9.2 | 9.3 | 9.1 | 8.8 | 8.5 | 8 | 7.7 | 7.4 | 7.2 | 8.4 | 8 | 7.6 | 3.8 | 0
Indian Queens 132 kV | Hayle | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.1 | 13.9 | 13.6 | 13.3 | 13 | 12.6 | 12.1 | 11.6 | 11 | 10.5 | 9.8 | 9.4 | 9.1 | 8.9 | 11.8 | 11.5 | 11.3 | 9.6 | 7.7
Indian Queens 132 kV | Hayle | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.1 | 13.6 | 12.9 | 11.9 | 10.9 | 10 | 8.9 | 7.8 | 7 | 6.2 | 5.3 | 4.4 | 3.6 | 2.7 | 4.1 | 3.1 | 2 | 0 | 0
Indian Queens 132 kV | Hayle | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.1 | 13.4 | 12.5 | 11.2 | 10 | 8.7 | 7.2 | 5.7 | 4.2 | 2.9 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Hayle | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.1 | 13.8 | 13.3 | 12.8 | 12.2 | 11.6 | 10.8 | 9.9 | 9.3 | 8.5 | 7.7 | 7.2 | 6.7 | 6.3 | 8.5 | 7.9 | 7.4 | 3.9 | 0.9
Indian Queens 132 kV | Hayle Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 49.1 | 48.6 | 47.6 | 46.6 | 45.7 | 44.6 | 43.1 | 41.6 | 40.2 | 38.8 | 37.1 | 35.9 | 35.1 | 34.2 | 41.3 | 38.4 | 35.1 | 8.8 | 0
Indian Queens 132 kV | Hayle Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 49.1 | 47.6 | 45 | 42.3 | 34.9 | 22.7 | 30.5 | 21.5 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Hayle Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 49.1 | 46.9 | 43.5 | 38.2 | 21.9 | 4.4 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Hayle Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 49.1 | 48.3 | 46.7 | 45.2 | 43.8 | 41.1 | 40 | 38 | 36.2 | 28.4 | 15.9 | 7.9 | 0 | 0 | 8.8 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Helston | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.9 | 16.2 | 15.1 | 14.9 | 14.7 | 14.4 | 13.9 | 13.1 | 12.2 | 10.3 | 6.6 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Helston | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.9 | 15.1 | 14.8 | 13.9 | 12.6 | 10.7 | 6.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Helston | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.9 | 15 | 14.6 | 13 | 11 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Helston | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.9 | 15.1 | 15 | 14.7 | 14.3 | 13.7 | 12.7 | 11.6 | 8.8 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Isles Of Scilly | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.8 | 1.8 | 1.7 | 1.7 | 1.7 | 1.6 | 1.6 | 1.6 | 1.5 | 1.5 | 1.5 | 1.4 | 1.4 | 1.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.3
Indian Queens 132 kV | Isles Of Scilly | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.8 | 1.8 | 1.6 | 1.6 | 1.5 | 1.4 | 1.4 | 1.3 | 1.3 | 1.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Isles Of Scilly | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.8 | 1.8 | 1.6 | 1.5 | 1.4 | 1.3 | 1.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Isles Of Scilly | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.8 | 1.8 | 1.7 | 1.7 | 1.6 | 1.6 | 1.5 | 1.5 | 1.5 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 4.4 | 4.4 | 4.4 | 4.1 | 0
Indian Queens 132 kV | Laneast | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Laneast | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Laneast | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Laneast | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Lanner | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.9 | 6.7 | 6.6 | 6.4 | 6.2 | 6 | 5.7 | 5.3 | 4.8 | 4.4 | 3.8 | 3.4 | 3.2 | 3 | 5.7 | 5.5 | 5.3 | 4 | 2.6
Indian Queens 132 kV | Lanner | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.9 | 6.6 | 6.3 | 5.7 | 5.1 | 4.5 | 3.8 | 3.1 | 2.4 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Lanner | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.9 | 6.5 | 6.2 | 5.4 | 4.6 | 3.6 | 2.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Lanner | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.9 | 6.7 | 6.5 | 6.3 | 6 | 5.7 | 5.2 | 4.7 | 4.2 | 3.5 | 2.6 | 2.1 | 1.6 | 1.3 | 3.7 | 3.3 | 1.6 | 0 | 0
Indian Queens 132 kV | Lostwithiel | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Lostwithiel | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Lostwithiel | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Lostwithiel | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Marazion | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.4 | 9.3 | 9.2 | 9 | 8.9 | 8.7 | 9 | 8.9 | 8.8 | 8.6 | 8.5 | 8.4 | 8.4 | 8.3 | 8.2 | 8.2 | 8.1 | 7.7 | 7.3
Indian Queens 132 kV | Marazion | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.4 | 9.2 | 8.8 | 8.4 | 7.9 | 7.5 | 8.3 | 6.7 | 5.2 | 3.6 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Marazion | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.4 | 9.1 | 8.6 | 8 | 7.3 | 6 | 4.6 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Marazion | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.4 | 9.3 | 9.1 | 8.8 | 8.6 | 8.3 | 8.6 | 8.5 | 8.3 | 8.2 | 8 | 7.9 | 7.8 | 7.7 | 7.5 | 7.4 | 7.2 | 3.8 | 0
Indian Queens 132 kV | Mevagissey | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.7 | 4.6 | 4.5 | 4.4 | 4.3 | 4.1 | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 2.9 | 2.8 | 2.6 | 2.4 | 2.3 | 2.1 | 1.1 | 0
Indian Queens 132 kV | Mevagissey | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.7 | 4.5 | 4.2 | 3.9 | 3.7 | 3.3 | 2.7 | 2.1 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mevagissey | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.7 | 4.4 | 4 | 3.7 | 3.2 | 2.5 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mevagissey | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.7 | 4.6 | 4.4 | 4.3 | 4.1 | 3.9 | 3.7 | 3.3 | 3.1 | 2.3 | 1.7 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mousehole | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.2 | 6.1 | 6.1 | 6.1 | 6 | 6 | 5.9 | 5.9 | 5.9 | 5.4 | 5.3 | 5.3 | 5.2 | 5.2 | 5.2 | 5.1 | 5.1 | 4.8 | 4.5
Indian Queens 132 kV | Mousehole | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.2 | 6.1 | 6 | 5.9 | 5.9 | 5.4 | 4.3 | 3.7 | 3.2 | 2.7 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mousehole | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.2 | 6.1 | 6 | 5.9 | 5.4 | 5.2 | 3.2 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mousehole | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.2 | 6.1 | 6.1 | 6 | 6 | 5.9 | 5.9 | 5.4 | 5.4 | 5.3 | 5.1 | 5 | 4.9 | 4.9 | 4.8 | 4.7 | 4.6 | 3.9 | 0
Indian Queens 132 kV | Mullion | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mullion | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mullion | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Mullion | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newlyn | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 5.3 | 5.2 | 5.2 | 5.1 | 5.1 | 4.9 | 4.9 | 4.8 | 4.7 | 4.6 | 4.5 | 4.5 | 4.4 | 4.4 | 4.3 | 4.3 | 4 | 3.6
Indian Queens 132 kV | Newlyn | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 5.2 | 5.1 | 4.9 | 4.8 | 4.7 | 4.4 | 4.2 | 4.1 | 3.4 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newlyn | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 5.2 | 5 | 4.8 | 4.6 | 4.4 | 4.1 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newlyn | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 5.3 | 5.2 | 5.1 | 5 | 5 | 4.7 | 4.6 | 4.5 | 4.4 | 4.2 | 4.1 | 4 | 3.9 | 3.9 | 3.8 | 3.7 | 3 | 0
Indian Queens 132 kV | Newquay Trencreek Ln | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.7 | 11.6 | 11.6 | 10 | 9.9 | 9.9 | 9.9 | 9.8 | 9.6 | 9.5 | 9.3 | 9.1 | 9 | 8.9 | 8.8 | 8.8 | 8.5 | 6.7 | 4.7
Indian Queens 132 kV | Newquay Trencreek Ln | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.7 | 11.6 | 9.9 | 9.7 | 9.4 | 9 | 8.7 | 8.2 | 7 | 5.9 | 4.6 | 3.4 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newquay Trencreek Ln | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.7 | 10 | 9.8 | 9.5 | 9.1 | 8.6 | 7.5 | 5.8 | 4 | 2.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newquay Trencreek Ln | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.7 | 11.6 | 10 | 9.9 | 9.6 | 9.4 | 9.1 | 8.8 | 8.5 | 8.1 | 7.3 | 6.5 | 5.9 | 5.3 | 4.7 | 4.2 | 3.5 | 0 | 0
Indian Queens 132 kV | Newquay Trevemper | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.3 | 14.2 | 14 | 13.8 | 13.6 | 13.3 | 12.8 | 12.4 | 11.9 | 11.3 | 10.6 | 10.1 | 9.7 | 9.4 | 9.1 | 8.9 | 8.6 | 6.8 | 4.7
Indian Queens 132 kV | Newquay Trevemper | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.3 | 14 | 13.5 | 12.6 | 11.5 | 10.4 | 9.5 | 8.3 | 7.1 | 5.9 | 4.7 | 3.4 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newquay Trevemper | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.3 | 13.9 | 13.1 | 11.8 | 10.4 | 8.9 | 7.6 | 5.9 | 4 | 2.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Newquay Trevemper | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.3 | 14.2 | 13.8 | 13.4 | 12.7 | 11.9 | 11.3 | 10.4 | 9.5 | 8.5 | 7.4 | 6.6 | 5.9 | 5.3 | 4.8 | 4.2 | 3.5 | 0 | 0
Indian Queens 132 kV | Padstow | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Padstow | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Padstow | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Padstow | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Par Harbour | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 12.8 | 12.6 | 12.3 | 12 | 11.7 | 11.5 | 11.3 | 11.2 | 11.6 | 11.5 | 11.3 | 10.3 | 5.7
Indian Queens 132 kV | Par Harbour | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 11.3 | 6 | 3.3 | 0 | 0 | 0 | 0 | 15.9 | 15.6 | 12.1 | 0 | 0
Indian Queens 132 kV | Par Harbour | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 10.8 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Par Harbour | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 12.7 | 12.4 | 12 | 11.4 | 10.8 | 10.5 | 10.2 | 5 | 19.2 | 18.9 | 18.6 | 15.9 | 0
Indian Queens 132 kV | Penryn | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.8 | 9.5 | 9.3 | 9.1 | 8.9 | 8.7 | 10.5 | 10.4 | 10.3 | 10 | 9.9 | 9.8 | 9.7 | 9.7 | 9.6 | 9.6 | 9.5 | 9.1 | 8.7
Indian Queens 132 kV | Penryn | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.8 | 9.3 | 8.8 | 8.4 | 8 | 7.5 | 9.8 | 9.6 | 9.4 | 9.3 | 9 | 8.8 | 8.6 | 8.4 | 8.2 | 7.9 | 7.7 | 4.1 | 0
Indian Queens 132 kV | Penryn | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.8 | 9.1 | 8.5 | 7.9 | 7.3 | 6.7 | 9.4 | 9.1 | 8.7 | 8.4 | 8.1 | 7.9 | 7.7 | 7.5 | 7.3 | 7 | 6.4 | 0 | 0
Indian Queens 132 kV | Penryn | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.8 | 9.4 | 9.1 | 8.9 | 8.6 | 8.3 | 10.4 | 10.3 | 9.9 | 9.8 | 9.6 | 9.5 | 9.4 | 9.3 | 9.2 | 9.1 | 9 | 8.2 | 7.3
Indian Queens 132 kV | Penzance Causewayhead | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.9 | 11.9 | 11.9 | 11.8 | 11.8 | 11.7 | 11.5 | 11.4 | 11.3 | 11.3 | 11.2 | 11.1 | 10.9 | 10.7 | 11 | 11 | 11 | 10.5 | 8.5
Indian Queens 132 kV | Penzance Causewayhead | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.9 | 11.9 | 11.6 | 11.5 | 11 | 10.2 | 6.7 | 5.7 | 4.8 | 3.3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Penzance Causewayhead | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.9 | 11.8 | 11.5 | 10.9 | 9.6 | 8.3 | 4.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Penzance Causewayhead | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.9 | 11.9 | 11.8 | 11.7 | 11.6 | 11.5 | 11.3 | 11.2 | 11.1 | 10.8 | 10.1 | 9.6 | 8.9 | 8.1 | 10.5 | 10.4 | 9.3 | 3.6 | 0
Indian Queens 132 kV | Penzance Heamoor | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.4 | 11.2 | 10.8 | 10.5 | 10.2 | 9.8 | 16.9 | 15.5 | 15.5 | 15.4 | 14.5 | 13.8 | 13.2 | 12.7 | 15.1 | 15 | 14.9 | 12.8 | 9.1
Indian Queens 132 kV | Penzance Heamoor | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.4 | 10.8 | 10 | 9.2 | 8.3 | 7.5 | 8.4 | 6.7 | 5.2 | 3.6 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Penzance Heamoor | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.4 | 10.6 | 9.5 | 8.4 | 7.2 | 6 | 4.6 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Penzance Heamoor | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.4 | 11.1 | 10.5 | 10.1 | 9.6 | 9 | 15.5 | 15.3 | 14.1 | 12.8 | 11.4 | 10.5 | 9.6 | 8.8 | 12.4 | 11.2 | 10.1 | 3.9 | 0
Indian Queens 132 kV | Perranporth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Perranporth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Perranporth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Perranporth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Polzeath | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Polzeath | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Polzeath | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Polzeath | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Probus 33 | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 1.8 | 1.6 | 1.5 | 1.3 | 1.2 | 1.1 | 1 | 0.9 | 0.9 | 0.8 | 0 | 0
Indian Queens 132 kV | Probus 33 | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 1.1 | 0.8 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Probus 33 | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Probus 33 | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 1.6 | 1.5 | 1.2 | 0.9 | 0.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Rame Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 26.4 | 25.4 | 24.6 | 23.6 | 22.7 | 21.6 | 17.7 | 15.9 | 14.1 | 12.2 | 10.1 | 8.3 | 6 | 5.2 | 7.7 | 7 | 5.4 | 0 | 0
Indian Queens 132 kV | Rame Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 26.4 | 24.5 | 22.7 | 20 | 17.4 | 14.7 | 8.1 | 5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Rame Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 26.4 | 24 | 21.5 | 18 | 14.6 | 10.2 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Rame Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 26.4 | 25.1 | 23.9 | 22.6 | 21.2 | 19.7 | 15 | 12.7 | 10.5 | 6.7 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Redruth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.1 | 8.9 | 8.8 | 8.6 | 7.8 | 7.7 | 7.4 | 7 | 6.7 | 6.3 | 5.8 | 5.4 | 5.1 | 4.9 | 5.3 | 5.2 | 5 | 3.9 | 2.6
Indian Queens 132 kV | Redruth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.1 | 8.8 | 7.8 | 7.3 | 6.6 | 5.8 | 5 | 4.2 | 3.5 | 2.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Redruth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.1 | 8.7 | 7.6 | 6.8 | 5.9 | 4.9 | 3.8 | 2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Redruth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.1 | 8.9 | 8.6 | 7.7 | 7.4 | 6.9 | 6.3 | 5.7 | 5.2 | 4.3 | 3.6 | 3.2 | 2.9 | 2.6 | 2.7 | 2.3 | 1.9 | 0 | 0
Indian Queens 132 kV | Roseland | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 3.1 | 3 | 2.8 | 2.6 | 2.5 | 2.4 | 2.3 | 2.2 | 2.1 | 2 | 1.4 | 0.7
Indian Queens 132 kV | Roseland | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 2.3 | 2 | 1.6 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Roseland | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Roseland | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 2.9 | 2.7 | 2.4 | 2.1 | 1.9 | 1.7 | 1.6 | 1.4 | 1.1 | 0.8 | 0 | 0
Indian Queens 132 kV | Sawles Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.8 | 5.7 | 5.5 | 5.3 | 5.1 | 4.9 | 4.5 | 4.2 | 3.9 | 3.5 | 3.4 | 3 | 2.8 | 2.6 | 2.5 | 2.3 | 2.1 | 1.1 | 0
Indian Queens 132 kV | Sawles Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.8 | 5.4 | 5 | 4.4 | 3.8 | 3.3 | 2.7 | 2.1 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Sawles Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.8 | 5.3 | 4.7 | 3.9 | 3.2 | 2.5 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Sawles Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.8 | 5.6 | 5.3 | 4.9 | 4.6 | 4.2 | 3.7 | 3.3 | 3.1 | 2.3 | 1.7 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Agnes | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Agnes | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Agnes | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Agnes | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Austell | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15 | 15 | 14.8 | 14.6 | 14.4 | 14.2 | 13.7 | 13.3 | 12.9 | 12.5 | 12 | 11.3 | 11 | 10.8 | 10.6 | 10.5 | 10.3 | 9.2 | 5.7
Indian Queens 132 kV | St Austell | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15 | 14.8 | 14.4 | 13.8 | 13.1 | 12.4 | 11.6 | 10.8 | 5 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Austell | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15 | 14.6 | 14.2 | 13.3 | 12.5 | 11.5 | 10.3 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Austell | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15 | 14.9 | 14.7 | 14.3 | 14 | 13.5 | 12.8 | 12.1 | 11.6 | 10.2 | 9.4 | 8.7 | 8.1 | 5 | 7.4 | 7.1 | 6.7 | 3.9 | 0
Indian Queens 132 kV | St Austell Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 20.1 | 18.6 | 16.9 | 15.2 | 13.4 | 11.5 | 10.6 | 10 | 10 | 9.4 | 8.8 | 4.6 | 0
Indian Queens 132 kV | St Austell Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 12.9 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Austell Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Austell Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 17.7 | 15.5 | 13.5 | 10.1 | 7.2 | 5.3 | 0 | 0 | 16.6 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Buryan | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.8 | 4.8 | 4.8 | 4.7 | 4.6 | 4.5 | 4.4 | 4.3 | 4.1 | 4 | 3.8 | 3.6 | 3.6 | 3.5 | 4 | 3.9 | 3.8 | 3.3 | 2.8
Indian Queens 132 kV | St Buryan | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.8 | 4.8 | 4.7 | 4.5 | 4.3 | 4.1 | 3.8 | 3.6 | 3.2 | 2.7 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Buryan | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.8 | 4.7 | 4.6 | 4.3 | 4.1 | 3.8 | 3.2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Buryan | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.8 | 4.8 | 4.7 | 4.7 | 4.6 | 4.5 | 4.3 | 4.1 | 3.9 | 3.7 | 3.5 | 3.3 | 3.2 | 3 | 3.3 | 3.1 | 2.9 | 1.9 | 0
Indian Queens 132 kV | St Columb Major | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.6 | 2.3 | 1.9 | 1.5 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Columb Major | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.6 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Columb Major | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.6 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Columb Major | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.6 | 2.2 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Ives | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.4 | 8.3 | 8.1 | 8.1 | 8 | 7.8 | 13.6 | 13.2 | 12.7 | 12.3 | 11.7 | 11.3 | 11 | 10.8 | 14.2 | 14.1 | 13.9 | 12 | 8.6
Indian Queens 132 kV | St Ives | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.4 | 8.2 | 7.8 | 7.4 | 7.1 | 6.7 | 6.7 | 5.8 | 4.9 | 3.4 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Ives | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.4 | 8.1 | 7.5 | 7 | 6.5 | 5.9 | 4.4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Ives | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.4 | 8.2 | 8.1 | 7.9 | 7.7 | 7.5 | 12.8 | 12.2 | 11.6 | 11 | 10.2 | 9.7 | 9 | 8.2 | 11.6 | 10.5 | 9.5 | 3.6 | 0
Indian Queens 132 kV | St Keverne | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Keverne | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Keverne | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Keverne | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Mawgan | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.6 | 2.3 | 1.9 | 1.5 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Mawgan | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.6 | 2.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Mawgan | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.6 | 1.9 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Mawgan | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.6 | 2.2 | 1.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Tudy | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.5 | 6.4 | 6.4 | 6.2 | 5.9 | 5.6 | 5.1 | 4.5 | 3.9 | 3.2 | 2.4 | 1.8 | 1.4 | 1.2 | 1 | 0.7 | 0 | 0 | 0
Indian Queens 132 kV | St Tudy | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.5 | 6.4 | 6.2 | 5.4 | 4.5 | 3.7 | 2.6 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Tudy | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.5 | 6.3 | 6.2 | 5 | 3.9 | 2.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Tudy | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.5 | 6.4 | 6.3 | 6.1 | 5.7 | 5.3 | 4.6 | 3.9 | 3.1 | 2.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Tudy Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 3 | 2.6 | 1.8 | 0 | 0 | 0 | 4.8 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Tudy Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Tudy Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | St Tudy Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 3 | 2.4 | 1.3 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Trebal | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.8 | 4.7 | 4.6 | 4.4 | 4.1 | 3.7 | 2.8 | 2.2 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Trebal | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.8 | 4.7 | 4.6 | 3.8 | 2.9 | 1.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 1.1 | 0 | 0 | 0
Indian Queens 132 kV | Trebal | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.8 | 4.7 | 4.6 | 3.5 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Trebal | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.8 | 4.7 | 4.6 | 4.3 | 3.8 | 3.3 | 2.1 | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.9 | 1.3 | 0 | 0
Indian Queens 132 kV | Truro Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 33.8 | 33.1 | 32.5 | 31.6 | 30.6 | 29.7 | 18.1 | 17.6 | 17 | 16.3 | 14.3 | 12.1 | 10.9 | 9.9 | 6.4 | 5.4 | 4.4 | 0 | 0
Indian Queens 132 kV | Truro Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 33.8 | 32.3 | 30.8 | 27.8 | 19.2 | 16.1 | 8.5 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 33.8 | 31.9 | 29.8 | 25.9 | 16.4 | 11.7 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 33.8 | 32.9 | 31.8 | 30.5 | 29 | 27.1 | 12.2 | 11.2 | 8.8 | 4.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Shortlanesend | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.9 | 13.5 | 13.2 | 12.8 | 12.3 | 11.8 | 11 | 10 | 9 | 6.5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Shortlanesend | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.9 | 13.1 | 12.3 | 10.6 | 9 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Shortlanesend | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.9 | 12.8 | 11.7 | 9.6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Shortlanesend | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.9 | 13.4 | 12.9 | 12.1 | 11.2 | 10.1 | 8.2 | 4.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Treyew Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 6.1 | 5.8 | 5.4 | 5 | 4.6 | 3.8 | 3.1 | 2.4 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Treyew Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 5.7 | 5 | 3.9 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Treyew Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 5.5 | 4.6 | 3.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Truro Treyew Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 6 | 5.5 | 4.9 | 4.3 | 3.5 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Twelveheads. | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Twelveheads. | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Twelveheads. | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Twelveheads. | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Wadebridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Wadebridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Wadebridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Wadebridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Wheal Reeth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.5 | 1.1 | 0.8 | 0 | 0 | 0 | 4 | 3.9 | 3.8 | 3.7 | 3.5 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Wheal Reeth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 3.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Wheal Reeth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indian Queens 132 kV | Wheal Reeth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.5 | 1 | 0.5 | 0 | 0 | 0 | 3.9 | 3.7 | 3.6 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Abbeywood Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.9 | 8.9 | 8.9 | 8.9 | 8.8 | 8.8 | 8.7 | 8.6 | 8.6 | 8.6 | 8.6 | 8.5 | 8.6 | 8.6 | 8.6 | 8.6 | 8.5 | 8.4 | 7.9
Iron Acton 132 kV | Abbeywood Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.9 | 8.9 | 8.7 | 8.7 | 8.7 | 8.6 | 8.6 | 8.6 | 8.6 | 8.5 | 8.5 | 8.5 | 8.4 | 8.4 | 8.3 | 8.3 | 8.2 | 7.8 | 7.7
Iron Acton 132 kV | Abbeywood Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.9 | 8.8 | 8.7 | 8.6 | 8.7 | 8.7 | 8.6 | 8.5 | 8.5 | 8.4 | 8.3 | 7.8 | 7.8 | 7.7 | 7.7 | 7.7 | 7.7 | 7.6 | 7.3
Iron Acton 132 kV | Abbeywood Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.9 | 8.9 | 8.8 | 8.7 | 8.7 | 8.7 | 8.6 | 8.6 | 8.6 | 8.6 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.4 | 8.2
Iron Acton 132 kV | Almondsbury | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.3 | 11.2 | 11.1 | 10.9 | 10.7 | 10.4 | 11.5 | 10 | 9.5 | 9.1 | 8.5 | 8.2 | 7.9 | 7.8 | 7.6 | 7.5 | 7.3 | 6 | 4.5
Iron Acton 132 kV | Almondsbury | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.3 | 11.1 | 10.8 | 10.1 | 6.3 | 5.5 | 7.4 | 6.5 | 5.7 | 4.9 | 4.1 | 3.2 | 2.4 | 1.6 | 0.7 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Almondsbury | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.3 | 11 | 10.7 | 10.1 | 3.3 | 1.7 | 6.4 | 5 | 3.3 | 1.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Almondsbury | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 11.2 | 10.9 | 10.5 | 10.1 | 6.3 | 8.9 | 8.2 | 7.6 | 6.8 | 5.8 | 5.2 | 4.8 | 4.4 | 4 | 3.6 | 3.2 | 0 | 0
Iron Acton 132 kV | Bedminster | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.4 | 13.3 | 13 | 12.7 | 12.5 | 12.2 | 19.7 | 19.3 | 19 | 18.6 | 18.3 | 18.2 | 18 | 17.8 | 17.7 | 17.6 | 17.5 | 14.5 | 14.1
Iron Acton 132 kV | Bedminster | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.4 | 12.9 | 12.2 | 11.8 | 10.8 | 10.1 | 17.3 | 14.6 | 14.4 | 14.2 | 13.9 | 13.6 | 13.1 | 12.7 | 12.2 | 11.6 | 11.1 | 8.5 | 5.9
Iron Acton 132 kV | Bedminster | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.4 | 12.5 | 11.6 | 10.6 | 9.7 | 9.4 | 14.2 | 13.6 | 13 | 12.3 | 11.7 | 11.2 | 10.6 | 10 | 9.5 | 8.9 | 8.3 | 5.2 | 2
Iron Acton 132 kV | Bedminster | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.4 | 13.1 | 12.7 | 12.4 | 11.8 | 11.1 | 18.2 | 17.7 | 17.3 | 15.1 | 14.5 | 14.4 | 14.3 | 14.2 | 14.1 | 13.9 | 13.7 | 12.2 | 10.4
Iron Acton 132 kV | Bishopsworth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.7 | 10.6 | 10.5 | 10.4 | 10.3 | 10.2 | 10.1 | 10 | 9.9 | 9.8 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 6.9 | 6.2
Iron Acton 132 kV | Bishopsworth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.7 | 10.4 | 10.2 | 10 | 9.8 | 9.7 | 9.4 | 9.4 | 7 | 6.9 | 6.2 | 6.2 | 6.2 | 6.2 | 5.9 | 5.7 | 5.4 | 3.9 | 2.5
Iron Acton 132 kV | Bishopsworth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.7 | 10.3 | 9.9 | 9.7 | 9.5 | 6.9 | 6.9 | 6.3 | 6.2 | 6 | 5.6 | 5.4 | 5.1 | 4.8 | 4.5 | 4.2 | 3.8 | 2 | 0
Iron Acton 132 kV | Bishopsworth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.7 | 10.6 | 10.4 | 10.3 | 10.1 | 10 | 9.8 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 6.9 | 6.9 | 6.9 | 6.8 | 6.2 | 6 | 5.1
Iron Acton 132 kV | Bower Ashton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.2 | 9.8 | 9.7 | 9.6 | 9.4 | 10.2 | 9.9 | 9.7 | 9.5 | 9.2 | 8.9 | 8.8 | 8.6 | 8.5 | 8.4 | 8.3 | 8.3 | 7.6 | 6.8
Iron Acton 132 kV | Bower Ashton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.2 | 9.6 | 9.4 | 9.1 | 8.7 | 9.3 | 8.8 | 8.4 | 8 | 7.6 | 7.2 | 6.8 | 6.4 | 6 | 5.6 | 5.2 | 4.8 | 2.8 | 1.2
Iron Acton 132 kV | Bower Ashton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.2 | 9.5 | 9.1 | 8.7 | 8.3 | 8.7 | 8.1 | 7.5 | 6.9 | 6.3 | 5.8 | 5.4 | 5.1 | 4.7 | 4.3 | 4 | 3.6 | 1.7 | 0
Iron Acton 132 kV | Bower Ashton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.2 | 9.8 | 9.6 | 9.4 | 9.2 | 9.8 | 9.5 | 9.2 | 8.8 | 8.4 | 8.1 | 7.9 | 7.7 | 7.5 | 7.3 | 7.1 | 6.8 | 5.5 | 4.2
Iron Acton 132 kV | Bradley Stoke | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.5 | 9.5 | 9.4 | 9.3 | 9.2 | 9 | 9 | 8.9 | 8.7 | 8.5 | 8.3 | 8.2 | 8.1 | 8 | 7.9 | 7.8 | 7.6 | 4.5 | 3.1
Iron Acton 132 kV | Bradley Stoke | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.5 | 9.4 | 9.2 | 8.9 | 8.5 | 8.3 | 8.2 | 7.9 | 7.7 | 7.3 | 7 | 4.5 | 4.5 | 4.5 | 3.1 | 3.1 | 3.1 | 2.7 | 1.1
Iron Acton 132 kV | Bradley Stoke | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.5 | 9.3 | 9 | 8.7 | 8.3 | 8 | 7.7 | 7.4 | 4.5 | 4.5 | 3.1 | 3.1 | 3.1 | 3 | 3 | 2.9 | 2.9 | 1.6 | 0
Iron Acton 132 kV | Bradley Stoke | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.5 | 9.5 | 9.3 | 9.1 | 8.8 | 8.6 | 8.5 | 8.3 | 8.1 | 7.8 | 7.5 | 7.2 | 7 | 4.5 | 4.5 | 4.5 | 4.5 | 3 | 2.5
Iron Acton 132 kV | Bradley Stoke Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 38.3 | 37.9 | 37.7 | 37.3 | 36.9 | 36.5 | 27.1 | 25.4 | 24.6 | 23.8 | 22.8 | 22 | 21.5 | 21 | 20.5 | 20 | 19.6 | 16.3 | 12.6
Iron Acton 132 kV | Bradley Stoke Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 38.3 | 37.6 | 37 | 35.9 | 30.1 | 29.4 | 20.5 | 16.8 | 12.2 | 7.3 | 4.6 | 2.1 | 0 | 0 | 10 | 8.5 | 6.9 | 0 | 0
Iron Acton 132 kV | Bradley Stoke Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 38.3 | 37.4 | 36.7 | 35.7 | 27.4 | 24.9 | 18.7 | 12.2 | 5.6 | 0 | 0 | 0 | 0 | 5 | 3.8 | 2.6 | 1.4 | 0 | 0
Iron Acton 132 kV | Bradley Stoke Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 38.3 | 37.8 | 37.3 | 36.6 | 35.9 | 33.8 | 21.9 | 18.4 | 15 | 11.4 | 9.5 | 7.8 | 6.3 | 4.9 | 14.8 | 13.9 | 12.9 | 6.1 | 0
Iron Acton 132 kV | Broadweir Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.6 | 10.6 | 10.5 | 10.5 | 10.5 | 10.5 | 4.2 | 4.4 | 4.6 | 4.8 | 4.7 | 4.7 | 4.8 | 4.9 | 5 | 5.1 | 5.2 | 5.6 | 6.2
Iron Acton 132 kV | Broadweir Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.6 | 10.6 | 10.5 | 10.5 | 10.5 | 10.5 | 5.1 | 4.9 | 4.7 | 4.7 | 5 | 5.3 | 5.6 | 5.9 | 6.2 | 6.5 | 6.8 | 7.3 | 7.2
Iron Acton 132 kV | Broadweir Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.6 | 10.6 | 10.5 | 10.5 | 10.6 | 10.3 | 5.8 | 5.9 | 5.8 | 5.9 | 6.3 | 6.7 | 7 | 7.3 | 7.3 | 7.3 | 7.3 | 7.2 | 7.1
Iron Acton 132 kV | Broadweir Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.6 | 10.6 | 10.5 | 10.5 | 10.5 | 10.6 | 4.5 | 4.3 | 3.9 | 3.8 | 4 | 4.2 | 4.4 | 4.5 | 4.7 | 4.8 | 5 | 5.9 | 6.9
Iron Acton 132 kV | Clifton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 21.5 | 21.6 | 21.5 | 21.5 | 21.4 | 21.4 | 20.3 | 20.3 | 20.3 | 19.7 | 19.5 | 19.4 | 19.4 | 19.3 | 21.4 | 21.3 | 21.2 | 20.5 | 19.8
Iron Acton 132 kV | Clifton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 21.5 | 21.5 | 21.5 | 21.5 | 20.9 | 20.5 | 19.2 | 19 | 18.9 | 13.8 | 13.7 | 13.5 | 13.4 | 13.1 | 19 | 19 | 13.7 | 12.7 | 10.9
Iron Acton 132 kV | Clifton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 21.5 | 21.5 | 21.5 | 20.6 | 20.1 | 19.6 | 18.8 | 13.7 | 13.4 | 13 | 12.5 | 12.1 | 11.7 | 11.3 | 13.2 | 12.9 | 12.6 | 10.2 | 7.7
Iron Acton 132 kV | Clifton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 21.5 | 21.6 | 21.5 | 21.5 | 21.4 | 21.4 | 19.7 | 19.5 | 19.2 | 19.1 | 19.1 | 19 | 19 | 19 | 20.2 | 20.1 | 19.9 | 19.1 | 13.6
Iron Acton 132 kV | Cotham Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 7.9 | 7.9 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8
Iron Acton 132 kV | Cotham Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 7.9 | 7.9 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8
Iron Acton 132 kV | Cotham Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 7.9 | 7.9 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 16.6 | 16.6
Iron Acton 132 kV | Cotham Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 7.9 | 7.9 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8
Iron Acton 132 kV | Cribbs Causeway | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.2 | 9.8 | 9.8 | 9.8 | 9.7 | 9.7 | 9.5 | 9.4 | 9.4 | 9.3 | 9.3 | 9.2 | 9.2 | 9.2 | 9.2 | 9.1 | 9.1 | 7.3 | 7.2
Iron Acton 132 kV | Cribbs Causeway | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.2 | 9.7 | 9.7 | 9.6 | 9.5 | 9.5 | 9.3 | 9.2 | 9.1 | 9.1 | 7.3 | 7.3 | 7.2 | 7.2 | 7.1 | 7 | 6.9 | 6.4 | 5.7
Iron Acton 132 kV | Cribbs Causeway | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.2 | 9.7 | 9.7 | 9.6 | 9.5 | 9.4 | 9.2 | 9.1 | 9.1 | 7.3 | 7.3 | 7.2 | 7 | 6.9 | 6.8 | 6.7 | 6.6 | 6.5 | 5.2
Iron Acton 132 kV | Cribbs Causeway | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.2 | 9.7 | 9.8 | 9.7 | 9.7 | 9.6 | 9.4 | 9.3 | 9.3 | 9.2 | 9.1 | 9.1 | 9.1 | 7.3 | 7.3 | 7.3 | 7.2 | 6.9 | 6.4
Iron Acton 132 kV | Eastville | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.3 | 11 | 10.8 | 10.6 | 10.4 | 10.2 | 10 | 9.9 | 9.7 | 9.5 | 9.3 | 9.1 | 9 | 8.9 | 8.8 | 8.6 | 8.5 | 7.6 | 6.6
Iron Acton 132 kV | Eastville | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.3 | 10.6 | 10.2 | 9.8 | 9.5 | 9.2 | 8.9 | 8.6 | 8.5 | 7.8 | 7.4 | 7 | 6.6 | 6.1 | 5.6 | 5.2 | 4.7 | 2.4 | 0
Iron Acton 132 kV | Eastville | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.3 | 10.3 | 9.6 | 9.1 | 8.6 | 7.9 | 7.4 | 6.9 | 6.3 | 5.7 | 5.2 | 4.7 | 4.2 | 3.7 | 3.2 | 2.8 | 2.2 | 0 | 0
Iron Acton 132 kV | Eastville | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 10.9 | 10.6 | 10.4 | 10.1 | 9.9 | 9.7 | 9.5 | 9.2 | 9 | 8.7 | 8.6 | 8.5 | 7.9 | 7.7 | 7.5 | 7.3 | 5.7 | 4.2
Iron Acton 132 kV | Emersons Green | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.3 | 9.3 | 9.3 | 9.3 | 9.2 | 9.1 | 9 | 9 | 8.9 | 8.8 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 7.7 | 7.6
Iron Acton 132 kV | Emersons Green | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.3 | 9.2 | 9 | 8.7 | 7.7 | 7.6 | 7.5 | 7.3 | 7.2 | 7.1 | 6.9 | 6.8 | 6.6 | 6.5 | 6.1 | 4.8 | 6.1 | 5.1 | 0
Iron Acton 132 kV | Emersons Green | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.3 | 9.2 | 8.9 | 8.7 | 7.7 | 7.5 | 7.4 | 7.2 | 6.9 | 6.7 | 6 | 4.6 | 3.3 | 2.1 | 1 | 0 | 5.9 | 0 | 0
Iron Acton 132 kV | Emersons Green | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.3 | 9.3 | 9 | 8.8 | 8.7 | 7.7 | 7.6 | 7.6 | 7.5 | 7.3 | 7.1 | 7.1 | 7 | 6.9 | 6.8 | 6.8 | 6.7 | 6.3 | 5.9
Iron Acton 132 kV | Feeder Rd 11kv | Primary Substation | 11 | Counterfactual | Headroom (MW) | 41.7 | 41.2 | 40.7 | 40.4 | 40 | 39.6 | 43.7 | 43.3 | 42.9 | 42.5 | 42 | 41.8 | 41.5 | 41.4 | 41.2 | 41.1 | 40.9 | 40 | 38.7
Iron Acton 132 kV | Feeder Rd 11kv | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 41.7 | 40.4 | 39.4 | 38.7 | 37.8 | 37.2 | 39.8 | 38.6 | 37.7 | 37.2 | 36.5 | 36 | 35.4 | 34.7 | 34 | 33.3 | 32.6 | 29.2 | 26.1
Iron Acton 132 kV | Feeder Rd 11kv | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 41.7 | 39.8 | 38.5 | 37.4 | 36.8 | 27 | 36.4 | 34.8 | 33.7 | 32.8 | 31.9 | 31.3 | 30.6 | 30 | 29.4 | 28.8 | 28.1 | 24 | 20
Iron Acton 132 kV | Feeder Rd 11kv | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 41.7 | 40.9 | 40.2 | 39.7 | 39 | 38.4 | 42.2 | 41.3 | 40.7 | 40.1 | 39.6 | 39.3 | 39.1 | 38.8 | 38.6 | 38.4 | 38.2 | 36.4 | 34.7
Iron Acton 132 kV | Feeder Road 33kv | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 97.6 | 95.4 | 93.5 | 91.8 | 90.1 | 88.5 | 64.1 | 63.2 | 62.5 | 61.5 | 60.8 | 60.5 | 55.6 | 55.6 | 55.4 | 55.1 | 54.9 | 52.8 | 49.7
Iron Acton 132 kV | Feeder Road 33kv | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 97.6 | 92.5 | 88.8 | 81.3 | 77 | 70.9 | 55 | 53.3 | 51.6 | 50 | 48.1 | 46.5 | 44.7 | 42.9 | 41.2 | 39.6 | 37.9 | 29.8 | 22.5
Iron Acton 132 kV | Feeder Road 33kv | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 97.6 | 90.4 | 81.4 | 76.6 | 70.9 | 62.4 | 51.3 | 48.6 | 45.9 | 43.5 | 41.2 | 39.3 | 37.3 | 35.7 | 34.2 | 32.7 | 31 | 21.6 | 4.7
Iron Acton 132 kV | Feeder Road 33kv | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 97.6 | 94.4 | 91.6 | 89.4 | 87.6 | 76.5 | 61.3 | 60.4 | 55.4 | 54.3 | 53.1 | 52.1 | 51.2 | 50.4 | 49.6 | 48.9 | 48 | 42.8 | 37.6
Iron Acton 132 kV | Feeder Road B | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.5 | 12.6 | 12.5 | 12.5 | 12.5
Iron Acton 132 kV | Feeder Road B | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.5 | 12.6 | 12.5 | 12.5 | 12.5
Iron Acton 132 kV | Feeder Road B | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.5 | 12.6 | 12.5 | 12.5 | 12.2
Iron Acton 132 kV | Feeder Road B | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.5 | 12.6 | 12.5 | 12.5 | 12.5
Iron Acton 132 kV | Filton Dc | Primary Substation | 11 | Counterfactual | Headroom (MW) | 33.9 | 33.9 | 33.7 | 33.5 | 32.5 | 32.3 | 32.5 | 32.4 | 31.3 | 31.2 | 31 | 30.9 | 30.7 | 30.6 | 30.4 | 30.3 | 30.1 | 28.9 | 27
Iron Acton 132 kV | Filton Dc | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 33.9 | 33.5 | 33 | 31.5 | 31 | 30.4 | 30.6 | 30.2 | 29.8 | 29.2 | 28.5 | 27.9 | 27.2 | 26.4 | 25.7 | 24.9 | 28 | 23.9 | 19.9
Iron Acton 132 kV | Filton Dc | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 33.9 | 33.2 | 31.5 | 30.7 | 30 | 29.2 | 29.6 | 28.7 | 27.7 | 26.7 | 25.8 | 25 | 24.2 | 27.2 | 26.5 | 25.7 | 24.8 | 16.3 | 11.6
Iron Acton 132 kV | Filton Dc | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 33.9 | 33.8 | 33.4 | 32.1 | 31.8 | 31.3 | 31.2 | 30.9 | 30.6 | 30.2 | 29.8 | 29.5 | 29.1 | 28.7 | 28.2 | 27.8 | 25.3 | 22.1 | 18.8
Iron Acton 132 kV | Hewlett Packard | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 6.3 | 6.2 | 6 | 5.7 | 5.2 | 10.7 | 10.5 | 10.2 | 10 | 9.8 | 9.6 | 9.3 | 9.2 | 9.1 | 9.1 | 9.1 | 7.2 | 7
Iron Acton 132 kV | Hewlett Packard | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 6.2 | 5.7 | 4.9 | 4.1 | 3 | 9.5 | 9.2 | 9 | 7.1 | 6.7 | 6.3 | 6 | 5.7 | 5.4 | 5 | 4.7 | 3.4 | 2.6
Iron Acton 132 kV | Hewlett Packard | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 6.1 | 5.5 | 4.5 | 3.5 | 2.3 | 9.3 | 9 | 7.3 | 7 | 6.1 | 5.8 | 5.4 | 5.1 | 4.8 | 4.5 | 4.2 | 2.8 | 2
Iron Acton 132 kV | Hewlett Packard | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 6.3 | 6 | 5.4 | 4.8 | 3.9 | 9.7 | 9.3 | 9.1 | 7.3 | 6.9 | 6.6 | 6.3 | 6.1 | 5.8 | 5.6 | 5.3 | 4.1 | 3.4
Iron Acton 132 kV | Keynsham West | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.6 | 9.5 | 9.4 | 9.4 | 9.3 | 9.3 | 8.9 | 8.8 | 8.7 | 8.6 | 8.5 | 8.5 | 8.4 | 8.4 | 8.3 | 8.3 | 8.3 | 7.5 | 7.4
Iron Acton 132 kV | Keynsham West | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.6 | 9.4 | 9.3 | 9.2 | 9.1 | 9 | 8.4 | 7.6 | 7.6 | 7.5 | 7.4 | 7.3 | 7.2 | 7.1 | 7 | 6.9 | 6.7 | 6.1 | 5.5
Iron Acton 132 kV | Keynsham West | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.6 | 9.4 | 9.2 | 9 | 8.9 | 8.9 | 7.5 | 7.4 | 7.2 | 7.1 | 6.9 | 6.7 | 6.5 | 6.4 | 6.4 | 6.2 | 6.1 | 5.4 | 4.8
Iron Acton 132 kV | Keynsham West | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.6 | 9.5 | 9.4 | 9.3 | 9.3 | 9.2 | 8.8 | 8.7 | 8.5 | 8.4 | 8.3 | 7.6 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.3 | 7
Iron Acton 132 kV | Lockleaze | Primary Substation | 11 | Counterfactual | Headroom (MW) | 21.9 | 21.7 | 21.6 | 21.5 | 21.3 | 21.2 | 20.9 | 20.7 | 20.5 | 20.4 | 20.2 | 20.1 | 20 | 20 | 19.9 | 19.9 | 19.9 | 17 | 16.6
Iron Acton 132 kV | Lockleaze | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 21.9 | 21.5 | 21.2 | 20.9 | 20.5 | 20.3 | 19.8 | 19.8 | 17 | 16.9 | 16.7 | 16.5 | 16.2 | 15.8 | 15.5 | 15.1 | 14.7 | 12.8 | 11
Iron Acton 132 kV | Lockleaze | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 21.9 | 21.3 | 20.9 | 20.4 | 20.1 | 20 | 16.9 | 16.6 | 16.1 | 15.6 | 15.2 | 14.8 | 14.4 | 14 | 13.6 | 13.3 | 12.9 | 10.6 | 8.5
Iron Acton 132 kV | Lockleaze | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 21.9 | 21.6 | 21.4 | 21.2 | 21 | 20.7 | 20.3 | 20.1 | 19.9 | 19.8 | 17 | 17 | 16.9 | 16.9 | 16.8 | 16.7 | 16.5 | 15.3 | 14
Iron Acton 132 kV | Lockleaze Bsp 132kv | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 31.6 | 30.9 | 30.5 | 29.9 | 29.2 | 28.3 | 70.8 | 69.7 | 68.7 | 67.5 | 66.3 | 65.4 | 64.5 | 63.9 | 63.4 | 62.9 | 65.2 | 61.6 | 57.8
Iron Acton 132 kV | Lockleaze Bsp 132kv | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 31.6 | 30.1 | 28.7 | 26.8 | 24.9 | 22.8 | 63.4 | 61.4 | 59.5 | 57.3 | 55.2 | 53.4 | 50.3 | 46.7 | 45.3 | 41.8 | 41.3 | 24.2 | 8.5
Iron Acton 132 kV | Lockleaze Bsp 132kv | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 31.6 | 29.7 | 27.8 | 25.4 | 23.1 | 20.4 | 59.9 | 56.9 | 53.3 | 48.3 | 43.1 | 33.6 | 30 | 29.4 | 28.3 | 25 | 24.4 | 8.3 | 0
Iron Acton 132 kV | Lockleaze Bsp 132kv | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 31.6 | 30.6 | 29.5 | 28.2 | 26.9 | 25.2 | 66.5 | 64.8 | 63.3 | 61.3 | 59.1 | 57.7 | 56.6 | 55.6 | 54.5 | 53.5 | 52.2 | 40.6 | 28.4
Iron Acton 132 kV | Mangotsfield | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.8 | 5.6 | 5.4 | 5.3 | 5.1 | 5 | 4.6 | 4.4 | 4.2 | 4 | 3.8 | 3.6 | 3.5 | 3.4 | 3.3 | 3.2 | 6.1 | 5.3 | 4.4
Iron Acton 132 kV | Mangotsfield | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.8 | 5.3 | 5 | 4.6 | 4.3 | 4 | 3.4 | 3.1 | 2.8 | 2.5 | 2.2 | 1.8 | 1.4 | 0.9 | 0 | 0 | 2.5 | 0 | 0
Iron Acton 132 kV | Mangotsfield | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.8 | 5.1 | 4.6 | 4.2 | 3.7 | 3.2 | 2.5 | 1.9 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0
Iron Acton 132 kV | Mangotsfield | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.8 | 5.5 | 5.3 | 5.1 | 4.9 | 4.7 | 4.3 | 4 | 3.8 | 3.5 | 3.2 | 3 | 2.9 | 2.7 | 2.5 | 2.4 | 5.1 | 3.6 | 2.2
Iron Acton 132 kV | Patchway Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.9 | 10.7 | 10.7 | 10.7 | 10.6 | 10.6 | 10.7 | 10.6 | 10.6 | 10.6 | 10.6 | 9.7 | 9.7 | 9.6 | 9.6 | 9.6 | 9.5 | 9.2 | 8.7
Iron Acton 132 kV | Patchway Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.9 | 10.7 | 10.6 | 10.5 | 10.5 | 10.4 | 10.6 | 9.7 | 9.6 | 9.6 | 9.4 | 9.3 | 9.2 | 9 | 8.8 | 8.7 | 8.5 | 7.5 | 6.4
Iron Acton 132 kV | Patchway Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.9 | 10.6 | 10.5 | 10.5 | 10.4 | 9.8 | 9.6 | 9.6 | 9.4 | 9.2 | 9 | 8.8 | 8.6 | 8.4 | 8.3 | 8.1 | 7.8 | 6.6 | 5.3
Iron Acton 132 kV | Patchway Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.9 | 10.7 | 10.7 | 10.6 | 10.6 | 10.5 | 10.6 | 10.6 | 10.6 | 9.7 | 9.6 | 9.5 | 9.4 | 9.3 | 9.2 | 9.1 | 9 | 8.1 | 7.2
Iron Acton 132 kV | Seabank Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 32.1 | 30.9 | 31 | 30.8 | 30.5 | 30 | 28.4 | 27.7 | 26.9 | 25.9 | 25.7 | 25.2 | 24.7 | 24.3 | 23.7 | 22.6 | 21.9 | 18.1 | 12.9
Iron Acton 132 kV | Seabank Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 32.1 | 30.8 | 29.9 | 28.4 | 26.3 | 23.7 | 20.2 | 16.9 | 12.2 | 7.3 | 4.6 | 2.2 | 0 | 0 | 10.8 | 9.1 | 9.9 | 8.2 | 45.6
Iron Acton 132 kV | Seabank Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 32.1 | 30.8 | 29.9 | 28.3 | 26.1 | 23.5 | 18.7 | 12.3 | 5.6 | 0 | 0 | 0 | 0 | 9 | 8.9 | 7.5 | 8.3 | 6.9 | 44.9
Iron Acton 132 kV | Seabank Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 32.1 | 30.8 | 30 | 28.5 | 26.5 | 24.1 | 20.7 | 17.9 | 15.1 | 11.5 | 9.6 | 7.8 | 6.3 | 4.9 | 11.6 | 10.7 | 11.6 | 10.1 | 47.4
Iron Acton 132 kV | St Pauls Bsp 11kv | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 24.3 | 24.4 | 24.5 | 24.5 | 24.4 | 24.3 | 18.8 | 18.2 | 17.8 | 17.2 | 16.6 | 16.3 | 16.1 | 15.9 | 15.7 | 15.5 | 15.3 | 14.3 | 13.1
Iron Acton 132 kV | St Pauls Bsp 11kv | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 24.3 | 24.4 | 24.5 | 23.7 | 22 | 20.3 | 13.4 | 12.1 | 6.1 | 6.1 | 5.9 | 5.8 | 5.5 | 5.2 | 4.9 | 4.5 | 4.1 | 1.8 | 0
Iron Acton 132 kV | St Pauls Bsp 11kv | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 24.3 | 24.4 | 23.9 | 22 | 20.1 | 18.3 | 6.1 | 5.8 | 5.4 | 4.9 | 4.3 | 3.9 | 3.4 | 2.9 | 2.4 | 1.9 | 1.3 | 0 | 0
Iron Acton 132 kV | St Pauls Bsp 11kv | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 24.3 | 24.4 | 24.5 | 24.4 | 23.1 | 21.6 | 14.9 | 13.8 | 13 | 12.3 | 11.8 | 11.6 | 6.1 | 6.1 | 6 | 6 | 5.9 | 5 | 3.7
Iron Acton 132 kV | Western Approach | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Western Approach | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Western Approach | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Western Approach | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Whitchurch | Primary Substation | 11 | Counterfactual | Headroom (MW) | 30.4 | 29.6 | 29.2 | 28.8 | 28.4 | 28.1 | 27.5 | 26.7 | 26.3 | 25.8 | 25.2 | 24.8 | 24.4 | 24 | 23.5 | 23.2 | 23 | 21.7 | 20.1
Iron Acton 132 kV | Whitchurch | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 30.4 | 29 | 28.2 | 27.5 | 25.1 | 24.1 | 23.1 | 22.2 | 21.4 | 20.4 | 19 | 17.8 | 16.6 | 15.6 | 14.7 | 13.8 | 13 | 8.7 | 5.2
Iron Acton 132 kV | Whitchurch | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 30.4 | 28.6 | 27.6 | 26.1 | 24.9 | 23.6 | 22.3 | 21.1 | 19.7 | 18.3 | 16.9 | 15.5 | 14.1 | 13.3 | 12.6 | 11.9 | 11.1 | 6.4 | 2.9
Iron Acton 132 kV | Whitchurch | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 30.4 | 29.4 | 28.8 | 28.2 | 27.6 | 26.5 | 25.8 | 25 | 24.2 | 23.3 | 22.2 | 21.3 | 20.5 | 19.8 | 19.2 | 18.8 | 18.3 | 15.5 | 12.6
Iron Acton 132 kV | Winterbourne | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 3.3 | 3 | 2.8 | 2.5 | 2.3 | 2.1 | 2 | 1.9 | 1.9 | 1.8 | 1.1 | 0
Iron Acton 132 kV | Winterbourne | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 1.3 | 0.8 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Winterbourne | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Winterbourne | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 2.2 | 1.9 | 1.6 | 1.1 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132 kV | Woodland Way | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.9 | 20.6 | 20.1 | 19.5 | 19 | 18.4 | 19.2 | 19 | 18.7 | 18.4 | 18.1 | 17.9 | 17.7 | 17.6 | 17.5 | 17.3 | 17.2 | 16.3 | 14
Iron Acton 132 kV | Woodland Way | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.9 | 19.6 | 18.5 | 17.5 | 16.5 | 15.3 | 17.4 | 17 | 16.7 | 15.6 | 14.9 | 14.2 | 13.3 | 12.2 | 11.2 | 10.2 | 9.2 | 4.4 | 0
Iron Acton 132 kV | Woodland Way | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.9 | 18.9 | 17.2 | 15.6 | 14.3 | 12.6 | 15.1 | 14.2 | 13 | 11.8 | 10.7 | 9.6 | 8.6 | 7.6 | 6.6 | 5.5 | 4.5 | 0 | 0
Iron Acton 132 kV | Woodland Way | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.9 | 20.3 | 19.5 | 18.9 | 18.2 | 17.3 | 18.5 | 18.1 | 17.8 | 17.4 | 17 | 16.8 | 16.7 | 16.5 | 15.6 | 15.1 | 14.7 | 11.6 | 8.4
Landulph 132 kV | Adelaide Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.2 | 10.2 | 10.1 | 10 | 9.9 | 9.8 | 9.7 | 9.4 | 9.2 | 8.8 | 8.7 | 7.4 | 7.4 | 7.3 | 7.3 | 7.3 | 7.2 | 7.1 | 6.9
Landulph 132 kV | Adelaide Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.2 | 10.1 | 9.9 | 9.7 | 9.4 | 9.2 | 8.7 | 7.4 | 7 | 6.4 | 5.8 | 5.4 | 5.3 | 5 | 4.8 | 4.6 | 4.4 | 3.9 | 3.4
Landulph 132 kV | Adelaide Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.2 | 10.1 | 9.8 | 9.5 | 9.2 | 9 | 8.6 | 7.2 | 6.7 | 6 | 5.4 | 4.9 | 4.8 | 4.6 | 4.4 | 4.1 | 3.9 | 3.2 | 2.5
Landulph 132 kV | Adelaide Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.2 | 10.2 | 10 | 9.9 | 9.6 | 9.4 | 8.9 | 8.7 | 7.3 | 6.7 | 6.2 | 5.8 | 5.7 | 5.6 | 5.5 | 5.3 | 5.2 | 4.8 | 4.5
Landulph 132 kV | Alexandra Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.2 | 12.2 | 12.1 | 12 | 11.9 | 11.8 | 12 | 11.9 | 11.7 | 11.5 | 11.3 | 11.2 | 10.7 | 10.7 | 10.7 | 10.6 | 10.6 | 10.4 | 10.2
Landulph 132 kV | Alexandra Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.2 | 12.1 | 11.8 | 11.5 | 11.2 | 10.8 | 11.1 | 10.8 | 10.3 | 9.6 | 9.2 | 8.9 | 8.1 | 7.9 | 7.8 | 7.6 | 7.5 | 6.8 | 6.1
Landulph 132 kV | Alexandra Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.2 | 12 | 11.7 | 11.3 | 10.9 | 10.6 | 10.8 | 10.4 | 9.9 | 9.3 | 8.6 | 8.3 | 7.5 | 7.4 | 7.3 | 7.1 | 7 | 6.2 | 5
Landulph 132 kV | Alexandra Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.2 | 12.2 | 11.9 | 11.7 | 11.4 | 11.1 | 11.4 | 11.1 | 10.7 | 10.1 | 9.6 | 9.4 | 8.7 | 8.6 | 8.6 | 8.5 | 8.5 | 8 | 7.6
Landulph 132 kV | Alma Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.5 | 10.4 | 10.2 | 10.1 | 10 | 9.9 | 9.8 | 9.7 | 9.7 | 9.6 | 9.5 | 9.4 | 9.4 | 9.4 | 9.3 | 9.3 | 9.3 | 9 | 8.5
Landulph 132 kV | Alma Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.5 | 10.1 | 9.9 | 9.7 | 9.5 | 9.3 | 9.2 | 9.1 | 9 | 8.9 | 8.8 | 8.7 | 8.5 | 8.3 | 8.1 | 7.9 | 7.7 | 6.7 | 5.7
Landulph 132 kV | Alma Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.5 | 10 | 9.6 | 9.4 | 9.1 | 8.8 | 8.6 | 8.4 | 8.2 | 8 | 7.8 | 7.7 | 7.5 | 7.3 | 7.2 | 7 | 6.7 | 5.4 | 4.1
Landulph 132 kV | Alma Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.5 | 10.3 | 10.1 | 10 | 9.9 | 9.8 | 9.7 | 9.6 | 9.5 | 9.4 | 9.4 | 9.4 | 9.4 | 9.3 | 9.3 | 9.2 | 9.1 | 8.5 | 7.9
Landulph 132 kV | Armada Street | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 19.3 | 19.2 | 19.2 | 19 | 18.9 | 18.8 | 18.8 | 18.7 | 18.7 | 18.7 | 18.6 | 18.4 | 18.1
Landulph 132 kV | Armada Street | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 18.7 | 18.6 | 18.5 | 18.4 | 18.3 | 18.1 | 18 | 17.9 | 17.7 | 17.7 | 17.6 | 14.8 | 14.2
Landulph 132 kV | Armada Street | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 18.3 | 18.1 | 17.9 | 17.8 | 17.7 | 17.6 | 17.5 | 17.5 | 14.8 | 14.8 | 14.8 | 14 | 13
Landulph 132 kV | Armada Street | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 19.1 | 19 | 18.9 | 18.8 | 18.7 | 18.6 | 18.6 | 18.5 | 18.5 | 18.4 | 18.4 | 17.9 | 17.6
Landulph 132 kV | Buckwell Street | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 9.7 | 9.6 | 9.5 | 9.5 | 9.4 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.2 | 9.1
Landulph 132 kV | Buckwell Street | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.5 | 9.3 | 9.1 | 9 | 9 | 8.9 | 8.9 | 7.3 | 7.3 | 7.3 | 7.3 | 7.1 | 6.8
Landulph 132 kV | Buckwell Street | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.3 | 9.1 | 8.9 | 8.9 | 7.3 | 7.3 | 7.3 | 7.2 | 7.2 | 7.2 | 7.1 | 6.8 | 6.3
Landulph 132 kV | Buckwell Street | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.7 | 9.5 | 9.3 | 9.1 | 9.1 | 9 | 9 | 9 | 9 | 9 | 8.9 | 8.9 | 7.3
Landulph 132 kV | Callington | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Callington | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Callington | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Callington | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Eggbuckland | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.8 | 8.8 | 8.8 | 7.1 | 7.1 | 7 | 7.1 | 7.1 | 7 | 7 | 6.9 | 6.9 | 6.8 | 6.8 | 8.8 | 8.8 | 8.8 | 7.1 | 7
Landulph 132 kV | Eggbuckland | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.8 | 7.1 | 7.1 | 7 | 6.9 | 6.6 | 6.9 | 6.8 | 6.7 | 6.6 | 6.5 | 6.4 | 6.3 | 6.1 | 6.7 | 6.6 | 6.5 | 5.8 | 5.1
Landulph 132 kV | Eggbuckland | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.8 | 7.1 | 7 | 6.9 | 6.1 | 5.1 | 6.5 | 6.3 | 6.1 | 6 | 5.8 | 5.7 | 5.6 | 5.4 | 6.1 | 6 | 5.8 | 5 | 4.1
Landulph 132 kV | Eggbuckland | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.8 | 8.8 | 7.1 | 7.1 | 7 | 7 | 7.1 | 7 | 7 | 6.9 | 6.8 | 6.8 | 6.8 | 6.8 | 7.1 | 7.1 | 7.1 | 6.9 | 6.6
Landulph 132 kV | Elim Terrace | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.7 | 4.6 | 4.5 | 4.4 | 4.4 | 4.3 | 11.9 | 11.9 | 11.8 | 11.8 | 11.8 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.6 | 10
Landulph 132 kV | Elim Terrace | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.7 | 4.5 | 4.3 | 4.2 | 4.1 | 4 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 10 | 10 | 10 | 9.9 | 9.8 | 9.8 | 9.2 | 8.6
Landulph 132 kV | Elim Terrace | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.7 | 4.4 | 4.1 | 3.8 | 3.6 | 3.4 | 10.1 | 10 | 10 | 9.9 | 9.8 | 9.8 | 9.7 | 9.6 | 9.5 | 9.4 | 9.2 | 8.4 | 7.5
Landulph 132 kV | Elim Terrace | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.7 | 4.6 | 4.5 | 4.5 | 4.5 | 4.5 | 11.8 | 11.8 | 11.8 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.6 | 11.6 | 10 | 9.8
Landulph 132 kV | Ernesettle B & S | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.1
Landulph 132 kV | Ernesettle B & S | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.5 | 1.5
Landulph 132 kV | Ernesettle B & S | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 1 | 1 | 1 | 1 | 1 | 0.9
Landulph 132 kV | Ernesettle B & S | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 1.6 | 1.5
Landulph 132 kV | Ernesettle Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 53.3 | 53.1 | 53 | 51.7 | 48.2 | 47.5 | 46.6 | 45.7 | 44.7 | 43.7 | 42.6 | 42 | 40.8 | 40.3 | 39.8 | 39.4 | 39 | 37 | 34.6
Landulph 132 kV | Ernesettle Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 53.3 | 52.8 | 51.4 | 51.1 | 16.8 | 0 | 40.9 | 39.1 | 37.4 | 34.8 | 33 | 31.5 | 29.4 | 27.8 | 25.1 | 23.6 | 14.7 | 0 | 0
Landulph 132 kV | Ernesettle Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 53.3 | 51.5 | 51.1 | 43.4 | 17.5 | 0 | 54.7 | 52.5 | 50.2 | 45.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Ernesettle Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 53.3 | 53 | 51.7 | 51.5 | 46 | 33.2 | 43.6 | 42.1 | 40.6 | 38.5 | 36.7 | 35.7 | 34.3 | 33.6 | 31.6 | 30.9 | 29.9 | 25.3 | 0.7
Landulph 132 kV | Gunnislake | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Gunnislake | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Gunnislake | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Gunnislake | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Ivybridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.1 | 4.9 | 4.7 | 4.3 | 3.9 | 3.4 | 6.5 | 5.9 | 5.1 | 4.4 | 3.4 | 2.9 | 2.4 | 2.2 | 1.9 | 1.7 | 1.5 | 0 | 0
Landulph 132 kV | Ivybridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.1 | 4.6 | 4.1 | 2.9 | 1.7 | 0.5 | 2.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Ivybridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.1 | 4.4 | 3.8 | 2.3 | 0.9 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Ivybridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.1 | 4.8 | 4.5 | 3.9 | 3.3 | 2.6 | 5.5 | 4.5 | 3.4 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Landulph Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Landulph Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Landulph Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Landulph Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Langage | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 1.7 | 1.6 | 1.4 | 1.2 | 1.1 | 1 | 1 | 0.9 | 0.9 | 0.9 | 0.7 | 0
Landulph 132 kV | Langage | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Langage | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Langage | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 1 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Lanreath | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Lanreath | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Lanreath | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Lanreath | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Lifton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Lifton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Lifton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Lifton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Linketty Lane | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.2 | 4.1 | 3.9 | 3.8 | 3.6 | 3.5 | 3 | 2.8 | 2.6 | 2.4 | 2.1 | 2 | 1.9 | 1.8 | 1.7 | 1.6 | 1.6 | 0.9 | 0
Landulph 132 kV | Linketty Lane | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.2 | 3.9 | 3.5 | 3.1 | 2.8 | 2.4 | 1.8 | 1.5 | 1.2 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Linketty Lane | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.2 | 3.7 | 3.3 | 2.7 | 2.3 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Linketty Lane | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.2 | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 2.7 | 2.5 | 2.2 | 2 | 1.7 | 1.5 | 1.4 | 1.2 | 1.1 | 0.9 | 0.7 | 0 | 0
Landulph 132 kV | Liskeard | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Liskeard | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Liskeard | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Liskeard | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Longbridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 2.4 | 2.3 | 2.1 | 2 | 1.9 | 1.9 | 1.9 | 1.8 | 1.8 | 1.8 | 1.5 | 1.1
Landulph 132 kV | Longbridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 1.4 | 1.2 | 0.9 | 0.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Longbridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0.9 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Longbridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 1.9 | 1.7 | 1.4 | 1.2 | 1.1 | 1.1 | 1 | 0.9 | 0.9 | 0.8 | 0 | 0
Landulph 132 kV | Looe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Looe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Looe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Looe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Merrivale | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.6 | 11.4 | 11.3 | 10.3 | 10.2 | 10.1 | 13.5 | 13.3 | 13.2 | 13.1 | 13 | 12.9 | 12.7 | 12.6 | 12.5 | 12.4 | 12.4 | 11.9 | 11.2
Landulph 132 kV | Merrivale | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.6 | 11.2 | 10 | 9.7 | 9.5 | 9.2 | 12.6 | 12.4 | 12.2 | 11.7 | 11.5 | 11.2 | 11 | 10.7 | 10.3 | 10 | 9.7 | 8.1 | 6.7
Landulph 132 kV | Merrivale | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.6 | 10.1 | 9.7 | 9.3 | 8.9 | 8.6 | 11.8 | 11.4 | 11 | 10.6 | 10 | 9.7 | 9.5 | 9.2 | 9 | 8.7 | 8.4 | 6.6 | 5
Landulph 132 kV | Merrivale | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.6 | 11.4 | 10.3 | 10.1 | 10 | 9.8 | 13.2 | 13.1 | 13 | 12.7 | 12.4 | 12.2 | 12.2 | 12.1 | 12 | 11.9 | 11.7 | 10.7 | 9.7
Landulph 132 kV | Milehouse Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 66.3 | 66 | 65.7 | 65.3 | 47.7 | 40.7 | 46.3 | 45.4 | 44.5 | 43.6 | 42.7 | 42.1 | 41.7 | 41.4 | 104.5 | 104.3 | 104.2 | 103.1 | 101.6
Landulph 132 kV | Milehouse Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 66.3 | 65.4 | 64.3 | 47.2 | 14.1 | 0 | 39.7 | 38.1 | 36.8 | 35.5 | 34 | 53.8 | 52.4 | 50.8 | 80.5 | 43.4 | 14.7 | 0 | 0
Landulph 132 kV | Milehouse Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 66.3 | 64.9 | 58.6 | 36.6 | 14.7 | 0 | 35.5 | 33.1 | 30.8 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Milehouse Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 66.3 | 65.9 | 65.2 | 63.4 | 38.7 | 28 | 43.2 | 42 | 40.9 | 39.8 | 38.6 | 58.8 | 58.3 | 57.8 | 102.4 | 102.2 | 101.8 | 68.5 | 0.7
Landulph 132 kV | Modbury | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.1 | 4.9 | 4.7 | 4.3 | 3.9 | 3.4 | 5.3 | 4.9 | 4.4 | 4 | 3.5 | 2.9 | 2.5 | 2.2 | 1.9 | 1.7 | 1.5 | 0 | 0
Landulph 132 kV | Modbury | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.1 | 4.6 | 4.1 | 2.9 | 1.7 | 0.5 | 2.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Modbury | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.1 | 4.4 | 3.8 | 2.3 | 0.9 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Modbury | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.1 | 4.8 | 4.5 | 3.9 | 3.3 | 2.6 | 4.6 | 4.1 | 3.4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Newport Street | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.9 | 8.8 | 8.7 | 8.6 | 8.5 | 8.4 | 28.5 | 28.3 | 28.1 | 28 | 27.9 | 27.8 | 27.8 | 27.7 | 27.7 | 27.7 | 27.6 | 27.4 | 27.1
Landulph 132 kV | Newport Street | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.9 | 8.7 | 8.4 | 8.2 | 8 | 7.8 | 27.7 | 27.3 | 27 | 26.8 | 26.6 | 26.4 | 26.3 | 26.2 | 26.1 | 25.9 | 25.8 | 25.1 | 24.4
Landulph 132 kV | Newport Street | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.9 | 8.6 | 8.2 | 7.9 | 7.7 | 7.5 | 27.3 | 26.8 | 26.5 | 26.2 | 26 | 25.8 | 25.7 | 25.6 | 25.4 | 25.3 | 25.2 | 24.3 | 23.4
Landulph 132 kV | Newport Street | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.9 | 8.8 | 8.6 | 8.4 | 8.2 | 8.1 | 28 | 27.7 | 27.4 | 27.2 | 27.1 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.7 | 26.3 | 25.9
Landulph 132 kV | Newton Ferrers | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5 | 4.8 | 4.6 | 4.2 | 3.8 | 3.4 | 5.3 | 5.3 | 5 | 4.2 | 3.3 | 2.8 | 2.4 | 2.1 | 1.9 | 1.6 | 1.4 | 0 | 0
Landulph 132 kV | Newton Ferrers | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5 | 4.6 | 4.1 | 2.9 | 1.7 | 0.5 | 2.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Newton Ferrers | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5 | 4.4 | 3.8 | 2.3 | 0.9 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Newton Ferrers | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5 | 4.8 | 4.4 | 3.9 | 3.2 | 2.5 | 5.3 | 4.3 | 3.3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Old Laira Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.1 | 9.1 | 9.1 | 9 | 9 | 9 | 9 | 9 | 9 | 8.9 | 8.9 | 8.8 | 8.8
Landulph 132 kV | Old Laira Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.8 | 8.8 | 8.8 | 8.7 | 8.5 | 8.8 | 7.6 | 7.6 | 7.6 | 7.5 | 7.5 | 7 | 6.5
Landulph 132 kV | Old Laira Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.7 | 7.7 | 7.6 | 7.6 | 7.5 | 7.4 | 7.4 | 7.3 | 7.2 | 7.1 | 7 | 6.3 | 5.6
Landulph 132 kV | Old Laira Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 9 | 9 | 9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.8 | 7.6 | 7.5
Landulph 132 kV | Pensilva | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Pensilva | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Pensilva | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Pensilva | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Plymouth 33 (New) | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 17.5 | 17 | 16.4 | 15.8 | 15.2 | 14.8 | 14.6 | 14.4 | 37.5 | 37.3 | 37.1 | 35.7 | 33.7
Landulph 132 kV | Plymouth 33 (New) | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 13.9 | 13 | 12.2 | 11.2 | 10.2 | 31.7 | 30.8 | 29.8 | 29.7 | 28.7 | 14.5 | 0 | 0
Landulph 132 kV | Plymouth 33 (New) | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 11.6 | 10.1 | 8.5 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Plymouth 33 (New) | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15.3 | 14.6 | 13.8 | 12.9 | 34.9 | 34.5 | 34.2 | 34.8 | 34.4 | 33.9 | 30.7 | 0.7
Landulph 132 kV | Plymstock South | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 14.4 | 14.2 | 14.1 | 13.9 | 13.7 | 13.6 | 13.5 | 13.4 | 13.4 | 13.3 | 12.7 | 11.8
Landulph 132 kV | Plymstock South | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 13.3 | 12.8 | 12.4 | 11.9 | 11.3 | 10.7 | 10.3 | 9.8 | 9.3 | 8.8 | 8.3 | 5.8 | 3.7
Landulph 132 kV | Plymstock South | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 12.4 | 11.7 | 10.9 | 10.1 | 9.3 | 8.7 | 8.2 | 7.8 | 7.4 | 7.1 | 6.6 | 4.3 | 2.3
Landulph 132 kV | Plymstock South | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 13.7 | 13.4 | 13 | 12.6 | 12.2 | 12 | 11.8 | 11.6 | 11.4 | 11.2 | 9.6 | 8.1
Landulph 132 kV | Prince Rock | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 10.5 | 10.4 | 10.2 | 10.1 | 10 | 10 | 10 | 9.9 | 9.9 | 9.9 | 9.9 | 9.8 | 9.6
Landulph 132 kV | Prince Rock | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 10.1 | 9.9 | 9.7 | 9.6 | 9.4 | 9.4 | 9.4 | 9.3 | 9.3 | 9.3 | 9.3 | 7.1 | 6.8
Landulph 132 kV | Prince Rock | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.9 | 9.7 | 9.5 | 9.4 | 9.3 | 9.3 | 9.3 | 7.1 | 7.1 | 7.1 | 7.1 | 6.8 | 6.3
Landulph 132 kV | Prince Rock | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 10.3 | 10.1 | 9.9 | 9.8 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.5 | 9.5 | 9.4 | 9.3
Landulph 132 kV | Saltash Dunheved Rd | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Saltash Dunheved Rd | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Saltash Dunheved Rd | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Saltash Dunheved Rd | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Saltash Whity Cross | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Saltash Whity Cross | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Saltash Whity Cross | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Saltash Whity Cross | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Southway | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.9 | 1.9 | 1.8 | 1.7 | 1.6 | 1.4 | 1.2 | 1.1 | 0.9 | 0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Southway | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.9 | 1.8 | 1.6 | 1.4 | 1.3 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Southway | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.9 | 1.7 | 1.5 | 1.3 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Southway | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.9 | 1.8 | 1.7 | 1.6 | 1.5 | 1.2 | 0.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | St Germans Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | St Germans Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | St Germans Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | St Germans Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | St Levan Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.8 | 9.8 | 9.8 | 9.7 | 9.6 | 9.5 | 9.3 | 9.2 | 9.2 | 9.1 | 9.1 | 9.1 | 9 | 9 | 8.9 | 8.9 | 8.9 | 8.7 | 8.6
Landulph 132 kV | St Levan Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.8 | 9.7 | 9.4 | 9.2 | 9 | 8.8 | 8.6 | 8.6 | 8.6 | 7.6 | 7.6 | 7.6 | 7.5 | 7.4 | 7.3 | 7.2 | 7.1 | 6.4 | 5.7
Landulph 132 kV | St Levan Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.8 | 9.6 | 9.2 | 9 | 8.8 | 8.5 | 7.6 | 7.5 | 7.4 | 7.3 | 7.2 | 7.2 | 7 | 6.9 | 6.7 | 6.6 | 6.5 | 5.6 | 4.7
Landulph 132 kV | St Levan Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.8 | 9.8 | 9.6 | 9.4 | 9.2 | 9 | 8.8 | 8.8 | 8.7 | 8.7 | 8.7 | 8.7 | 8.6 | 8.6 | 8.6 | 7.6 | 7.6 | 7.4 | 7.1
Landulph 132 kV | St Neot | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | St Neot | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | St Neot | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | St Neot | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Stentaway | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 17.6 | 17.4 | 17.2 | 16.9 | 16.6 | 16.3 | 16.2 | 16.1 | 16 | 15.9 | 15.8 | 15 | 13.8
Landulph 132 kV | Stentaway | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 15.8 | 15.2 | 14.6 | 13.9 | 13.1 | 12.4 | 11.8 | 11.2 | 10.6 | 10 | 9.4 | 6.4 | 3.9
Landulph 132 kV | Stentaway | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 14.7 | 13.7 | 12.6 | 11.6 | 10.7 | 9.9 | 9.3 | 8.8 | 8.4 | 7.9 | 7.4 | 4.5 | 2.3
Landulph 132 kV | Stentaway | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 16.9 | 16.5 | 16 | 15.4 | 14.7 | 14.3 | 14 | 13.7 | 13.5 | 13.3 | 13 | 11 | 9.1
Landulph 132 kV | Tavistock | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.5 | 6.4 | 6.2 | 6 | 5.8 | 5.7 | 12.8 | 12.7 | 12.5 | 12.3 | 12.1 | 12 | 11.9 | 11.9 | 11.8 | 11.7 | 11.6 | 11.2 | 10.6
Landulph 132 kV | Tavistock | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.5 | 6.1 | 5.7 | 5.3 | 4.8 | 4.3 | 11 | 10.5 | 10.1 | 9.6 | 9.3 | 8.9 | 7.5 | 1.4 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Tavistock | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.5 | 5.9 | 5.4 | 5 | 4.4 | 2.7 | 10.6 | 10 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Tavistock | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.5 | 6.3 | 6 | 5.7 | 5.4 | 5 | 11.8 | 11.4 | 11 | 10.7 | 10.5 | 10.3 | 10.2 | 10 | 9.9 | 2.5 | 0.8 | 0 | 0
Landulph 132 kV | Torpoint Antony | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.6 | 3.4 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torpoint Antony | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torpoint Antony | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torpoint Antony | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.6 | 2.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torpoint Town | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torpoint Town | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torpoint Town | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torpoint Town | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Torycombe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 4.5 | 4.2 | 3.9 | 3.6 | 3.3 | 3.2 | 3.1 | 3.1 | 3 | 2.9 | 2.3 | 1.6
Landulph 132 kV | Torycombe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 3.3 | 2.9 | 2.6 | 2.3 | 1.9 | 1.6 | 1.4 | 1.1 | 0.8 | 0.5 | 0 | 1.2
Landulph 132 kV | Torycombe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 2.7 | 2 | 1.5 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0.5
Landulph 132 kV | Torycombe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 4.2 | 3.9 | 3.6 | 3.1 | 2.9 | 2.7 | 2.6 | 2.5 | 2.3 | 2.2 | 1.1 | 2.7
Landulph 132 kV | Weston Mill | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.7 | 13.6 | 13.6 | 13.5 | 13.5 | 13.5 | 11.2 | 11.2 | 11.1 | 11.1 | 11.1 | 11 | 11 | 11 | 11 | 11 | 10.9 | 10.7 | 10.4
Landulph 132 kV | Weston Mill | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.7 | 13.5 | 13.5 | 11.4 | 11.3 | 11.1 | 10.8 | 10.7 | 10.6 | 10.5 | 10.4 | 10.3 | 10.1 | 9.9 | 9.8 | 9.6 | 9.4 | 8.4 | 7.4
Landulph 132 kV | Weston Mill | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.7 | 13.5 | 11.4 | 11.4 | 11.1 | 10.8 | 10.4 | 10.2 | 10 | 9.7 | 9.5 | 9.4 | 9.3 | 9.1 | 8.9 | 8.7 | 8.5 | 7.3 | 6.1
Landulph 132 kV | Weston Mill | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.7 | 13.6 | 13.5 | 13.5 | 11.4 | 11.3 | 11.1 | 11 | 10.9 | 10.9 | 10.8 | 10.8 | 10.7 | 10.7 | 10.6 | 10.6 | 10.5 | 10 | 9.4
Landulph 132 kV | Yelverton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.5 | 8.4 | 8.3 | 8.3 | 8.3 | 8.1 | 8.1 | 8 | 8 | 7.9 | 7.9 | 7.8 | 7.8 | 7.8 | 7.7 | 7.7 | 7.7 | 7.5 | 7.2
Landulph 132 kV | Yelverton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.5 | 8.3 | 8.1 | 8 | 7.9 | 7.8 | 7.7 | 7.6 | 7.6 | 7.5 | 7.4 | 7.3 | 7.1 | 2.2 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Yelverton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.5 | 8.3 | 8 | 7.9 | 7.7 | 7.6 | 7.4 | 7.3 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Landulph 132 kV | Yelverton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.5 | 8.4 | 8.3 | 8.1 | 8.1 | 8 | 8 | 7.9 | 7.9 | 7.8 | 7.7 | 7.6 | 7.6 | 7.5 | 7.5 | 7.3 | 6.8 | 0 | 0
Melksham 132 kV | Bath (Dolemeads) 132 | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 43.9 | 43.6 | 43.2 | 42.8 | 42.4 | 42.1 | 45.3 | 44.4 | 43.7 | 43 | 42.3 | 41.9 | 41.7 | 40.5 | 39.8 | 39.2 | 38.9 | 36.3 | 34.2
Melksham 132 kV | Bath (Dolemeads) 132 | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 43.9 | 43 | 42.2 | 40.7 | 39.3 | 37.8 | 40 | 38.8 | 37.6 | 36 | 33.8 | 31.5 | 30 | 28.4 | 26.9 | 25.4 | 23.9 | 16 | 10.2
Melksham 132 kV | Bath (Dolemeads) 132 | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 43.9 | 42.7 | 40.5 | 39.7 | 37.5 | 35.5 | 36 | 35.4 | 33.8 | 32.1 | 30 | 26.8 | 23.7 | 23.8 | 22.6 | 21.1 | 19.4 | 10 | 0
Melksham 132 kV | Bath (Dolemeads) 132 | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 43.9 | 43.4 | 42.8 | 42.2 | 40.7 | 39.7 | 42.5 | 41.5 | 40.3 | 39.3 | 36.4 | 35.7 | 34.8 | 34.2 | 33.7 | 33.1 | 32.3 | 26.4 | 21.2
Melksham 132 kV | Batheaston | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.8 | 10.6 | 10.5 | 10.4 | 10.3 | 10.1 | 9.9 | 9.8 | 9.7 | 9.6 | 9.5 | 9.4 | 9.4 | 9.4 | 9.4 | 9.3 | 9.3 | 9.2 | 6.9
Melksham 132 kV | Batheaston | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.8 | 10.4 | 10.1 | 9.9 | 9.7 | 9.5 | 9.2 | 9.1 | 9.1 | 6.9 | 6.9 | 6.9 | 6.8 | 6.7 | 6.6 | 6.4 | 6.3 | 5.4 | 4.5
Melksham 132 kV | Batheaston | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.8 | 10.2 | 9.9 | 9.6 | 9.4 | 9.3 | 7 | 6.9 | 6.7 | 6.5 | 6.3 | 6.1 | 6 | 5.8 | 5.7 | 5.5 | 5.3 | 4.2 | 3.1
Melksham 132 kV | Batheaston | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.8 | 10.6 | 10.4 | 10.2 | 10.1 | 9.9 | 9.7 | 9.5 | 9.4 | 9.4 | 9.3 | 9.3 | 9.3 | 9.2 | 9.2 | 9.2 | 9.2 | 6.9 | 6.7
Melksham 132 kV | Combe Park | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 7.4 | 7.3 | 7.2 | 7.2 | 7.1 | 7 | 7 | 6.9 | 6.8 | 6.7 | 6.7 | 6.6 | 6.6 | 6.6 | 6.5 | 6.5 | 6.5 | 6.4 | 6.2
Melksham 132 kV | Combe Park | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 7.4 | 7.2 | 7.1 | 6.9 | 6.8 | 6.7 | 6.5 | 6.3 | 6.1 | 6 | 5.8 | 5.7 | 5.6 | 5.5 | 5.4 | 5.3 | 5.2 | 4.8 | 6
Melksham 132 kV | Combe Park | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 7.4 | 7.2 | 6.9 | 6.8 | 6.6 | 6.4 | 6.2 | 5.9 | 5.7 | 5.6 | 5.4 | 5.2 | 5.1 | 6.7 | 6.6 | 6.5 | 6.4 | 5.9 | 3.5
Melksham 132 kV | Combe Park | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 7.4 | 7.3 | 7.2 | 7.1 | 7 | 6.9 | 6.8 | 6.6 | 6.5 | 6.4 | 6.2 | 6.2 | 6.1 | 6.1 | 6.1 | 6.1 | 6 | 4.9 | 4.6
Melksham 132 kV | Dorchester St - New | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 12.3 | 12.3 | 12.3 | 12.2 | 12.2 | 12.2 | 11.5 | 11.1 | 11 | 10.9 | 10.8 | 10.8 | 10.7 | 10.5 | 10.2 | 10 | 10 | 9.8 | 9.7
Melksham 132 kV | Dorchester St - New | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 12.3 | 12.3 | 12.3 | 12.1 | 11.8 | 11.4 | 10.4 | 10.1 | 10 | 9.8 | 6.6 | 6.3 | 6.2 | 6 | 5.9 | 5.7 | 5.6 | 4.8 | 3.9
Melksham 132 kV | Dorchester St - New | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 12.3 | 12.3 | 12.3 | 12 | 11.6 | 11.2 | 10.1 | 9.8 | 9.7 | 9.6 | 6.6 | 6.3 | 5.7 | 5.5 | 5.4 | 5.3 | 5.1 | 4.1 | 3
Melksham 132 kV | Dorchester St - New | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 12.3 | 12.3 | 12.3 | 12.3 | 12 | 11.7 | 10.7 | 10.3 | 10.2 | 10.1 | 9.7 | 6.6 | 6.5 | 6.5 | 6.4 | 6.4 | 6.3 | 5.9 | 5.4
Melksham 132 kV | Entry Hill | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 9.8 | 9.8 | 9.7 | 9.6 | 9.5 | 9.4 | 9.2 | 9.2 | 9.1 | 9.1 | 9 | 9 | 7.4 | 7.4 | 7.3 | 7.3 | 7.3 | 7 | 6.6
Melksham 132 kV | Entry Hill | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 9.8 | 9.6 | 9.4 | 9.3 | 9.1 | 9.1 | 7.4 | 7.4 | 7.3 | 7.1 | 6.9 | 6.7 | 6.4 | 6.2 | 6 | 5.7 | 5.5 | 2.8 | 0
Melksham 132 kV | Entry Hill | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 9.8 | 9.5 | 9.3 | 9.1 | 9.1 | 7.2 | 7.2 | 7 | 6.7 | 6.4 | 6.1 | 5.8 | 5.5 | 5.2 | 5 | 4.8 | 3.9 | 0 | 0
Melksham 132 kV | Entry Hill | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 9.8 | 9.7 | 9.6 | 9.4 | 9.3 | 9.2 | 9 | 9 | 9 | 7.4 | 7.3 | 7.2 | 7.1 | 7 | 6.9 | 6.8 | 6.6 | 5.7 | 4.8
Melksham 132 kV | Oldfield Park | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 6.2 | 6.1 | 6 | 5.9 | 5.7 | 5.5 | 5.4 | 5.3 | 5.2 | 5.1 | 4.7 | 4.7 | 4.6 | 4.5 | 4.4 | 4.3 | 4.3 | 3.8 | 3.2
Melksham 132 kV | Oldfield Park | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 6.2 | 5.9 | 5.6 | 5.3 | 4.7 | 4.5 | 4.4 | 4.2 | 4 | 3.8 | 3.5 | 3.2 | 3 | 2.7 | 2.5 | 2.2 | 1.9 | 0.7 | 0
Melksham 132 kV | Oldfield Park | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 6.2 | 5.8 | 5.5 | 5.2 | 4.3 | 4.1 | 3.9 | 3.6 | 3.3 | 2.9 | 2.6 | 2.3 | 2 | 1.7 | 1.5 | 1.2 | 0.9 | 0 | 0
Melksham 132 kV | Oldfield Park | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 6.2 | 6 | 5.8 | 5.5 | 5.2 | 4.8 | 4.7 | 4.7 | 4.5 | 4.3 | 4.1 | 3.9 | 3.7 | 3.6 | 3.5 | 3.3 | 3.2 | 2.2 | 1.3
Melksham 132 kV | Park Street | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.2 | 17.8 | 17.7 | 17.6 | 17.5 | 17.4 | 17.3 | 17.2 | 17.1 | 17 | 16.9 | 16.8 | 16.4 | 15.7
Melksham 132 kV | Park Street | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 7.3 | 7.3 | 7.2 | 7 | 6.8 | 6.6 | 17.2 | 17 | 16.9 | 16.6 | 16.3 | 16.2 | 15.7 | 15.5 | 15.3 | 15.1 | 14.9 | 13.7 | 12.6
Melksham 132 kV | Park Street | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 7.3 | 7.3 | 7 | 6.8 | 6.4 | 6.2 | 16.8 | 16.5 | 16.2 | 15.7 | 15.5 | 15.2 | 15 | 14.7 | 14.5 | 14.2 | 14 | 12.6 | 11.1
Melksham 132 kV | Park Street | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 7.3 | 7.3 | 7.3 | 7.3 | 7 | 6.9 | 17.6 | 17.4 | 17.3 | 17.1 | 16.9 | 16.7 | 16.6 | 16.4 | 16.3 | 16.2 | 15.7 | 15.1 | 14.3
Melksham 132 kV | Twerton | Primary Substation | 6.6 | Counterfactual | Headroom (MW) | 18.2 | 18.2 | 18.1 | 18 | 17.9 | 17.8 | 17.7 | 17.6 | 17.5 | 17.3 | 17.3 | 17.2 | 17.1 | 17.1 | 17 | 17 | 16.3 | 16.2 | 15.9
Melksham 132 kV | Twerton | Primary Substation | 6.6 | Electric Engagement | Headroom (MW) | 18.2 | 18 | 17.9 | 17.7 | 17.5 | 17.2 | 16.3 | 16.3 | 16.2 | 16.1 | 15.9 | 15.7 | 15.5 | 15.3 | 15.2 | 15 | 14.8 | 13.6 | 13
Melksham 132 kV | Twerton | Primary Substation | 6.6 | Holistic Transition | Headroom (MW) | 18.2 | 17.9 | 17.7 | 17.5 | 17.2 | 16.1 | 16.2 | 16.1 | 15.9 | 15.6 | 15.4 | 15.1 | 14.9 | 14.7 | 14.6 | 14.4 | 14.2 | 13 | 10.3
Melksham 132 kV | Twerton | Primary Substation | 6.6 | Hydrogen Evolution | Headroom (MW) | 18.2 | 18.1 | 18 | 17.9 | 17.8 | 17.5 | 17.2 | 17.1 | 17 | 16.3 | 16.2 | 16.1 | 16 | 15.9 | 15.8 | 15.8 | 15.7 | 14.8 | 13.9
Sandford 132 kV | Axbridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Axbridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Axbridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Axbridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Blagdon 33/11kv S/S | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.2 | 5.2 | 5.2 | 5.1 | 5.1 | 5 | 8.9 | 8.6 | 8.4 | 8.1 | 7.8 | 7.6 | 7.5 | 7.4 | 7.3 | 7.2 | 7.1 | 6.4 | 5.7
Sandford 132 kV | Blagdon 33/11kv S/S | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.2 | 5.2 | 5.1 | 5 | 3.9 | 3.7 | 7.9 | 7.5 | 7.1 | 6.7 | 6.3 | 5.9 | 5.5 | 5.1 | 4.7 | 4.3 | 3.3 | 0 | 0
Sandford 132 kV | Blagdon 33/11kv S/S | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.2 | 5.2 | 5.1 | 4 | 3.8 | 3.4 | 7.4 | 6.8 | 6.1 | 5.5 | 4.8 | 4.4 | 3.9 | 3 | 2.4 | 1.8 | 1.1 | 0 | 0
Sandford 132 kV | Blagdon 33/11kv S/S | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.2 | 5.2 | 5.2 | 5.1 | 5 | 5 | 8.7 | 8.4 | 8.1 | 7.7 | 7.2 | 6.9 | 6.7 | 6.5 | 6.3 | 6 | 5.8 | 4.4 | 1.7
Sandford 132 kV | Bournville | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.2 | 8 | 7.8 | 7.4 | 7 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Bournville | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.2 | 7.8 | 7.3 | 5.9 | 4.6 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Bournville | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.2 | 7.6 | 7 | 5.3 | 3.7 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Bournville | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.2 | 7.9 | 7.6 | 7.2 | 6.5 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Cheddar | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Cheddar | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Cheddar | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Cheddar | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Chew Stoke | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 4.1 | 4.1 | 4 | 4 | 3.9 | 3.8 | 3.7 | 3.6 | 3.5 | 3.4 | 3.3 | 3.2 | 3.2 | 3.1 | 3 | 3 | 2.6 | 2.3
Sandford 132 kV | Chew Stoke | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 4 | 4 | 3.9 | 3.7 | 3.6 | 3.4 | 3.2 | 3 | 2.8 | 2.6 | 2.4 | 2.2 | 1.9 | 1.7 | 1.5 | 1.3 | 0 | 0
Sandford 132 kV | Chew Stoke | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 4 | 3.9 | 3.8 | 3.6 | 3.4 | 3.1 | 2.8 | 2.5 | 2.2 | 1.9 | 1.6 | 1.4 | 1.3 | 1.1 | 1 | 0.8 | 0 | 0
Sandford 132 kV | Chew Stoke | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 4.1 | 4 | 4 | 3.9 | 3.8 | 3.7 | 3.6 | 3.5 | 3.3 | 3.1 | 2.9 | 2.8 | 2.7 | 2.6 | 2.4 | 2.3 | 1.6 | 1
Sandford 132 kV | Churchill Bsp 132kv | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Churchill Bsp 132kv | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Churchill Bsp 132kv | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Churchill Bsp 132kv | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Churchill Gate 33/11 | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Churchill Gate 33/11 | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Churchill Gate 33/11 | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Churchill Gate 33/11 | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Compton Martin 33/11kv S/S | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.4 | 2.3 | 2.3 | 2.2 | 2.2 | 2.1 | 1.9 | 1.8 | 1.6 | 1.4 | 1.2 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6 | 0 | 0
Sandford 132 kV | Compton Martin 33/11kv S/S | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.4 | 2.3 | 2.2 | 2 | 1.7 | 1.5 | 1.2 | 0.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Compton Martin 33/11kv S/S | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.4 | 2.3 | 2.2 | 1.9 | 1.6 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Compton Martin 33/11kv S/S | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.4 | 2.3 | 2.3 | 2.2 | 2.1 | 2 | 1.8 | 1.6 | 1.4 | 1.1 | 0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Congresbury | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 3.9 | 3.7 | 3.4 | 3.1 | 2.7 | 2.4 | 1.9 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Congresbury | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 3.7 | 3.3 | 2.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Congresbury | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 3.5 | 3 | 1.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Congresbury | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 3.9 | 3.6 | 3.2 | 2.7 | 2.1 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | East Brent | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.7 | 4.6 | 4.5 | 4.2 | 3.9 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | East Brent | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.7 | 4.5 | 4.3 | 3.3 | 2.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | East Brent | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.7 | 4.5 | 4.2 | 3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | East Brent | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.7 | 4.6 | 4.4 | 4.1 | 3.7 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Lypstone Farm | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.5 | 10.4 | 10.3 | 10.3 | 10.1 | 10 | 10 | 6 | 5.9 | 5.8 | 5.6 | 5.4 | 5.3 | 5 | 4.5 | 4.1 | 3.9 | 2.8 | 1.4
Sandford 132 kV | Lypstone Farm | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.5 | 10.1 | 6.2 | 5.5 | 4.9 | 4.4 | 3.6 | 3 | 2.5 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Lypstone Farm | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.5 | 9.9 | 6.1 | 4.8 | 4.1 | 3.2 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Lypstone Farm | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.5 | 10.3 | 9.7 | 6 | 5.8 | 5.4 | 4.9 | 4.5 | 4 | 3.5 | 2.6 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Nailsea | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.4 | 13.7 | 13.7 | 13.6 | 12.7 | 11.5 | 9.3 | 7.3 | 5.2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Nailsea | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.4 | 13.7 | 13.1 | 10.4 | 7.3 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Nailsea | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.4 | 13.6 | 12.3 | 8.9 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Nailsea | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.4 | 13.7 | 13.6 | 12.9 | 11.5 | 9.8 | 6.6 | 4.1 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Weston Bsp 132kv | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 20.5 | 20.1 | 19.5 | 18.4 | 17.5 | 16.5 | 61 | 59.7 | 58.4 | 57 | 55.4 | 54.2 | 53.4 | 52 | 50.2 | 49.9 | 49.2 | 45.2 | 39.6
Sandford 132 kV | Weston Bsp 132kv | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 20.5 | 19.5 | 17.3 | 13.7 | 11.2 | 8.6 | 51.8 | 49.2 | 46.9 | 44.2 | 39.7 | 35.1 | 31.4 | 27.7 | 25.8 | 22.3 | 15.2 | 0 | 0
Sandford 132 kV | Weston Bsp 132kv | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 20.5 | 19.1 | 16.1 | 11.9 | 8.7 | 5.1 | 46.9 | 42.8 | 38.2 | 33.9 | 29.1 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Weston Bsp 132kv | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 20.5 | 20 | 18.4 | 16.2 | 14.8 | 13.2 | 56.8 | 54.9 | 53.1 | 50.8 | 47.1 | 43.7 | 40.4 | 38.4 | 38.1 | 36.2 | 34.4 | 20.4 | 0
Sandford 132 kV | Weston Central | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.2 | 11.2 | 11.1 | 11.1 | 11.1 | 11 | 10.4 | 10.2 | 10.1 | 9.9 | 9.8 | 9.7 | 9.6 | 9.5 | 9.4 | 9.3 | 9.2 | 8.7 | 8
Sandford 132 kV | Weston Central | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.2 | 11.2 | 11 | 10.8 | 10.5 | 10.2 | 9.5 | 9.2 | 9 | 8.7 | 8.4 | 8 | 7.8 | 7.6 | 7.3 | 7 | 6.7 | 5.3 | 3.9
Sandford 132 kV | Weston Central | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.2 | 11.2 | 10.8 | 10.5 | 10.1 | 9.7 | 8.8 | 8.4 | 8 | 7.6 | 7.3 | 7 | 6.7 | 6.4 | 6.1 | 5.8 | 5.5 | 3.7 | 2
Sandford 132 kV | Weston Central | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.2 | 11.2 | 11.1 | 11.1 | 10.9 | 10.7 | 10 | 9.8 | 9.6 | 9.3 | 9.1 | 9 | 8.8 | 8.7 | 8.6 | 8.4 | 8.3 | 7.2 | 6.2
Sandford 132 kV | Weston Locking Rd | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18 | 17.9 | 14.5 | 14.3 | 14.1 | 13.9 | 13.5 | 13.1 | 12.8 | 12.6 | 12.3 | 12.1 | 11.9 | 11.1 | 10.2 | 9.2 | 8.9 | 8.7 | 7.4
Sandford 132 kV | Weston Locking Rd | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18 | 17.8 | 14.2 | 13.3 | 12.8 | 12.1 | 11.3 | 10.6 | 10.1 | 9.4 | 7.4 | 5.5 | 4.3 | 3.2 | 2.2 | 1.2 | 0 | 0 | 0
Sandford 132 kV | Weston Locking Rd | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18 | 14.5 | 14 | 12.9 | 12 | 11.1 | 10 | 9 | 8.1 | 7.3 | 6.1 | 3.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Weston Locking Rd | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18 | 17.9 | 14.4 | 13.8 | 13.5 | 13 | 12.3 | 11.7 | 11.4 | 10.9 | 9.6 | 8 | 6.4 | 5.7 | 5.1 | 4.4 | 3.9 | 2.7 | 0.6
Sandford 132 kV | Westwick | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Westwick | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Westwick | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Westwick | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Winscombe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Winscombe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Winscombe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandford 132 kV | Winscombe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Avonmouth | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 2.4 | 2.2 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Avonmouth | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Avonmouth | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Avonmouth | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Avonmouth Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 2.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Avonmouth Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Avonmouth Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Avonmouth Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Cairns Road | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.6 | 12.4 | 12.2 | 12 | 11.8 | 11.6 | 11.4 | 11.2 | 11 | 10.8 | 10.5 | 10.4 | 10.2 | 9.9 | 9.6 | 9.2 | 9 | 6.2 | 5.7
Seabank 132 kV | Cairns Road | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.6 | 12.1 | 11.6 | 11.2 | 10.8 | 10.5 | 10.1 | 9.8 | 9.5 | 9.1 | 6.2 | 6 | 5.6 | 5.1 | 4.5 | 3.9 | 3.2 | 0.9 | 0
Seabank 132 kV | Cairns Road | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.6 | 11.7 | 11.1 | 10.5 | 9.9 | 9.4 | 8.9 | 6.3 | 6.1 | 5.7 | 5.2 | 4.3 | 3.3 | 2.5 | 1.9 | 1.4 | 0.9 | 0 | 0
Seabank 132 kV | Cairns Road | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.6 | 12.3 | 12 | 11.7 | 11.5 | 11.3 | 11 | 10.7 | 10.5 | 10.2 | 9.7 | 9.2 | 8.9 | 6.2 | 6.1 | 5.9 | 5.6 | 4.2 | 2.6
Seabank 132 kV | Chewton Mendip | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Chewton Mendip | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 3.6 | 3.5 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Chewton Mendip | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 3.6 | 3.4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Chewton Mendip | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 3.7 | 3.6 | 3.4 | 2.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Clevedon | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.2 | 13 | 12.9 | 12.3 | 12.2 | 12 | 11.8 | 11.5 | 11.2 | 10.9 | 10.5 | 10.3 | 10.1 | 9.9 | 9.7 | 9.5 | 9.4 | 8.3 | 7.2
Seabank 132 kV | Clevedon | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.2 | 12.9 | 12.1 | 11.7 | 11.1 | 10.6 | 10.1 | 9.6 | 9.1 | 8.5 | 7.8 | 7.2 | 6.6 | 6 | 5.5 | 4.9 | 4.3 | 1.3 | 0
Seabank 132 kV | Clevedon | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.2 | 12.3 | 11.8 | 11.2 | 10.5 | 9.7 | 9 | 8.1 | 7.2 | 6.4 | 5.5 | 4.8 | 4.2 | 3.6 | 3.2 | 2.7 | 2.2 | 0 | 0
Seabank 132 kV | Clevedon | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.2 | 13 | 12.3 | 12.2 | 11.9 | 11.6 | 11.2 | 10.8 | 10.4 | 9.9 | 9.3 | 8.8 | 8.5 | 8.2 | 7.9 | 7.6 | 7.3 | 5.2 | 3.3
Seabank 132 kV | Dinder | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Dinder | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3.5 | 3.4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Dinder | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.5 | 3.3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Dinder | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.6 | 3.5 | 3.3 | 2.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Easton-In-Gordano | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.8 | 9.8 | 9.7 | 9.7 | 9.7 | 9.6 | 9.6 | 9.4 | 9.3 | 9.2 | 9 | 8.9 | 8.9 | 8.8 | 8.8 | 8.7 | 8.6 | 8.2 | 7.8
Seabank 132 kV | Easton-In-Gordano | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.8 | 9.7 | 9.7 | 9.6 | 9.4 | 9.2 | 9 | 5.3 | 5 | 4.8 | 4.6 | 4.3 | 4.1 | 3.8 | 3.6 | 3.3 | 3.1 | 1.9 | 1
Seabank 132 kV | Easton-In-Gordano | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.8 | 9.7 | 9.6 | 9.4 | 9.2 | 8.9 | 8.6 | 8.3 | 7.9 | 7.5 | 7.2 | 6.9 | 6.7 | 6.5 | 6.4 | 6.2 | 6 | 5 | 4.3
Seabank 132 kV | Easton-In-Gordano | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.8 | 9.8 | 9.7 | 9.7 | 9.6 | 9.5 | 9.4 | 5.8 | 5.6 | 5.4 | 5.1 | 5 | 4.8 | 4.7 | 4.6 | 4.5 | 4.3 | 3.5 | 2.7
Seabank 132 kV | Evercreech | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2 | 1.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Evercreech | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2 | 1.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Evercreech | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2 | 1.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Evercreech | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2 | 1.6 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Foxhills | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.3 | 11.1 | 10.9 | 10.5 | 10 | 9.4 | 8.3 | 7.3 | 6.2 | 5.2 | 4.1 | 2.3 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Foxhills | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.3 | 10.9 | 10.4 | 8.9 | 7.2 | 5.4 | 3.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Foxhills | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.3 | 10.7 | 10.1 | 8.2 | 6.2 | 4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Foxhills | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 11 | 10.7 | 10.1 | 9.3 | 8.2 | 6.6 | 5.5 | 4.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Gas Lane | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.9 | 7.5 | 7.2 | 7.2 | 7 | 7 | 7 | 6.9 | 6.7 | 6.5 | 6.3 | 6.1 | 6 | 5.9 | 5.8 | 5.7 | 5.6 | 5 | 4.2
Seabank 132 kV | Gas Lane | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.9 | 7.2 | 7.1 | 6.9 | 6.7 | 6.4 | 6.1 | 5.8 | 5.4 | 5.1 | 4.7 | 4.3 | 3.9 | 3.5 | 3.1 | 2.7 | 2.3 | 0 | 0
Seabank 132 kV | Gas Lane | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.9 | 7.2 | 7 | 6.7 | 6.3 | 5.9 | 5.4 | 4.9 | 4.3 | 3.7 | 3.1 | 2.7 | 2.3 | 2 | 1.7 | 1.3 | 1 | 0 | 0
Seabank 132 kV | Gas Lane | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.9 | 7.2 | 7.2 | 7.1 | 7 | 6.9 | 6.7 | 6.5 | 6.2 | 5.9 | 5.6 | 5.3 | 5.1 | 5 | 4.8 | 4.6 | 4.3 | 2.9 | 1.6
Seabank 132 kV | High Littleton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.7 | 10.7 | 10.6 | 9.7 | 9.6 | 9.5 | 9.2 | 8.9 | 8.5 | 8 | 7.5 | 7.1 | 6.8 | 6.7 | 6.5 | 6.3 | 6.1 | 4.9 | 3.5
Seabank 132 kV | High Littleton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.7 | 10.6 | 9.7 | 9.4 | 8.8 | 8.3 | 7.6 | 6.9 | 6.2 | 5.5 | 4.8 | 3.9 | 3.2 | 2.4 | 1.7 | 0.8 | 0 | 0 | 0
Seabank 132 kV | High Littleton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.7 | 9.7 | 9.7 | 9.1 | 8.5 | 7.6 | 6.7 | 5.6 | 4.3 | 3.1 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | High Littleton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.7 | 10.6 | 10.6 | 9.7 | 9.5 | 9.3 | 8.9 | 8.5 | 8 | 7.3 | 6.4 | 5.8 | 5.4 | 5 | 4.6 | 4.1 | 3.7 | 1 | 0
Seabank 132 kV | Keynsham East | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.8 | 9.7 | 9.6 | 9.4 | 9.3 | 9.2 | 9 | 8.9 | 8.8 | 8.7 | 8.6 | 7.8 | 7.8 | 7.5 | 7 | 6.4 | 6.3 | 5.8 | 5.4
Seabank 132 kV | Keynsham East | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.8 | 9.6 | 9.3 | 9 | 8.7 | 8.6 | 7.8 | 7.7 | 7.5 | 7.2 | 5.9 | 4.8 | 4.2 | 3.6 | 3.1 | 2.6 | 1.1 | 0 | 0
Seabank 132 kV | Keynsham East | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.8 | 9.5 | 9.1 | 8.8 | 8.6 | 7.7 | 7.4 | 7 | 6.6 | 6.2 | 5.5 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Keynsham East | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.8 | 9.7 | 9.5 | 9.3 | 9.1 | 8.9 | 8.7 | 8.6 | 8.6 | 7.8 | 7.1 | 6.1 | 5.2 | 4.8 | 4.5 | 4.3 | 4 | 2.7 | 0
Seabank 132 kV | Kingsweston | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.9 | 1.4 | 1.2 | 0.9 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Kingsweston | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Kingsweston | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Kingsweston | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.9 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Midsomer Norton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.2 | 3.9 | 3.7 | 3.5 | 3.3 | 3.1 | 2.5 | 2.2 | 1.9 | 1.6 | 1.2 | 0.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Midsomer Norton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.2 | 3.6 | 3.2 | 2.6 | 2.2 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Midsomer Norton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.2 | 3.5 | 2.9 | 2.3 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Midsomer Norton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.2 | 3.8 | 3.5 | 3.2 | 2.9 | 2.7 | 2 | 1.6 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Newbury | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.7 | 5.6 | 5.3 | 5 | 4.6 | 3.8 | 3.1 | 2.3 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Newbury | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.6 | 5.4 | 4.3 | 3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Newbury | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.5 | 5.2 | 3.9 | 2.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Newbury | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.7 | 5.5 | 5.2 | 4.6 | 3.9 | 2.9 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Paulton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.6 | 7.5 | 7.5 | 7.4 | 7.3 | 7.3 | 7.2 | 7.1 | 7 | 6.5 | 6.4 | 6.3 | 6.3 | 6.2 | 6.2 | 6.1 | 6.1 | 5.8 | 5.4
Seabank 132 kV | Paulton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.6 | 7.4 | 7.4 | 7.2 | 7.1 | 6.4 | 6.4 | 6.2 | 5.9 | 5.7 | 5.5 | 5.3 | 5.1 | 4.4 | 3.2 | 2 | 0.6 | 0 | 0
Seabank 132 kV | Paulton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.6 | 7.4 | 7.3 | 7.1 | 6.4 | 6.3 | 6.2 | 5.8 | 5.3 | 5 | 4.7 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Paulton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.6 | 7.5 | 7.4 | 7.3 | 7.2 | 7.2 | 7.1 | 6.5 | 6.3 | 6.2 | 6 | 5.8 | 5.7 | 5.6 | 5.5 | 5.4 | 5.3 | 1.7 | 0
Seabank 132 kV | Peasedown | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.8 | 4.8 | 4.8 | 4.2 | 4.1 | 4 | 3.8 | 3.6 | 3.3 | 3 | 2.6 | 2.3 | 2.1 | 2 | 1.9 | 1.8 | 1.7 | 0.8 | 0
Seabank 132 kV | Peasedown | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.8 | 4.8 | 4.2 | 3.9 | 3.4 | 3 | 2.5 | 2.1 | 1.6 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Peasedown | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.8 | 4.2 | 4.2 | 3.7 | 3.1 | 2.5 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Peasedown | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.8 | 4.8 | 4.8 | 4.2 | 4 | 3.8 | 3.5 | 3.2 | 2.8 | 2.3 | 1.7 | 1.3 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Portishead Ashlands | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.9 | 9.8 | 9.7 | 9.7 | 9.6 | 9.5 | 9.5 | 9.4 | 9.3 | 9.2 | 9.1 | 9.1 | 9.1 | 9 | 8.9 | 8.9 | 8.8 | 8.6 | 8.4
Seabank 132 kV | Portishead Ashlands | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.9 | 9.7 | 9.6 | 9.5 | 9.3 | 9.2 | 9.1 | 9 | 8.8 | 8.7 | 8.5 | 8.4 | 8 | 8 | 7.9 | 7.7 | 7.6 | 7 | 6.5
Seabank 132 kV | Portishead Ashlands | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.9 | 9.6 | 9.5 | 9.3 | 9.2 | 9 | 8.8 | 8.6 | 8.5 | 8.3 | 8 | 7.8 | 7.6 | 7.5 | 7.4 | 7.3 | 7.2 | 6.5 | 5.8
Seabank 132 kV | Portishead Ashlands | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.9 | 9.8 | 9.7 | 9.6 | 9.5 | 9.4 | 9.3 | 9.2 | 9.1 | 9 | 8.8 | 8.7 | 8.6 | 8.5 | 8.5 | 8.4 | 8.4 | 7.8 | 7.4
Seabank 132 kV | Portishead New Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 14.9 | 14.4 | 13.9 | 13.3 | 12.7 | 12.1 | 11.3 | 10.4 | 9.5 | 8.5 | 6.5 | 5 | 4 | 3 | 2.1 | 1.1 | 0 | 0 | 0
Seabank 132 kV | Portishead New Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 14.9 | 13.7 | 12.7 | 11.3 | 9.8 | 8.3 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Portishead New Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 14.9 | 13.2 | 11.9 | 10.1 | 8.1 | 5.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Portishead New Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 14.9 | 14.2 | 13.5 | 12.9 | 12 | 10.9 | 9.8 | 5 | 3.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Radstock Bsp 132kv | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 48.1 | 45.7 | 40.5 | 38.5 | 36.4 | 33.8 | 22.2 | 18.5 | 14.5 | 10.4 | 5.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Radstock Bsp 132kv | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 48.1 | 44.5 | 42.2 | 35.6 | 26.4 | 19.1 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Radstock Bsp 132kv | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 48.1 | 43.8 | 40.7 | 32.6 | 24 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Radstock Bsp 132kv | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 48.1 | 45.4 | 43.8 | 41.3 | 37.9 | 33.8 | 20.2 | 15.5 | 10.4 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Shepton Mallet | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 5.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Shepton Mallet | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 5 | 4.3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Shepton Mallet | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 4.8 | 3.9 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Shepton Mallet | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 5.1 | 4.7 | 3.9 | 2.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seabank 132 kV | Stoke Bishop | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.1 | 10 | 9.9 | 9.8 | 9.7 | 9.6 | 9.5 | 9.3 | 9.2 | 9.1 | 8.9 | 8.8 | 8.7 | 8.7 | 8.6 | 8.5 | 8.5 | 7.1 | 6.8
Seabank 132 kV | Stoke Bishop | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.1 | 9.9 | 9.7 | 9.5 | 9.3 | 9.1 | 8.8 | 8.6 | 8.5 | 7.2 | 7.1 | 7 | 6.9 | 6.7 | 6.5 | 6.2 | 6 | 4.8 | 3.6
Seabank 132 kV | Stoke Bishop | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.1 | 9.7 | 9.4 | 9.1 | 8.9 | 8.6 | 7.2 | 7.1 | 6.9 | 6.6 | 6.3 | 6.1 | 5.8 | 5.6 | 5.4 | 5.1 | 4.9 | 3.5 | 2.2
Seabank 132 kV | Stoke Bishop | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.1 | 10 | 9.9 | 9.7 | 9.6 | 9.5 | 9.3 | 9.1 | 9 | 8.8 | 8.6 | 8.5 | 8.4 | 7.1 | 7.1 | 7.1 | 7 | 6.4 | 5.6
Seabank 132 kV | Weston-In-Gordano | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5 | 5 | 5 | 5 | 5 | 4 | 9.7 | 9.7 | 9.6 | 9.4 | 9.3 | 9.2 | 9.1 | 9 | 9 | 8.9 | 8.9 | 8.4 | 7.9
Seabank 132 kV | Weston-In-Gordano | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5 | 5 | 5 | 4 | 3.9 | 3.7 | 9.3 | 9 | 8.8 | 8.6 | 8.3 | 8.1 | 7.9 | 7.6 | 6.9 | 6.1 | 5.2 | 1.3 | 0
Seabank 132 kV | Weston-In-Gordano | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5 | 5 | 4 | 4 | 3.8 | 3.5 | 8.9 | 8.5 | 8.1 | 7.7 | 7 | 6.1 | 5.2 | 4.4 | 3.8 | 3.2 | 2.4 | 0 | 0
Seabank 132 kV | Weston-In-Gordano | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5 | 5 | 5 | 5 | 4 | 4 | 9.6 | 9.5 | 9.3 | 9.1 | 8.9 | 8.7 | 8.6 | 8.4 | 8.3 | 8.2 | 8 | 6.5 | 3.7
Taunton 132 kV | Alcombe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.3 | 3.1 | 2.8 | 2.5 | 2.2 | 1.5 | 2.6 | 2.4 | 2 | 1.6 | 1.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Alcombe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.3 | 2.9 | 2.2 | 0.7 | 0 | 0 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Alcombe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.3 | 2.7 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Alcombe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.3 | 3 | 2.6 | 2.3 | 1.6 | 0.5 | 2 | 1.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Bowhays Cross | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.7 | 4.7 | 4.6 | 4.4 | 4.1 | 3.7 | 3.1 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Bowhays Cross | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.7 | 4.7 | 4.4 | 3.3 | 2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Bowhays Cross | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.7 | 4.6 | 4.2 | 2.8 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Bowhays Cross | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.7 | 4.7 | 4.6 | 4.2 | 3.7 | 2.9 | 1.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Bowhays Cross Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 21.7 | 21.3 | 20.5 | 19.1 | 17.5 | 15.6 | 10 | 7 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Bowhays Cross Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 21.7 | 20.7 | 18.9 | 13.8 | 8.5 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Bowhays Cross Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 21.7 | 20.4 | 17.9 | 11.7 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Bowhays Cross Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 21.7 | 21.1 | 19.9 | 18.2 | 15.8 | 12.9 | 6.3 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Culmhead | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 4.1 | 4 | 3.9 | 3.8 | 3.7 | 3.4 | 3.2 | 2.9 | 2.6 | 2.3 | 2 | 1.8 | 1.7 | 1.6 | 1.5 | 1.4 | 0.5 | 0
Taunton 132 kV | Culmhead | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 4.1 | 3.9 | 3.5 | 3.1 | 2.7 | 2.2 | 1.8 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Culmhead | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 4 | 3.8 | 3.3 | 2.8 | 2.1 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Culmhead | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 4.1 | 4 | 3.9 | 3.7 | 3.5 | 3.1 | 2.8 | 2.5 | 2.1 | 1.5 | 1.2 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Exebridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 3.7 | 3.7 | 3.4 | 2.9 | 2.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Exebridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 3.7 | 3.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Exebridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 3.7 | 3.4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Exebridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 3.7 | 3.6 | 3.3 | 2.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Holford | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Holford | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Holford | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Holford | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Luckwell Bridge | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 3.9 | 3.5 | 2.9 | 2.3 | 1.5 | 3.8 | 3.1 | 2.3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Luckwell Bridge | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 3.6 | 2.6 | 0.7 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Luckwell Bridge | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 3.4 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Luckwell Bridge | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 3.8 | 3.2 | 2.5 | 1.6 | 0 | 3.2 | 2.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Lydeard St Lawrence Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2 | 1.9 | 1.8 | 1.5 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Lydeard St Lawrence Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2 | 1.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Lydeard St Lawrence Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2 | 1.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Lydeard St Lawrence Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2 | 1.9 | 1.7 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Periton | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 3.9 | 3.5 | 2.9 | 2.3 | 1.5 | 5.3 | 5 | 4.7 | 4.4 | 4 | 3.8 | 3.6 | 3.5 | 3.4 | 3.2 | 2.8 | 0 | 0
Taunton 132 kV | Periton | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 3.6 | 2.6 | 0.7 | 0 | 0 | 4 | 3.6 | 2.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Periton | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 3.4 | 2.1 | 0 | 0 | 0 | 3.4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Periton | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 3.8 | 3.2 | 2.5 | 1.6 | 0 | 5 | 4.7 | 4.3 | 3.8 | 3.3 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Priorswood | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.4 | 12.9 | 12.8 | 12.7 | 12.5 | 12.3 | 12.3 | 11.4 | 10.5 | 9.6 | 8.4 | 7.6 | 7 | 6.7 | 6.3 | 5.9 | 5.5 | 0 | 0
Taunton 132 kV | Priorswood | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.4 | 12.8 | 12.5 | 12 | 10.9 | 9.4 | 8.1 | 6.3 | 4.7 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Priorswood | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.4 | 12.7 | 12.3 | 11.4 | 9.9 | 8.2 | 6.5 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Priorswood | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.4 | 12.9 | 12.7 | 12.4 | 12.1 | 11.4 | 10.4 | 9 | 7.5 | 6.1 | 4.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Staplegrove | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.1 | 5.7 | 5.5 | 5.3 | 5.1 | 4.8 | 4.3 | 3.6 | 3 | 2.3 | 1.6 | 1.1 | 0.9 | 0.7 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Staplegrove | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.1 | 5.4 | 5.1 | 4.5 | 3.6 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Staplegrove | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.1 | 5.3 | 4.9 | 4 | 2.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Staplegrove | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.1 | 5.6 | 5.4 | 5.1 | 4.3 | 3.5 | 2.5 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Taunton Local | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.5 | 9.5 | 9.4 | 9.3 | 9.1 | 8.9 | 8.4 | 8 | 7.6 | 7.2 | 6.7 | 6.5 | 6.2 | 6.1 | 6.1 | 6 | 5.9 | 5.2 | 4.6
Taunton 132 kV | Taunton Local | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.5 | 9.4 | 8.9 | 8.6 | 8.2 | 7.4 | 6.5 | 6 | 5.3 | 4.6 | 3.8 | 3.3 | 2.8 | 2.5 | 2.1 | 1.8 | 1.4 | 0 | 0
Taunton 132 kV | Taunton Local | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.5 | 9.2 | 8.6 | 8.1 | 7.5 | 6.7 | 5.8 | 5.1 | 4.2 | 3.4 | 2.5 | 2 | 1.4 | 1 | 0.7 | 0 | 0 | 0 | 0
Taunton 132 kV | Taunton Local | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.5 | 9.5 | 9.3 | 9.1 | 8.7 | 8.1 | 7.3 | 6.8 | 6.1 | 5.3 | 4.8 | 4.4 | 4.1 | 4 | 3.8 | 3.7 | 3.5 | 2.3 | 1.2
Taunton 132 kV | Taunton Main Bsp | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 109.5 | 108 | 106.9 | 104.9 | 102.4 | 99.5 | 88.5 | 84.3 | 79.7 | 74.9 | 69 | 65.8 | 63.4 | 61.7 | 60.2 | 58.6 | 56.9 | 44.3 | 30.5
Taunton 132 kV | Taunton Main Bsp | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 109.5 | 106.9 | 103.5 | 96 | 86.4 | 77.1 | 65.4 | 56.4 | 47.7 | 39.7 | 31 | 23.7 | 16.1 | 7.6 | 1.4 | 0 | 0 | 0 | 0
Taunton 132 kV | Taunton Main Bsp | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 109.5 | 106 | 101.5 | 92.2 | 82 | 70.5 | 56.8 | 43.8 | 27.1 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Taunton Main Bsp | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 109.5 | 107.7 | 105.8 | 102.3 | 97.5 | 91.8 | 80.6 | 74.3 | 66.8 | 58.6 | 49.2 | 44.3 | 39.8 | 34.9 | 32.5 | 24.5 | 18.4 | 0 | 0
Taunton 132 kV | Trull | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.9 | 7.8 | 7.5 | 7.1 | 6.7 | 6.2 | 5.6 | 5 | 4.3 | 3.5 | 2.6 | 1.9 | 1.5 | 1.1 | 0.8 | 0.6 | 0 | 0 | 0
Taunton 132 kV | Trull | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.9 | 7.4 | 6.7 | 5.5 | 4.3 | 3.2 | 2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Trull | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.9 | 7.2 | 6.3 | 4.9 | 3.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Trull | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.9 | 7.6 | 7.1 | 6.5 | 5.7 | 4.9 | 4 | 3.1 | 2.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wellington Primary | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wellington Primary | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wellington Primary | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wellington Primary | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wellington Town | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wellington Town | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wellington Town | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wellington Town | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wiveliscombe | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.2 | 5.1 | 5 | 4.6 | 4.1 | 3.6 | 2.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wiveliscombe | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.2 | 5 | 4.7 | 3.2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wiveliscombe | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.2 | 5 | 4.6 | 2.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taunton 132 kV | Wiveliscombe | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.2 | 5.1 | 4.9 | 4.4 | 3.7 | 2.9 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Fault Level Contribution
[6 empty] | Break contribution (kA) | [17 empty] | Make contribution (kA)
Licence Area | Associated GSP | Substation | Supply Level | Voltage Level (kV) | Scenario | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050
South West | Abham 132 kV | Ashburton | Primary Substation | 11 | Counterfactual | 0.32778 | 0.3692 | 0.44593 | 0.53654 | 0.63392 | 0.76966 | 0.9447 | 1.1566 | 1.3449 | 1.5508 | 1.7537 | 2.0162 | 2.2125 | 2.3996 | 2.5642 | 2.7093 | 3.142 | 3.4061 | 0.78975 | 0.87864 | 1.0449 | 1.2405 | 1.4522 | 1.7461 | 2.1265 | 2.5845 | 2.9948 | 3.4484 | 3.8923 | 4.4838 | 4.9058 | 5.3041 | 5.6534 | 5.9604 | 6.901 | 7.5039
South West | Abham 132 kV | Ashburton | Primary Substation | 11 | Electric Engagement | 0.36331 | 0.44823 | 0.62376 | 0.82041 | 1.0252 | 1.2791 | 1.5881 | 1.947 | 2.41 | 2.7361 | 9.346 | 9.5678 | 9.7783 | 9.995 | 10.1881 | 10.3586 | 10.911 | 11.3016 | 0.86856 | 1.0529 | 1.4471 | 1.8857 | 2.3409 | 2.8998 | 3.5759 | 4.3541 | 5.409 | 6.1334 | 22.5744 | 23.0815 | 23.5619 | 24.057 | 24.4989 | 24.8916 | 26.1749 | 27.1125
South West | Abham 132 kV | Ashburton | Primary Substation | 11 | Holistic Transition | 0.35554 | 0.42585 | 0.58568 | 0.76076 | 0.95529 | 1.2002 | 1.5161 | 1.8955 | 2.266 | 2.7627 | 9.3703 | 9.653 | 9.9323 | 10.1838 | 10.4048 | 10.5633 | 11.0126 | 11.2572 | 0.85699 | 1.0159 | 1.3858 | 1.788 | 2.237 | 2.793 | 3.511 | 4.3714 | 5.219 | 6.3776 | 22.8098 | 23.433 | 24.0484 | 24.5964 | 25.078 | 25.4298 | 26.4618 | 27.0277
South West | Abham 132 kV | Ashburton | Primary Substation | 11 | Hydrogen Evolution | 0.3391 | 0.39296 | 0.49076 | 0.6114 | 0.74335 | 0.92967 | 1.1651 | 1.4355 | 1.7998 | 2.1779 | 2.4695 | 2.7351 | 2.9799 | 3.2245 | 3.4397 | 3.5888 | 4.0129 | 4.3739 | 0.81485 | 0.93216 | 1.1466 | 1.412 | 1.7038 | 2.1148 | 2.6332 | 3.2226 | 4.0554 | 4.9192 | 5.5639 | 6.1453 | 6.676 | 7.2088 | 7.6775 | 8.0097 | 9.0027 | 9.8528
South West | Abham 132 kV | Barton. | Primary Substation | 11 | Counterfactual | 0.28975 | 0.37952 | 0.48856 | 0.6033 | 0.73154 | 0.88395 | 1.0478 | 1.2928 | 1.5001 | 1.7198 | 1.9499 | 2.171 | 2.4136 | 2.6562 | 2.8949 | 3.132 | 3.9299 | 4.2159 | 0.66148 | 0.85134 | 1.0801 | 1.3208 | 1.5894 | 1.9075 | 2.2492 | 2.7535 | 3.184 | 3.6406 | 4.1175 | 4.5725 | 5.0695 | 5.5663 | 6.0549 | 6.5401 | 8.1928 | 8.8154
South West | Abham 132 kV | Barton. | Primary Substation | 11 | Electric Engagement | 0.39541 | 0.59284 | 0.84801 | 1.1247 | 1.4388 | 1.7862 | 2.1885 | 2.7183 | 3.1629 | 3.538 | 3.8811 | 4.0019 | 4.1093 | 4.2193 | 4.3326 | 4.4393 | 4.9382 | 5.3696 | 0.89638 | 1.3168 | 1.8552 | 2.4378 | 3.0963 | 3.8222 | 4.6574 | 5.7464 | 6.6655 | 7.4461 | 8.1646 | 8.433 | 8.6743 | 8.9217 | 9.1752 | 9.4157 | 10.5401 | 11.5138
South West | Abham 132 kV | Barton. | Primary Substation | 11 | Holistic Transition | 0.37311 | 0.52157 | 0.70401 | 0.89596 | 1.1196 | 1.3753 | 1.6549 | 2.0286 | 2.3688 | 2.7304 | 3.1214 | 3.4921 | 3.8523 | 4.1853 | 4.4989 | 4.6903 | 5.2622 | 5.7014 | 0.86381 | 1.1938 | 1.5941 | 2.0141 | 2.5006 | 3.0526 | 3.6518 | 4.4404 | 5.1622 | 5.9264 | 6.7468 | 7.5223 | 8.2759 | 8.9724 | 9.6294 | 10.0424 | 11.3313 | 12.3332
South West | Abham 132 kV | Barton. | Primary Substation | 11 | Hydrogen Evolution | 0.32216 | 0.43732 | 0.58541 | 0.74692 | 0.9312 | 1.1475 | 1.3932 | 1.7304 | 2.037 | 2.3706 | 2.7259 | 3.0562 | 3.3696 | 3.6668 | 3.9412 | 4.0892 | 4.4846 | 4.8073 | 0.7337 | 0.98017 | 1.293 | 1.6345 | 2.0238 | 2.4791 | 2.9928 | 3.6881 | 4.3263 | 5.0199 | 5.755 | 6.4346 | 7.0791 | 7.6915 | 8.2581 | 8.5716 | 9.4515 | 10.1752
South West | Abham 132 kV | Blackawton | Primary Substation | 11 | Counterfactual | 0.066443 | 0.07324 | 0.084587 | 0.097021 | 0.112 | 0.13987 | 0.16984 | 0.2087 | 0.24254 | 0.27936 | 0.314 | 0.3439 | 0.37407 | 0.4053 | 0.43439 | 0.46398 | 0.6085 | 0.72371 | 0.15811 | 0.17265 | 0.19802 | 0.22585 | 0.25949 | 0.31986 | 0.38569 | 0.47018 | 0.54447 | 0.6268 | 0.70232 | 0.76628 | 0.82974 | 0.89591 | 0.9569 | 1.0188 | 1.3291 | 1.5812
South West | Abham 132 kV | Blackawton | Primary Substation | 11 | Electric Engagement | 0.074294 | 0.089463 | 0.12496 | 0.16313 | 0.20331 | 0.264 | 0.33051 | 0.4126 | 0.49049 | 0.56734 | 0.64605 | 0.70255 | 0.75954 | 0.81806 | 0.87587 | 0.93453 | 1.2238 | 1.3567 | 0.17555 | 0.20821 | 0.28941 | 0.37609 | 0.46664 | 0.59791 | 0.74095 | 0.9168 | 1.0841 | 1.2501 | 1.4205 | 1.5452 | 1.6716 | 1.8019 | 1.9297 | 2.0597 | 2.6911 | 3.0019
South West | Abham 132 kV | Blackawton | Primary Substation | 11 | Holistic Transition | 0.072473 | 0.084188 | 0.117 | 0.15102 | 0.19072 | 0.25082 | 0.32188 | 0.41238 | 0.49579 | 0.58238 | 0.65807 | 0.72469 | 0.78917 | 0.84408 | 0.89737 | 0.94214 | 1.1623 | 1.2475 | 0.17275 | 0.19927 | 0.27714 | 0.35747 | 0.45129 | 0.58584 | 0.74752 | 0.95321 | 1.1419 | 1.3362 | 1.5012 | 1.646 | 1.7862 | 1.9032 | 2.0162 | 2.1123 | 2.5888 | 2.7772
South West | Abham 132 kV | Blackawton | Primary Substation | 11 | Hydrogen Evolution | 0.069014 | 0.077795 | 0.092591 | 0.11115 | 0.13308 | 0.17323 | 0.21573 | 0.2678 | 0.32869 | 0.39819 | 0.45771 | 0.51187 | 0.56344 | 0.61434 | 0.66398 | 0.7042 | 0.88687 | 1.0282 | 0.16379 | 0.18277 | 0.21564 | 0.25713 | 0.30623 | 0.393 | 0.48519 | 0.59695 | 0.731 | 0.8854 | 1.0143 | 1.1303 | 1.24 | 1.3495 | 1.4557 | 1.5434 | 1.9512 | 2.2718
South West | Abham 132 kV | Bovey Tracey | Primary Substation | 11 | Counterfactual | 0.39464 | 0.43671 | 0.48343 | 0.52773 | 0.5878 | 0.65657 | 0.73348 | 0.84359 | 0.93228 | 1.0207 | 1.1257 | 1.2481 | 1.3623 | 1.4766 | 1.5703 | 1.6677 | 2.0385 | 2.2239 | 0.95153 | 1.0418 | 1.1419 | 1.2369 | 1.3651 | 1.5118 | 1.6763 | 1.9082 | 2.097 | 2.2863 | 2.5094 | 2.7725 | 3.0104 | 3.248 | 3.4415 | 3.6427 | 4.4245 | 4.8328
South West | Abham 132 kV | Bovey Tracey | Primary Substation | 11 | Electric Engagement | 0.43325 | 0.51971 | 0.63572 | 0.75229 | 0.89086 | 1.0428 | 1.2176 | 1.4396 | 1.6652 | 1.8148 | 1.9679 | 2.051 | 2.1301 | 2.212 | 2.2724 | 2.3338 | 2.6246 | 2.8578 | 1.0373 | 1.225 | 1.4769 | 1.7286 | 2.0263 | 2.3506 | 2.721 | 3.1857 | 3.6764 | 3.9936 | 4.3225 | 4.5108 | 4.691 | 4.8779 | 5.017 | 5.1591 | 5.8326 | 6.3788
South West | Abham 132 kV | Bovey Tracey | Primary Substation | 11 | Holistic Transition | 0.42512 | 0.4961 | 0.58921 | 0.67652 | 0.78692 | 0.91217 | 1.058 | 1.2465 | 1.4156 | 1.6039 | 1.7704 | 1.9372 | 2.1023 | 2.2569 | 2.3825 | 2.4683 | 2.771 | 2.9811 | 1.0253 | 1.1861 | 1.3965 | 1.5938 | 1.8417 | 2.1195 | 2.4424 | 2.8548 | 3.2278 | 3.648 | 4.005 | 4.3621 | 4.7157 | 5.0455 | 5.3125 | 5.5007 | 6.1923 | 6.6772
South West | Abham 132 kV | Bovey Tracey | Primary Substation | 11 | Hydrogen Evolution | 0.4076 | 0.46099 | 0.52665 | 0.58979 | 0.67384 | 0.77224 | 0.88585 | 1.0349 | 1.1993 | 1.3544 | 1.5092 | 1.6616 | 1.808 | 1.9504 | 2.0646 | 2.1356 | 2.3789 | 2.5842 | 0.98041 | 1.0968 | 1.2379 | 1.3738 | 1.5546 | 1.7657 | 2.0083 | 2.3217 | 2.6811 | 3.0175 | 3.3444 | 3.6652 | 3.9728 | 4.2733 | 4.5131 | 4.6673 | 5.2239 | 5.6959
South West | Abham 132 kV | Bradley Lane | Primary Substation | 11 | Counterfactual | 0.74731 | 0.84104 | 0.9668 | 1.1049 | 1.2664 | 1.4531 | 1.6537 | 1.9413 | 2.1706 | 2.4002 | 2.6271 | 2.9762 | 3.2404 | 3.4873 | 3.7368 | 3.9782 | 4.8319 | 5.1763 | 1.6498 | 1.8491 | 2.1149 | 2.406 | 2.7462 | 3.1393 | 3.5617 | 4.16 | 4.6411 | 5.1232 | 5.6012 | 6.3839 | 6.9421 | 7.4556 | 7.9746 | 8.4705 | 10.2539 | 11.0113
South West | Abham 132 kV | Bradley Lane | Primary Substation | 11 | Electric Engagement | 0.85073 | 1.0547 | 1.339 | 1.6522 | 2.0065 | 2.4122 | 2.8565 | 3.4293 | 4.1277 | 4.56 | 4.9161 | 5.0533 | 5.1656 | 5.2876 | 5.3929 | 5.5045 | 6.0423 | 6.4979 | 1.8795 | 2.3166 | 2.924 | 3.59 | 4.3411 | 5.2 | 6.1326 | 7.3226 | 8.8737 | 9.803 | 10.572 | 10.8962 | 11.1628 | 11.451 | 11.6942 | 11.9524 | 13.1963 | 14.2545
South West | Abham 132 kV | Bradley Lane | Primary Substation | 11 | Holistic Transition | 0.82906 | 0.98582 | 1.202 | 1.4306 | 1.6949 | 2.0127 | 2.3565 | 2.802 | 3.237 | 3.8917 | 4.2857 | 4.6391 | 4.9899 | 5.2987 | 5.5952 | 5.7849 | 6.3916 | 6.8571 | 1.8479 | 2.1988 | 2.6782 | 3.1827 | 3.7641 | 4.4587 | 5.2067 | 6.163 | 7.1192 | 8.6213 | 9.469 | 10.2224 | 10.971 | 11.6202 | 12.246 | 12.66 | 14.051 | 15.1258
South West | Abham 132 kV | Bradley Lane | Primary Substation | 11 | Hydrogen Evolution | 0.77946 | 0.90012 | 1.0701 | 1.2565 | 1.4768 | 1.75 | 2.0376 | 2.4189 | 2.8985 | 3.3775 | 3.7476 | 4.0894 | 4.4021 | 4.7071 | 4.9762 | 5.128 | 5.5814 | 5.9771 | 1.7213 | 1.9812 | 2.3439 | 2.7418 | 3.212 | 3.7952 | 4.4044 | 5.2009 | 6.2671 | 7.3295 | 8.1164 | 8.8397 | 9.4947 | 10.1369 | 10.696 | 11.0226 | 12.055 | 12.9563
South West | Abham 132 kV | Buckfastleigh | Primary Substation | 11 | Counterfactual | 0.62283 | 0.65047 | 0.68747 | 0.72868 | 0.77665 | 0.83427 | 0.90136 | 0.99901 | 1.0799 | 1.1724 | 1.2574 | 1.3357 | 1.4176 | 1.5008 | 1.583 | 1.6666 | 2.0063 | 2.2008 | 1.3675 | 1.4268 | 1.5077 | 1.5977 | 1.7026 | 1.8287 | 1.9763 | 2.1869 | 2.3636 | 2.5676 | 2.7518 | 2.9174 | 3.0883 | 3.2623 | 3.4338 | 3.6082 | 4.3366 | 4.774
South West | Abham 132 kV | Buckfastleigh | Primary Substation | 11 | Electric Engagement | 0.65465 | 0.71778 | 0.82503 | 0.94115 | 1.0658 | 1.2015 | 1.3568 | 1.555 | 1.7262 | 1.8796 | 2.021 | 2.0942 | 2.164 | 2.2344 | 2.3055 | 2.3766 | 2.699 | 2.9587 | 1.4381 | 1.5746 | 1.8137 | 2.0707 | 2.3446 | 2.6399 | 2.9744 | 3.396 | 3.7632 | 4.0958 | 4.4059 | 4.5768 | 4.7415 | 4.9085 | 5.0765 | 5.2452 | 6.0059 | 6.6273
South West | Abham 132 kV | Buckfastleigh | Primary Substation | 11 | Holistic Transition | 0.64767 | 0.69743 | 0.78852 | 0.88331 | 0.99215 | 1.1146 | 1.262 | 1.4574 | 1.6278 | 1.8039 | 1.956 | 2.096 | 2.2319 | 2.3469 | 2.4574 | 2.5327 | 2.8171 | 2.997 | 1.4277 | 1.5407 | 1.7526 | 1.972 | 2.2237 | 2.5024 | 2.8387 | 3.28 | 3.6652 | 4.0601 | 4.3923 | 4.697 | 4.9934 | 5.2406 | 5.4784 | 5.6463 | 6.3068 | 6.7239
South West | Abham 132 kV | Buckfastleigh | Primary Substation | 11 | Hydrogen Evolution | 0.6329 | 0.66893 | 0.71958 | 0.77921 | 0.84873 | 0.93349 | 1.0325 | 1.1632 | 1.2993 | 1.4542 | 1.5928 | 1.7177 | 1.8338 | 1.9446 | 2.0511 | 2.1191 | 2.3853 | 2.6202 | 1.3899 | 1.4682 | 1.5786 | 1.7092 | 1.8615 | 2.0465 | 2.2617 | 2.5406 | 2.8379 | 3.1785 | 3.476 | 3.7418 | 3.9878 | 4.2243 | 4.4522 | 4.6035 | 5.2282 | 5.7803
South West | Abham 132 kV | Chudleigh Knighton | Primary Substation | 11 | Counterfactual | 2.7167 | 2.7631 | 2.8422 | 2.9405 | 2.3177 | 2.435 | 2.555 | 2.7226 | 2.3345 | 2.4959 | 1.5108 | 1.6653 | 1.8008 | 1.9391 | 2.0757 | 2.2172 | 2.8173 | 3.1808 | 6.7437 | 6.8436 | 7.0165 | 7.23 | 5.6416 | 5.899 | 6.1654 | 6.531 | 5.5197 | 5.8808 | 3.3727 | 3.7118 | 3.9972 | 4.2888 | 4.5757 | 4.8728 | 6.1713 | 6.9951
South West | Abham 132 kV | Chudleigh Knighton | Primary Substation | 11 | Electric Engagement | 2.767 | 2.8703 | 3.0759 | 3.31 | 2.823 | 3.08 | 3.3501 | 3.6508 | 3.4371 | 3.6651 | 2.9063 | 3.05 | 3.1929 | 3.3439 | 3.4965 | 3.6538 | 4.3728 | 4.8939 | 6.8558 | 7.0796 | 7.5415 | 8.0635 | 6.7794 | 7.3428 | 7.9297 | 8.5613 | 7.9269 | 8.4126 | 6.4416 | 6.7765 | 7.1121 | 7.467 | 7.8239 | 8.1917 | 9.8604 | 11.1044
South West | Abham 132 kV | Chudleigh Knighton | Primary Substation | 11 | Holistic Transition | 2.7568 | 2.8395 | 3.0236 | 3.2278 | 2.7242 | 2.966 | 3.1775 | 3.4541 | 3.1599 | 3.4315 | 2.8891 | 3.1382 | 3.3825 | 3.5915 | 3.793 | 3.9429 | 4.551 | 4.8924 | 6.8409 | 7.0287 | 7.4573 | 7.9285 | 6.63 | 7.1828 | 7.6567 | 8.2704 | 7.4676 | 8.0728 | 6.6377 | 7.1844 | 7.7202 | 8.1711 | 8.606 | 8.939 | 10.3324 | 11.1205
South West | Abham 132 kV | Chudleigh Knighton | Primary Substation | 11 | Hydrogen Evolution | 2.7329 | 2.7933 | 2.8973 | 3.0314 | 2.4477 | 2.6141 | 2.7848 | 3.0034 | 2.7046 | 2.9433 | 2.1286 | 2.3367 | 2.5322 | 2.7264 | 2.9144 | 3.0474 | 3.6054 | 4.0767 | 6.7798 | 6.9114 | 7.1397 | 7.4351 | 5.9355 | 6.3019 | 6.6768 | 7.1485 | 6.3351 | 6.861 | 4.7491 | 5.1962 | 5.6141 | 6.0329 | 6.4386 | 6.7358 | 8.0385 | 9.1465
South West | Abham 132 kV | Churston | Primary Substation | 11 | Counterfactual | 1.5421 | 1.5984 | 1.6675 | 1.7563 | 1.8552 | 1.9693 | 2.0919 | 2.2597 | 2.3975 | 2.5223 | 2.6393 | 2.7616 | 2.8985 | 3.0345 | 3.1671 | 3.2983 | 3.7553 | 3.9369 | 3.1885 | 3.3076 | 3.4531 | 3.6391 | 3.8462 | 4.0853 | 4.3419 | 4.6897 | 4.9769 | 5.2366 | 5.4786 | 5.7302 | 6.0116 | 6.2913 | 6.5638 | 6.8323 | 7.7788 | 8.1702
South West | Abham 132 kV | Churston | Primary Substation | 11 | Electric Engagement | 1.5987 | 1.714 | 1.8675 | 2.0525 | 2.2582 | 2.4916 | 2.754 | 3.0876 | 3.3585 | 3.5767 | 3.7543 | 3.8199 | 3.879 | 3.9363 | 3.9962 | 4.0529 | 4.3125 | 4.532 | 3.3141 | 3.5604 | 3.8857 | 4.2768 | 4.7111 | 5.2038 | 5.7541 | 6.4465 | 7.0111 | 7.4696 | 7.8429 | 7.989 | 8.122 | 8.2518 | 8.3866 | 8.515 | 9.1088 | 9.6105
South West | Abham 132 kV | Churston | Primary Substation | 11 | Holistic Transition | 1.5864 | 1.6762 | 1.7927 | 1.932 | 2.0894 | 2.2754 | 2.4716 | 2.7229 | 2.9363 | 3.141 | 3.3452 | 3.5508 | 3.7436 | 3.9257 | 4.0974 | 4.2036 | 4.5178 | 4.7489 | 3.2959 | 3.4954 | 3.7508 | 4.0547 | 4.3974 | 4.8004 | 5.2232 | 5.7567 | 6.2118 | 6.6456 | 7.0755 | 7.508 | 7.9126 | 8.2941 | 8.6546 | 8.8841 | 9.5958 | 10.1278
South West | Abham 132 kV | Churston | Primary Substation | 11 | Hydrogen Evolution | 1.5601 | 1.631 | 1.7276 | 1.8488 | 1.9867 | 2.1529 | 2.3324 | 2.5626 | 2.7644 | 2.963 | 3.1513 | 3.3348 | 3.5071 | 3.6693 | 3.8187 | 3.9014 | 4.1145 | 4.2927 | 3.2285 | 3.3805 | 3.5857 | 3.8437 | 4.137 | 4.4905 | 4.8704 | 5.351 | 5.7739 | 6.1894 | 6.5799 | 6.959 | 7.3138 | 7.6483 | 7.9573 | 8.1327 | 8.6102 | 9.0105
South West | Abham 132 kV | Colley End | Primary Substation | 11 | Counterfactual | 0.24911 | 0.35229 | 0.46842 | 0.61549 | 0.75035 | 0.92384 | 1.1164 | 1.3868 | 1.6009 | 1.8479 | 2.1023 | 2.3643 | 2.6517 | 2.9383 | 3.2176 | 3.4975 | 4.4129 | 4.708 | 0.55594 | 0.77553 | 1.019 | 1.3268 | 1.6086 | 1.9703 | 2.3708 | 2.9253 | 3.3672 | 3.8783 | 4.4041 | 4.9438 | 5.5335 | 6.1212 | 6.6941 | 7.268 | 9.1637 | 9.8049
South West | Abham 132 kV | Colley End | Primary Substation | 11 | Electric Engagement | 0.36832 | 0.59905 | 0.87429 | 1.2076 | 1.5421 | 1.9381 | 2.3964 | 2.9789 | 3.5004 | 3.926 | 4.3041 | 4.4525 | 4.5914 | 4.6936 | 4.7959 | 4.8961 | 5.3515 | 5.7786 | 0.82101 | 1.3155 | 1.8941 | 2.5944 | 3.2927 | 4.1202 | 5.0718 | 6.267 | 7.3473 | 8.233 | 9.0246 | 9.3551 | 9.666 | 9.8971 | 10.1284 | 10.3549 | 11.3971 | 12.3643
South West | Abham 132 kV | Colley End | Primary Substation | 11 | Holistic Transition | 0.34379 | 0.52251 | 0.71544 | 0.95264 | 1.1825 | 1.4737 | 1.8337 | 2.2674 | 2.649 | 3.0543 | 3.4895 | 3.8877 | 4.277 | 4.6392 | 4.9795 | 5.1817 | 5.7531 | 6.2328 | 0.78549 | 1.186 | 1.6081 | 2.1239 | 2.6217 | 3.2489 | 4.0204 | 4.9321 | 5.7381 | 6.5911 | 7.5038 | 8.3362 | 9.1498 | 9.9083 | 10.6228 | 11.0607 | 12.3651 | 13.4678
South West | Abham 132 kV | Colley End | Primary Substation | 11 | Hydrogen Evolution | 0.2859 | 0.42005 | 0.58259 | 0.78042 | 0.97473 | 1.2268 | 1.513 | 1.8842 | 2.2267 | 2.5942 | 2.9808 | 3.3598 | 3.7242 | 4.0623 | 4.3804 | 4.5516 | 4.9569 | 5.2814 | 0.63797 | 0.92686 | 1.2697 | 1.6891 | 2.0977 | 2.6289 | 3.2275 | 3.9912 | 4.7012 | 5.4618 | 6.2585 | 7.0395 | 7.7903 | 8.4883 | 9.1462 | 9.5101 | 10.4142 | 11.1389
South West | Abham 132 kV | Dartmouth | Primary Substation | 11 | Counterfactual | 0.21786 | 0.27188 | 0.33367 | 0.40174 | 0.47936 | 0.57301 | 0.67494 | 0.82265 | 0.943 | 1.0701 | 1.1982 | 1.3275 | 1.4564 | 1.5842 | 1.7082 | 1.8324 | 2.2676 | 2.4563 | 0.49995 | 0.61588 | 0.74644 | 0.8899 | 1.0536 | 1.2507 | 1.4648 | 1.7709 | 2.0226 | 2.2888 | 2.5549 | 2.8218 | 3.0854 | 3.3471 | 3.6005 | 3.8541 | 4.7554 | 5.1633
South West | Abham 132 kV | Dartmouth | Primary Substation | 11 | Electric Engagement | 0.27375 | 0.39228 | 0.53649 | 0.70321 | 0.89292 | 1.1078 | 1.3517 | 1.6621 | 1.9227 | 2.144 | 2.3415 | 2.4251 | 2.4895 | 2.5526 | 2.615 | 2.675 | 2.9908 | 3.2064 | 0.62424 | 0.88074 | 1.1875 | 1.5427 | 1.9475 | 2.4017 | 2.9127 | 3.5545 | 4.0947 | 4.5559 | 4.9698 | 5.155 | 5.2987 | 5.4397 | 5.5788 | 5.713 | 6.4176 | 6.9162
South West | Abham 132 kV | Dartmouth | Primary Substation | 11 | Holistic Transition | 0.26245 | 0.35767 | 0.46749 | 0.58869 | 0.72248 | 0.88454 | 1.0631 | 1.2951 | 1.4973 | 1.7092 | 1.9267 | 2.1343 | 2.3209 | 2.493 | 2.6544 | 2.7515 | 3.0793 | 3.3188 | 0.60801 | 0.82345 | 1.0673 | 1.336 | 1.6313 | 1.9836 | 2.3699 | 2.864 | 3.2948 | 3.7437 | 4.201 | 4.6373 | 5.0282 | 5.3883 | 5.7263 | 5.9355 | 6.6717 | 7.2232
South West | Abham 132 kV | Dartmouth | Primary Substation | 11 | Hydrogen Evolution | 0.23514 | 0.30566 | 0.38952 | 0.48889 | 0.60611 | 0.74555 | 0.90018 | 1.1035 | 1.2861 | 1.4789 | 1.6749 | 1.8639 | 2.0317 | 2.1866 | 2.3319 | 2.406 | 2.6153 | 2.8132 | 0.53846 | 0.69182 | 0.87046 | 1.0839 | 1.3369 | 1.6346 | 1.9618 | 2.3849 | 2.7655 | 3.1669 | 3.5726 | 3.9631 | 4.3075 | 4.6265 | 4.9254 | 5.0823 | 5.5488 | 5.991
South West | Abham 132 kV | Dawlish | Primary Substation | 11 | Counterfactual | 0.35184 | 0.44512 | 0.56192 | 0.69839 | 0.84328 | 0.98972 | 1.155 | 1.3931 | 1.5887 | 1.8055 | 2.0138 | 2.2564 | 2.4664 | 2.675 | 2.8839 | 3.0992 | 3.9459 | 4.3988 | 0.81031 | 1.0093 | 1.2606 | 1.5533 | 1.8658 | 2.1828 | 2.5423 | 3.0505 | 3.4734 | 3.9465 | 4.3946 | 4.9252 | 5.3642 | 5.7987 | 6.2325 | 6.6801 | 8.4845 | 9.4974
South West | Abham 132 kV | Dawlish | Primary Substation | 11 | Electric Engagement | 0.43691 | 0.62387 | 0.90732 | 1.2304 | 1.5718 | 1.915 | 2.3059 | 2.7995 | 3.2926 | 3.6858 | 4.0443 | 4.2145 | 4.376 | 4.5507 | 4.7288 | 4.9148 | 5.7871 | 6.4102 | 1 | 1.4032 | 2.0267 | 2.735 | 3.4814 | 4.2224 | 5.0582 | 6.0997 | 7.1738 | 8.0258 | 8.8087 | 9.2028 | 9.5782 | 9.9838 | 10.3954 | 10.8251 | 12.8258 | 14.2957
South West | Abham 132 kV | Dawlish | Primary Substation | 11 | Holistic Transition | 0.41978 | 0.57061 | 0.81067 | 1.0745 | 1.3602 | 1.6511 | 2.0022 | 2.46 | 2.8742 | 3.3795 | 3.7474 | 4.0878 | 4.4242 | 4.7282 | 5.0185 | 5.2255 | 6.0197 | 6.5011 | 0.97523 | 1.3134 | 1.8626 | 2.4629 | 3.1146 | 3.7697 | 4.5618 | 5.5837 | 6.5141 | 7.6628 | 8.4607 | 9.1946 | 9.9199 | 10.5676 | 11.1874 | 11.6426 | 13.4479 | 14.5558
South West | Abham 132 kV | Dawlish | Primary Substation | 11 | Hydrogen Evolution | 0.38009 | 0.49886 | 0.65414 | 0.84422 | 1.0518 | 1.2656 | 1.5092 | 1.8251 | 2.1793 | 2.5753 | 2.9124 | 3.2137 | 3.4942 | 3.7729 | 4.0413 | 4.2189 | 4.8912 | 5.4537 | 0.87382 | 1.1312 | 1.4676 | 1.8826 | 2.3379 | 2.803 | 3.3297 | 4.0006 | 4.783 | 5.6625 | 6.3877 | 7.0261 | 7.6158 | 8.2061 | 8.7757 | 9.1659 | 10.7134 | 12.0179
South West | Abham 132 kV | Higher Woodway | Primary Substation | 11 | Counterfactual | 0.3136 | 0.36677 | 0.43252 | 0.50568 | 0.57995 | 0.65057 | 0.74322 | 0.87225 | 0.96816 | 1.0704 | 1.1737 | 1.2793 | 1.3958 | 1.5152 | 1.6368 | 1.7622 | 2.1964 | 2.3541 | 0.69843 | 0.8114 | 0.95007 | 1.1041 | 1.2604 | 1.4087 | 1.6031 | 1.87 | 2.0697 | 2.283 | 2.497 | 2.7143 | 2.9526 | 3.1973 | 3.4467 | 3.7043 | 4.6098 | 4.959
South West | Abham 132 kV | Higher Woodway | Primary Substation | 11 | Electric Engagement | 0.37082 | 0.48373 | 0.64318 | 0.80686 | 0.98363 | 1.1538 | 1.3568 | 1.625 | 1.8457 | 2.0258 | 2.1791 | 2.2222 | 2.2616 | 2.3074 | 2.3574 | 2.4127 | 2.6848 | 2.9136 | 0.82606 | 1.0677 | 1.4078 | 1.755 | 2.1284 | 2.4843 | 2.9062 | 3.4579 | 3.9141 | 4.289 | 4.6102 | 4.7103 | 4.8027 | 4.9093 | 5.025 | 5.1521 | 5.7768 | 6.3059
South West | Abham 132 kV | Higher Woodway | Primary Substation | 11 | Holistic Transition | 0.35942 | 0.44658 | 0.5553 | 0.69577 | 0.81795 | 0.93889 | 1.0854 | 1.281 | 1.4478 | 1.6226 | 1.7976 | 1.9674 | 2.1366 | 2.2983 | 2.4529 | 2.5502 | 2.8577 | 3.0971 | 0.80973 | 1.004 | 1.2444 | 1.5524 | 1.8205 | 2.0831 | 2.3997 | 2.8154 | 3.1714 | 3.5424 | 3.9098 | 4.2656 | 4.6207 | 4.9599 | 5.2857 | 5.4977 | 6.2019 | 6.7555
South West | Abham 132 kV | Higher Woodway | Primary Substation | 11 | Hydrogen Evolution | 0.33155 | 0.40022 | 0.5001 | 0.60164 | 0.70234 | 0.8014 | 0.91919 | 1.0823 | 1.2253 | 1.3796 | 1.5372 | 1.6901 | 1.8365 | 1.9802 | 2.1178 | 2.193 | 2.4125 | 2.6042 | 0.7388 | 0.88669 | 1.1003 | 1.3172 | 1.5314 | 1.7401 | 1.9867 | 2.3234 | 2.6213 | 2.9426 | 3.2678 | 3.5824 | 3.883 | 4.1797 | 4.4649 | 4.6264 | 5.1253 | 5.5617
South West | Abham 132 kV | Hollicombe | Primary Substation | 11 | Counterfactual | 0.1805 | 0.2335 | 0.29648 | 0.37571 | 0.46388 | 0.54946 | 0.63931 | 0.77836 | 0.88889 | 1.006 | 1.1245 | 1.2518 | 1.3919 | 1.5316 | 1.6661 | 1.8027 | 2.2552 | 2.4162 | 0.40755 | 0.51978 | 0.65191 | 0.81778 | 1.0018 | 1.18 | 1.3668 | 1.652 | 1.8802 | 2.1219 | 2.366 | 2.6275 | 2.9141 | 3.1996 | 3.4748 | 3.754 | 4.6889 | 5.0367
South West | Abham 132 kV | Hollicombe | Primary Substation | 11 | Electric Engagement | 0.24076 | 0.35586 | 0.50643 | 0.67794 | 0.86712 | 1.0598 | 1.2867 | 1.5813 | 1.8223 | 2.0198 | 2.1946 | 2.2517 | 2.3045 | 2.3553 | 2.4089 | 2.4569 | 2.6811 | 2.893 | 0.54144 | 0.78715 | 1.1048 | 1.4651 | 1.8617 | 2.2637 | 2.7337 | 3.3382 | 3.8342 | 4.2431 | 4.6072 | 4.7352 | 4.854 | 4.9695 | 5.0904 | 5.2001 | 5.7145 | 6.1957
South West | Abham 132 kV | Hollicombe | Primary Substation | 11 | Holistic Transition | 0.22804 | 0.31617 | 0.42515 | 0.54956 | 0.68875 | 0.83114 | 0.98437 | 1.1867 | 1.365 | 1.5555 | 1.7592 | 1.9631 | 2.1609 | 2.3457 | 2.518 | 2.6193 | 2.9096 | 3.1463 | 0.52288 | 0.71939 | 0.95728 | 1.2279 | 1.5291 | 1.8352 | 2.1615 | 2.5856 | 2.9608 | 3.3601 | 3.7855 | 4.2115 | 4.6251 | 5.0118 | 5.3733 | 5.5926 | 6.254 | 6.7988
South West | Abham 132 kV | Hollicombe | Primary Substation | 11 | Hydrogen Evolution | 0.19916 | 0.26654 | 0.36141 | 0.46572 | 0.58281 | 0.70567 | 0.84585 | 1.0373 | 1.2021 | 1.379 | 1.5693 | 1.7526 | 1.9283 | 2.095 | 2.247 | 2.3286 | 2.5228 | 2.6844 | 0.44908 | 0.59354 | 0.79447 | 1.0151 | 1.2628 | 1.5208 | 1.813 | 2.2069 | 2.5469 | 2.9115 | 3.3024 | 3.6788 | 4.0397 | 4.3825 | 4.6956 | 4.8679 | 5.3012 | 5.6631
South West | Abham 132 kV | Ivybridge | Primary Substation | 11 | Counterfactual | 0.61274 | 0.67277 | 0.74887 | 0.82197 | 0.90042 | 0.99261 | 1.0972 | 1.2534 | 1.3789 | 1.5232 | 1.6653 | 1.81 | 1.9562 | 2.1008 | 2.2395 | 2.3794 | 2.9022 | 3.1571 | 1.466 | 1.5936 | 1.7559 | 1.9118 | 2.0794 | 2.2761 | 2.4996 | 2.8275 | 3.0939 | 3.4018 | 3.7019 | 4.0075 | 4.3088 | 4.6068 | 4.8922 | 5.1797 | 6.2773 | 6.8386
South West | Abham 132 kV | Ivybridge | Primary Substation | 11 | Electric Engagement | 0.67365 | 0.79792 | 0.98009 | 1.1686 | 1.3667 | 1.5868 | 1.8401 | 2.1527 | 2.4395 | 2.6639 | 2.8599 | 2.9268 | 2.9827 | 3.0662 | 3.1478 | 3.2347 | 3.6086 | 3.9178 | 1.6013 | 1.8677 | 2.2617 | 2.668 | 3.092 | 3.5591 | 4.0931 | 4.737 | 5.3416 | 5.8091 | 6.2203 | 6.3683 | 6.4917 | 6.6858 | 6.875 | 7.0749 | 7.9488 | 8.6779
South West | Abham 132 kV | Ivybridge | Primary Substation | 11 | Holistic Transition | 0.66112 | 0.75798 | 0.90441 | 1.0444 | 1.1957 | 1.3723 | 1.5436 | 1.7763 | 2.0166 | 2.2513 | 2.4931 | 2.72 | 2.9397 | 3.1355 | 3.3196 | 3.4412 | 3.8199 | 4.246 | 1.5832 | 1.7997 | 2.1291 | 2.4437 | 2.7832 | 3.1733 | 3.5429 | 4.0376 | 4.5649 | 5.0689 | 5.5851 | 6.0675 | 6.5347 | 6.9479 | 7.3367 | 7.6006 | 8.4703 | 9.4853
South West | Abham 132 kV | Ivybridge | Primary Substation | 11 | Hydrogen Evolution | 0.63227 | 0.70837 | 0.81325 | 0.92021 | 1.0347 | 1.1705 | 1.328 | 1.5435 | 1.7509 | 1.9695 | 2.1763 | 2.3641 | 2.5424 | 2.7164 | 2.8658 | 2.9398 | 3.2326 | 3.6641 | 1.5093 | 1.6733 | 1.8982 | 2.1283 | 2.3738 | 2.6637 | 2.9979 | 3.4484 | 3.8869 | 4.3477 | 4.7754 | 5.1616 | 5.5257 | 5.8874 | 6.1921 | 6.3444 | 7.0214 | 8.0473
South West | Abham 132 kV | Kingsbridge | Primary Substation | 11 | Counterfactual | 0.51804 | 0.59567 | 0.6914 | 0.78231 | 0.89647 | 1.0348 | 1.1849 | 1.4051 | 1.5928 | 1.8105 | 2.0292 | 2.2266 | 2.4259 | 2.625 | 2.8158 | 3.0081 | 3.7394 | 4.118 | 1.2236 | 1.3891 | 1.5939 | 1.7888 | 2.0335 | 2.3286 | 2.6501 | 3.1136 | 3.513 | 3.9794 | 4.4421 | 4.854 | 5.2649 | 5.6764 | 6.0694 | 6.465 | 8.0031 | 8.8357
South West | Abham 132 kV | Kingsbridge | Primary Substation | 11 | Electric Engagement | 0.59923 | 0.76629 | 1.0049 | 1.2575 | 1.5414 | 1.8646 | 2.228 | 2.6983 | 3.1119 | 3.4902 | 3.8443 | 4.0083 | 4.1518 | 4.2937 | 4.4328 | 4.5677 | 5.2372 | 5.6931 | 1.4041 | 1.7634 | 2.2819 | 2.83 | 3.4416 | 4.13 | 4.8973 | 5.8797 | 6.749 | 7.552 | 8.31 | 8.6797 | 9.0063 | 9.3315 | 9.6485 | 9.9577 | 11.4801 | 12.5535
South West | Abham 132 kV | Kingsbridge | Primary Substation | 11 | Holistic Transition | 0.5827 | 0.71414 | 0.90768 | 1.095 | 1.317 | 1.5828 | 1.8828 | 2.2817 | 2.6415 | 3.0339 | 3.4142 | 3.7531 | 4.0654 | 4.3407 | 4.6005 | 4.7658 | 5.3773 | 5.7696 | 1.3803 | 1.6755 | 2.1148 | 2.5393 | 3.04 | 3.6277 | 4.2926 | 5.1664 | 5.9556 | 6.8103 | 7.6242 | 8.3471 | 9.0126 | 9.5942 | 10.1431 | 10.503 | 11.8858 | 12.7856
South West | Abham 132 kV | Kingsbridge | Primary Substation | 11 | Hydrogen Evolution | 0.54348 | 0.64375 | 0.77241 | 0.91025 | 1.0766 | 1.2801 | 1.5057 | 1.8081 | 2.1179 | 2.4706 | 2.8134 | 3.116 | 3.391 | 3.646 | 3.8873 | 4.0237 | 4.4956 | 4.9255 | 1.2802 | 1.4969 | 1.7736 | 2.0724 | 2.4319 | 2.8678 | 3.3481 | 3.9818 | 4.641 | 5.396 | 6.1191 | 6.7528 | 7.3252 | 7.8594 | 8.3648 | 8.6606 | 9.74 | 10.7241
South West | Abham 132 kV | Langage | Primary Substation | 11 | Counterfactual | 1.8256 | 2.2651 | 2.5861 | 2.6264 | 2.6864 | 2.7572 | 2.8379 | 2.9521 | 3.0502 | 3.1506 | 3.2505 | 3.3528 | 3.4472 | 3.538 | 3.6264 | 3.717 | 4.0081 | 4.0913 | 4.5387 | 5.4214 | 6.209 | 6.2937 | 6.4206 | 6.5701 | 6.7401 | 6.9772 | 7.1828 | 7.3937 | 7.602 | 7.8138 | 8.007 | 8.1924 | 8.3729 | 8.5575 | 9.1591 | 9.3416
South West | Abham 132 kV | Langage | Primary Substation | 11 | Electric Engagement | 1.869 | 2.6339 | 2.728 | 2.8465 | 2.9977 | 3.1581 | 3.3391 | 3.5665 | 3.7548 | 3.9127 | 4.05 | 4.1042 | 4.2123 | 4.2452 | 4.2738 | 4.3 | 4.4113 | 4.5104 | 4.6355 | 6.3163 | 6.515 | 6.7697 | 7.0931 | 7.4342 | 7.8154 | 8.2868 | 8.6781 | 9.0084 | 9.2974 | 9.4196 | 9.6839 | 9.7589 | 9.8252 | 9.8864 | 10.1477 | 10.3791
South West | Abham 132 kV | Langage | Primary Substation | 11 | Holistic Transition | 2.1438 | 2.6055 | 2.6786 | 2.755 | 2.8634 | 2.9826 | 3.1141 | 3.4369 | 3.5847 | 3.7341 | 3.8875 | 4.0373 | 4.1668 | 4.2837 | 4.3918 | 4.4508 | 4.5918 | 4.7284 | 5.3315 | 6.2671 | 6.4301 | 6.5997 | 6.8382 | 7.0992 | 7.3845 | 8.1293 | 8.444 | 8.7606 | 9.0836 | 9.3975 | 9.6666 | 9.9098 | 10.1354 | 10.2631 | 10.591 | 10.9165
South West | Abham 132 kV | Langage | Primary Substation | 11 | Hydrogen Evolution | 1.8402 | 2.5726 | 2.6248 | 2.6938 | 2.7926 | 2.9011 | 3.0205 | 3.1774 | 3.3091 | 3.4481 | 3.5915 | 3.7327 | 3.9278 | 4.0352 | 4.1327 | 4.1781 | 4.2616 | 5.0264 | 4.5714 | 6.1836 | 6.294 | 6.4452 | 6.6593 | 6.8935 | 7.1483 | 7.4766 | 7.7524 | 8.0429 | 8.3408 | 8.6338 | 9.0688 | 9.2896 | 9.4904 | 9.5868 | 9.7784 | 11.6753
South West | Abham 132 kV | Lawes Bridge | Primary Substation | 11 | Counterfactual | 0.48607 | 0.60275 | 0.97435 | 1.1768 | 1.397 | 1.6174 | 1.8548 | 2.176 | 2.4579 | 2.762 | 3.0327 | 3.2955 | 3.581 | 3.8493 | 4.111 | 4.3698 | 5.1986 | 5.5026 | 1.1321 | 1.3787 | 2.2394 | 2.6629 | 3.1261 | 3.5922 | 4.0957 | 4.7699 | 5.3716 | 6.0221 | 6.5896 | 7.1347 | 7.7227 | 8.2738 | 8.8108 | 9.3419 | 11.0578 | 11.7163
South West | Abham 132 kV | Lawes Bridge | Primary Substation | 11 | Electric Engagement | 0.79513 | 1.024 | 1.3582 | 1.771 | 2.2428 | 2.7597 | 3.3296 | 3.9864 | 4.5004 | 4.9245 | 5.2891 | 5.447 | 5.591 | 5.72 | 5.8472 | 5.9723 | 6.47 | 6.9012 | 1.875 | 2.364 | 3.0739 | 3.9585 | 4.9782 | 6.1033 | 7.3372 | 8.7252 | 9.8018 | 10.6906 | 11.4565 | 11.8062 | 12.1275 | 12.4152 | 12.6991 | 12.9787 | 14.1016 | 15.0746
South West | Abham 132 kV | Lawes Bridge | Primary Substation | 11 | Holistic Transition | 0.77237 | 0.95159 | 1.2261 | 1.5577 | 1.9368 | 2.3427 | 2.7642 | 3.272 | 3.6804 | 4.0923 | 4.5042 | 4.9084 | 5.3069 | 5.6608 | 5.9947 | 6.2081 | 6.7196 | 7.1707 | 1.8415 | 2.2389 | 2.8428 | 3.5743 | 4.4166 | 5.3209 | 6.2529 | 7.3556 | 8.2324 | 9.1077 | 9.9727 | 10.8216 | 11.6586 | 12.4004 | 13.1015 | 13.5619 | 14.6932 | 15.7212
South West | Abham 132 kV | Lawes Bridge | Primary Substation | 11 | Hydrogen Evolution | 0.72204 | 0.86796 | 1.0994 | 1.388 | 1.7273 | 2.1044 | 2.5121 | 3.0074 | 3.3915 | 3.7832 | 4.169 | 4.5419 | 4.9044 | 5.2238 | 5.5243 | 5.6964 | 6.1163 | 6.4512 | 1.7129 | 2.0264 | 2.5189 | 3.1424 | 3.8845 | 4.7165 | 5.612 | 6.681 | 7.4939 | 8.3151 | 9.1159 | 9.8882 | 10.6386 | 11.2982 | 11.9199 | 12.2848 | 13.2153 | 13.9628
South West | Abham 132 kV | Laywell Brixham | Primary Substation | 11 | Counterfactual | 0.27321 | 0.35053 | 0.43267 | 0.53326 | 0.64077 | 0.76691 | 0.90266 | 1.1172 | 1.2892 | 1.4603 | 1.6374 | 1.8247 | 2.0317 | 2.2374 | 2.4395 | 2.6407 | 3.3133 | 3.5383 | 0.62855 | 0.79364 | 0.96648 | 1.1775 | 1.4026 | 1.6661 | 1.9485 | 2.3897 | 2.7461 | 3.0991 | 3.4641 | 3.8488 | 4.2727 | 4.6934 | 5.107 | 5.5185 | 6.9086 | 7.3977
South West | Abham 132 kV | Laywell Brixham | Primary Substation | 11 | Electric Engagement | 0.36448 | 0.54011 | 0.74304 | 0.98982 | 1.2566 | 1.5522 | 1.8935 | 2.3525 | 2.7254 | 3.0231 | 3.2766 | 3.3549 | 3.4242 | 3.4947 | 3.5651 | 3.6317 | 3.9368 | 4.2255 | 0.83146 | 1.2084 | 1.635 | 2.1546 | 2.7134 | 3.3311 | 4.0391 | 4.9827 | 5.7515 | 6.3677 | 6.8957 | 7.0726 | 7.2307 | 7.3919 | 7.5527 | 7.7056 | 8.4156 | 9.0801
South West | Abham 132 kV | Laywell Brixham | Primary Substation | 11 | Holistic Transition | 0.34565 | 0.48146 | 0.62588 | 0.79683 | 0.98142 | 1.1951 | 1.4233 | 1.7411 | 2.0169 | 2.2979 | 2.596 | 2.8983 | 3.1918 | 3.4677 | 3.7247 | 3.875 | 4.2848 | 4.6273 | 0.80421 | 1.1091 | 1.4259 | 1.7985 | 2.1987 | 2.6588 | 3.1449 | 3.8113 | 4.3922 | 4.9806 | 5.6034 | 6.2352 | 6.8489 | 7.4269 | 7.9668 | 8.2931 | 9.2373 | 10.0352
South West | Abham 132 kV | Laywell Brixham | Primary Substation | 11 | Hydrogen Evolution | 0.30122 | 0.40238 | 0.51704 | 0.66262 | 0.81934 | 1.002 | 1.2096 | 1.5055 | 1.7604 | 2.0184 | 2.2915 | 2.5597 | 2.8183 | 3.0581 | 3.2813 | 3.3912 | 3.6435 | 3.8722 | 0.69091 | 0.90919 | 1.1517 | 1.4614 | 1.793 | 2.1782 | 2.6122 | 3.2236 | 3.7507 | 4.2817 | 4.8425 | 5.3935 | 5.9247 | 6.418 | 6.878 | 7.1113 | 7.6819 | 8.1969
South West | Abham 132 kV | Linketty Lane | Primary Substation | 11 | Counterfactual | 2.0146 | 2.0869 | 2.1838 | 2.2748 | 2.3782 | 2.4966 | 2.6301 | 2.8364 | 2.9986 | 3.1722 | 3.3477 | 3.5261 | 3.7323 | 3.9364 | 4.1342 | 4.3594 | 5.1724 | 5.5367 | 4.9487 | 5.1022 | 5.3067 | 5.4986 | 5.716 | 5.9644 | 6.2443 | 6.6703 | 7.0078 | 7.3698 | 7.7332 | 8.0999 | 8.5225 | 8.9407 | 9.3454 | 9.8046 | 11.4807 | 12.2523
South West | Abham 132 kV | Linketty Lane | Primary Substation | 11 | Electric Engagement | 2.1049 | 2.2684 | 2.4984 | 2.7324 | 2.9903 | 3.2729 | 3.6054 | 4.0492 | 4.4144 | 4.7133 | 4.9702 | 5.0549 | 5.1607 | 5.2586 | 5.3505 | 5.4353 | 5.8014 | 6.0725 | 5.1495 | 5.4989 | 5.9879 | 6.4825 | 7.0248 | 7.6156 | 8.3069 | 9.2208 | 9.9767 | 10.5994 | 11.1387 | 11.3313 | 11.5686 | 11.7898 | 11.9982 | 12.1924 | 13.0429 | 13.6822
South West | Abham 132 kV | Linketty Lane | Primary Substation | 11 | Holistic Transition | 2.0863 | 2.2084 | 2.3788 | 2.5388 | 2.7174 | 2.9233 | 3.159 | 3.4813 | 3.7575 | 4.0474 | 4.3395 | 4.6196 | 4.9059 | 5.168 | 5.4121 | 5.5583 | 5.9721 | 6.2527 | 5.1225 | 5.3963 | 5.773 | 6.126 | 6.5182 | 6.9645 | 7.4734 | 8.1587 | 8.7483 | 9.3638 | 9.9776 | 10.5654 | 11.168 | 11.7182 | 12.2315 | 12.5488 | 13.5005 | 14.1591
South West | Abham 132 kV | Linketty Lane | Primary Substation | 11 | Hydrogen Evolution | 2.0428 | 2.1347 | 2.2687 | 2.397 | 2.543 | 2.7132 | 2.9134 | 3.1952 | 3.4507 | 3.7213 | 4.0187 | 4.3428 | 4.6677 | 4.9679 | 5.2449 | 5.4025 | 5.7916 | 6.4768 | 5.0115 | 5.2089 | 5.4934 | 5.7653 | 6.0735 | 6.4311 | 6.8495 | 7.4306 | 7.9622 | 8.5254 | 9.1373 | 9.8006 | 10.4664 | 11.083 | 11.6523 | 11.983 | 12.8413 | 14.5078
South West | Abham 132 kV | Marldon | Primary Substation | 11 | Counterfactual | 0.052875 | 0.060533 | 0.071723 | 0.083406 | 0.09753 | 0.11793 | 0.14048 | 0.17212 | 0.19842 | 0.22743 | 0.25461 | 0.27965 | 0.30533 | 0.33168 | 0.35671 | 0.38175 | 0.48522 | 0.54651 | 0.12301 | 0.13924 | 0.16363 | 0.1892 | 0.2201 | 0.26417 | 0.31327 | 0.38116 | 0.43822 | 0.502 | 0.56058 | 0.61357 | 0.66709 | 0.72224 | 0.7743 | 0.82636 | 1.0477 | 1.1849
South West | Abham 132 kV | Marldon | Primary Substation | 11 | Electric Engagement | 0.062711 | 0.080294 | 0.11247 | 0.14679 | 0.18406 | 0.23054 | 0.283 | 0.35002 | 0.40944 | 0.46345 | 0.51508 | 0.54418 | 0.57309 | 0.60283 | 0.63201 | 0.66157 | 0.80471 | 0.88728 | 0.14488 | 0.18232 | 0.25398 | 0.32996 | 0.41183 | 0.51187 | 0.62394 | 0.76598 | 0.89269 | 1.0089 | 1.1208 | 1.1868 | 1.2528 | 1.3207 | 1.387 | 1.4543 | 1.7752 | 1.9708
South West | Abham 132 kV | Marldon | Primary Substation | 11 | Holistic Transition | 0.060648 | 0.07367 | 0.1007 | 0.12834 | 0.16074 | 0.20198 | 0.25149 | 0.31635 | 0.37433 | 0.43422 | 0.48764 | 0.53705 | 0.5846 | 0.62536 | 0.6634 | 0.69027 | 0.80513 | 0.86036 | 0.14189 | 0.1709 | 0.23376 | 0.29782 | 0.37281 | 0.46543 | 0.57749 | 0.7233 | 0.85355 | 0.9871 | 1.1031 | 1.21 | 1.3127 | 1.3994 | 1.4801 | 1.5386 | 1.7945 | 1.9205
South West | Abham 132 kV | Marldon | Primary Substation | 11 | Hydrogen Evolution | 0.05594 | 0.06587 | 0.080393 | 0.096932 | 0.11664 | 0.14533 | 0.17719 | 0.21832 | 0.26168 | 0.31081 | 0.35456 | 0.39532 | 0.43355 | 0.47079 | 0.50591 | 0.52928 | 0.62449 | 0.70355 | 0.12986 | 0.15111 | 0.18277 | 0.21912 | 0.26243 | 0.32448 | 0.39327 | 0.48085 | 0.5756 | 0.68379 | 0.7777 | 0.86434 | 0.9451 | 1.0244 | 1.0991 | 1.1505 | 1.3683 | 1.5513
South West | Abham 132 kV | Modbury | Primary Substation | 11 | Counterfactual | 0.18235 | 0.20916 | 0.25748 | 0.31492 | 0.38027 | 0.46316 | 0.54529 | 0.65978 | 0.76156 | 0.86714 | 0.9634 | 1.0497 | 1.1368 | 1.2087 | 1.2759 | 1.3435 | 1.6419 | 1.8434 | 0.43308 | 0.49029 | 0.59557 | 0.72019 | 0.86309 | 1.0437 | 1.2251 | 1.4746 | 1.6986 | 1.9345 | 2.1455 | 2.3311 | 2.5154 | 2.6681 | 2.8097 | 2.9519 | 3.601 | 4.0578
South West | Abham 132 kV | Modbury | Primary Substation | 11 | Electric Engagement | 0.20591 | 0.25965 | 0.37703 | 0.51161 | 0.65316 | 0.81824 | 0.98424 | 1.1967 | 1.3899 | 1.5619 | 1.7296 | 1.8419 | 1.9541 | 2.0483 | 2.1397 | 2.2314 | 2.6546 | 2.9323 | 0.48538 | 0.60146 | 0.86616 | 1.1684 | 1.4848 | 1.8485 | 2.2113 | 2.6715 | 3.0922 | 3.4702 | 3.8416 | 4.0989 | 4.3572 | 4.5771 | 4.7895 | 5.003 | 5.9767 | 6.6435
South West | Abham 132 kV | Modbury | Primary Substation | 11 | Holistic Transition | 0.20087 | 0.24429 | 0.3543 | 0.47374 | 0.60955 | 0.77036 | 0.94577 | 1.1787 | 1.3874 | 1.5891 | 1.7608 | 1.9179 | 2.0704 | 2.1785 | 2.2803 | 2.3555 | 2.6849 | 2.8445 | 0.47798 | 0.5756 | 0.83177 | 1.1079 | 1.4229 | 1.789 | 2.1928 | 2.7256 | 3.2024 | 3.6609 | 4.0409 | 4.3876 | 4.7238 | 4.9578 | 5.1774 | 5.344 | 6.0929 | 6.4603
South West | Abham 132 kV | Modbury | Primary Substation | 11 | Hydrogen Evolution | 0.18984 | 0.22377 | 0.2865 | 0.36802 | 0.4593 | 0.57685 | 0.69118 | 0.84011 | 1.0023 | 1.174 | 1.3226 | 1.4578 | 1.5856 | 1.6904 | 1.7894 | 1.8598 | 2.1676 | 2.4281 | 0.44969 | 0.52331 | 0.66111 | 0.84188 | 1.045 | 1.3047 | 1.5569 | 1.8811 | 2.2416 | 2.6266 | 2.9519 | 3.2452 | 3.5209 | 3.7483 | 3.9629 | 4.1207 | 4.8386 | 5.452
South West | Abham 132 kV | Newton Abbot Main | Primary Substation | 11 | Counterfactual | 0.9212 | 1.0252 | 1.1698 | 1.3408 | 1.5184 | 1.7145 | 1.9348 | 2.2614 | 2.55 | 2.865 | 3.1763 | 3.4776 | 3.7831 | 4.0768 | 4.3684 | 4.6723 | 5.8189 | 6.3804 | 2.2109 | 2.4325 | 2.7417 | 3.1063 | 3.487 | 3.9078 | 4.3827 | 5.0748 | 5.6952 | 6.3765 | 7.0377 | 7.6704 | 8.3026 | 8.91 | 9.5124 | 10.1405 | 12.5613 | 13.8049
South West | Abham 132 kV | Newton Abbot Main | Primary Substation | 11 | Electric Engagement | 1.0428 | 1.2765 | 1.6343 | 2.053 | 2.5003 | 2.9846 | 3.5456 | 4.2466 | 4.8473 | 5.3546 | 5.8259 | 6.0486 | 6.2468 | 6.4355 | 6.6345 | 6.8427 | 7.6151 | 8.2365 | 2.4811 | 2.9821 | 3.7598 | 4.6687 | 5.639 | 6.684 | 7.8867 | 9.3645 | 10.6353 | 11.7134 | 12.7252 | 13.2342 | 13.6926 | 14.1313 | 14.5902 | 15.0706 | 16.8034 | 18.236
South West | Abham 132 kV | Newton Abbot Main | Primary Substation | 11 | Holistic Transition | 1.0168 | 1.1954 | 1.4853 | 1.8132 | 2.1672 | 2.5578 | 3.0226 | 3.62 | 4.1446 | 4.6907 | 5.2044 | 5.6415 | 6.0636 | 6.4309 | 6.8021 | 7.0443 | 7.8609 | 8.8398 | 2.4428 | 2.8437 | 3.5016 | 4.2423 | 5.0452 | 5.9216 | 6.9638 | 8.284 | 9.4416 | 10.6382 | 11.7393 | 12.6555 | 13.5405 | 14.3037 | 15.083 | 15.6052 | 17.4292 | 19.744
South West | Abham 132 kV | Newton Abbot Main | Primary Substation | 11 | Hydrogen Evolution | 0.95894 | 1.0933 | 1.2874 | 1.5312 | 1.7977 | 2.1044 | 2.4591 | 2.9254 | 3.3624 | 3.838 | 4.3026 | 4.7426 | 5.1463 | 5.5194 | 5.8813 | 6.1061 | 6.7386 | 7.5593 | 2.2949 | 2.5846 | 3.002 | 3.5313 | 4.1139 | 4.7827 | 5.5535 | 6.5489 | 7.4877 | 8.5104 | 9.4916 | 10.4155 | 11.2597 | 12.0423 | 12.8029 | 13.2923 | 14.7074 | 16.6243
South West | Abham 132 kV | Newton Ferrers | Primary Substation | 11 | Counterfactual | 0.19611 | 0.21904 | 0.24681 | 0.27835 | 0.30149 | 0.32706 | 0.3557 | 0.40113 | 0.4364 | 0.47368 | 0.51199 | 0.5523 | 0.59756 | 0.64253 | 0.68627 | 0.72989 | 0.8756 | 0.9251 | 0.43757 | 0.48627 | 0.54454 | 0.61052 | 0.65882 | 0.71201 | 0.77132 | 0.86427 | 0.93686 | 1.0134 | 1.0919 | 1.1743 | 1.2666 | 1.3582 | 1.4473 | 1.536 | 1.8357 | 1.9428
South West | Abham 132 kV | Newton Ferrers | Primary Substation | 11 | Electric Engagement | 0.21795 | 0.26431 | 0.32174 | 0.38732 | 0.44544 | 0.50838 | 0.58322 | 0.68406 | 0.76667 | 0.83366 | 0.88968 | 0.90368 | 0.91553 | 0.92626 | 0.93687 | 0.94619 | 0.99794 | 1.0567 | 0.48619 | 0.5855 | 0.7068 | 0.84486 | 0.96582 | 1.0963 | 1.2506 | 1.4566 | 1.626 | 1.7638 | 1.8797 | 1.9114 | 1.9386 | 1.9636 | 1.9882 | 2.0101 | 2.132 | 2.2676
South West | Abham 132 kV | Newton Ferrers | Primary Substation | 11 | Holistic Transition | 0.21358 | 0.24994 | 0.2924 | 0.33983 | 0.37742 | 0.42033 | 0.46885 | 0.53584 | 0.59345 | 0.65525 | 0.7205 | 0.784 | 0.84536 | 0.90214 | 0.95463 | 0.98187 | 1.0545 | 1.1276 | 0.47997 | 0.56094 | 0.65364 | 0.75662 | 0.83777 | 0.92949 | 1.0322 | 1.1715 | 1.2919 | 1.4204 | 1.5558 | 1.6877 | 1.8152 | 1.9334 | 2.0429 | 2.1019 | 2.2711 | 2.4416
South West | Abham 132 kV | Newton Ferrers | Primary Substation | 11 | Hydrogen Evolution | 0.20283 | 0.23212 | 0.26875 | 0.31096 | 0.34359 | 0.38042 | 0.42424 | 0.48696 | 0.54203 | 0.60018 | 0.66096 | 0.71965 | 0.77614 | 0.82735 | 0.87486 | 0.89482 | 0.93537 | 0.98146 | 0.45256 | 0.51569 | 0.59365 | 0.6833 | 0.7517 | 0.82849 | 0.9192 | 1.0476 | 1.1604 | 1.2792 | 1.4031 | 1.5228 | 1.6379 | 1.7425 | 1.8395 | 1.8814 | 1.9737 | 2.0775
South West | Abham 132 kV | Salcombe 340038 | Primary Substation | 11 | Counterfactual | 0.1572 | 0.19015 | 0.2245 | 0.2621 | 0.30438 | 0.35107 | 0.4033 | 0.48532 | 0.54936 | 0.61721 | 0.68724 | 0.76097 | 0.84532 | 0.92861 | 1.009 | 1.0884 | 1.3599 | 1.4621 | 0.3621 | 0.43315 | 0.50562 | 0.58469 | 0.67319 | 0.77064 | 0.87913 | 1.0472 | 1.1792 | 1.3188 | 1.4626 | 1.6135 | 1.7864 | 1.957 | 2.1214 | 2.2832 | 2.8428 | 3.0629
South West | Abham 132 kV | Salcombe 340038 | Primary Substation | 11 | Electric Engagement | 0.1951 | 0.27094 | 0.3569 | 0.452 | 0.55729 | 0.6716 | 0.80737 | 0.98954 | 1.1403 | 1.2668 | 1.3723 | 1.4017 | 1.4275 | 1.4513 | 1.4742 | 1.4942 | 1.6025 | 1.7151 | 0.44642 | 0.6111 | 0.79234 | 0.99192 | 1.2118 | 1.4494 | 1.7301 | 2.1032 | 2.4136 | 2.6767 | 2.8969 | 2.9629 | 3.0217 | 3.0763 | 3.1291 | 3.1758 | 3.431 | 3.6923
South West | Abham 132 kV | Salcombe 340038 | Primary Substation | 11 | Holistic Transition | 0.18739 | 0.24815 | 0.30858 | 0.37234 | 0.4422 | 0.52197 | 0.61164 | 0.73484 | 0.84093 | 0.95535 | 1.078 | 1.1978 | 1.3116 | 1.4169 | 1.5145 | 1.5677 | 1.7149 | 1.8564 | 0.43531 | 0.57389 | 0.70678 | 0.84621 | 0.9977 | 1.1689 | 1.3594 | 1.6165 | 1.8389 | 2.0781 | 2.3346 | 2.5854 | 2.8229 | 3.0432 | 3.2476 | 3.3631 | 3.7064 | 4.0374
South West | Abham 132 kV | Salcombe 340038 | Primary Substation | 11 | Hydrogen Evolution | 0.16908 | 0.21202 | 0.26092 | 0.31434 | 0.37453 | 0.44268 | 0.52365 | 0.63909 | 0.74119 | 0.85169 | 0.96663 | 1.0764 | 1.1807 | 1.2755 | 1.3631 | 1.402 | 1.4854 | 1.5742 | 0.38858 | 0.48233 | 0.58598 | 0.69885 | 0.82526 | 0.96762 | 1.1356 | 1.3722 | 1.5817 | 1.8092 | 2.0453 | 2.2703 | 2.4834 | 2.6774 | 2.8568 | 2.9389 | 3.1284 | 3.3288
South West | Abham 132 kV | South Brent | Primary Substation | 11 | Counterfactual | 0.32651 | 0.35245 | 0.39129 | 0.43437 | 0.48612 | 0.55885 | 0.64132 | 0.75464 | 0.85066 | 0.95895 | 1.0583 | 1.1477 | 1.2395 | 1.3328 | 1.4206 | 1.5094 | 1.8949 | 2.1488 | 0.77042 | 0.82551 | 0.91116 | 1.0061 | 1.1205 | 1.2794 | 1.4611 | 1.7069 | 1.9176 | 2.1585 | 2.3746 | 2.565 | 2.7572 | 2.9538 | 3.1373 | 3.3227 | 4.152 | 4.7188
South West | Abham 132 kV | South Brent | Primary Substation | 11 | Electric Engagement | 0.35792 | 0.41632 | 0.53566 | 0.66596 | 0.8042 | 0.9725 | 1.1592 | 1.3945 | 1.6059 | 1.8022 | 1.9921 | 2.1084 | 2.2236 | 2.3491 | 2.487 | 2.601 | 3.1395 | 3.4718 | 0.84016 | 0.96512 | 1.2343 | 1.5267 | 1.8345 | 2.2016 | 2.6054 | 3.1092 | 3.5647 | 3.992 | 4.408 | 4.6733 | 4.9376 | 5.2246 | 5.534 | 5.7962 | 7.0206 | 7.8131
South West | Abham 132 kV | South Brent | Primary Substation | 11 | Holistic Transition | 0.35129 | 0.39534 | 0.49968 | 0.60772 | 0.73289 | 0.89 | 1.0774 | 1.3225 | 1.54 | 1.7639 | 1.9569 | 2.1321 | 2.3008 | 2.4504 | 2.6084 | 2.7064 | 3.1322 | 3.3404 | 0.83043 | 0.92927 | 1.1741 | 1.4265 | 1.7188 | 2.0748 | 2.5034 | 3.0606 | 3.5544 | 4.0587 | 4.4817 | 4.8641 | 5.2324 | 5.5523 | 5.887 | 6.102 | 7.0585 | 7.5331
South West | Abham 132 kV | South Brent | Primary Substation | 11 | Hydrogen Evolution | 0.33657 | 0.36986 | 0.42309 | 0.48915 | 0.56592 | 0.67302 | 0.79275 | 0.94577 | 1.1151 | 1.306 | 1.4716 | 1.6209 | 1.7619 | 1.9008 | 2.0417 | 2.1308 | 2.5098 | 2.8295 | 0.79275 | 0.86432 | 0.98129 | 1.1277 | 1.2978 | 1.5318 | 1.7929 | 2.1214 | 2.4935 | 2.9167 | 3.2747 | 3.5948 | 3.8949 | 4.1931 | 4.4938 | 4.6912 | 5.5647 | 6.3079
South West | Abham 132 kV | Stokenham | Primary Substation | 11 | Counterfactual | 0.16258 | 0.18425 | 0.20874 | 0.22889 | 0.25178 | 0.28308 | 0.31719 | 0.3676 | 0.40801 | 0.45004 | 0.49325 | 0.53649 | 0.58432 | 0.63214 | 0.67845 | 0.72485 | 0.89651 | 0.98227 | 0.38651 | 0.43275 | 0.48456 | 0.52725 | 0.57561 | 0.64105 | 0.71241 | 0.81667 | 0.90086 | 0.98871 | 1.0783 | 1.1673 | 1.2653 | 1.3635 | 1.4583 | 1.5532 | 1.909 | 2.0931
South West | Abham 132 kV | Stokenham | Primary Substation | 11 | Electric Engagement | 0.18262 | 0.22708 | 0.28242 | 0.33597 | 0.39481 | 0.46868 | 0.55429 | 0.6663 | 0.76326 | 0.84792 | 0.92546 | 0.96061 | 0.99451 | 1.0283 | 1.062 | 1.0953 | 1.2688 | 1.3614 | 0.43108 | 0.52701 | 0.64547 | 0.75923 | 0.88352 | 1.0377 | 1.2153 | 1.4461 | 1.6466 | 1.8225 | 1.9844 | 2.061 | 2.1352 | 2.2095 | 2.283 | 2.3559 | 2.7328 | 2.9451
South West | Abham 132 kV | Stokenham | Primary Substation | 11 | Holistic Transition | 0.17873 | 0.21467 | 0.25685 | 0.29421 | 0.33581 | 0.39254 | 0.45681 | 0.54208 | 0.61864 | 0.70032 | 0.78301 | 0.85985 | 0.93453 | 1.003 | 1.0677 | 1.1096 | 1.2685 | 1.3622 | 0.42564 | 0.50634 | 0.60008 | 0.68303 | 0.77492 | 0.89697 | 1.0355 | 1.2171 | 1.3805 | 1.5538 | 1.7272 | 1.8883 | 2.0448 | 2.1877 | 2.3228 | 2.4123 | 2.7604 | 2.9728
South West | Abham 132 kV | Stokenham | Primary Substation | 11 | Hydrogen Evolution | 0.16876 | 0.19681 | 0.22943 | 0.25833 | 0.29108 | 0.33651 | 0.38774 | 0.45707 | 0.52335 | 0.59485 | 0.66607 | 0.73412 | 0.79993 | 0.86119 | 0.91926 | 0.95218 | 1.0599 | 1.1512 | 0.40029 | 0.46113 | 0.53094 | 0.59246 | 0.66193 | 0.75703 | 0.86392 | 1.0069 | 1.1449 | 1.2941 | 1.4412 | 1.5813 | 1.7166 | 1.8431 | 1.9629 | 2.0325 | 2.2685 | 2.4709
South West | Abham 132 kV | Teignmouth Gasworks | Primary Substation | 11 | Counterfactual | 0.22974 | 0.27844 | 0.3351 | 0.40331 | 0.47899 | 0.56262 | 0.65025 | 0.78519 | 0.89115 | 1.0045 | 1.1183 | 1.2347 | 1.3634 | 1.4947 | 1.6281 | 1.7656 | 2.2558 | 2.4521 | 0.52328 | 0.62745 | 0.74752 | 0.89164 | 1.0512 | 1.2273 | 1.4115 | 1.6908 | 1.912 | 2.1491 | 2.3854 | 2.6254 | 2.8891 | 3.1584 | 3.4323 | 3.715 | 4.7381 | 5.1699
South West | Abham 132 kV | Teignmouth Gasworks | Primary Substation | 11 | Electric Engagement | 0.28916 | 0.40218 | 0.54442 | 0.70954 | 0.89073 | 1.0858 | 1.3089 | 1.6028 | 1.8455 | 2.0459 | 2.2178 | 2.2724 | 2.3221 | 2.3768 | 2.668 | 2.7321 | 3.0447 | 3.3091 | 0.65539 | 0.89824 | 1.2014 | 1.5519 | 1.9345 | 2.3441 | 2.8088 | 3.4145 | 3.9172 | 4.3351 | 4.6963 | 4.8216 | 4.9371 | 5.0643 | 5.6648 | 5.8124 | 6.5312 | 7.1432
South West | Abham 132 kV | Teignmouth Gasworks | Primary Substation | 11 | Holistic Transition | 0.2769 | 0.36356 | 0.46626 | 0.58308 | 0.71215 | 0.85584 | 1.0198 | 1.2385 | 1.4261 | 1.6231 | 1.8187 | 2.0086 | 2.1966 | 2.3754 | 2.7779 | 2.8878 | 3.2397 | 3.5135 | 0.63763 | 0.83281 | 1.0614 | 1.3196 | 1.6036 | 1.9167 | 2.2718 | 2.7383 | 3.1399 | 3.5592 | 3.9706 | 4.3696 | 4.7647 | 5.1405 | 5.9643 | 6.2041 | 7.0096 | 7.6419
South West | Abham 132 kV | Teignmouth Gasworks | Primary Substation | 11 | Hydrogen Evolution | 0.24792 | 0.31204 | 0.38927 | 0.48202 | 0.58612 | 0.70412 | 0.83581 | 1.0175 | 1.1785 | 1.3527 | 1.5295 | 1.7004 | 1.8638 | 2.0232 | 2.2975 | 2.3832 | 2.6395 | 2.8668 | 0.56377 | 0.70224 | 0.86666 | 1.0645 | 1.2858 | 1.5353 | 1.8116 | 2.1871 | 2.5231 | 2.8868 | 3.2522 | 3.6042 | 3.9405 | 4.2701 | 4.8303 | 5.0146 | 5.5966 | 6.113
South West | Abham 132 kV | Torwood | Primary Substation | 11 | Counterfactual | 0.11585 | 0.1642 | 0.21561 | 0.27114 | 0.34066 | 0.42551 | 0.51095 | 0.63122 | 0.72879 | 0.83606 | 0.94893 | 1.062 | 1.1867 | 1.3112 | 1.431 | 1.5522 | 1.9585 | 2.0962 | 0.25999 | 0.36273 | 0.47052 | 0.58671 | 0.73202 | 0.90893 | 1.0864 | 1.3332 | 1.5345 | 1.756 | 1.9894 | 2.2216 | 2.477 | 2.7317 | 2.977 | 3.225 | 4.0646 | 4.3639
South West | Abham 132 kV | Torwood | Primary Substation | 11 | Electric Engagement | 0.16897 | 0.27544 | 0.39796 | 0.54608 | 0.70995 | 0.88503 | 1.0872 | 1.3492 | 1.5623 | 1.7444 | 1.9137 | 1.9707 | 2.0186 | 2.0699 | 2.1222 | 2.1729 | 2.4049 | 2.6304 | 0.378 | 0.60586 | 0.8631 | 1.1737 | 1.5168 | 1.8817 | 2.3006 | 2.838 | 3.2764 | 3.654 | 4.0071 | 4.133 | 4.2403 | 4.3547 | 4.4715 | 4.5848 | 5.1077 | 5.6111
South West | Abham 132 kV | Torwood | Primary Substation | 11 | Holistic Transition | 0.15774 | 0.24063 | 0.33587 | 0.43808 | 0.54269 | 0.66996 | 0.8033 | 0.98503 | 1.142 | 1.3143 | 1.5074 | 1.697 | 1.882 | 2.056 | 2.2182 | 2.3182 | 2.6119 | 2.8575 | 0.36158 | 0.54671 | 0.7543 | 0.97652 | 1.2027 | 1.4761 | 1.7601 | 2.1401 | 2.47 | 2.831 | 3.2347 | 3.6303 | 4.0163 | 4.3798 | 4.7196 | 4.935 | 5.5965 | 6.1547
South West | Abham 132 kV | Torwood | Primary Substation | 11 | Hydrogen Evolution | 0.13205 | 0.19498 | 0.26855 | 0.35228 | 0.45202 | 0.56512 | 0.68592 | 0.85452 | 0.99694 | 1.1581 | 1.3338 | 1.497 | 1.6567 | 1.8033 | 1.9423 | 2.0162 | 2.2072 | 2.3738 | 0.29603 | 0.43125 | 0.58611 | 0.76336 | 0.97377 | 1.2117 | 1.464 | 1.811 | 2.1048 | 2.4373 | 2.7997 | 3.1348 | 3.4625 | 3.7635 | 4.0496 | 4.2055 | 4.6271 | 4.9954
South West | Abham 132 kV | Torycombe | Primary Substation | 11 | Counterfactual | 2.797 | 2.8177 | 2.8469 | 2.8751 | 2.9076 | 2.9473 | 2.9931 | 3.0524 | 3.1046 | 3.1646 | 3.2169 | 3.2625 | 3.3011 | 3.3336 | 3.3726 | 3.4121 | 3.5731 | 3.6794 | 6.9805 | 7.0274 | 7.0942 | 7.1595 | 7.2347 | 7.326 | 7.4316 | 7.5655 | 7.6852 | 7.8239 | 7.9426 | 8.0443 | 8.1265 | 8.1937 | 8.2775 | 8.3624 | 8.7188 | 8.9666
South West | Abham 132 kV | Torycombe | Primary Substation | 11 | Electric Engagement | 2.8104 | 2.8445 | 2.9128 | 2.9837 | 3.0607 | 3.1454 | 3.2359 | 3.3253 | 3.4019 | 3.4703 | 3.5333 | 3.5651 | 3.5918 | 3.6089 | 3.6347 | 3.6564 | 3.7984 | 2.7776 | 7.0102 | 7.0858 | 7.2434 | 7.4071 | 7.584 | 7.7766 | 7.9797 | 8.1719 | 8.3371 | 8.4861 | 8.6246 | 8.6984 | 8.7598 | 8.7979 | 8.8576 | 8.9071 | 9.2371 | 6.6744
South West | Abham 132 kV | Torycombe | Primary Substation | 11 | Holistic Transition | 2.8077 | 2.8361 | 2.9008 | 2.9653 | 3.0398 | 3.1224 | 3.1899 | 3.2756 | 3.3415 | 3.4064 | 3.4579 | 3.5122 | 3.5658 | 3.6085 | 3.6563 | 3.6872 | 2.4482 | 3.1316 | 7.0063 | 7.0717 | 7.2259 | 7.3801 | 7.5579 | 7.7522 | 7.9072 | 8.1015 | 8.2487 | 8.3917 | 8.4998 | 8.6164 | 8.7318 | 8.8217 | 8.9251 | 8.9939 | 5.8724 | 7.5675
South West | Abham 132 kV | Torycombe | Primary Substation | 11 | Hydrogen Evolution | 2.8011 | 2.8212 | 2.8522 | 2.8871 | 2.9294 | 2.9825 | 3.0406 | 3.1112 | 3.1705 | 3.2363 | 3.2946 | 3.3465 | 3.3918 | 3.4241 | 3.4606 | 3.477 | 3.5732 | 2.7798 | 6.9896 | 7.0341 | 7.1039 | 7.1837 | 7.2808 | 7.4019 | 7.5334 | 7.6902 | 7.8199 | 7.965 | 8.0906 | 8.2011 | 8.2957 | 8.3597 | 8.4351 | 8.4685 | 8.692 | 6.693
South West | Abham 132 kV | Totnes | Primary Substation | 11 | Counterfactual | 0.79878 | 0.86699 | 0.96171 | 1.0607 | 1.1857 | 1.3506 | 1.5404 | 1.7964 | 2.0077 | 2.2374 | 2.4511 | 2.6465 | 2.8532 | 3.0615 | 3.2517 | 3.4377 | 4.1817 | 4.6129 | 1.9329 | 2.0782 | 2.2831 | 2.4973 | 2.7682 | 3.1245 | 3.5365 | 4.0845 | 4.5421 | 5.0444 | 5.5035 | 5.9156 | 6.3463 | 6.7819 | 7.1771 | 7.5628 | 9.1488 | 10.1097
South West | Abham 132 kV | Totnes | Primary Substation | 11 | Electric Engagement | 0.87163 | 1.0176 | 1.2691 | 1.5418 | 1.8546 | 2.222 | 2.6297 | 3.1299 | 3.5598 | 3.9428 | 4.2983 | 4.4904 | 4.6776 | 4.8667 | 5.0405 | 5.2056 | 5.9831 | 6.5336 | 2.0945 | 2.4079 | 2.9639 | 3.5657 | 4.2527 | 5.0514 | 5.9294 | 6.9925 | 7.9112 | 8.7385 | 9.5128 | 9.9524 | 10.3838 | 10.8216 | 11.2238 | 11.6082 | 13.4047 | 14.7173
South West | Abham 132 kV | Totnes | Primary Substation | 11 | Holistic Transition | 0.85602 | 0.96907 | 1.1839 | 1.4022 | 1.6684 | 1.9909 | 2.3653 | 2.8421 | 3.2545 | 3.6731 | 4.0489 | 4.3935 | 4.7254 | 5.0122 | 5.2724 | 5.4445 | 6.1115 | 6.5018 | 2.0714 | 2.3253 | 2.82 | 3.3223 | 3.9329 | 4.6586 | 5.505 | 6.573 | 7.4974 | 8.4288 | 9.2459 | 9.9926 | 10.7115 | 11.3248 | 11.8802 | 12.2586 | 13.7806 | 14.6807
South West | Abham 132 kV | Totnes | Primary Substation | 11 | Hydrogen Evolution | 0.82224 | 0.90915 | 1.0399 | 1.1891 | 1.3798 | 1.6282 | 1.9038 | 2.2463 | 2.5868 | 2.9589 | 3.2961 | 3.6013 | 3.8901 | 4.1651 | 4.4148 | 4.5679 | 5.1468 | 5.656 | 1.9848 | 2.1723 | 2.4555 | 2.7827 | 3.2018 | 3.7447 | 4.3438 | 5.0755 | 5.8149 | 6.6288 | 7.3509 | 7.9991 | 8.6097 | 9.1954 | 9.726 | 10.0634 | 11.4067 | 12.593
South West | Abham 132 kV | Upton Valley | Primary Substation | 11 | Counterfactual | 1.4227 | 1.5257 | 1.6418 | 1.745 | 1.8936 | 2.0412 | 2.1985 | 2.4505 | 2.6531 | 2.8515 | 3.0606 | 3.2785 | 3.522 | 3.7615 | 3.9994 | 4.2362 | 5.0329 | 5.3332 | 2.8869 | 3.1052 | 3.349 | 3.5653 | 3.8753 | 4.1822 | 4.5087 | 5.0257 | 5.4442 | 5.8527 | 6.2828 | 6.7301 | 7.2279 | 7.7175 | 8.2038 | 8.6878 | 10.3327 | 10.9772
South West | Abham 132 kV | Upton Valley | Primary Substation | 11 | Electric Engagement | 1.5223 | 1.7349 | 1.9949 | 2.2536 | 2.5808 | 2.916 | 3.3007 | 3.8236 | 4.2449 | 4.5849 | 4.8909 | 5.0065 | 5.1089 | 5.2129 | 5.3168 | 5.4148 | 5.8681 | 6.2887 | 3.1076 | 3.563 | 4.1111 | 4.6522 | 5.3374 | 6.0355 | 6.8325 | 7.9071 | 8.7759 | 9.4797 | 10.1159 | 10.3699 | 10.5968 | 10.8276 | 11.0583 | 11.2768 | 12.2999 | 13.2399
South West | Abham 132 kV | Upton Valley | Primary Substation | 11 | Holistic Transition | 1.5006 | 1.6701 | 1.8621 | 2.0368 | 2.2717 | 2.5126 | 2.7741 | 3.1355 | 3.4528 | 3.7722 | 4.1279 | 4.4896 | 4.8377 | 5.1692 | 5.4804 | 5.6739 | 6.2461 | 6.7194 | 3.0755 | 3.4539 | 3.873 | 4.2528 | 4.7609 | 5.2784 | 5.8336 | 6.5901 | 7.2576 | 7.926 | 8.6677 | 9.4222 | 10.1489 | 10.8417 | 11.4941 | 11.9107 | 13.1985 | 14.2726
South West | Abham 132 kV | Upton Valley | Primary Substation | 11 | Hydrogen Evolution | 1.4539 | 1.5835 | 1.7477 | 1.8964 | 2.1036 | 2.3174 | 2.5607 | 2.9084 | 3.2085 | 3.512 | 3.839 | 4.1631 | 4.475 | 4.7661 | 5.0376 | 5.1851 | 5.5736 | 5.8946 | 2.9561 | 3.2341 | 3.582 | 3.8949 | 4.3324 | 4.7805 | 5.287 | 6.0038 | 6.6238 | 7.2476 | 7.9187 | 8.5837 | 9.2235 | 9.8216 | 10.3805 | 10.6911 | 11.5446 | 12.2524
South West | Alverdiscott 132 kV | Ashwater | Primary Substation | 11 | Counterfactual | 0.26121 | 0.26931 | 0.28218 | 0.29637 | 0.31428 | 0.34236 | 0.37347 | 0.41534 | 0.45155 | 0.49128 | 0.52762 | 0.56085 | 0.59511 | 0.63033 | 0.66343 | 0.69708 | 0.86474 | 0.99074 | 0.59627 | 0.6136 | 0.64212 | 0.67356 | 0.71355 | 0.7747 | 0.84312 | 0.93394 | 1.0134 | 1.1018 | 1.1807 | 1.2513 | 1.323 | 1.3972 | 1.4664 | 1.5366 | 1.8933 | 2.1668
South West | Alverdiscott 132 kV | Ashwater | Primary Substation | 11 | Electric Engagement | 0.27074 | 0.2894 | 0.32851 | 0.3763 | 0.42593 | 0.49338 | 0.56776 | 0.65856 | 0.74348 | 0.82713 | 0.91001 | 0.96735 | 1.0222 | 1.0761 | 1.1817 | 1.2447 | 1.5336 | 1.6601 | 0.61744 | 0.65759 | 0.74605 | 0.85404 | 0.96529 | 1.1117 | 1.2716 | 1.465 | 1.6462 | 1.8255 | 2.0038 | 2.13 | 2.2516 | 2.3724 | 2.5956 | 2.7338 | 3.364 | 3.6613
South West | Alverdiscott 132 kV | Ashwater | Primary Substation | 11 | Holistic Transition | 0.26867 | 0.28327 | 0.32103 | 0.36175 | 0.40849 | 0.47427 | 0.55134 | 0.65 | 0.73938 | 0.83413 | 0.918 | 0.99325 | 1.0641 | 1.1227 | 1.2321 | 1.2865 | 1.526 | 1.6145 | 0.61441 | 0.64739 | 0.73667 | 0.83192 | 0.94143 | 1.089 | 1.2637 | 1.4864 | 1.687 | 1.8975 | 2.0789 | 2.2413 | 2.3945 | 2.5195 | 2.7453 | 2.8613 | 3.3788 | 3.576
South West | Alverdiscott 132 kV | Ashwater | Primary Substation | 11 | Hydrogen Evolution | 0.26427 | 0.27483 | 0.2919 | 0.31864 | 0.34832 | 0.39396 | 0.44399 | 0.50543 | 0.57534 | 0.65493 | 0.72438 | 0.78713 | 0.84527 | 0.89887 | 0.97796 | 1.0222 | 1.2104 | 1.3456 | 0.60312 | 0.6259 | 0.66348 | 0.72333 | 0.78963 | 0.88888 | 0.99728 | 1.1286 | 1.2803 | 1.4542 | 1.6027 | 1.7358 | 1.8587 | 1.9734 | 2.1385 | 2.2341 | 2.6526 | 2.9597
South West | Alverdiscott 132 kV | Barnstaple Quay | Primary Substation | 11 | Counterfactual | 0.20887 | 0.28167 | 0.35369 | 0.45967 | 0.55186 | 0.68201 | 0.78853 | 0.94393 | 1.0665 | 1.2081 | 1.3446 | 1.4864 | 1.6425 | 1.7964 | 1.9508 | 2.1064 | 2.6617 | 2.9091 | 0.47868 | 0.63364 | 0.78576 | 1.0083 | 1.202 | 1.4753 | 1.6987 | 2.0198 | 2.2751 | 2.5711 | 2.854 | 3.1461 | 3.4655 | 3.7807 | 4.097 | 4.4158 | 5.5704 | 6.1041
South West | Alverdiscott 132 kV | Barnstaple Quay | Primary Substation | 11 | Electric Engagement | 0.27125 | 0.41961 | 0.6043 | 0.82234 | 1.035 | 1.2833 | 1.5317 | 1.8625 | 2.1367 | 2.3757 | 2.5804 | 2.6645 | 2.7395 | 2.8118 | 2.889 | 2.9598 | 3.2989 | 3.5552 | 0.6168 | 0.9366 | 1.3303 | 1.7934 | 2.2423 | 2.7656 | 3.2825 | 3.9645 | 4.5328 | 5.0328 | 5.4637 | 5.652 | 5.8219 | 5.9865 | 6.1615 | 6.3236 | 7.1064 | 7.7044
South West | Alverdiscott 132 kV | Barnstaple Quay | Primary Substation | 11 | Holistic Transition | 0.25737 | 0.37808 | 0.51341 | 0.68556 | 0.84127 | 1.0389 | 1.2189 | 1.4653 | 1.6769 | 1.915 | 2.1486 | 2.3769 | 2.5958 | 2.7959 | 2.9911 | 3.1127 | 3.4933 | 3.7709 | 0.59576 | 0.86618 | 1.1653 | 1.5429 | 1.8845 | 2.3138 | 2.7027 | 3.2268 | 3.6788 | 4.1858 | 4.6777 | 5.1587 | 5.6197 | 6.0402 | 6.4518 | 6.7161 | 7.5843 | 8.2226
South West | Alverdiscott 132 kV | Barnstaple Quay | Primary Substation | 11 | Hydrogen Evolution | 0.22928 | 0.32525 | 0.44028 | 0.58728 | 0.71694 | 0.88212 | 1.0368 | 1.2546 | 1.4566 | 1.6818 | 1.9009 | 2.114 | 2.3174 | 2.5038 | 2.6855 | 2.7849 | 3.0669 | 3.3092 | 0.5238 | 0.73147 | 0.9762 | 1.2892 | 1.5637 | 1.9137 | 2.2365 | 2.6856 | 3.1056 | 3.5757 | 4.0288 | 4.469 | 4.8884 | 5.274 | 5.6512 | 5.8636 | 6.5015 | 7.0475
South West | Alverdiscott 132 kV | Bideford Main | Primary Substation | 11 | Counterfactual | 0.35433 | 0.41838 | 0.50027 | 0.59852 | 0.70663 | 0.81505 | 0.95295 | 1.1425 | 1.3013 | 1.4693 | 1.6233 | 1.779 | 1.9688 | 2.1607 | 2.3443 | 2.505 | 3.013 | 3.2197 | 0.78316 | 0.91939 | 1.0927 | 1.2998 | 1.5284 | 1.7576 | 2.0493 | 2.4457 | 2.7805 | 3.136 | 3.4589 | 3.7827 | 4.1837 | 4.5896 | 4.9761 | 5.3077 | 6.3697 | 6.8262
South West | Alverdiscott 132 kV | Bideford Main | Primary Substation | 11 | Electric Engagement | 0.4161 | 0.5488 | 0.73146 | 0.94834 | 1.1817 | 1.4195 | 1.7135 | 2.084 | 2.4104 | 2.7391 | 2.9938 | 3.0955 | 3.1941 | 3.2952 | 3.3956 | 3.4858 | 3.822 | 4.089 | 0.92022 | 1.2051 | 1.5968 | 2.0621 | 2.5606 | 3.065 | 3.6861 | 4.4596 | 5.1496 | 5.8687 | 6.4226 | 6.6534 | 6.8782 | 7.109 | 7.3378 | 7.5445 | 8.3246 | 8.9514
South West | Alverdiscott 132 kV | Bideford Main | Primary Substation | 11 | Holistic Transition | 0.40294 | 0.50777 | 0.65285 | 0.81613 | 0.99495 | 1.1807 | 1.4127 | 1.7084 | 1.9678 | 2.2448 | 2.535 | 2.8192 | 3.0681 | 3.2941 | 3.5072 | 3.6404 | 3.9997 | 4.265 | 0.90087 | 1.1354 | 1.4587 | 1.8204 | 2.2163 | 2.6239 | 3.1319 | 3.7713 | 4.3337 | 4.9344 | 5.5662 | 6.1842 | 6.7158 | 7.1948 | 7.6474 | 7.9385 | 8.764 | 9.3781
South West | Alverdiscott 132 kV | Bideford Main | Primary Substation | 11 | Hydrogen Evolution | 0.37363 | 0.45564 | 0.56573 | 0.70313 | 0.8535 | 1.0085 | 1.2064 | 1.4602 | 1.6959 | 1.9839 | 2.2513 | 2.4963 | 2.7142 | 2.9224 | 3.1195 | 3.2302 | 3.4969 | 3.7349 | 0.82609 | 1.0031 | 1.2384 | 1.5343 | 1.8577 | 2.1893 | 2.6116 | 3.1447 | 3.6445 | 4.2712 | 4.8466 | 5.367 | 5.822 | 6.2584 | 6.6723 | 6.9119 | 7.5235 | 8.0684
South West | Alverdiscott 132 kV | Bratton Fleming | Primary Substation | 11 | Counterfactual | 0.10419 | 0.11627 | 0.12853 | 0.14329 | 0.16055 | 0.18627 | 0.21334 | 0.25865 | 0.29474 | 0.32732 | 0.36244 | 0.39914 | 0.43954 | 0.47896 | 0.51829 | 0.55862 | 0.73505 | 0.85387 | 0.25039 | 0.27638 | 0.30242 | 0.33354 | 0.36976 | 0.42309 | 0.47927 | 0.57276 | 0.64759 | 0.715 | 0.78734 | 0.86261 | 0.94508 | 1.0257 | 1.1061 | 1.1884 | 1.5516 | 1.7981
South West | Alverdiscott 132 kV | Bratton Fleming | Primary Substation | 11 | Electric Engagement | 0.11669 | 0.1435 | 0.17757 | 0.21661 | 0.25929 | 0.32033 | 0.3895 | 0.4861 | 0.57215 | 0.64727 | 0.72037 | 0.76568 | 0.80688 | 0.84509 | 0.88476 | 0.92239 | 1.1201 | 1.2046 | 0.27797 | 0.33626 | 0.40855 | 0.49082 | 0.58036 | 0.70654 | 0.84919 | 1.0485 | 1.2262 | 1.3809 | 1.532 | 1.6272 | 1.7141 | 1.7953 | 1.8793 | 1.9593 | 2.3805 | 2.5687
South West | Alverdiscott 132 kV | Bratton Fleming | Primary Substation | 11 | Holistic Transition | 0.11374 | 0.13555 | 0.16083 | 0.1887 | 0.21969 | 0.27081 | 0.32473 | 0.40211 | 0.47187 | 0.54478 | 0.62116 | 0.69231 | 0.75927 | 0.81992 | 0.8822 | 0.92739 | 1.1187 | 1.2193 | 0.27342 | 0.32318 | 0.37914 | 0.44017 | 0.50774 | 0.61563 | 0.72977 | 0.89274 | 1.0397 | 1.1919 | 1.3505 | 1.4984 | 1.6377 | 1.764 | 1.8936 | 1.989 | 2.3976 | 2.6186
South West | Alverdiscott 132 kV | Bratton Fleming | Primary Substation | 11 | Hydrogen Evolution | 0.10843 | 0.12396 | 0.14361 | 0.16825 | 0.19598 | 0.23705 | 0.28301 | 0.35206 | 0.42349 | 0.4924 | 0.56148 | 0.62524 | 0.68742 | 0.7412 | 0.79666 | 0.83277 | 0.96847 | 1.0702 | 0.25968 | 0.29356 | 0.33513 | 0.38679 | 0.44487 | 0.52976 | 0.6245 | 0.76691 | 0.91434 | 1.0559 | 1.1974 | 1.3281 | 1.4555 | 1.5664 | 1.6806 | 1.7561 | 2.045 | 2.2622
South West | Alverdiscott 132 kV | Braunton | Primary Substation | 11 | Counterfactual | 0.44437 | 0.50053 | 0.56588 | 0.64031 | 0.72077 | 0.8227 | 0.9371 | 1.1039 | 1.2329 | 1.3718 | 1.5151 | 1.6631 | 1.8476 | 2.0318 | 2.2091 | 2.3635 | 2.9349 | 3.2067 | 1.0648 | 1.1843 | 1.323 | 1.4803 | 1.6502 | 1.8643 | 2.1049 | 2.4512 | 2.7209 | 3.0124 | 3.3109 | 3.6169 | 4.0088 | 4.4006 | 4.7753 | 5.0919 | 6.2821 | 6.8685
South West | Alverdiscott 132 kV | Braunton | Primary Substation | 11 | Electric Engagement | 0.50558 | 0.6264 | 0.79048 | 0.97258 | 1.1674 | 1.3999 | 1.6701 | 2.0222 | 2.3452 | 2.6537 | 2.9455 | 3.0611 | 3.1568 | 3.2509 | 3.3498 | 3.445 | 3.9117 | 4.1978 | 1.2005 | 1.4597 | 1.8105 | 2.1977 | 2.6098 | 3.0976 | 3.6616 | 4.3905 | 5.0681 | 5.7379 | 6.3777 | 6.6372 | 6.8507 | 7.0614 | 7.282 | 7.4954 | 8.5394 | 9.2028
South West | Alverdiscott 132 kV | Braunton | Primary Substation | 11 | Holistic Transition | 0.49203 | 0.58479 | 0.70781 | 0.83876 | 0.98023 | 1.1615 | 1.3882 | 1.6615 | 1.8945 | 2.154 | 2.4614 | 2.7578 | 2.9995 | 3.2103 | 3.4167 | 3.5507 | 4.0177 | 4.3059 | 1.1801 | 1.3883 | 1.6623 | 1.9523 | 2.2647 | 2.6578 | 3.1501 | 3.7356 | 4.2359 | 4.795 | 5.4657 | 6.112 | 6.6249 | 7.0674 | 7.5012 | 7.7906 | 8.833 | 9.4907
South West | Alverdiscott 132 kV | Braunton | Primary Substation | 11 | Hydrogen Evolution | 0.46414 | 0.53522 | 0.62813 | 0.73393 | 0.84897 | 0.99751 | 1.169 | 1.4006 | 1.6215 | 1.8917 | 2.1836 | 2.4467 | 2.6562 | 2.8498 | 3.0395 | 3.1493 | 3.4941 | 3.7668 | 1.1087 | 1.262 | 1.4597 | 1.6847 | 1.9286 | 2.2417 | 2.6016 | 3.082 | 3.5444 | 4.1273 | 4.7583 | 5.3219 | 5.7545 | 6.1561 | 6.5502 | 6.7847 | 7.554 | 8.1667
South West | Alverdiscott 132 kV | Clovelly | Primary Substation | 11 | Counterfactual | 0.24482 | 0.26994 | 0.29641 | 0.33066 | 0.37024 | 0.42206 | 0.47751 | 0.55762 | 0.61867 | 0.68239 | 0.74703 | 0.8132 | 0.88715 | 0.96196 | 1.0342 | 1.1071 | 1.3988 | 1.5623 | 0.58849 | 0.64261 | 0.69878 | 0.77095 | 0.85448 | 0.9629 | 1.0789 | 1.2444 | 1.3713 | 1.5041 | 1.6376 | 1.7736 | 1.9248 | 2.0781 | 2.2258 | 2.3749 | 2.9777 | 3.3225
South West | Alverdiscott 132 kV | Clovelly | Primary Substation | 11 | Electric Engagement | 0.27259 | 0.32932 | 0.40049 | 0.48921 | 0.58517 | 0.70503 | 0.84185 | 1.0155 | 1.1614 | 1.2909 | 1.4093 | 1.4703 | 1.5256 | 1.5791 | 1.6325 | 1.6933 | 1.9566 | 2.0969 | 0.64996 | 0.7733 | 0.92461 | 1.1138 | 1.3173 | 1.5685 | 1.8532 | 2.2111 | 2.5119 | 2.78 | 3.0258 | 3.1566 | 3.2761 | 3.3928 | 3.5086 | 3.6394 | 4.2115 | 4.5314
South West | Alverdiscott 132 kV | Clovelly | Primary Substation | 11 | Holistic Transition | 0.26623 | 0.3117 | 0.36527 | 0.42774 | 0.49643 | 0.59092 | 0.69508 | 0.82922 | 0.94447 | 1.0693 | 1.1971 | 1.3179 | 1.4331 | 1.5388 | 1.6401 | 1.7178 | 1.9777 | 2.1297 | 0.64025 | 0.74419 | 0.86373 | 1.0017 | 1.1528 | 1.3558 | 1.5794 | 1.8639 | 2.1081 | 2.3708 | 2.6374 | 2.89 | 3.1309 | 3.3519 | 3.5638 | 3.7284 | 4.2965 | 4.6399
South West | Alverdiscott 132 kV | Clovelly | Primary Substation | 11 | Hydrogen Evolution | 0.25374 | 0.28585 | 0.32562 | 0.38025 | 0.4404 | 0.52052 | 0.60986 | 0.72722 | 0.83536 | 0.95136 | 1.0666 | 1.1765 | 1.2817 | 1.3781 | 1.4709 | 1.5309 | 1.7156 | 1.8592 | 0.60825 | 0.67839 | 0.76282 | 0.87982 | 1.0081 | 1.1768 | 1.3636 | 1.606 | 1.8295 | 2.0693 | 2.3059 | 2.5314 | 2.7472 | 2.9461 | 3.1374 | 3.2633 | 3.6645 | 3.98
South West | Alverdiscott 132 kV | East Curry | Primary Substation | 11 | Counterfactual | 0.86541 | 0.88582 | 0.9297 | 0.97954 | 1.0407 | 1.1512 | 1.2751 | 1.4309 | 1.5698 | 1.728 | 1.8679 | 1.9825 | 2.0932 | 2.2098 | 2.3171 | 2.4253 | 2.9704 | 3.4096 | 1.9625 | 2.0059 | 2.1066 | 2.2211 | 2.362 | 2.6066 | 2.8856 | 3.233 | 3.5458 | 3.9091 | 4.222 | 4.4729 | 4.71 | 4.962 | 5.1911 | 5.4219 | 6.6213 | 7.6107
South West | Alverdiscott 132 kV | East Curry | Primary Substation | 11 | Electric Engagement | 0.89027 | 0.93664 | 1.0899 | 1.2517 | 1.4205 | 1.66 | 1.9178 | 2.2308 | 2.5302 | 2.8283 | 3.1365 | 3.3707 | 3.6886 | 3.9367 | 4.2473 | 4.6225 | 5.9564 | 6.5534 | 2.0176 | 2.117 | 2.4761 | 2.8529 | 3.243 | 3.7738 | 4.3413 | 5.0275 | 5.686 | 6.3456 | 7.0298 | 7.5596 | 8.2985 | 8.8638 | 9.549 | 10.3652 | 13.3006 | 14.7233
South West | Alverdiscott 132 kV | East Curry | Primary Substation | 11 | Holistic Transition | 0.88478 | 0.91971 | 1.0821 | 1.2492 | 1.449 | 1.7194 | 2.0473 | 2.636 | 3.015 | 3.3979 | 3.7044 | 3.9765 | 4.2433 | 4.4565 | 4.729 | 5.0344 | 6.0842 | 6.4112 | 2.0094 | 2.0879 | 2.4807 | 2.8834 | 3.3648 | 3.9875 | 4.7537 | 6.1573 | 7.0394 | 7.9242 | 8.6113 | 9.219 | 9.8135 | 10.2775 | 10.8559 | 11.5009 | 13.7867 | 14.5206
South West | Alverdiscott 132 kV | East Curry | Primary Substation | 11 | Hydrogen Evolution | 0.87332 | 0.89951 | 0.95599 | 1.0299 | 1.1194 | 1.277 | 1.4449 | 1.6447 | 1.893 | 2.1811 | 2.412 | 2.6195 | 2.8936 | 3.0921 | 3.3183 | 3.5458 | 4.4111 | 5.0214 | 1.9801 | 2.0365 | 2.165 | 2.3345 | 2.54 | 2.8891 | 3.2626 | 3.7028 | 4.265 | 4.924 | 5.4381 | 5.8939 | 6.5154 | 6.9525 | 7.441 | 7.9335 | 9.8859 | 11.3016
South West | Alverdiscott 132 kV | Fremington | Primary Substation | 11 | Counterfactual | 0.53746 | 0.56625 | 0.60935 | 0.66604 | 0.72198 | 0.79515 | 0.87697 | 0.99042 | 1.0884 | 1.2014 | 1.2875 | 1.3673 | 1.4505 | 1.5351 | 1.6177 | 1.6994 | 2.034 | 2.2237 | 1.268 | 1.329 | 1.4227 | 1.5451 | 1.667 | 1.8257 | 2.0045 | 2.2493 | 2.4629 | 2.7117 | 2.8986 | 3.0684 | 3.243 | 3.4217 | 3.5948 | 3.7655 | 4.4862 | 4.916
South West | Alverdiscott 132 kV | Fremington | Primary Substation | 11 | Electric Engagement | 0.56732 | 0.62751 | 0.7405 | 0.87313 | 1.0054 | 1.1619 | 1.3358 | 1.5585 | 1.7587 | 1.9505 | 2.1099 | 2.2011 | 2.2923 | 2.3861 | 2.4889 | 2.6365 | 3.1983 | 3.4706 | 1.3344 | 1.4629 | 1.7154 | 2.0093 | 2.3011 | 2.6414 | 3.0164 | 3.4928 | 3.9243 | 4.3429 | 4.6928 | 4.9027 | 5.1135 | 5.3309 | 5.565 | 5.8894 | 7.1699 | 7.8198
South West | Alverdiscott 132 kV | Fremington | Primary Substation | 11 | Holistic Transition | 0.56118 | 0.60741 | 0.70597 | 0.81993 | 0.93974 | 1.0843 | 1.2548 | 1.4799 | 1.6808 | 1.893 | 2.0603 | 2.3494 | 2.499 | 2.6257 | 2.756 | 2.8962 | 3.3077 | 3.4835 | 1.3254 | 1.4282 | 1.6568 | 1.9183 | 2.195 | 2.5216 | 2.9099 | 3.4191 | 3.8734 | 4.3502 | 4.7176 | 5.3913 | 5.7175 | 5.989 | 6.2669 | 6.5647 | 7.4805 | 7.8834
South West | Alverdiscott 132 kV | Fremington | Primary Substation | 11 | Hydrogen Evolution | 0.54682 | 0.58377 | 0.64 | 0.71705 | 0.79466 | 0.89726 | 1.0103 | 1.1574 | 1.3144 | 1.4971 | 1.6372 | 1.7673 | 1.8884 | 2.0061 | 2.1246 | 2.2281 | 2.6358 | 2.8931 | 1.2889 | 1.3683 | 1.4912 | 1.6601 | 1.8311 | 2.0551 | 2.3016 | 2.618 | 2.9637 | 3.3696 | 3.6737 | 3.9529 | 4.211 | 4.4637 | 4.7174 | 4.9416 | 5.8893 | 6.4905
South West | Alverdiscott 132 kV | Georgeham | Primary Substation | 11 | Counterfactual | 0.43567 | 0.46671 | 0.50201 | 0.53667 | 0.57475 | 0.61688 | 0.66296 | 0.73358 | 0.78931 | 0.84802 | 0.91012 | 0.97473 | 1.0434 | 1.1113 | 1.1805 | 1.2489 | 1.4888 | 1.587 | 1.065 | 1.1325 | 1.207 | 1.2799 | 1.3597 | 1.4478 | 1.5438 | 1.6889 | 1.8043 | 1.9255 | 2.0537 | 2.1868 | 2.3274 | 2.4663 | 2.6082 | 2.7483 | 3.2452 | 3.4565
South West | Alverdiscott 132 kV | Georgeham | Primary Substation | 11 | Electric Engagement | 0.46467 | 0.53315 | 0.61181 | 0.69374 | 0.7833 | 0.88035 | 0.99344 | 1.1434 | 1.267 | 1.3693 | 1.46 | 1.494 | 1.5193 | 1.5418 | 1.5673 | 1.5905 | 1.7663 | 1.8698 | 1.1293 | 1.2798 | 1.4466 | 1.6192 | 1.807 | 2.0099 | 2.2447 | 2.5529 | 2.8082 | 3.0204 | 3.2103 | 3.2862 | 3.3437 | 3.3956 | 3.4539 | 3.5075 | 3.9292 | 4.1696
South West | Alverdiscott 132 kV | Georgeham | Primary Substation | 11 | Holistic Transition | 0.45828 | 0.51639 | 0.57493 | 0.63194 | 0.6935 | 0.76326 | 0.84063 | 0.94455 | 1.0349 | 1.1329 | 1.2389 | 1.4715 | 1.5666 | 1.6542 | 1.7392 | 1.7901 | 1.9402 | 2.0698 | 1.1198 | 1.2535 | 1.3823 | 1.5072 | 1.6412 | 1.7916 | 1.9568 | 2.1748 | 2.3652 | 2.571 | 2.7935 | 3.334 | 3.5336 | 3.7179 | 3.8976 | 4.0092 | 4.3571 | 4.6601
South West | Alverdiscott 132 kV | Georgeham | Primary Substation | 11 | Hydrogen Evolution | 0.44496 | 0.48561 | 0.53478 | 0.58321 | 0.63685 | 0.6979 | 0.76857 | 0.86714 | 0.95365 | 1.0455 | 1.1442 | 1.2396 | 1.3271 | 1.4066 | 1.4835 | 1.5233 | 1.6866 | 1.7718 | 1.0856 | 1.1753 | 1.2801 | 1.3827 | 1.4959 | 1.6241 | 1.7714 | 1.9743 | 2.1527 | 2.3415 | 2.5444 | 2.7407 | 2.9204 | 3.0837 | 3.2425 | 3.3269 | 3.7105 | 3.9024
South West | Alverdiscott 132 kV | Great Torrington | Primary Substation | 11 | Counterfactual | 1.0994 | 1.1417 | 1.2192 | 1.305 | 0.62793 | 0.84039 | 1.061 | 1.2976 | 1.4943 | 1.7104 | 1.8782 | 2.024 | 2.1828 | 2.3484 | 2.5018 | 2.6459 | 3.3001 | 3.7439 | 2.6939 | 2.7837 | 2.9548 | 3.1443 | 1.4202 | 1.8807 | 2.3641 | 2.8812 | 3.3163 | 3.8018 | 4.1721 | 4.4863 | 4.8267 | 5.1839 | 5.5114 | 5.8151 | 7.2402 | 8.2456
South West | Alverdiscott 132 kV | Great Torrington | Primary Substation | 11 | Electric Engagement | 1.1455 | 1.2367 | 1.4536 | 1.6957 | 1.1719 | 1.5724 | 1.9855 | 2.4297 | 2.827 | 3.2301 | 3.5777 | 3.7929 | 4.0111 | 4.2389 | 4.4881 | 4.7294 | 5.7874 | 6.4053 | 2.7961 | 2.9914 | 3.485 | 4.0348 | 2.6602 | 3.5427 | 4.447 | 5.41 | 6.2779 | 7.1751 | 7.95 | 8.4439 | 8.9466 | 9.473 | 10.0375 | 10.588 | 12.988 | 14.4676
South West | Alverdiscott 132 kV | Great Torrington | Primary Substation | 11 | Holistic Transition | 1.1355 | 1.205 | 1.4098 | 1.6222 | 1.0906 | 1.4853 | 1.9251 | 2.4226 | 2.8521 | 3.2879 | 3.6434 | 3.9672 | 4.2639 | 4.5069 | 4.7646 | 4.96 | 5.7706 | 6.1213 | 2.7813 | 2.9367 | 3.4197 | 3.9186 | 2.5501 | 3.4446 | 4.4514 | 5.5928 | 6.5771 | 7.5707 | 8.3657 | 9.0875 | 9.7433 | 10.2684 | 10.8194 | 11.2464 | 13.066 | 13.8656
South West | Alverdiscott 132 kV | Great Torrington | Primary Substation | 11 | Hydrogen Evolution | 1.114 | 1.1683 | 1.2689 | 1.3994 | 0.77055 | 1.0686 | 1.3695 | 1.6756 | 1.9967 | 2.3799 | 2.6751 | 2.9352 | 3.1684 | 3.401 | 3.6359 | 3.8091 | 4.552 | 5.1514 | 2.7263 | 2.8431 | 3.0657 | 3.3588 | 1.7463 | 2.4046 | 3.0689 | 3.7364 | 4.4529 | 5.3216 | 5.9768 | 6.5453 | 7.0476 | 7.5536 | 8.0609 | 8.4461 | 10.1634 | 11.5666
South West | Alverdiscott 132 kV | Hatherleigh | Primary Substation | 11 | Counterfactual | 0.53767 | 0.56918 | 0.61838 | 0.66538 | 0.72051 | 0.79807 | 0.89771 | 1.0235 | 1.1233 | 1.2371 | 1.3436 | 1.4452 | 1.5512 | 1.659 | 1.7623 | 1.8658 | 2.3054 | 2.5745 | 1.2818 | 1.3486 | 1.455 | 1.557 | 1.6769 | 1.8445 | 2.0604 | 2.3293 | 2.5451 | 2.7939 | 3.0226 | 3.2367 | 3.4569 | 3.682 | 3.8964 | 4.1113 | 5.0434 | 5.6335
South West | Alverdiscott 132 kV | Hatherleigh | Primary Substation | 11 | Electric Engagement | 0.57479 | 0.64397 | 0.77422 | 0.90946 | 1.0542 | 1.2327 | 1.4508 | 1.711 | 1.935 | 2.1443 | 2.3406 | 2.4541 | 2.5595 | 2.6989 | 2.7981 | 2.9084 | 3.3837 | 3.6732 | 1.364 | 1.5118 | 1.7997 | 2.0971 | 2.413 | 2.7978 | 3.2649 | 3.8154 | 4.2916 | 4.74 | 5.1638 | 5.4195 | 5.6596 | 5.979 | 6.2067 | 6.4649 | 7.5423 | 8.2303
South West | Alverdiscott 132 kV | Hatherleigh | Primary Substation | 11 | Holistic Transition | 0.56623 | 0.61764 | 0.72771 | 0.83504 | 0.95779 | 1.1174 | 1.323 | 1.5741 | 1.8312 | 2.0631 | 2.3028 | 2.4951 | 2.6762 | 2.8463 | 2.9892 | 3.0861 | 3.5017 | 3.7007 | 1.351 | 1.4661 | 1.7195 | 1.9659 | 2.2476 | 2.6052 | 3.0671 | 3.6275 | 4.2115 | 4.7242 | 5.2523 | 5.6662 | 6.0569 | 6.4174 | 6.7219 | 6.9346 | 7.8651 | 8.3218
South West | Alverdiscott 132 kV | Hatherleigh | Primary Substation | 11 | Hydrogen Evolution | 0.54982 | 0.58965 | 0.65716 | 0.72936 | 0.81191 | 0.93066 | 1.0819 | 1.2603 | 1.4396 | 1.6458 | 1.8339 | 2.0069 | 2.1653 | 2.3406 | 2.4797 | 2.584 | 2.9368 | 3.2038 | 1.3087 | 1.3942 | 1.5404 | 1.6976 | 1.8772 | 2.1339 | 2.4599 | 2.8383 | 3.2254 | 3.6731 | 4.0731 | 4.4384 | 4.7719 | 5.1508 | 5.4462 | 5.6802 | 6.4864 | 7.109
South West | Alverdiscott 132 kV | Heddon Cross | Primary Substation | 11 | Counterfactual | 0.1422 | 0.15292 | 0.1844 | 0.22035 | 0.26741 | 0.34925 | 0.43859 | 0.54829 | 0.6476 | 0.76496 | 0.86374 | 0.94063 | 1.0104 | 1.0849 | 1.1534 | 1.2224 | 1.6087 | 1.9462 | 0.34637 | 0.36915 | 0.44296 | 0.52731 | 0.63752 | 0.82214 | 1.0277 | 1.2784 | 1.5075 | 1.7831 | 2.0094 | 2.1814 | 2.3337 | 2.4978 | 2.6467 | 2.7965 | 3.6622 | 4.4322
South West | Alverdiscott 132 kV | Heddon Cross | Primary Substation | 11 | Electric Engagement | 0.1549 | 0.17955 | 0.29607 | 0.41841 | 0.54793 | 0.71995 | 0.89683 | 1.1089 | 1.3154 | 1.5264 | 1.7485 | 1.9239 | 2.1025 | 2.2878 | 2.4691 | 2.6535 | 3.5048 | 3.9799 | 0.37458 | 0.42731 | 0.70556 | 0.99613 | 1.3012 | 1.6903 | 2.0881 | 2.5631 | 3.0267 | 3.5026 | 4.0045 | 4.4077 | 4.8198 | 5.2488 | 5.6661 | 6.0909 | 8.0218 | 9.1664
South West | Alverdiscott 132 kV | Heddon Cross | Primary Substation | 11 | Holistic Transition | 0.15232 | 0.17103 | 0.29265 | 0.4175 | 0.57077 | 0.76703 | 1.0053 | 1.31 | 1.5854 | 1.8631 | 2.0765 | 2.2619 | 2.4406 | 2.5772 | 2.7092 | 2.8277 | 3.4335 | 3.6513 | 0.3709 | 0.41282 | 0.70966 | 1.0133 | 1.3853 | 1.8431 | 2.4073 | 3.1294 | 3.7791 | 4.4296 | 4.9146 | 5.3352 | 5.74 | 6.0416 | 6.331 | 6.5939 | 7.9491 | 8.4412
South West | Alverdiscott 132 kV | Heddon Cross | Primary Substation | 11 | Hydrogen Evolution | 0.14627 | 0.16047 | 0.1997 | 0.25369 | 0.3233 | 0.43859 | 0.55657 | 0.69432 | 0.87677 | 1.0942 | 1.2605 | 1.405 | 1.5373 | 1.6724 | 1.804 | 1.9208 | 2.5125 | 2.9843 | 0.3554 | 0.38588 | 0.47709 | 0.6033 | 0.76583 | 1.026 | 1.294 | 1.6039 | 2.0253 | 2.5319 | 2.9094 | 3.233 | 3.5268 | 3.8301 | 4.1239 | 4.3893 | 5.763 | 6.8742
South West | Alverdiscott 132 kV | Holsworthy | Primary Substation | 11 | Counterfactual | 4.1519 | 4.1952 | 4.2816 | 4.3923 | 4.5258 | 4.7541 | 5.0036 | 5.286 | 5.5199 | 5.7826 | 6.0129 | 6.2045 | 6.4086 | 6.6239 | 6.8201 | 7.0046 | 7.9563 | 8.7338 | 10.1545 | 10.2464 | 10.4412 | 10.6883 | 10.9894 | 11.4898 | 12.0442 | 12.6697 | 13.1948 | 13.7958 | 14.3087 | 14.7255 | 15.1669 | 15.6356 | 16.0577 | 16.449 | 18.5262 | 20.2573
South West | Alverdiscott 132 kV | Holsworthy | Primary Substation | 11 | Electric Engagement | 4.1943 | 4.2833 | 4.6576 | 5.1027 | 5.5496 | 6.1345 | 6.7184 | 7.3936 | 8.0463 | 8.6888 | 9.2966 | 9.7668 | 10.3043 | 10.921 | 11.436 | 12.0069 | 14.2142 | 15.3799 | 10.2481 | 10.4394 | 11.3265 | 12.3773 | 13.4265 | 14.7501 | 16.0594 | 17.5713 | 19.0453 | 20.5005 | 21.8688 | 22.947 | 24.1866 | 25.6095 | 26.7438 | 28.0201 | 32.9789 | 35.7756
South West | Alverdiscott 132 kV | Holsworthy | Primary Substation | 11 | Holistic Transition | 4.1843 | 4.2538 | 4.6162 | 5.0015 | 5.4416 | 5.9806 | 6.5668 | 7.2703 | 8.041 | 8.6611 | 9.2138 | 9.7063 | 10.1778 | 10.5969 | 11.0653 | 11.4831 | 13.0818 | 13.7143 | 10.2327 | 10.3886 | 11.2654 | 12.1894 | 13.2466 | 14.4864 | 15.8421 | 17.4735 | 19.2846 | 20.7063 | 21.948 | 23.0531 | 24.099 | 25.0039 | 26.001 | 26.8981 | 30.4302 | 31.8715
South West | Alverdiscott 132 kV | Holsworthy | Primary Substation | 11 | Hydrogen Evolution | 4.1661 | 4.22 | 4.3336 | 4.5109 | 4.7114 | 5.0454 | 5.3959 | 5.771 | 6.1907 | 6.7117 | 7.1389 | 7.5112 | 7.8525 | 8.2887 | 8.6665 | 8.9916 | 10.3036 | 11.2912 | 10.1857 | 10.3019 | 10.5567 | 10.9593 | 11.4157 | 12.1546 | 12.9309 | 13.7529 | 14.6954 | 15.8844 | 16.8366 | 17.6536 | 18.3904 | 19.3643 | 20.1769 | 20.8862 | 23.8621 | 26.1464
South West | Alverdiscott 132 kV | Ilfracombe | Primary Substation | 11 | Counterfactual | 0.63873 | 0.72957 | 0.82445 | 0.93823 | 1.0666 | 1.2232 | 1.3961 | 1.6678 | 1.8896 | 2.115 | 2.339 | 2.5633 | 2.8248 | 3.0901 | 3.3309 | 3.5571 | 4.3206 | 4.6233 | 1.3965 | 1.5901 | 1.7894 | 2.0272 | 2.2949 | 2.6211 | 2.9805 | 3.5401 | 4.0003 | 4.4667 | 4.9299 | 5.3914 | 5.9359 | 6.4895 | 6.992 | 7.4562 | 9.0326 | 9.6768
South West | Alverdiscott 132 kV | Ilfracombe | Primary Substation | 11 | Electric Engagement | 0.73439 | 0.92805 | 1.1622 | 1.4228 | 1.718 | 2.0533 | 2.4394 | 2.968 | 3.4164 | 3.8245 | 4.1735 | 4.3059 | 4.573 | 4.7363 | 4.8223 | 4.9635 | 5.3095 | 5.6099 | 1.6093 | 2.0265 | 2.5192 | 3.065 | 3.6822 | 4.3829 | 5.1857 | 6.2766 | 7.2093 | 8.0772 | 8.8211 | 9.1161 | 9.6797 | 10.035 | 10.2313 | 10.5377 | 11.335 | 12.0231
South West | Alverdiscott 132 kV | Ilfracombe | Primary Substation | 11 | Holistic Transition | 0.71338 | 0.86582 | 1.0304 | 1.2114 | 1.416 | 1.6637 | 1.9335 | 2.3135 | 2.6446 | 3.0034 | 3.4044 | 3.7909 | 4.2847 | 4.6488 | 4.9188 | 5.1373 | 5.5907 | 5.9646 | 1.5774 | 1.9207 | 2.2798 | 2.6726 | 3.1144 | 3.6463 | 4.2209 | 5.0191 | 5.7174 | 6.4745 | 7.3314 | 8.1599 | 9.1874 | 9.9511 | 10.5173 | 10.9799 | 12.0156 | 12.8773
South West | Alverdiscott 132 kV | Ilfracombe | Primary Substation | 11 | Hydrogen Evolution | 0.67145 | 0.7878 | 0.93213 | 1.0921 | 1.2771 | 1.5006 | 1.7543 | 2.1232 | 2.453 | 2.8181 | 3.1966 | 3.5513 | 3.9449 | 4.2658 | 4.5226 | 4.6892 | 5.0002 | 5.2579 | 1.4698 | 1.7217 | 2.0269 | 2.3642 | 2.7538 | 3.2243 | 3.7548 | 4.5196 | 5.2045 | 5.9721 | 6.7678 | 7.5105 | 8.3211 | 8.9861 | 9.5182 | 9.8699 | 10.5608 | 11.1337
South West | Alverdiscott 132 kV | Lynton | Primary Substation | 11 | Counterfactual | 0.3501 | 0.36531 | 0.38161 | 0.3999 | 0.42085 | 0.44624 | 0.47458 | 0.51682 | 0.55089 | 0.58788 | 0.62469 | 0.6618 | 0.70229 | 0.74178 | 0.78153 | 0.82201 | 0.98385 | 1.0736 | 0.85501 | 0.88832 | 0.92348 | 0.96277 | 1.0077 | 1.0619 | 1.1225 | 1.2114 | 1.2838 | 1.3628 | 1.4405 | 1.5177 | 1.6012 | 1.6827 | 1.7647 | 1.8482 | 2.1879 | 2.3819
South West | Alverdiscott 132 kV | Lynton | Primary Substation | 11 | Electric Engagement | 0.36442 | 0.39943 | 0.44363 | 0.49246 | 0.54533 | 0.6061 | 0.67572 | 0.76508 | 0.84202 | 0.91 | 2.5475 | 2.5807 | 4.1846 | 4.2112 | 4.2399 | 5.8416 | 5.9753 | 6.0687 | 0.88677 | 0.96419 | 1.0605 | 1.1662 | 1.28 | 1.4092 | 1.5564 | 1.7429 | 1.9043 | 2.0479 | 6.1185 | 6.1924 | 10.1951 | 10.2555 | 10.3207 | 14.319 | 14.6245 | 14.844
South West | Alverdiscott 132 kV | Lynton | Primary Substation | 11 | Holistic Transition | 0.36115 | 0.39152 | 0.42656 | 0.4635 | 0.50479 | 0.55536 | 0.61083 | 0.68472 | 0.7494 | 0.81896 | 2.4625 | 2.5295 | 4.1671 | 4.2226 | 4.2775 | 5.8886 | 6.0229 | 6.1139 | 0.88178 | 0.95218 | 1.032 | 1.1156 | 1.2087 | 1.3203 | 1.4424 | 1.603 | 1.7438 | 1.8939 | 5.9769 | 6.1194 | 10.1901 | 10.3079 | 10.4247 | 14.4411 | 14.7456 | 14.9549
South West | Alverdiscott 132 kV | Lynton | Primary Substation | 11 | Hydrogen Evolution | 0.35483 | 0.37513 | 0.39853 | 0.42582 | 0.45675 | 0.49522 | 0.5398 | 0.60024 | 0.6604 | 0.72535 | 0.78901 | 0.84856 | 0.90518 | 0.955 | 1.0051 | 1.0351 | 1.1408 | 1.231 | 0.86552 | 0.91046 | 0.96082 | 1.0194 | 1.0857 | 1.1676 | 1.2621 | 1.3883 | 1.5151 | 1.6524 | 1.7855 | 1.9096 | 2.0273 | 2.1313 | 2.2363 | 2.301 | 2.5398 | 2.7441
South West | Alverdiscott 132 kV | Middle Barlington | Primary Substation | 11 | Counterfactual | 0.094885 | 0.10786 | 0.13543 | 0.16537 | 0.20164 | 0.27822 | 0.33999 | 0.41923 | 0.48937 | 0.57168 | 0.64155 | 0.698 | 0.75149 | 0.80846 | 0.86059 | 0.91349 | 1.19 | 1.419 | 0.22873 | 0.25597 | 0.31859 | 0.38677 | 0.46978 | 0.63844 | 0.77915 | 0.95766 | 1.1174 | 1.3081 | 1.466 | 1.5904 | 1.7056 | 1.8293 | 1.9412 | 2.0545 | 2.6669 | 3.1857
South West | Alverdiscott 132 kV | Middle Barlington | Primary Substation | 11 | Electric Engagement | 0.10708 | 0.1318 | 0.22036 | 0.31202 | 0.40641 | 0.55371 | 0.67993 | 0.8338 | 0.97917 | 1.1245 | 1.2735 | 1.3863 | 1.5 | 1.6178 | 1.7324 | 1.8484 | 2.38 | 2.6853 | 0.2556 | 0.30826 | 0.51545 | 0.72885 | 0.94745 | 1.2763 | 1.5572 | 1.8975 | 2.2204 | 2.5455 | 2.8801 | 3.139 | 3.4011 | 3.6742 | 3.9381 | 4.2056 | 5.4138 | 6.1491
South West | Alverdiscott 132 kV | Middle Barlington | Primary Substation | 11 | Holistic Transition | 0.10394 | 0.12234 | 0.21038 | 0.29897 | 0.40349 | 0.56101 | 0.71979 | 0.92488 | 1.1089 | 1.2948 | 1.4398 | 1.5675 | 1.6905 | 1.7864 | 1.8774 | 1.9555 | 2.3403 | 2.4799 | 0.25062 | 0.2914 | 0.50288 | 0.71531 | 0.96648 | 1.3287 | 1.7022 | 2.1842 | 2.6152 | 3.0472 | 3.3744 | 3.6615 | 3.9381 | 4.1482 | 4.3464 | 4.5195 | 5.3814 | 5.6985
South West | Alverdiscott 132 kV | Middle Barlington | Primary Substation | 11 | Hydrogen Evolution | 0.099121 | 0.11449 | 0.15108 | 0.19539 | 0.24786 | 0.35567 | 0.44059 | 0.54279 | 0.66981 | 0.82038 | 0.93812 | 1.042 | 1.1376 | 1.2345 | 1.327 | 1.4055 | 1.7851 | 2.0825 | 0.23802 | 0.27093 | 0.35339 | 0.45446 | 0.57466 | 0.81467 | 1.0052 | 1.2317 | 1.5216 | 1.8683 | 2.1321 | 2.3618 | 2.5714 | 2.7863 | 2.9908 | 3.1678 | 4.0481 | 4.7497
South West | Alverdiscott 132 kV | Mortonhampstead | Primary Substation | 11 | Counterfactual | 0.23398 | 0.25539 | 0.28495 | 0.31774 | 0.35621 | 0.40978 | 0.47023 | 0.55258 | 0.62223 | 0.70161 | 0.77314 | 0.83125 | 0.88988 | 0.93521 | 0.99907 | 1.065 | 1.36 | 1.5689 | 0.56868 | 0.61555 | 0.68132 | 0.75424 | 0.84003 | 0.95802 | 1.0926 | 1.2729 | 1.4274 | 1.6059 | 1.7633 | 1.8865 | 2.0082 | 2.0963 | 2.2307 | 2.3694 | 3.0073 | 3.4727
South West | Alverdiscott 132 kV | Mortonhampstead | Primary Substation | 11 | Electric Engagement | 0.25317 | 0.301 | 0.38798 | 0.48054 | 0.57762 | 0.69431 | 0.82308 | 0.96849 | 1.0978 | 1.2223 | 1.3496 | 1.4329 | 1.5138 | 1.597 | 1.6825 | 1.7696 | 2.1853 | 2.452 | 0.61095 | 0.71686 | 0.91576 | 1.126 | 1.3451 | 1.6026 | 1.8844 | 2.1951 | 2.4731 | 2.7449 | 3.0267 | 3.2177 | 3.4044 | 3.5965 | 3.793 | 3.9933 | 4.9392 | 5.5749
South West | Alverdiscott 132 kV | Mortonhampstead | Primary Substation | 11 | Holistic Transition | 0.24762 | 0.28886 | 0.36773 | 0.44886 | 0.54236 | 0.65637 | 0.77276 | 0.93403 | 1.0841 | 1.2362 | 1.3621 | 1.4784 | 1.5926 | 1.6896 | 1.7847 | 1.8607 | 2.1995 | 2.3723 | 0.60186 | 0.69768 | 0.88483 | 1.0766 | 1.2976 | 1.5595 | 1.825 | 2.1933 | 2.5374 | 2.8837 | 3.1618 | 3.4181 | 3.6697 | 3.8794 | 4.085 | 4.253 | 5.0159 | 5.4131
South West | Alverdiscott 132 kV | Mortonhampstead | Primary Substation | 11 | Hydrogen Evolution | 0.24187 | 0.27095 | 0.31104 | 0.35853 | 0.41373 | 0.49038 | 0.57602 | 0.68373 | 0.78854 | 0.90723 | 1.016 | 1.1176 | 1.2129 | 1.3059 | 1.3976 | 1.4684 | 1.7811 | 2.0296 | 0.58567 | 0.64994 | 0.7387 | 0.84467 | 0.96799 | 1.1367 | 1.3251 | 1.5584 | 1.7881 | 2.0504 | 2.2865 | 2.5058 | 2.7096 | 2.9099 | 3.1076 | 3.264 | 3.9814 | 4.5605
South West | Alverdiscott 132 kV | Morwenstow | Primary Substation | 11 | Counterfactual | 0.86668 | 0.87594 | 0.89203 | 0.90322 | 0.91622 | 0.93612 | 0.95725 | 0.98878 | 1.0143 | 1.0403 | 1.0683 | 1.0968 | 1.1289 | 1.1608 | 1.1918 | 1.2227 | 1.3526 | 1.4357 | 1.9296 | 1.9493 | 1.9831 | 2.0065 | 2.0336 | 2.0745 | 2.1179 | 2.1823 | 2.2346 | 2.288 | 2.3451 | 2.4034 | 2.4688 | 2.534 | 2.5971 | 2.6601 | 2.9258 | 3.0972
South West | Alverdiscott 132 kV | Morwenstow | Primary Substation | 11 | Electric Engagement | 0.87733 | 0.89739 | 0.93052 | 0.96049 | 0.99363 | 1.0413 | 1.097 | 1.169 | 1.2336 | 1.2937 | 1.3511 | 1.6682 | 1.6988 | 1.8068 | 1.8361 | 1.8962 | 2.1779 | 2.2353 | 1.9531 | 1.9962 | 2.0662 | 2.1288 | 2.1979 | 2.2961 | 2.4103 | 2.5572 | 2.6894 | 2.8123 | 2.9301 | 3.567 | 3.6311 | 3.8894 | 3.9511 | 4.0741 | 4.6512 | 4.7776
South West | Alverdiscott 132 kV | Morwenstow | Primary Substation | 11 | Holistic Transition | 0.87486 | 0.89018 | 0.91597 | 0.93669 | 0.95968 | 0.99786 | 1.0401 | 1.0945 | 1.3183 | 1.3747 | 1.4342 | 1.7725 | 1.8244 | 1.8717 | 1.9177 | 1.9828 | 2.2557 | 2.3225 | 1.9494 | 1.9839 | 2.0401 | 2.0849 | 2.1343 | 2.2143 | 2.3029 | 2.4161 | 2.9544 | 3.071 | 3.1939 | 3.8742 | 3.9815 | 4.0796 | 4.1749 | 4.3083 | 4.87 | 5.017
South West | Alverdiscott 132 kV | Morwenstow | Primary Substation | 11 | Hydrogen Evolution | 0.87027 | 0.88178 | 0.90436 | 0.9229 | 0.94395 | 0.9763 | 1.0129 | 1.0616 | 1.1096 | 1.1614 | 1.2142 | 1.406 | 1.4537 | 1.5756 | 1.6177 | 1.6613 | 1.8231 | 1.8898 | 1.9375 | 1.9624 | 2.0104 | 2.0493 | 2.0934 | 2.1601 | 2.2354 | 2.3348 | 2.4328 | 2.5387 | 2.6463 | 3.0319 | 3.1291 | 3.4145 | 3.5008 | 3.59 | 3.9229 | 4.0644
South West | Alverdiscott 132 kV | North Tawton | Primary Substation | 11 | Counterfactual | 0.14635 | 0.159 | 0.18295 | 0.2088 | 0.24009 | 0.28725 | 0.34235 | 0.41531 | 0.47998 | 0.55581 | 0.6223 | 0.67852 | 0.73401 | 0.79174 | 0.84564 | 0.89911 | 1.1413 | 1.3097 | 0.32932 | 0.35604 | 0.40982 | 0.46812 | 0.53908 | 0.64388 | 0.76764 | 0.92926 | 1.0741 | 1.2465 | 1.3942 | 1.5162 | 1.6343 | 1.758 | 1.8723 | 1.9857 | 2.5176 | 2.9023
South West | Alverdiscott 132 kV | North Tawton | Primary Substation | 11 | Electric Engagement | 0.16277 | 0.1919 | 0.26827 | 0.35044 | 0.4363 | 0.54346 | 0.66175 | 0.80838 | 0.94424 | 1.0763 | 1.2073 | 1.2957 | 1.3853 | 1.4781 | 1.5683 | 1.712 | 2.1302 | 2.3744 | 0.36579 | 0.42766 | 0.60375 | 0.79227 | 0.98779 | 1.2253 | 1.4852 | 1.8045 | 2.1022 | 2.3942 | 2.6857 | 2.8894 | 3.0965 | 3.3115 | 3.5197 | 3.8353 | 4.7872 | 5.3747
South West | Alverdiscott 132 kV | North Tawton | Primary Substation | 11 | Holistic Transition | 0.15926 | 0.18043 | 0.25243 | 0.32678 | 0.41401 | 0.52327 | 0.65857 | 0.83353 | 0.99142 | 1.1526 | 1.2841 | 1.4011 | 1.514 | 1.6054 | 1.6914 | 1.8121 | 2.1203 | 2.2455 | 0.3606 | 0.40766 | 0.57972 | 0.75665 | 0.96442 | 1.2164 | 1.5313 | 1.9373 | 2.3025 | 2.6726 | 2.966 | 3.2262 | 3.477 | 3.6756 | 3.862 | 4.1179 | 4.8123 | 5.0986
South West | Alverdiscott 132 kV | North Tawton | Primary Substation | 11 | Hydrogen Evolution | 0.15151 | 0.16781 | 0.19793 | 0.23613 | 0.28102 | 0.34955 | 0.42558 | 0.51892 | 0.62867 | 0.75863 | 0.86548 | 0.96224 | 1.0514 | 1.141 | 1.2257 | 1.3166 | 1.6075 | 1.8416 | 0.34085 | 0.37561 | 0.44306 | 0.52983 | 0.63195 | 0.78435 | 0.9534 | 1.158 | 1.4058 | 1.7015 | 1.938 | 2.1495 | 2.3431 | 2.5396 | 2.7247 | 2.9228 | 3.5996 | 4.1515
South West | Alverdiscott 132 kV | Northam | Primary Substation | 11 | Counterfactual | 0.17923 | 0.23242 | 0.3022 | 0.36378 | 0.42246 | 0.49805 | 0.58322 | 0.70208 | 0.80145 | 0.907 | 1.0038 | 1.1026 | 1.2133 | 1.3253 | 1.4357 | 1.5449 | 1.9169 | 2.0259 | 0.4157 | 0.52915 | 0.67581 | 0.80513 | 0.92885 | 1.0883 | 1.268 | 1.5155 | 1.7267 | 1.9509 | 2.152 | 2.3547 | 2.5809 | 2.8099 | 3.0355 | 3.2587 | 4.0292 | 4.2714
South West | Alverdiscott 132 kV | Northam | Primary Substation | 11 | Electric Engagement | 0.23201 | 0.34463 | 0.48968 | 0.64199 | 0.80205 | 0.99592 | 1.2284 | 1.5087 | 1.7108 | 1.8741 | 2.0107 | 2.045 | 2.0773 | 2.1109 | 2.1442 | 2.1761 | 2.3463 | 2.5089 | 0.53315 | 0.77558 | 1.0835 | 1.4082 | 1.7496 | 2.1658 | 2.6642 | 3.2535 | 3.6696 | 4.0076 | 4.2924 | 4.3725 | 4.4487 | 4.5277 | 4.606 | 4.6812 | 5.0808 | 5.4602
South West | Alverdiscott 132 kV | Northam | Primary Substation | 11 | Holistic Transition | 0.22091 | 0.31032 | 0.42393 | 0.53241 | 0.64279 | 0.78626 | 0.95009 | 1.1434 | 1.2949 | 1.4475 | 1.6089 | 1.772 | 1.9322 | 2.083 | 2.2222 | 2.2979 | 2.5095 | 2.6944 | 0.51674 | 0.71722 | 0.96793 | 1.2081 | 1.4534 | 1.772 | 2.1339 | 2.5503 | 2.873 | 3.1938 | 3.5314 | 3.8722 | 4.2072 | 4.5231 | 4.8152 | 4.9804 | 5.4746 | 5.9081
South West | Alverdiscott 132 kV | Northam | Primary Substation | 11 | Hydrogen Evolution | 0.19576 | 0.26522 | 0.357 | 0.44839 | 0.54184 | 0.66731 | 0.81636 | 1.0075 | 1.1398 | 1.2785 | 1.4229 | 1.5672 | 1.7072 | 1.8398 | 1.9621 | 2.0178 | 2.1526 | 2.2806 | 0.45275 | 0.60313 | 0.79903 | 0.99633 | 1.199 | 1.4729 | 1.7979 | 2.2087 | 2.4832 | 2.7691 | 3.0654 | 3.3614 | 3.6486 | 3.9213 | 4.1733 | 4.2918 | 4.6017 | 4.8945
South West | Alverdiscott 132 kV | Okehampton | Primary Substation | 11 | Counterfactual | 0.52456 | 0.58873 | 0.66721 | 0.75689 | 0.8618 | 0.97311 | 1.0794 | 1.2297 | 1.3563 | 1.4958 | 1.6334 | 1.7717 | 1.9283 | 2.084 | 2.2346 | 2.4072 | 3.0818 | 3.4482 | 1.2232 | 1.3593 | 1.5247 | 1.7131 | 1.9347 | 2.1699 | 2.394 | 2.7062 | 2.9719 | 3.2656 | 3.552 | 3.8373 | 4.1612 | 4.4837 | 4.7945 | 5.1466 | 6.5345 | 7.3013
South West | Alverdiscott 132 kV | Okehampton | Primary Substation | 11 | Electric Engagement | 0.58431 | 0.71392 | 0.89044 | 1.105 | 1.3482 | 1.6078 | 1.8779 | 2.2103 | 2.4965 | 2.7587 | 2.9966 | 3.104 | 3.2146 | 3.3158 | 3.4129 | 3.4993 | 3.8805 | 4.1335 | 1.3558 | 1.6337 | 2.0119 | 2.4744 | 2.9992 | 3.5542 | 4.1235 | 4.8124 | 5.4079 | 5.961 | 6.4671 | 6.7065 | 6.9499 | 7.1744 | 7.3903 | 7.5847 | 8.4469 | 9.0373
South West | Alverdiscott 132 kV | Okehampton | Primary Substation | 11 | Holistic Transition | 0.57138 | 0.67327 | 0.81298 | 0.97203 | 1.1505 | 1.3522 | 1.5544 | 1.8085 | 2.0348 | 2.2821 | 2.5391 | 2.783 | 3.0071 | 3.2088 | 3.3996 | 3.5189 | 3.8974 | 4.1497 | 1.3366 | 1.5638 | 1.8749 | 2.2278 | 2.6231 | 3.0647 | 3.5048 | 4.0486 | 4.5328 | 5.0593 | 5.6047 | 6.1222 | 6.5948 | 7.0189 | 7.4206 | 7.6791 | 8.5329 | 9.1132
South West | Alverdiscott 132 kV | Okehampton | Primary Substation | 11 | Hydrogen Evolution | 0.54328 | 0.62466 | 0.73178 | 0.86915 | 1.0302 | 1.2064 | 1.3799 | 1.5988 | 1.8014 | 2.0319 | 2.2922 | 2.581 | 2.8454 | 3.089 | 3.3153 | 3.4546 | 3.8274 | 4.0489 | 1.2648 | 1.4402 | 1.6692 | 1.9671 | 2.3174 | 2.6974 | 3.0666 | 3.5228 | 3.9457 | 4.4302 | 4.9726 | 5.5707 | 6.1132 | 6.6145 | 7.0808 | 7.373 | 8.1862 | 8.6868
South West | Alverdiscott 132 kV | Park Lane SWEB | Primary Substation | 11 | Counterfactual | 0.72901 | 0.81778 | 0.96247 | 1.1607 | 1.3863 | 1.698 | 2.0274 | 2.4025 | 2.7247 | 3.075 | 3.3467 | 3.5905 | 3.8887 | 4.1771 | 4.4462 | 4.676 | 5.5391 | 5.973 | 1.6093 | 1.7974 | 2.1063 | 2.5269 | 3.0078 | 3.6712 | 4.376 | 5.1739 | 5.8649 | 6.622 | 7.2031 | 7.7171 | 8.3597 | 8.983 | 9.5593 | 10.0372 | 11.8708 | 12.8348
South West | Alverdiscott 132 kV | Park Lane SWEB | Primary Substation | 11 | Electric Engagement | 0.80792 | 0.98308 | 1.2959 | 1.696 | 2.1326 | 2.6932 | 3.2928 | 3.9635 | 4.5737 | 5.2553 | 5.7835 | 6.0297 | 6.2633 | 6.4927 | 6.7716 | 6.9939 | 7.9833 | 8.5313 | 1.7843 | 2.1599 | 2.8459 | 3.7207 | 4.6728 | 5.889 | 7.1809 | 8.61 | 9.9247 | 11.4416 | 12.6159 | 13.1717 | 13.702 | 14.2234 | 14.8404 | 15.3453 | 17.5756 | 18.8747
South West | Alverdiscott 132 kV | Park Lane SWEB | Primary Substation | 11 | Holistic Transition | 0.79061 | 0.92893 | 1.2021 | 1.5386 | 1.922 | 2.4325 | 2.989 | 3.6192 | 4.1749 | 4.7753 | 5.3308 | 5.8371 | 6.2482 | 6.5915 | 6.9706 | 7.204 | 8.0722 | 8.4758 | 1.7585 | 2.0666 | 2.6863 | 3.4412 | 4.3035 | 5.4377 | 6.6785 | 8.0768 | 9.3097 | 10.6419 | 11.8761 | 13 | 13.8925 | 14.6237 | 15.4239 | 15.9331 | 17.8748 | 18.8011
South West | Alverdiscott 132 kV | Park Lane SWEB | Primary Substation | 11 | Hydrogen Evolution | 0.7539 | 0.86577 | 1.0552 | 1.3282 | 1.6381 | 2.0731 | 2.5291 | 3.0245 | 3.5037 | 4.1156 | 4.6239 | 5.0478 | 5.3939 | 5.7148 | 6.0465 | 6.2504 | 6.9748 | 7.4882 | 1.6647 | 1.9059 | 2.3157 | 2.9102 | 3.587 | 4.5356 | 5.5268 | 6.5897 | 7.6299 | 8.9926 | 10.1149 | 11.0354 | 11.7675 | 12.4492 | 13.1501 | 13.5963 | 15.2446 | 16.4344
South West | Alverdiscott 132 kV | Rock Park | Primary Substation | 11 | Counterfactual | 0.33532 | 0.41817 | 0.54053 | 0.70693 | 0.90215 | 1.117 | 1.3219 | 1.581 | 1.8093 | 2.0486 | 2.2718 | 2.4865 | 2.7711 | 3.062 | 3.3256 | 3.5555 | 4.2852 | 4.5731 | 0.78042 | 0.95617 | 1.2152 | 1.5657 | 1.9774 | 2.4314 | 2.8654 | 3.4077 | 3.89 | 4.3975 | 4.8668 | 5.3139 | 5.9209 | 6.5421 | 7.1013 | 7.5763 | 9.1059 | 9.7452
South West | Alverdiscott 132 kV | Rock Park | Primary Substation | 11 | Electric Engagement | 0.42294 | 0.59903 | 0.86807 | 1.2033 | 1.5904 | 2.0037 | 2.4219 | 2.9331 | 3.4064 | 3.9117 | 4.3016 | 4.4389 | 4.5823 | 4.7312 | 4.8632 | 4.9907 | 5.4464 | 5.8205 | 0.97493 | 1.3517 | 1.9304 | 2.6486 | 3.4771 | 4.3605 | 5.2449 | 6.3127 | 7.3188 | 8.4388 | 9.2966 | 9.6106 | 9.9397 | 10.2821 | 10.5863 | 10.8818 | 11.9541 | 12.8385
South West | Alverdiscott 132 kV | Rock Park | Primary Substation | 11 | Holistic Transition | 0.40425 | 0.53944 | 0.75189 | 1.0176 | 1.3321 | 1.675 | 2.0098 | 2.4211 | 2.7976 | 3.2044 | 3.648 | 4.0661 | 4.4239 | 4.7444 | 5.0316 | 5.2168 | 5.6988 | 6.0423 | 0.94735 | 1.2491 | 1.7225 | 2.3092 | 3.004 | 3.7583 | 4.4936 | 5.3859 | 6.2055 | 7.0937 | 8.07 | 8.9886 | 9.7566 | 10.4376 | 11.0478 | 11.4541 | 12.5725 | 13.3724
South West | Alverdiscott 132 kV | Rock Park | Primary Substation | 11 | Hydrogen Evolution | 0.36291 | 0.4691 | 0.63299 | 0.8554 | 1.1241 | 1.4217 | 1.7045 | 2.051 | 2.3915 | 2.8313 | 3.2451 | 3.5996 | 3.9118 | 4.2132 | 4.4825 | 4.6404 | 5.0228 | 5.3446 | 0.84177 | 1.0702 | 1.421 | 1.8982 | 2.4764 | 3.1176 | 3.7211 | 4.4488 | 5.1736 | 6.1418 | 7.0428 | 7.8016 | 8.455 | 9.089 | 9.6552 | 9.9984 | 10.8839 | 11.6302
South West | Alverdiscott 132 kV | Roundswell | Primary Substation | 11 | Counterfactual | 0.73807 | 0.79582 | 0.86554 | 0.9568 | 1.0527 | 1.1665 | 1.2836 | 1.4523 | 1.5902 | 1.7458 | 1.8941 | 2.0372 | 2.2012 | 2.3661 | 2.5264 | 2.6757 | 3.2562 | 3.5705 | 1.7581 | 1.8813 | 2.0323 | 2.2279 | 2.4343 | 2.6796 | 2.9341 | 3.2942 | 3.5921 | 3.9315 | 4.2493 | 4.5503 | 4.8964 | 5.2453 | 5.5825 | 5.8919 | 7.1281 | 7.8298
South West | Alverdiscott 132 kV | Roundswell | Primary Substation | 11 | Electric Engagement | 0.80081 | 0.92338 | 1.116 | 1.3352 | 1.5644 | 1.8128 | 2.0758 | 2.4186 | 2.719 | 3.0142 | 3.2732 | 3.3978 | 3.5162 | 3.6348 | 3.7953 | 3.9115 | 4.4246 | 4.8145 | 1.8986 | 2.1645 | 2.5896 | 3.0687 | 3.5672 | 4.103 | 4.6646 | 5.3889 | 6.0319 | 6.682 | 7.2534 | 7.5419 | 7.8186 | 8.0975 | 8.4796 | 8.7531 | 9.9586 | 10.8912
South West | Alverdiscott 132 kV | Roundswell | Primary Substation | 11 | Holistic Transition | 0.78726 | 0.88199 | 1.0418 | 1.2182 | 1.4127 | 1.6285 | 1.866 | 2.1861 | 2.463 | 2.838 | 3.1235 | 3.3947 | 3.635 | 3.8365 | 4.0298 | 4.1595 | 4.621 | 4.883 | 1.8775 | 2.0918 | 2.4592 | 2.86 | 3.3031 | 3.7884 | 4.326 | 5.0429 | 5.6645 | 6.5244 | 7.1533 | 7.7488 | 8.2706 | 8.7009 | 9.114 | 9.4001 | 10.4647 | 11.0733
South West | Alverdiscott 132 kV | Roundswell | Primary Substation | 11 | Hydrogen Evolution | 0.76327 | 0.84211 | 0.94461 | 1.0717 | 1.2102 | 1.3738 | 1.5422 | 1.7703 | 2.0007 | 2.285 | 2.5482 | 2.7858 | 2.9958 | 3.1948 | 3.4267 | 3.547 | 3.9768 | 4.3214 | 1.8155 | 1.989 | 2.2111 | 2.4862 | 2.7864 | 3.1405 | 3.5028 | 3.9853 | 4.4846 | 5.1138 | 5.6845 | 6.193 | 6.6357 | 7.0581 | 7.5664 | 7.8315 | 8.8329 | 9.6457
South West | Alverdiscott 132 kV | Shebbear | Primary Substation | 11 | Counterfactual | 0.35339 | 0.36872 | 0.4141 | 0.46625 | 0.53079 | 0.66275 | 0.80812 | 0.97242 | 1.1208 | 1.2914 | 1.4384 | 1.553 | 1.659 | 1.7732 | 1.8767 | 1.9819 | 2.5691 | 3.0895 | 0.81828 | 0.85091 | 0.95671 | 1.0783 | 1.2294 | 1.5225 | 1.8512 | 2.2227 | 2.5612 | 2.9584 | 3.2917 | 3.546 | 3.7757 | 4.0259 | 4.2493 | 4.4759 | 5.7793 | 6.9519
South West | Alverdiscott 132 kV | Shebbear | Primary Substation | 11 | Electric Engagement | 0.37135 | 0.40595 | 0.56898 | 0.74164 | 0.91829 | 1.1907 | 1.4779 | 1.8042 | 2.1241 | 2.4532 | 2.801 | 3.0782 | 3.3634 | 3.6772 | 3.9698 | 4.3747 | 5.7992 | 6.4992 | 0.85809 | 0.93223 | 1.3206 | 1.7292 | 2.1452 | 2.7532 | 3.3911 | 4.1144 | 4.8245 | 5.5577 | 6.3334 | 6.9604 | 7.6072 | 8.3247 | 8.9861 | 9.8742 | 13.0409 | 14.7114
South West | Alverdiscott 132 kV | Shebbear | Primary Substation | 11 | Holistic Transition | 0.36735 | 0.39378 | 0.56327 | 0.73881 | 0.94718 | 1.2501 | 1.6173 | 2.0657 | 2.5059 | 2.9191 | 3.2464 | 3.5299 | 3.8066 | 4.0276 | 4.2406 | 4.5413 | 5.5669 | 5.9156 | 0.85207 | 0.91146 | 1.3242 | 1.7498 | 2.2558 | 2.9528 | 3.8116 | 4.8654 | 5.8992 | 6.858 | 7.594 | 8.2303 | 8.8501 | 9.332 | 9.7931 | 10.4305 | 12.6818 | 13.458
South West | Alverdiscott 132 kV | Shebbear | Primary Substation | 11 | Hydrogen Evolution | 0.35943 | 0.37951 | 0.43554 | 0.51316 | 0.60646 | 0.79265 | 0.98625 | 1.194 | 1.4641 | 1.7829 | 2.0292 | 2.2468 | 2.451 | 2.6777 | 2.8838 | 3.1237 | 4.061 | 4.7856 | 0.83167 | 0.87484 | 1.0046 | 1.1853 | 1.4034 | 1.8179 | 2.252 | 2.715 | 3.3334 | 4.0705 | 4.625 | 5.1082 | 5.5573 | 6.0654 | 6.5203 | 7.0444 | 9.1838 | 10.8659
South West | Alverdiscott 132 kV | South Molton | Primary Substation | 11 | Counterfactual | 0.72325 | 0.93803 | 1.0223 | 1.1173 | 1.2329 | 1.4022 | 1.5937 | 1.8304 | 2.0429 | 2.2666 | 2.4626 | 2.6378 | 2.8641 | 3.0882 | 3.2902 | 3.455 | 4.2357 | 4.7966 | 1.7457 | 2.2622 | 2.4511 | 2.6635 | 2.9228 | 3.2981 | 3.7273 | 4.2524 | 4.7288 | 5.2401 | 5.678 | 6.0587 | 6.559 | 7.0574 | 7.502 | 7.8518 | 9.5659 | 10.8394
South West | Alverdiscott 132 kV | South Molton | Primary Substation | 11 | Electric Engagement | 0.92782 | 1.042 | 1.3171 | 1.6123 | 1.9254 | 2.3047 | 2.7051 | 3.1821 | 3.649 | 4.1656 | 4.6571 | 4.9495 | 5.2444 | 5.5266 | 5.7859 | 6.0545 | 7.2676 | 8.0761 | 2.2436 | 2.4918 | 3.1291 | 3.8094 | 4.5255 | 5.3755 | 6.2656 | 7.3173 | 8.3598 | 9.5484 | 10.6807 | 11.3623 | 12.0529 | 12.7164 | 13.3215 | 13.9524 | 16.7749 | 18.7285
South West | Alverdiscott 132 kV | South Molton | Primary Substation | 11 | Holistic Transition | 0.91723 | 1.0127 | 1.2735 | 1.5413 | 1.8589 | 2.2409 | 2.6804 | 3.2317 | 3.7259 | 4.2249 | 4.7083 | 5.1623 | 5.5307 | 5.8058 | 6.07 | 6.2768 | 7.201 | 7.6413 | 2.2275 | 2.4435 | 3.0656 | 3.7017 | 4.4555 | 5.338 | 6.3612 | 7.6425 | 8.7887 | 9.9449 | 11.0537 | 12.0923 | 12.9195 | 13.5225 | 14.0996 | 14.5625 | 16.6785 | 17.6953
South West | Alverdiscott 132 kV | South Molton | Primary Substation | 11 | Hydrogen Evolution | 0.89614 | 0.96858 | 1.0812 | 1.221 | 1.3906 | 1.6359 | 1.9024 | 2.2139 | 2.5868 | 3.0633 | 3.4884 | 3.8485 | 4.1299 | 4.3932 | 4.6471 | 4.8384 | 5.7193 | 6.4485 | 2.1734 | 2.3314 | 2.5823 | 2.8958 | 3.2769 | 3.8227 | 4.4154 | 5.0989 | 5.9364 | 7.0371 | 8.0061 | 8.8142 | 9.4263 | 10.0054 | 10.5624 | 10.9955 | 13.0604 | 14.7832
South West | Alverdiscott 132 kV | Stratton | Primary Substation | 11 | Counterfactual | 0.86879 | 0.96952 | 1.0869 | 1.2259 | 1.3646 | 1.5405 | 1.7367 | 2.0164 | 2.2471 | 2.4856 | 2.7242 | 2.9563 | 3.2095 | 3.4635 | 3.7076 | 3.9532 | 4.869 | 5.3462 | 1.9429 | 2.1589 | 2.4093 | 2.7041 | 3.0008 | 3.3742 | 3.7911 | 4.3777 | 4.8661 | 5.3741 | 5.8762 | 6.3589 | 6.881 | 7.4062 | 7.9092 | 8.4149 | 10.3345 | 11.3709
South West | Alverdiscott 132 kV | Stratton | Primary Substation | 11 | Electric Engagement | 0.96128 | 1.1708 | 1.4546 | 1.7949 | 2.1364 | 2.5765 | 3.0369 | 3.626 | 4.1288 | 4.5616 | 4.9618 | 5.1675 | 5.3706 | 5.6181 | 5.898 | 6.2549 | 7.2083 | 7.7473 | 2.148 | 2.6031 | 3.2166 | 3.9552 | 4.6915 | 5.6232 | 6.5949 | 7.8267 | 8.8803 | 9.7928 | 10.6419 | 11.0984 | 11.5513 | 12.0947 | 12.7004 | 13.4747 | 15.5922 | 16.8469
South West | Alverdiscott 132 kV | Stratton | Primary Substation | 11 | Holistic Transition | 0.9406 | 1.1116 | 1.3501 | 1.6122 | 1.8841 | 2.2254 | 2.6124 | 3.114 | 3.5587 | 4.0064 | 4.5039 | 4.9117 | 5.3112 | 5.7167 | 6.1399 | 6.508 | 7.4013 | 7.9017 | 2.1166 | 2.5043 | 3.0438 | 3.6327 | 4.2445 | 4.9955 | 5.8491 | 6.9435 | 7.9151 | 8.8849 | 9.9684 | 10.8359 | 11.6859 | 12.5383 | 13.4235 | 14.1985 | 16.1825 | 17.3228
South West | Alverdiscott 132 kV | Stratton | Primary Substation | 11 | Hydrogen Evolution | 0.8987 | 1.0284 | 1.1914 | 1.4028 | 1.6128 | 1.8793 | 2.1774 | 2.5668 | 2.9461 | 3.3378 | 3.7161 | 4.0763 | 4.4279 | 4.7813 | 5.1361 | 5.4271 | 6.0945 | 6.6202 | 2.0094 | 2.2926 | 2.6423 | 3.1021 | 3.5574 | 4.1281 | 4.7629 | 5.5796 | 6.3845 | 7.2163 | 8.0084 | 8.7596 | 9.4915 | 10.2292 | 10.9675 | 11.5932 | 13.0836 | 14.2695
South West | Alverdiscott 132 kV | Tinkers Cross | Primary Substation | 11 | Counterfactual | 0.43665 | 0.46981 | 0.53367 | 0.61564 | 0.71312 | 0.84694 | 0.99435 | 1.1864 | 1.3516 | 1.535 | 1.6988 | 1.8317 | 1.9612 | 2.097 | 2.2246 | 2.3539 | 3.0085 | 3.5294 | 1.009 | 1.0799 | 1.2233 | 1.4058 | 1.6242 | 1.9197 | 2.2501 | 2.6757 | 3.0461 | 3.4652 | 3.8299 | 4.1191 | 4.3951 | 4.6868 | 4.958 | 5.2325 | 6.6626 | 7.8263
South West | Alverdiscott 132 kV | Tinkers Cross | Primary Substation | 11 | Electric Engagement | 0.46735 | 0.53612 | 0.72818 | 0.94975 | 1.1838 | 1.4678 | 1.7731 | 2.1486 | 2.4967 | 2.8371 | 3.1873 | 3.4419 | 3.6981 | 3.9773 | 4.2373 | 4.4992 | 5.8417 | 6.4955 | 1.0769 | 1.2255 | 1.6702 | 2.1789 | 2.713 | 3.3416 | 4.0125 | 4.8327 | 5.5954 | 6.3455 | 7.1205 | 7.6959 | 8.2777 | 8.9102 | 9.4998 | 10.0947 | 13.0757 | 14.6346
South West | Alverdiscott 132 kV | Tinkers Cross | Primary Substation | 11 | Holistic Transition | 0.46016 | 0.51541 | 0.70485 | 0.91421 | 1.1597 | 1.4568 | 1.8128 | 2.2722 | 2.681 | 3.094 | 3.4358 | 3.7353 | 4.0239 | 4.2745 | 4.5032 | 4.6957 | 5.7338 | 6.0976 | 1.0657 | 1.1905 | 1.6423 | 2.1364 | 2.7171 | 3.3972 | 4.2226 | 5.2864 | 6.2295 | 7.1754 | 7.9347 | 8.5983 | 9.2374 | 9.7778 | 10.2707 | 10.6919 | 12.9661 | 13.7842
South West | Alverdiscott 132 kV | Tinkers Cross | Primary Substation | 11 | Hydrogen Evolution | 0.44727 | 0.48999 | 0.57383 | 0.69603 | 0.8394 | 1.0318 | 1.2376 | 1.4912 | 1.7861 | 2.1212 | 2.3974 | 2.6388 | 2.8637 | 3.0954 | 3.3137 | 3.4934 | 4.3913 | 5.0506 | 1.0323 | 1.125 | 1.3127 | 1.5877 | 1.9115 | 2.337 | 2.7931 | 3.3486 | 4.0109 | 4.7706 | 5.3806 | 5.9072 | 6.3944 | 6.9006 | 7.3766 | 7.7766 | 9.8154 | 11.3468
South West | Alverdiscott 132 kV | Whiddon Down | Primary Substation | 11 | Counterfactual | 0.24669 | 0.26834 | 0.29534 | 0.32533 | 0.35988 | 0.40627 | 0.45846 | 0.53496 | 0.59992 | 0.67231 | 0.74333 | 0.81315 | 0.88715 | 0.96126 | 1.0336 | 1.1195 | 1.486 | 1.7162 | 0.59239 | 0.63847 | 0.69645 | 0.76079 | 0.8349 | 0.9335 | 1.0449 | 1.2058 | 1.3437 | 1.4986 | 1.6486 | 1.7942 | 1.947 | 2.1004 | 2.2498 | 2.4259 | 3.1863 | 3.6724
South West | Alverdiscott 132 kV | Whiddon Down | Primary Substation | 11 | Electric Engagement | 0.27323 | 0.3226 | 0.39754 | 0.4811 | 0.57174 | 0.68389 | 0.81497 | 0.98482 | 1.1373 | 1.2789 | 1.4111 | 1.4845 | 1.5612 | 1.6323 | 1.7014 | 1.765 | 2.051 | 2.2171 | 0.65127 | 0.75697 | 0.92 | 1.1005 | 1.2949 | 1.5323 | 1.8078 | 2.1618 | 2.4813 | 2.7799 | 3.0603 | 3.2217 | 3.3901 | 3.5479 | 3.7008 | 3.8429 | 4.4802 | 4.868
South West | Alverdiscott 132 kV | Whiddon Down | Primary Substation | 11 | Holistic Transition | 0.26749 | 0.30452 | 0.3633 | 0.42634 | 0.49754 | 0.59164 | 0.703 | 0.85005 | 0.98536 | 1.1321 | 1.2717 | 1.4019 | 1.5249 | 1.6324 | 1.7346 | 1.8038 | 2.0578 | 2.1951 | 0.64275 | 0.7259 | 0.85967 | 1.0019 | 1.1624 | 1.369 | 1.6142 | 1.935 | 2.23 | 2.5475 | 2.8442 | 3.1205 | 3.3816 | 3.6085 | 3.824 | 3.9736 | 4.5379 | 4.8501
South West | Alverdiscott 132 kV | Whiddon Down | Primary Substation | 11 | Hydrogen Evolution | 0.25515 | 0.28293 | 0.32055 | 0.36517 | 0.41616 | 0.48732 | 0.57014 | 0.68064 | 0.79384 | 0.92299 | 1.0589 | 1.2067 | 1.3451 | 1.4735 | 1.5935 | 1.674 | 1.9248 | 2.0833 | 0.61119 | 0.67098 | 0.7517 | 0.84752 | 0.95694 | 1.1079 | 1.283 | 1.5137 | 1.7541 | 2.0294 | 2.3134 | 2.619 | 2.9048 | 3.1714 | 3.4206 | 3.5907 | 4.1424 | 4.5031
South West | Axminster 132 kV | Axminster | Primary Substation | 11 | Counterfactual | 0.28793 | 0.33076 | 0.38766 | 0.45557 | 0.5358 | 0.63094 | 0.73897 | 0.89207 | 1.0186 | 1.1552 | 1.2885 | 1.4207 | 1.5649 | 1.708 | 1.851 | 2.0241 | 2.5434 | 2.7892 | 0.67635 | 0.76749 | 0.88879 | 1.033 | 1.2033 | 1.4053 | 1.635 | 1.9562 | 2.224 | 2.5147 | 2.7957 | 3.0712 | 3.3701 | 3.6674 | 3.9656 | 4.3389 | 5.4387 | 5.9781
South West | Axminster 132 kV | Axminster | Primary Substation | 11 | Electric Engagement | 0.34019 | 0.43717 | 0.58189 | 0.75272 | 0.94176 | 1.154 | 1.3981 | 1.7097 | 1.977 | 2.2119 | 2.4288 | 2.6122 | 2.7051 | 2.7958 | 2.884 | 2.9678 | 3.3533 | 3.6561 | 0.79237 | 1.0001 | 1.3123 | 1.6794 | 2.0837 | 2.5353 | 3.0515 | 3.7034 | 4.2664 | 4.7669 | 5.2355 | 5.6711 | 5.8835 | 6.0918 | 6.2942 | 6.4876 | 7.3796 | 8.0863
South West | Axminster 132 kV | Axminster | Primary Substation | 11 | Holistic Transition | 0.32923 | 0.40259 | 0.51819 | 0.65042 | 0.80248 | 0.98119 | 1.1843 | 1.4466 | 1.6773 | 1.9179 | 2.1502 | 2.3714 | 2.639 | 2.866 | 3.0452 | 3.162 | 3.5593 | 3.8428 | 0.77636 | 0.94131 | 1.2015 | 1.4965 | 1.8353 | 2.2291 | 2.6765 | 3.2478 | 3.7513 | 4.2736 | 4.7714 | 5.245 | 5.8375 | 6.3345 | 6.7159 | 6.9722 | 7.8804 | 8.5306
South West | Axminster 132 kV | Axminster | Primary Substation | 11 | Hydrogen Evolution | 0.3043 | 0.35906 | 0.43826 | 0.53998 | 0.65766 | 0.79906 | 0.96184 | 1.1743 | 1.38 | 1.6032 | 1.8173 | 2.0572 | 2.3032 | 2.4798 | 2.6469 | 2.7446 | 3.0653 | 3.3392 | 0.71274 | 0.83073 | 1.0002 | 1.2184 | 1.4709 | 1.7738 | 2.1207 | 2.567 | 3.004 | 3.4812 | 3.9326 | 4.4523 | 4.9898 | 5.3613 | 5.7128 | 5.9257 | 6.6595 | 7.2867
South West | Axminster 132 kV | Beaminster | Primary Substation | 11 | Counterfactual | 0.32942 | 0.36909 | 0.42979 | 0.48792 | 0.54323 | 0.59687 | 0.65741 | 0.75196 | 0.83042 | 0.91912 | 1.0072 | 1.0955 | 1.2011 | 1.3084 | 1.4144 | 1.5332 | 1.8823 | 2.0149 | 0.7922 | 0.87646 | 1.0046 | 1.1267 | 1.2428 | 1.3553 | 1.4822 | 1.6775 | 1.8412 | 2.0267 | 2.2096 | 2.3915 | 2.6086 | 2.8295 | 3.0484 | 3.2992 | 4.0269 | 4.3139
South West | Axminster 132 kV | Beaminster | Primary Substation | 11 | Electric Engagement | 0.37049 | 0.45448 | 0.58089 | 0.70889 | 0.83785 | 0.96891 | 1.1293 | 1.3372 | 1.5148 | 1.6696 | 1.8074 | 1.8907 | 1.9451 | 1.999 | 2.0523 | 2.1015 | 2.295 | 2.4387 | 0.88351 | 1.0635 | 1.3342 | 1.6054 | 1.8771 | 2.1507 | 2.4861 | 2.9146 | 3.2823 | 3.6051 | 3.8959 | 4.0916 | 4.2141 | 4.3363 | 4.4569 | 4.569 | 5.0141 | 5.3489
South West | Axminster 132 kV | Beaminster | Primary Substation | 11 | Holistic Transition | 0.36196 | 0.42704 | 0.52368 | 0.61856 | 0.71166 | 0.80882 | 0.92349 | 1.0771 | 1.2163 | 1.3683 | 1.5211 | 1.665 | 1.836 | 1.9901 | 2.1211 | 2.2025 | 2.4222 | 2.5795 | 0.87105 | 1.0165 | 1.2295 | 1.4378 | 1.6418 | 1.852 | 2.1003 | 2.4272 | 2.7241 | 3.0462 | 3.3672 | 3.6692 | 4.0385 | 4.3695 | 4.646 | 4.8233 | 5.3251 | 5.6884
South West | Axminster 132 kV | Beaminster | Primary Substation | 11 | Hydrogen Evolution | 0.34232 | 0.39329 | 0.47606 | 0.55627 | 0.63459 | 0.71378 | 0.81247 | 0.94796 | 1.0776 | 1.2205 | 1.3634 | 1.5116 | 1.6714 | 1.7991 | 1.9206 | 1.9871 | 2.1473 | 2.2773 | 0.82093 | 0.93077 | 1.1087 | 1.2793 | 1.4451 | 1.6111 | 1.8189 | 2.0994 | 2.3689 | 2.6666 | 2.9619 | 3.2743 | 3.6149 | 3.8805 | 4.1335 | 4.2762 | 4.6382 | 4.9318
South West | Axminster 132 kV | Bridport | Primary Substation | 11 | Counterfactual | 0.6938 | 0.80708 | 0.95895 | 1.1673 | 1.3882 | 1.6458 | 1.8711 | 2.1971 | 2.4318 | 2.6786 | 2.9398 | 3.2019 | 3.4872 | 3.7632 | 4.0312 | 4.3028 | 5.2218 | 5.5708 | 1.6299 | 1.8714 | 2.1902 | 2.6256 | 3.087 | 3.6251 | 4.0947 | 4.7668 | 5.2525 | 5.762 | 6.3055 | 6.8437 | 7.4268 | 7.9902 | 8.5374 | 9.0913 | 10.9867 | 11.732
South West | Axminster 132 kV | Bridport | Primary Substation | 11 | Electric Engagement | 0.81197 | 1.0535 | 1.3768 | 1.7837 | 2.2234 | 2.7255 | 3.2424 | 3.9 | 4.4059 | 4.8207 | 5.1948 | 5.3244 | 5.4382 | 5.5383 | 5.6366 | 5.7236 | 6.1678 | 6.5322 | 1.8922 | 2.412 | 3.0944 | 3.9527 | 4.8785 | 5.9367 | 7.0213 | 8.3808 | 9.4249 | 10.2845 | 11.0727 | 11.3602 | 11.6135 | 11.8386 | 12.0597 | 12.2571 | 13.2788 | 14.1154
South West | Axminster 132 kV | Bridport | Primary Substation | 11 | Holistic Transition | 0.78681 | 0.97634 | 1.2175 | 1.5233 | 1.8495 | 2.2446 | 2.611 | 3.0857 | 3.4652 | 3.8568 | 4.2871 | 4.6896 | 5.0789 | 5.4338 | 5.769 | 5.9646 | 6.5416 | 7.0047 | 1.8551 | 2.2816 | 2.8077 | 3.4712 | 4.1775 | 5.0297 | 5.816 | 6.8167 | 7.6156 | 8.4355 | 9.3423 | 10.1841 | 10.9971 | 11.7403 | 12.4436 | 12.8667 | 14.1819 | 15.2489
South West | Axminster 132 kV | Bridport | Primary Substation | 11 | Hydrogen Evolution | 0.73097 | 0.87487 | 1.084 | 1.3635 | 1.6655 | 2.0256 | 2.371 | 2.8294 | 3.2001 | 3.5804 | 3.9906 | 4.3708 | 4.7329 | 5.0584 | 5.3655 | 5.5165 | 5.8937 | 6.213 | 1.7125 | 2.0237 | 2.4679 | 3.0617 | 3.7031 | 4.4686 | 5.1991 | 6.153 | 6.9182 | 7.7002 | 8.5514 | 9.3327 | 10.0756 | 10.7444 | 11.3758 | 11.6945 | 12.5342 | 13.243
South West | Axminster 132 kV | Chard | Primary Substation | 11 | Counterfactual | 1.0493 | 1.1484 | 1.2455 | 1.3975 | 1.5722 | 1.7639 | 1.9199 | 2.1441 | 2.3312 | 2.5391 | 2.7398 | 2.9345 | 3.1424 | 3.3539 | 3.567 | 3.7755 | 4.5042 | 4.8019 | 2.588 | 2.7986 | 3.0036 | 3.3226 | 3.6928 | 4.0984 | 4.4292 | 4.8976 | 5.2953 | 5.7412 | 6.1657 | 6.5713 | 6.9968 | 7.4297 | 7.8662 | 8.2932 | 9.8035 | 10.4466
South West | Axminster 132 kV | Chard | Primary Substation | 11 | Electric Engagement | 1.1396 | 1.357 | 1.6302 | 1.9664 | 2.4789 | 2.8221 | 3.2209 | 3.7242 | 4.1316 | 4.4764 | 4.7748 | 4.8789 | 4.9815 | 5.0833 | 5.1859 | 5.2819 | 5.8334 | 6.1615 | 2.7884 | 3.2564 | 3.8397 | 4.5674 | 5.7183 | 6.4543 | 7.304 | 8.3579 | 9.2087 | 9.9338 | 10.5639 | 10.7949 | 11.0239 | 11.2517 | 11.4813 | 11.6971 | 12.9675 | 13.7262
South West | Axminster 132 kV | Chard | Primary Substation | 11 | Holistic Transition | 1.1202 | 1.2968 | 1.5049 | 1.7738 | 2.0721 | 2.3403 | 2.6281 | 3.0147 | 3.342 | 3.6704 | 3.9874 | 4.5083 | 4.8139 | 5.0971 | 5.3628 | 5.5249 | 6.0562 | 6.4157 | 2.76 | 3.1538 | 3.619 | 4.2154 | 4.8781 | 5.4723 | 6.1059 | 6.945 | 7.6538 | 8.3546 | 9.0166 | 10.1912 | 10.8317 | 11.4251 | 11.9834 | 12.3337 | 13.5446 | 14.3728
South West | Axminster 132 kV | Chard | Primary Substation | 11 | Hydrogen Evolution | 1.0773 | 1.221 | 1.3964 | 1.6308 | 1.8851 | 2.1095 | 2.3656 | 2.7149 | 3.0043 | 3.312 | 3.6195 | 3.9031 | 4.1794 | 4.4405 | 4.6852 | 4.8111 | 5.2839 | 5.5771 | 2.6504 | 2.9612 | 3.3361 | 3.8485 | 4.4046 | 4.8926 | 5.4464 | 6.191 | 6.8025 | 7.4504 | 8.0909 | 8.6734 | 9.2408 | 9.7789 | 10.284 | 10.5509 | 11.6424 | 12.3036
South West | Axminster 132 kV | Coker | Primary Substation | 11 | Counterfactual | 0.40526 | 0.42798 | 0.45989 | 0.50907 | 0.56287 | 0.64094 | 0.73283 | 0.81783 | 0.8918 | 1.0088 | 1.1141 | 1.1955 | 1.2665 | 1.3406 | 1.4022 | 1.4636 | 1.7476 | 1.9435 | 1.0001 | 1.0489 | 1.1206 | 1.229 | 1.3487 | 1.5208 | 1.7251 | 1.915 | 2.0824 | 2.3462 | 2.5795 | 2.7567 | 2.9083 | 3.0672 | 3.1985 | 3.3293 | 3.9558 | 4.4068
South West | Axminster 132 kV | Coker | Primary Substation | 11 | Electric Engagement | 0.425 | 0.47631 | 0.58825 | 0.70882 | 0.84038 | 0.97976 | 1.1322 | 1.3002 | 1.5195 | 1.698 | 1.8604 | 1.9596 | 2.0571 | 2.1571 | 2.2546 | 2.3521 | 2.7897 | 3.0811 | 1.044 | 1.1556 | 1.4124 | 1.687 | 1.9848 | 2.2958 | 2.633 | 3.0008 | 3.4837 | 3.8804 | 4.2439 | 4.4747 | 4.703 | 4.938 | 5.1664 | 5.3953 | 6.4116 | 7.1176
South West | Axminster 132 kV | Coker | Primary Substation | 11 | Holistic Transition | 0.42099 | 0.46465 | 0.56486 | 0.68369 | 0.8198 | 0.96672 | 1.2056 | 1.4413 | 1.6397 | 1.8254 | 1.9724 | 2.1063 | 2.2357 | 2.3382 | 2.4348 | 2.5094 | 2.8353 | 2.9842 | 1.0383 | 1.1368 | 1.3748 | 1.6526 | 1.972 | 2.3117 | 2.8596 | 3.4051 | 3.8645 | 4.2928 | 4.6224 | 4.9214 | 5.2106 | 5.4349 | 5.6461 | 5.8135 | 6.5623 | 6.9085
South West | Axminster 132 kV | Coker | Primary Substation | 11 | Hydrogen Evolution | 0.41133 | 0.4454 | 0.49999 | 0.5695 | 0.6488 | 0.74229 | 0.84524 | 0.95494 | 1.1183 | 1.3041 | 1.4489 | 1.5695 | 1.6811 | 1.7806 | 1.8751 | 1.9452 | 2.2642 | 2.5313 | 1.0137 | 1.0881 | 1.2096 | 1.365 | 1.5432 | 1.7522 | 1.9821 | 2.2239 | 2.5917 | 3.0131 | 3.3343 | 3.5989 | 3.8424 | 4.0614 | 4.269 | 4.4284 | 5.1822 | 5.8192
South West | Axminster 132 kV | Colyford | Primary Substation | 11 | Counterfactual | 0.44616 | 0.5237 | 0.62277 | 0.7398 | 0.87826 | 1.0275 | 1.1905 | 1.4269 | 1.6189 | 1.8208 | 2.0254 | 2.2363 | 2.4694 | 2.7001 | 2.9266 | 3.1612 | 3.9269 | 4.2295 | 1.0326 | 1.1978 | 1.4059 | 1.6511 | 1.9409 | 2.253 | 2.5931 | 3.0804 | 3.4792 | 3.8982 | 4.3219 | 4.7569 | 5.2367 | 5.7114 | 6.178 | 6.6653 | 8.2569 | 8.9115
South West | Axminster 132 kV | Colyford | Primary Substation | 11 | Electric Engagement | 0.53985 | 0.71551 | 0.94062 | 1.2145 | 1.5252 | 1.8591 | 2.2426 | 2.7368 | 3.1518 | 3.5031 | 3.806 | 3.9493 | 4.0535 | 4.1518 | 4.258 | 4.3474 | 4.7671 | 5.1384 | 1.2414 | 1.6179 | 2.093 | 2.671 | 3.3254 | 4.0266 | 4.8268 | 5.8469 | 6.7077 | 7.4422 | 8.0797 | 8.4081 | 8.643 | 8.8657 | 9.1036 | 9.3074 | 10.272 | 11.1216
South West | Axminster 132 kV | Colyford | Primary Substation | 11 | Holistic Transition | 0.52112 | 0.65557 | 0.82495 | 1.0253 | 1.2566 | 1.5154 | 1.7966 | 2.1591 | 2.4775 | 2.8138 | 3.1608 | 3.4986 | 3.8428 | 4.1579 | 4.4505 | 4.6224 | 5.1402 | 5.5853 | 1.2145 | 1.5163 | 1.8879 | 2.3246 | 2.827 | 3.3864 | 3.9892 | 4.754 | 5.4284 | 6.1379 | 6.8679 | 7.5793 | 8.3114 | 8.9805 | 9.5975 | 9.9722 | 11.1567 | 12.178
South West | Axminster 132 kV | Colyford | Primary Substation | 11 | Hydrogen Evolution | 0.47578 | 0.57672 | 0.71058 | 0.88155 | 1.0808 | 1.3017 | 1.5508 | 1.8804 | 2.1769 | 2.4909 | 2.8113 | 3.1331 | 3.4476 | 3.7183 | 3.9771 | 4.1104 | 4.4669 | 4.7905 | 1.0992 | 1.3168 | 1.601 | 1.9648 | 2.3885 | 2.8569 | 3.3812 | 4.0653 | 4.6823 | 5.3356 | 5.9996 | 6.6719 | 7.3308 | 7.8919 | 8.4288 | 8.7143 | 9.5173 | 10.2424
South West | Axminster 132 kV | Crewkerne | Primary Substation | 11 | Counterfactual | 2.9336 | 3.0028 | 3.0807 | 3.2054 | 3.3267 | 3.4894 | 3.639 | 3.8443 | 4.0212 | 4.2541 | 4.4754 | 4.6631 | 4.868 | 5.0778 | 5.2704 | 5.4588 | 6.2096 | 6.6209 | 7.3042 | 7.4518 | 7.6206 | 7.8871 | 8.1498 | 8.5 | 8.826 | 9.2667 | 9.6532 | 10.1645 | 10.6427 | 11.0383 | 11.4672 | 11.9071 | 12.3093 | 12.7012 | 14.2974 | 15.207
South West | Axminster 132 kV | Crewkerne | Primary Substation | 11 | Electric Engagement | 2.9995 | 3.1533 | 3.3992 | 3.9696 | 4.2638 | 4.5888 | 4.9497 | 5.4135 | 5.859 | 6.2733 | 6.6471 | 6.8791 | 7.097 | 7.2605 | 7.4213 | 7.5793 | 8.2041 | 8.5756 | 7.4504 | 7.7826 | 8.3237 | 9.5199 | 10.1676 | 10.8767 | 11.6597 | 12.657 | 13.6094 | 14.5044 | 15.3153 | 15.8363 | 16.3287 | 16.7028 | 17.0698 | 17.4312 | 18.8274 | 19.6965
South West | Axminster 132 kV | Crewkerne | Primary Substation | 11 | Holistic Transition | 2.9853 | 3.1105 | 3.6127 | 3.8481 | 4.1019 | 4.3917 | 4.7946 | 5.2853 | 5.7109 | 6.1276 | 6.511 | 6.7813 | 7.1357 | 7.3641 | 7.5894 | 7.739 | 8.2635 | 8.8422 | 7.4295 | 7.7105 | 8.7742 | 9.3105 | 9.8922 | 10.548 | 11.4579 | 12.5561 | 13.5075 | 14.4275 | 15.2588 | 15.8301 | 16.6147 | 17.0905 | 17.5647 | 17.8861 | 19.0437 | 20.4244
South West | Axminster 132 kV | Crewkerne | Primary Substation | 11 | Hydrogen Evolution | 2.9545 | 3.3571 | 3.498 | 3.6599 | 3.8405 | 4.0561 | 4.2909 | 4.6038 | 4.9318 | 5.2851 | 5.599 | 5.8977 | 6.1791 | 6.4385 | 6.6843 | 6.8481 | 7.4043 | 9.165 | 7.3506 | 8.1724 | 8.4779 | 8.8344 | 9.2338 | 9.7084 | 10.2246 | 10.9044 | 11.6209 | 12.3919 | 13.0638 | 13.6983 | 14.293 | 14.8432 | 15.3652 | 15.7233 | 16.977 | 21.2936
South West | Axminster 132 kV | Dowlish Ford | Primary Substation | 11 | Counterfactual | 0.35273 | 0.41732 | 0.47823 | 0.57258 | 0.67386 | 0.80686 | 0.92029 | 1.0787 | 1.2174 | 1.4225 | 1.6172 | 1.7928 | 1.9479 | 2.1047 | 2.2567 | 2.411 | 3.0193 | 3.3537 | 0.84106 | 0.97954 | 1.11 | 1.3102 | 1.5267 | 1.811 | 2.0557 | 2.3925 | 2.6939 | 3.1436 | 3.5653 | 3.939 | 4.2597 | 4.5839 | 4.8981 | 5.2152 | 6.4814 | 7.1966
South West | Axminster 132 kV | Dowlish Ford | Primary Substation | 11 | Electric Engagement | 0.40971 | 0.55347 | 0.73378 | 0.94801 | 1.2012 | 1.459 | 1.7566 | 2.1267 | 2.5404 | 2.8292 | 3.0874 | 3.2078 | 3.3318 | 3.4316 | 3.5295 | 3.6187 | 4.0193 | 4.313 | 0.9675 | 1.2796 | 1.6703 | 2.1364 | 2.6892 | 3.2512 | 3.8976 | 4.6883 | 5.578 | 6.2002 | 6.7587 | 7.027 | 7.3032 | 7.528 | 7.7486 | 7.9515 | 8.868 | 9.5567
South West | Axminster 132 kV | Dowlish Ford | Primary Substation | 11 | Holistic Transition | 0.3979 | 0.51859 | 0.65959 | 0.83997 | 1.0476 | 1.2681 | 1.616 | 1.9571 | 2.2543 | 2.5438 | 2.7984 | 3.0283 | 3.2511 | 3.452 | 3.6424 | 3.7648 | 4.1679 | 4.4381 | 0.95028 | 1.2222 | 1.5419 | 1.948 | 2.4171 | 2.9139 | 3.6919 | 4.4525 | 5.1142 | 5.7494 | 6.29 | 6.7768 | 7.2496 | 7.6741 | 8.0772 | 8.3442 | 9.2606 | 9.8852
South West | Axminster 132 kV | Dowlish Ford | Primary Substation | 11 | Hydrogen Evolution | 0.37066 | 0.46506 | 0.57206 | 0.7119 | 0.87823 | 1.0497 | 1.2473 | 1.5186 | 1.8035 | 2.1021 | 2.3905 | 2.6429 | 2.8848 | 3.1076 | 3.3047 | 3.4241 | 3.7797 | 4.037 | 0.88092 | 1.0867 | 1.3169 | 1.6219 | 1.9882 | 2.3666 | 2.8023 | 3.3943 | 4.0142 | 4.6624 | 5.2778 | 5.802 | 6.3039 | 6.7673 | 7.1769 | 7.4308 | 8.2272 | 8.8167
South West | Axminster 132 kV | East Chinnock Primary | Primary Substation | 11 | Counterfactual | 0.44682 | 0.46184 | 0.48351 | 0.50741 | 0.53566 | 0.57313 | 0.61676 | 0.67654 | 0.62385 | 0.68293 | 0.73585 | 0.78166 | 0.82856 | 0.87692 | 0.92385 | 0.97075 | 1.1806 | 1.3195 | 1.1081 | 1.141 | 1.1896 | 1.2433 | 1.3068 | 1.3903 | 1.4882 | 1.6198 | 1.4743 | 1.6078 | 1.7248 | 1.8236 | 1.9229 | 2.0256 | 2.1249 | 2.224 | 2.6809 | 2.996
South West | Axminster 132 kV | East Chinnock Primary | Primary Substation | 11 | Electric Engagement | 0.46278 | 0.49641 | 0.56175 | 0.63243 | 0.707 | 0.79423 | 0.89216 | 1.0137 | 1.0195 | 1.1235 | 1.2237 | 1.2872 | 1.3497 | 1.4126 | 1.4746 | 1.5344 | 1.8099 | 1.9945 | 1.1437 | 1.2173 | 1.3665 | 1.5266 | 1.6941 | 1.8866 | 2.1005 | 2.3629 | 2.3412 | 2.5692 | 2.7906 | 2.9367 | 3.0815 | 3.228 | 3.3721 | 3.5117 | 4.1487 | 4.5936
South West | Axminster 132 kV | East Chinnock Primary | Primary Substation | 11 | Holistic Transition | 0.45969 | 0.48721 | 0.54682 | 0.6092 | 0.6813 | 0.76694 | 0.86881 | 1.0019 | 1.0165 | 1.1385 | 1.242 | 1.3372 | 1.4289 | 1.5038 | 1.5746 | 1.6271 | 1.8454 | 1.9585 | 1.1394 | 1.2026 | 1.344 | 1.491 | 1.6609 | 1.8578 | 2.093 | 2.3983 | 2.4099 | 2.6866 | 2.9149 | 3.1247 | 3.3267 | 3.4892 | 3.6429 | 3.7599 | 4.2603 | 4.5235
South West | Axminster 132 kV | East Chinnock Primary | Primary Substation | 11 | Hydrogen Evolution | 0.45175 | 0.47038 | 0.49811 | 0.53266 | 0.57276 | 0.62783 | 0.69044 | 0.76975 | 0.75348 | 0.85576 | 0.9426 | 1.0222 | 1.0955 | 1.1658 | 1.2326 | 1.2786 | 1.4766 | 1.641 | 1.1192 | 1.1601 | 1.2219 | 1.2992 | 1.389 | 1.5107 | 1.6486 | 1.8207 | 1.7557 | 1.9845 | 2.1738 | 2.3455 | 2.503 | 2.6552 | 2.8 | 2.9032 | 3.3675 | 3.7564
South West | Axminster 132 kV | Martock | Primary Substation | 11 | Counterfactual | 0.63748 | 0.71106 | 0.79586 | 0.89238 | 1.0035 | 1.1362 | 1.2849 | 1.5068 | 1.6865 | 1.9312 | 2.1671 | 2.3843 | 2.6097 | 2.8383 | 3.0455 | 3.2513 | 4.0089 | 4.3732 | 1.5533 | 1.711 | 1.8924 | 2.0982 | 2.337 | 2.6206 | 2.9384 | 3.4042 | 3.7858 | 4.3084 | 4.8064 | 5.2588 | 5.7241 | 6.1962 | 6.6226 | 7.0459 | 8.6298 | 9.4223
South West | Axminster 132 kV | Martock | Primary Substation | 11 | Electric Engagement | 0.72255 | 0.89044 | 1.1407 | 1.4366 | 1.7506 | 2.0957 | 2.4833 | 2.9781 | 3.4946 | 3.9203 | 4.2713 | 4.4461 | 4.6047 | 4.7519 | 4.8839 | 5.0183 | 5.6257 | 6.0679 | 1.7423 | 2.1051 | 2.6534 | 3.3054 | 3.9912 | 4.7358 | 5.5609 | 6.5993 | 7.698 | 8.6046 | 9.3541 | 9.7485 | 10.1126 | 10.4506 | 10.7501 | 11.0593 | 12.4555 | 13.5003
South West | Axminster 132 kV | Martock | Primary Substation | 11 | Holistic Transition | 0.70459 | 0.83632 | 1.0395 | 1.2544 | 1.4899 | 1.7586 | 2.1403 | 2.5894 | 2.9513 | 3.3145 | 3.6594 | 3.9919 | 4.3134 | 4.603 | 4.8761 | 5.0513 | 5.6307 | 6.0214 | 1.716 | 2.0147 | 2.4812 | 2.9709 | 3.5064 | 4.1047 | 4.9454 | 5.9229 | 6.7086 | 7.4894 | 8.2197 | 8.9249 | 9.6078 | 10.2206 | 10.8001 | 11.1832 | 12.5052 | 13.4138
South West | Axminster 132 kV | Martock | Primary Substation | 11 | Hydrogen Evolution | 0.66406 | 0.76011 | 0.88205 | 1.0365 | 1.2066 | 1.4123 | 1.646 | 1.9584 | 2.304 | 2.6755 | 3.022 | 3.3428 | 3.6489 | 3.9136 | 4.1632 | 4.303 | 4.7262 | 5.0763 | 1.6125 | 1.8211 | 2.0824 | 2.4207 | 2.7907 | 3.2334 | 3.7314 | 4.3853 | 5.1185 | 5.9072 | 6.6325 | 7.3008 | 7.9379 | 8.4887 | 9.009 | 9.3096 | 10.2728 | 11.0765
South West | Axminster 132 kV | Montacute | Primary Substation | 11 | Counterfactual | 0.25386 | 0.28067 | 0.30613 | 0.34207 | 0.39423 | 0.45804 | 0.52545 | 0.61319 | 0.6957 | 0.79558 | 0.87245 | 0.92785 | 0.99036 | 1.0524 | 1.1145 | 1.1779 | 1.4182 | 1.5542 | 0.61809 | 0.67669 | 0.73146 | 0.808 | 0.92283 | 1.0641 | 1.2146 | 1.4069 | 1.5924 | 1.8162 | 1.9816 | 2.0959 | 2.2242 | 2.3513 | 2.479 | 2.6093 | 3.1108 | 3.4012
South West | Axminster 132 kV | Montacute | Primary Substation | 11 | Electric Engagement | 0.27553 | 0.33485 | 0.40765 | 0.53585 | 0.70174 | 0.89364 | 1.0846 | 1.2608 | 1.4026 | 1.5027 | 1.5948 | 1.6442 | 1.6923 | 1.7406 | 1.6694 | 1.719 | 1.9635 | 2.1047 | 0.66606 | 0.79737 | 0.95499 | 1.2476 | 1.6303 | 2.0738 | 2.5087 | 2.8916 | 3.1903 | 3.4002 | 3.5941 | 3.7017 | 3.8071 | 3.9127 | 3.7193 | 3.8295 | 4.3751 | 4.7033
South West | Axminster 132 kV | Montacute | Primary Substation | 11 | Holistic Transition | 0.27084 | 0.3238 | 0.40362 | 0.51221 | 0.64671 | 0.79726 | 0.96833 | 1.1282 | 1.236 | 1.333 | 1.4316 | 1.5289 | 1.6254 | 1.7161 | 1.6948 | 1.7604 | 2.0057 | 2.1535 | 0.65905 | 0.78139 | 0.96696 | 1.221 | 1.5372 | 1.8886 | 2.2817 | 2.643 | 2.8797 | 3.0865 | 3.2937 | 3.4992 | 3.7032 | 3.8946 | 3.8071 | 3.9492 | 4.4949 | 4.8323
South West | Axminster 132 kV | Montacute | Primary Substation | 11 | Hydrogen Evolution | 0.2612 | 0.29809 | 0.34206 | 0.43656 | 0.56316 | 0.71369 | 0.86176 | 1.0208 | 1.1267 | 1.2307 | 1.3204 | 1.4075 | 1.4937 | 1.5737 | 1.5228 | 1.5751 | 1.7501 | 1.8916 | 0.63427 | 0.71598 | 0.81038 | 1.0284 | 1.3243 | 1.6771 | 2.0202 | 2.3789 | 2.6033 | 2.8223 | 3.0084 | 3.1888 | 3.3671 | 3.5329 | 3.3724 | 3.4842 | 3.8736 | 4.1894
South West | Axminster 132 kV | Penn Cross | Primary Substation | 11 | Counterfactual | 0.29987 | 0.34486 | 0.39695 | 0.45431 | 0.51993 | 0.59772 | 0.68434 | 0.82292 | 0.9395 | 1.0611 | 1.1818 | 1.2998 | 1.4281 | 1.5562 | 1.6803 | 1.8035 | 2.2355 | 2.4162 | 0.69188 | 0.78858 | 0.89944 | 1.0212 | 1.1603 | 1.3246 | 1.5076 | 1.7963 | 2.0414 | 2.298 | 2.5506 | 2.7953 | 3.0595 | 3.3234 | 3.5788 | 3.8321 | 4.7366 | 5.1353
South West | Axminster 132 kV | Penn Cross | Primary Substation | 11 | Electric Engagement | 0.35172 | 0.45553 | 0.58918 | 0.73757 | 0.90061 | 1.0823 | 1.2927 | 1.5807 | 1.8305 | 2.0384 | 2.2217 | 2.2953 | 2.3663 | 2.4368 | 2.5059 | 2.5718 | 2.8882 | 3.1176 | 0.80704 | 1.0317 | 1.3185 | 1.6353 | 1.9813 | 2.3643 | 2.8047 | 3.4031 | 3.9258 | 4.3638 | 4.7531 | 4.9205 | 5.0831 | 5.245 | 5.4033 | 5.555 | 6.2818 | 6.8212
South West | Axminster 132 kV | Penn Cross | Primary Substation | 11 | Holistic Transition | 0.34086 | 0.42281 | 0.52329 | 0.63008 | 0.74977 | 0.89 | 1.0515 | 1.2769 | 1.4827 | 1.6934 | 1.8997 | 2.0918 | 2.2777 | 2.4478 | 2.6066 | 2.7058 | 3.0318 | 3.2604 | 0.79122 | 0.97741 | 1.2029 | 1.441 | 1.7069 | 2.014 | 2.367 | 2.8531 | 3.2989 | 3.7526 | 4.1912 | 4.5989 | 4.9936 | 5.3534 | 5.6899 | 5.9068 | 6.6532 | 7.1832
South West | Axminster 132 kV | Penn Cross | Primary Substation | 11 | Hydrogen Evolution | 0.31613 | 0.37476 | 0.4463 | 0.52748 | 0.62026 | 0.73158 | 0.85985 | 1.0467 | 1.2289 | 1.4188 | 1.6051 | 1.7793 | 1.9471 | 2.1045 | 2.2517 | 2.3315 | 2.5709 | 2.7756 | 0.72808 | 0.85558 | 1.0084 | 1.1819 | 1.3796 | 1.6155 | 1.8856 | 2.2751 | 2.6599 | 3.061 | 3.4502 | 3.8126 | 4.161 | 4.4892 | 4.7963 | 4.9685 | 5.5155 | 5.984
South West | Axminster 132 kV | Waterlake Primary | Primary Substation | 11 | Counterfactual | 0.44549 | 0.4694 | 0.5018 | 0.53786 | 0.58101 | 0.63511 | 0.69669 | 0.78437 | 0.8582 | 0.94045 | 1.0177 | 1.0892 | 1.1657 | 1.2432 | 1.3183 | 1.3935 | 1.6959 | 1.8661 | 1.0989 | 1.1502 | 1.2206 | 1.2988 | 1.3929 | 1.5102 | 1.6444 | 1.8322 | 1.992 | 2.172 | 2.3381 | 2.4886 | 2.6478 | 2.8094 | 2.9658 | 3.122 | 3.7655 | 4.1437
South West | Axminster 132 kV | Waterlake Primary | Primary Substation | 11 | Electric Engagement | 0.47386 | 0.52902 | 0.61855 | 0.72196 | 0.83264 | 0.96042 | 1.1046 | 1.2855 | 1.4447 | 1.5895 | 1.7228 | 1.7965 | 1.867 | 1.9371 | 2.0061 | 2.0729 | 2.3796 | 2.5954 | 1.162 | 1.2811 | 1.4794 | 1.7076 | 1.95 | 2.2263 | 2.5352 | 2.9176 | 3.2561 | 3.5668 | 3.8552 | 4.0226 | 4.1842 | 4.3457 | 4.5044 | 4.6587 | 5.3626 | 5.8738
South West | Axminster 132 kV | Waterlake Primary | Primary Substation | 11 | Holistic Transition | 0.46804 | 0.51111 | 0.58795 | 0.67066 | 0.76542 | 0.87847 | 1.0091 | 1.1801 | 1.3315 | 1.4896 | 1.633 | 1.7677 | 1.8982 | 2.0107 | 2.1173 | 2.1898 | 2.4628 | 2.6239 | 1.1535 | 1.2511 | 1.4291 | 1.6191 | 1.8366 | 2.0909 | 2.3853 | 2.7668 | 3.1043 | 3.4537 | 3.7636 | 4.054 | 4.3356 | 4.5759 | 4.8038 | 4.9634 | 5.584 | 5.9547
South West | Axminster 132 kV | Waterlake Primary | Primary Substation | 11 | Hydrogen Evolution | 0.45425 | 0.48545 | 0.52875 | 0.58523 | 0.64913 | 0.73116 | 0.82404 | 0.94433 | 1.0675 | 1.2066 | 1.3328 | 1.4504 | 1.5608 | 1.6647 | 1.7637 | 1.8248 | 2.0564 | 2.2545 | 1.1184 | 1.1861 | 1.2803 | 1.4044 | 1.5447 | 1.723 | 1.9237 | 2.1796 | 2.446 | 2.7484 | 3.0173 | 3.2663 | 3.4991 | 3.7198 | 3.9303 | 4.0647 | 4.5993 | 5.059
South West | Bridgwater 132 kV | Bath Road Primary | Primary Substation | 11 | Counterfactual | 5.1212 | 5.2966 | 5.5219 | 5.7622 | 6.0132 | 6.3014 | 6.6253 | 7.0484 | 7.2899 | 7.559 | 7.8072 | 6.4793 | 6.7273 | 6.8 | 7.0633 | 7.3777 | 7.7169 | 8.1873 | 12.7524 | 13.1309 | 13.6186 | 14.1408 | 14.6903 | 15.3226 | 16.0368 | 16.9575 | 17.4767 | 18.0604 | 18.589 | 15.1714 | 15.6776 | 15.7445 | 16.2888 | 16.9612 | 17.4457 | 18.5048
South West | Bridgwater 132 kV | Bath Road Primary | Primary Substation | 11 | Electric Engagement | 5.2448 | 5.7586 | 6.2622 | 6.8132 | 7.4017 | 8.055 | 8.7708 | 9.4202 | 9.8851 | 10.2745 | 10.6294 | 9.2241 | 9.5053 | 9.5875 | 9.7942 | 9.9984 | 10.3208 | 10.9074 | 13.0316 | 14.2185 | 15.3443 | 16.578 | 17.898 | 19.3615 | 20.9503 | 22.3082 | 23.2774 | 24.096 | 24.8471 | 21.2953 | 21.9043 | 22.065 | 22.5441 | 23.0184 | 23.5218 | 24.8833
South West | Bridgwater 132 kV | Bath Road Primary | Primary Substation | 11 | Holistic Transition | 5.2216 | 5.6909 | 6.1321 | 6.6096 | 7.1271 | 7.7198 | 8.3121 | 9.0716 | 9.4399 | 9.8169 | 10.1846 | 9.0045 | 9.494 | 9.8894 | 10.2272 | 10.4445 | 10.7654 | 11.2758 | 12.9967 | 14.1051 | 15.12 | 16.22 | 17.4211 | 18.7885 | 20.1398 | 21.864 | 22.6593 | 23.4663 | 24.2316 | 21.1308 | 22.147 | 22.9892 | 23.7019 | 24.1716 | 24.6564 | 25.8221
South West | Bridgwater 132 kV | Bath Road Primary | Primary Substation | 11 | Hydrogen Evolution | 5.1734 | 5.4272 | 5.9461 | 6.3335 | 6.7576 | 7.2591 | 7.7999 | 8.4181 | 8.7595 | 9.1326 | 9.495 | 8.2919 | 8.7134 | 8.8488 | 9.1875 | 9.3961 | 9.3415 | 9.8329 | 12.8735 | 13.442 | 14.6461 | 15.5202 | 16.4834 | 17.6223 | 18.843 | 20.2091 | 20.9313 | 21.7245 | 22.4806 | 19.3237 | 20.2008 | 20.3977 | 21.1144 | 21.5709 | 21.2806 | 22.3992
South West | Bridgwater 132 kV | Bridgwater Local | Primary Substation | 11 | Counterfactual | 0.21734 | 0.33078 | 0.46391 | 0.60931 | 0.76452 | 0.90751 | 1.0646 | 1.2936 | 1.4634 | 1.6464 | 1.8273 | 2.008 | 2.212 | 2.4205 | 2.6301 | 2.8314 | 3.5088 | 3.7654 | 0.5065 | 0.74657 | 1.027 | 1.3331 | 1.6603 | 1.9619 | 2.2933 | 2.7701 | 3.1261 | 3.5113 | 3.8884 | 4.2617 | 4.6804 | 5.109 | 5.5395 | 5.9529 | 7.3692 | 7.9396
South West | Bridgwater 132 kV | Bridgwater Local | Primary Substation | 11 | Electric Engagement | 0.30694 | 0.51933 | 0.79485 | 1.0971 | 1.4256 | 1.7385 | 2.0941 | 2.5607 | 2.9264 | 3.2246 | 3.4928 | 3.5953 | 3.6966 | 3.8069 | 3.915 | 4.0199 | 4.4988 | 4.9257 | 0.70542 | 1.1613 | 1.7517 | 2.3979 | 3.0974 | 3.7585 | 4.5042 | 5.472 | 6.2329 | 6.8588 | 7.4255 | 7.66 | 7.8935 | 8.1466 | 8.3942 | 8.6353 | 9.7338 | 10.7125
South West | Bridgwater 132 kV | Bridgwater Local | Primary Substation | 11 | Holistic Transition | 0.28801 | 0.46223 | 0.67974 | 0.91356 | 1.1674 | 1.4106 | 1.6841 | 2.0438 | 2.3354 | 2.6353 | 2.9523 | 3.2597 | 3.5667 | 3.851 | 4.1148 | 4.277 | 4.7868 | 5.1845 | 0.67767 | 1.0644 | 1.5464 | 2.0629 | 2.6234 | 3.157 | 3.7538 | 4.5287 | 5.1583 | 5.8023 | 6.4721 | 7.1218 | 7.7708 | 8.3696 | 8.9262 | 9.2795 | 10.4409 | 11.3468
South West | Bridgwater 132 kV | Bridgwater Local | Primary Substation | 11 | Hydrogen Evolution | 0.24465 | 0.38728 | 0.56192 | 0.75309 | 0.96433 | 1.1617 | 1.3865 | 1.6899 | 1.9426 | 2.219 | 2.4963 | 2.7729 | 3.0423 | 3.3049 | 3.5484 | 3.6811 | 4.068 | 4.4067 | 0.56744 | 0.87464 | 1.2471 | 1.6565 | 2.1087 | 2.5285 | 3.0031 | 3.6349 | 4.1661 | 4.7481 | 5.3237 | 5.8963 | 6.4536 | 6.9991 | 7.5056 | 7.7905 | 8.6678 | 9.4372
South West | Bridgwater 132 kV | Burnham | Primary Substation | 11 | Counterfactual | 0.93763 | 1.0372 | 1.1493 | 1.2743 | 1.4132 | 1.5677 | 1.7467 | 2.0171 | 2.2294 | 2.4583 | 2.686 | 2.9184 | 3.1794 | 3.4492 | 3.7135 | 3.978 | 4.8461 | 5.1495 | 2.2906 | 2.5013 | 2.7384 | 3.0024 | 3.2953 | 3.6204 | 3.9967 | 4.5572 | 5.001 | 5.4808 | 5.9541 | 6.4331 | 6.9684 | 7.5223 | 8.0647 | 8.6071 | 10.417 | 11.0921
South West | Bridgwater 132 kV | Burnham | Primary Substation | 11 | Electric Engagement | 1.0552 | 1.2766 | 1.5614 | 1.878 | 2.2249 | 2.593 | 3.0297 | 3.6071 | 4.0835 | 4.4721 | 4.8126 | 4.9259 | 5.0447 | 5.1727 | 5.2984 | 5.4234 | 6.0245 | 6.474 | 2.5519 | 3.0242 | 3.632 | 4.3045 | 5.0375 | 5.8099 | 6.7195 | 7.9109 | 8.8988 | 9.7108 | 10.4278 | 10.6896 | 10.9639 | 11.2592 | 11.5484 | 11.836 | 13.2287 | 14.2768
South West | Bridgwater 132 kV | Burnham | Primary Substation | 11 | Holistic Transition | 1.0304 | 1.1965 | 1.4027 | 1.6238 | 1.8682 | 2.1402 | 2.4526 | 2.8816 | 3.248 | 3.6293 | 4.0251 | 4.4123 | 4.8881 | 5.2455 | 5.5759 | 5.7783 | 6.3714 | 6.8089 | 2.5157 | 2.8859 | 3.3458 | 3.836 | 4.3758 | 4.9699 | 5.649 | 6.5676 | 7.355 | 8.1701 | 9.0049 | 9.8217 | 10.8617 | 11.614 | 12.3107 | 12.7511 | 14.111 | 15.1233
South West | Bridgwater 132 kV | Burnham | Primary Substation | 11 | Hydrogen Evolution | 0.97374 | 1.1018 | 1.2548 | 1.4263 | 1.6216 | 1.8391 | 2.0939 | 2.4517 | 2.7736 | 3.1192 | 3.4688 | 3.8157 | 4.1547 | 4.4878 | 4.7965 | 4.9593 | 5.4423 | 5.8186 | 2.3713 | 2.6458 | 2.9711 | 3.3366 | 3.7511 | 4.2102 | 4.7449 | 5.4853 | 6.1591 | 6.8839 | 7.6079 | 8.3247 | 9.025 | 9.7158 | 10.3572 | 10.7064 | 11.8178 | 12.6793
South West | Bridgwater 132 kV | Colley Lane | Primary Substation | 11 | Counterfactual | 6.3492 | 6.4595 | 6.6005 | 6.7539 | 6.9365 | 7.1594 | 7.4153 | 7.798 | 8.0784 | 8.3881 | 8.6845 | 8.9659 | 9.2826 | 9.5978 | 9.7477 | 10.1064 | 11.3505 | 11.9517 | 15.7166 | 15.9479 | 16.2467 | 16.5736 | 16.9641 | 17.4411 | 17.9917 | 18.8015 | 19.3905 | 20.0473 | 20.6668 | 21.2409 | 21.882 | 22.5173 | 22.7391 | 23.4781 | 26.0578 | 27.3626
South West | Bridgwater 132 kV | Colley Lane | Primary Substation | 11 | Electric Engagement | 6.4403 | 6.6963 | 7.0843 | 7.5197 | 8.0056 | 8.5646 | 9.2031 | 9.9978 | 10.5869 | 11.0804 | 11.5357 | 11.7419 | 11.9045 | 12.0711 | 12.2786 | 12.4801 | 13.2826 | 13.9122 | 15.9041 | 16.4474 | 17.2876 | 18.2304 | 19.2812 | 20.484 | 21.8464 | 23.5106 | 24.7201 | 25.74 | 26.6913 | 27.1544 | 27.5053 | 27.8664 | 28.3302 | 28.7823 | 30.5489 | 31.9714
South West | Bridgwater 132 kV | Colley Lane | Primary Substation | 11 | Holistic Transition | 6.3778 | 6.5559 | 6.8441 | 7.1584 | 7.53 | 7.9755 | 8.4422 | 9.0647 | 9.5121 | 9.9756 | 10.4928 | 10.9696 | 11.5592 | 12.0611 | 12.4594 | 12.696 | 13.4431 | 13.9451 | 15.779 | 16.1721 | 16.8212 | 17.5301 | 18.3701 | 19.3659 | 20.3956 | 21.7504 | 22.6967 | 23.6706 | 24.7538 | 25.7373 | 27.0062 | 28.0661 | 28.8819 | 29.3731 | 30.9909 | 32.0908
South West | Bridgwater 132 kV | Colley Lane | Primary Substation | 11 | Hydrogen Evolution | 6.3846 | 6.5406 | 6.7619 | 7.0127 | 7.3101 | 7.6792 | 8.1014 | 8.6563 | 9.0785 | 9.542 | 10.0094 | 10.5546 | 11.0257 | 11.3794 | 11.8139 | 12.0703 | 12.7809 | 13.3505 | 15.7925 | 16.1292 | 16.6064 | 17.1548 | 17.807 | 18.6153 | 19.533 | 20.7183 | 21.5975 | 22.5681 | 23.5301 | 24.6751 | 25.6409 | 26.3238 | 27.2232 | 27.7666 | 29.3296 | 30.603
South West | Bridgwater 132 kV | Creech St Michael | Primary Substation | 11 | Counterfactual | 1.6394 | 1.6953 | 1.7684 | 1.8475 | 1.9365 | 2.0531 | 2.3093 | 2.5514 | 2.8091 | 3.0898 | 3.3228 | 3.5304 | 3.7425 | 3.9568 | 4.169 | 4.3815 | 5.2762 | 5.902 | 3.8595 | 3.9804 | 4.1401 | 4.3128 | 4.5083 | 4.7629 | 5.3158 | 5.8374 | 6.3983 | 7.0172 | 7.526 | 7.9691 | 8.4143 | 8.8645 | 9.3102 | 9.756 | 11.6712 | 13.046
South West | Bridgwater 132 kV | Creech St Michael | Primary Substation | 11 | Electric Engagement | 1.6979 | 1.8238 | 2.0257 | 2.2498 | 2.5922 | 2.941 | 3.3356 | 3.81 | 4.272 | 4.6912 | 5.0395 | 5.2524 | 5.4659 | 5.7003 | 5.9164 | 6.1441 | 7.1532 | 7.9212 | 3.9893 | 4.2645 | 4.7141 | 5.212 | 5.9669 | 6.7325 | 7.5953 | 8.6193 | 9.6206 | 10.5365 | 11.2987 | 11.7801 | 12.2641 | 12.8003 | 13.29 | 13.8108 | 16.093 | 17.8671
South West | Bridgwater 132 kV | Creech St Michael | Primary Substation | 11 | Holistic Transition | 1.686 | 1.7902 | 1.9669 | 2.1937 | 2.4635 | 2.7871 | 3.1509 | 3.6142 | 4.1087 | 4.5456 | 4.9298 | 5.2678 | 5.5998 | 5.8975 | 6.1849 | 6.4054 | 7.3214 | 7.967 | 3.9722 | 4.2112 | 4.622 | 5.1414 | 5.7605 | 6.4935 | 7.3204 | 8.368 | 9.4905 | 10.4636 | 11.3087 | 12.0427 | 12.7642 | 13.4049 | 14.0242 | 14.5094 | 16.5676 | 18.0263
South West | Bridgwater 132 kV | Creech St Michael | Primary Substation | 11 | Hydrogen Evolution | 1.6575 | 1.73 | 1.8291 | 1.9898 | 2.1854 | 2.4326 | 2.7111 | 3.0623 | 3.4488 | 3.8539 | 4.1786 | 4.4774 | 4.7651 | 5.0615 | 5.3305 | 5.5406 | 6.353 | 7.0774 | 3.8997 | 4.0588 | 4.2752 | 4.6284 | 5.0607 | 5.6066 | 6.2218 | 6.9907 | 7.8423 | 8.7371 | 9.4395 | 10.0783 | 10.6915 | 11.3324 | 11.9092 | 12.376 | 14.2198 | 15.8684
South West | Bridgwater 132 kV | Curry Mallet | Primary Substation | 11 | Counterfactual | 0.30807 | 0.32651 | 0.34965 | 0.375 | 0.40461 | 0.44555 | 0.49183 | 0.55618 | 0.61027 | 0.67068 | 0.72693 | 0.77666 | 0.82946 | 0.88342 | 0.93662 | 0.99014 | 1.2139 | 1.3556 | 0.75704 | 0.79751 | 0.84858 | 0.90447 | 0.9699 | 1.0593 | 1.161 | 1.3001 | 1.4183 | 1.5521 | 1.6741 | 1.7794 | 1.8895 | 2.0022 | 2.1133 | 2.225 | 2.7034 | 3.017
South West | Bridgwater 132 kV | Curry Mallet | Primary Substation | 11 | Electric Engagement | 0.32623 | 0.36897 | 0.43594 | 0.50971 | 0.58804 | 0.68293 | 0.78984 | 0.92117 | 1.0384 | 1.1471 | 1.2512 | 1.3142 | 1.376 | 1.4371 | 1.4988 | 1.5588 | 1.8457 | 2.0182 | 0.79736 | 0.89194 | 1.0425 | 1.2073 | 1.3809 | 1.5871 | 1.8174 | 2.0963 | 2.3467 | 2.5805 | 2.806 | 2.9475 | 3.0873 | 3.2258 | 3.3653 | 3.5016 | 4.1486 | 4.5582
South West | Bridgwater 132 kV | Curry Mallet | Primary Substation | 11 | Holistic Transition | 0.32236 | 0.35963 | 0.419 | 0.48138 | 0.55254 | 0.64133 | 0.74065 | 0.86978 | 0.98431 | 1.1028 | 1.2097 | 1.3089 | 1.4049 | 1.4874 | 1.5673 | 1.6264 | 1.867 | 1.9967 | 0.79162 | 0.87817 | 1.0174 | 1.1626 | 1.3282 | 1.529 | 1.7538 | 2.0438 | 2.3003 | 2.5634 | 2.7943 | 3.0091 | 3.2172 | 3.3938 | 3.5652 | 3.6946 | 4.2348 | 4.5325
South West | Bridgwater 132 kV | Curry Mallet | Primary Substation | 11 | Hydrogen Evolution | 0.31377 | 0.33823 | 0.36923 | 0.40728 | 0.45078 | 0.51149 | 0.58001 | 0.66768 | 0.7582 | 0.8607 | 0.95244 | 1.0379 | 1.1181 | 1.1938 | 1.267 | 1.3162 | 1.5135 | 1.6762 | 0.76969 | 0.82407 | 0.89229 | 0.9765 | 1.0727 | 1.2049 | 1.3536 | 1.5411 | 1.7379 | 1.9623 | 2.1585 | 2.34 | 2.5094 | 2.6703 | 2.826 | 2.9339 | 3.3856 | 3.7616
South West | Bridgwater 132 kV | Edgarley | Primary Substation | 11 | Counterfactual | 0.16803 | 0.19348 | 0.22969 | 0.26933 | 0.31577 | 0.37498 | 0.44438 | 0.54504 | 0.63249 | 0.74541 | 0.85086 | 0.93386 | 1.0111 | 1.0909 | 1.1683 | 1.2456 | 1.5503 | 1.7216 | 0.4072 | 0.4622 | 0.5423 | 0.63008 | 0.73317 | 0.86411 | 1.0186 | 1.2383 | 1.4314 | 1.6825 | 1.913 | 2.0908 | 2.2533 | 2.4219 | 2.5846 | 2.7472 | 3.4113 | 3.808
South West | Bridgwater 132 kV | Edgarley | Primary Substation | 11 | Electric Engagement | 0.19669 | 0.25593 | 0.36334 | 0.47796 | 0.60037 | 0.7357 | 0.88806 | 1.0846 | 1.2892 | 1.4687 | 1.61 | 1.6893 | 1.7715 | 1.8577 | 1.9418 | 2.0259 | 2.4031 | 2.676 | 0.47088 | 0.59978 | 0.84273 | 1.1004 | 1.3733 | 1.6712 | 2.0033 | 2.4265 | 2.8717 | 3.2664 | 3.5808 | 3.7683 | 3.9627 | 4.1665 | 4.365 | 4.5638 | 5.449 | 6.1089
South West | Bridgwater 132 kV | Edgarley | Primary Substation | 11 | Holistic Transition | 0.19077 | 0.23878 | 0.33436 | 0.43284 | 0.5461 | 0.67496 | 0.85766 | 1.0951 | 1.2781 | 1.4551 | 1.6053 | 1.7458 | 1.8836 | 1.9995 | 2.1087 | 2.1866 | 2.4917 | 2.6569 | 0.46231 | 0.57203 | 0.79717 | 1.0282 | 1.2939 | 1.5908 | 2.0099 | 2.5512 | 2.9706 | 3.3741 | 3.7068 | 4.0173 | 4.3217 | 4.5734 | 4.8105 | 4.9851 | 5.6936 | 6.0804
South West | Bridgwater 132 kV | Edgarley | Primary Substation | 11 | Hydrogen Evolution | 0.17674 | 0.21029 | 0.25778 | 0.31356 | 0.3786 | 0.462 | 0.55746 | 0.6858 | 0.84845 | 1.0235 | 1.1622 | 1.2809 | 1.3931 | 1.5042 | 1.6095 | 1.6789 | 1.9635 | 2.2072 | 0.42663 | 0.5 | 0.60486 | 0.72907 | 0.87391 | 1.0584 | 1.2689 | 1.547 | 1.9082 | 2.3001 | 2.6033 | 2.8597 | 3.1007 | 3.3412 | 3.5692 | 3.7256 | 4.3995 | 4.9795
South West | Bridgwater 132 kV | Millfield | Primary Substation | 11 | Counterfactual | 1.0489 | 1.1445 | 1.2642 | 1.4282 | 1.615 | 1.825 | 2.0359 | 2.3245 | 2.5683 | 2.8222 | 3.0463 | 3.278 | 3.5192 | 3.7635 | 4.0088 | 4.2786 | 5.1651 | 5.5625 | 2.57 | 2.7746 | 3.0295 | 3.3768 | 3.7728 | 4.218 | 4.6662 | 5.2714 | 5.7877 | 6.3276 | 6.7992 | 7.2865 | 7.7836 | 8.2872 | 8.7941 | 9.3624 | 11.226 | 12.0984
South West | Bridgwater 132 kV | Millfield | Primary Substation | 11 | Electric Engagement | 1.1484 | 1.3561 | 1.6605 | 2.0389 | 2.454 | 2.8762 | 3.329 | 3.9016 | 4.4592 | 4.8643 | 5.2109 | 5.4236 | 5.726 | 5.8746 | 6.0218 | 6.1614 | 6.8174 | 7.3064 | 2.7908 | 3.2391 | 3.8963 | 4.7105 | 5.6013 | 6.5009 | 7.4563 | 8.6498 | 9.8369 | 10.6914 | 11.4298 | 11.9276 | 12.6526 | 12.9929 | 13.3296 | 13.6504 | 15.1663 | 16.3134
South West | Bridgwater 132 kV | Millfield | Primary Substation | 11 | Holistic Transition | 1.1274 | 1.2925 | 1.5405 | 1.8511 | 2.1801 | 2.5196 | 2.9065 | 3.6848 | 4.1015 | 4.5363 | 4.9208 | 5.3387 | 5.7581 | 6.1316 | 6.4547 | 6.6596 | 7.3186 | 7.7763 | 2.76 | 3.1324 | 3.6881 | 4.3772 | 5.1081 | 5.8557 | 6.7051 | 8.4971 | 9.4046 | 10.3525 | 11.1683 | 12.0679 | 12.9749 | 13.7759 | 14.4602 | 14.9077 | 16.4139 | 17.4729
South West | Bridgwater 132 kV | Millfield | Primary Substation | 11 | Hydrogen Evolution | 1.0801 | 1.2038 | 1.3844 | 1.6294 | 1.8916 | 2.1746 | 2.4746 | 2.8634 | 3.2616 | 3.6543 | 3.998 | 4.3611 | 4.8843 | 5.1921 | 5.4818 | 5.6446 | 6.1528 | 6.5791 | 2.6393 | 2.9077 | 3.2953 | 3.8231 | 4.3882 | 4.9957 | 5.6349 | 6.4507 | 7.3044 | 8.1431 | 8.8602 | 9.6282 | 10.7999 | 11.4426 | 12.0484 | 12.4002 | 13.5689 | 14.5472
South West | Bridgwater 132 kV | Nether Stowey | Primary Substation | 11 | Counterfactual | 0.87685 | 0.90879 | 0.97438 | 1.0382 | 1.1151 | 1.2223 | 1.3532 | 1.52 | 1.673 | 1.8478 | 1.9941 | 2.0909 | 2.183 | 2.146 | 2.2589 | 2.3713 | 2.8952 | 3.2652 | 2.1738 | 2.2436 | 2.3922 | 2.5386 | 2.7157 | 2.9598 | 3.2601 | 3.6377 | 3.9873 | 4.3937 | 4.7266 | 4.9349 | 5.1266 | 4.9928 | 5.2359 | 5.4778 | 6.6525 | 7.5214
South West | Bridgwater 132 kV | Nether Stowey | Primary Substation | 11 | Electric Engagement | 0.91092 | 0.98647 | 1.2172 | 1.4532 | 1.6952 | 1.9715 | 2.2561 | 2.5516 | 2.8302 | 3.0711 | 3.3263 | 3.5374 | 3.7656 | 3.9968 | 4.1957 | 4.4121 | 5.3637 | 6.0341 | 2.2495 | 2.4157 | 2.9591 | 3.5145 | 4.0804 | 4.713 | 5.3581 | 6.008 | 6.6266 | 7.1632 | 7.7413 | 8.2444 | 8.7905 | 9.3411 | 9.812 | 10.3265 | 12.566 | 14.2026
South West | Bridgwater 132 kV | Nether Stowey | Primary Substation | 11 | Holistic Transition | 0.90389 | 0.9678 | 1.1914 | 1.4092 | 1.6629 | 1.9441 | 2.176 | 2.4793 | 2.8509 | 3.2104 | 3.4914 | 3.7491 | 4.001 | 4.2061 | 4.3935 | 4.5434 | 5.2204 | 5.5412 | 2.2394 | 2.3869 | 2.9265 | 3.4531 | 4.0664 | 4.7303 | 5.2692 | 5.9704 | 6.8464 | 7.6894 | 8.3302 | 8.9157 | 9.4876 | 9.9428 | 10.3585 | 10.6994 | 12.2738 | 13.0305
South West | Bridgwater 132 kV | Nether Stowey | Primary Substation | 11 | Hydrogen Evolution | 0.88737 | 0.93034 | 1.0127 | 1.1041 | 1.2124 | 1.3695 | 1.5372 | 1.7425 | 1.9376 | 2.1581 | 2.3387 | 2.5036 | 2.6878 | 2.8816 | 3.0595 | 3.1969 | 3.8573 | 4.4125 | 2.1973 | 2.2923 | 2.479 | 2.6895 | 2.9394 | 3.2965 | 3.678 | 4.1377 | 4.5763 | 5.077 | 5.4749 | 5.8331 | 6.2403 | 6.6716 | 7.0676 | 7.3835 | 8.9558 | 10.2897
South West | Bridgwater 132 kV | North Street Langport | Primary Substation | 11 | Counterfactual | 0.22552 | 0.26787 | 0.32703 | 0.39316 | 0.4722 | 0.57716 | 0.69804 | 0.86596 | 1.0082 | 1.1838 | 1.3425 | 1.4843 | 1.6307 | 1.777 | 1.9116 | 2.0454 | 2.5995 | 2.9378 | 0.53853 | 0.62966 | 0.76034 | 0.90633 | 1.0818 | 1.3133 | 1.5818 | 1.9478 | 2.262 | 2.6534 | 3 | 3.3027 | 3.6102 | 3.9184 | 4.2004 | 4.4806 | 5.6765 | 6.4402
South West | Bridgwater 132 kV | North Street Langport | Primary Substation | 11 | Electric Engagement | 0.27334 | 0.37039 | 0.54861 | 0.74972 | 0.96712 | 1.2139 | 1.488 | 1.8253 | 2.1636 | 2.453 | 2.7266 | 2.8802 | 3.0321 | 3.1858 | 3.3374 | 3.4866 | 4.1573 | 4.6138 | 0.64466 | 0.85535 | 1.2575 | 1.71 | 2.1966 | 2.7397 | 3.336 | 4.0587 | 4.7895 | 5.42 | 6.0209 | 6.3744 | 6.7265 | 7.0842 | 7.4361 | 7.7835 | 9.3325 | 10.4294
South West | Bridgwater 132 kV | North Street Langport | Primary Substation | 11 | Holistic Transition | 0.26299 | 0.34034 | 0.50141 | 0.67243 | 0.86804 | 1.0981 | 1.4097 | 1.7798 | 2.1017 | 2.4144 | 2.6847 | 2.9352 | 3.1777 | 3.3801 | 3.5707 | 3.7076 | 4.2501 | 4.5311 | 0.62936 | 0.80579 | 1.1851 | 1.5859 | 2.0444 | 2.5721 | 3.2839 | 4.1261 | 4.8572 | 5.5622 | 6.1546 | 6.7027 | 7.2338 | 7.6703 | 8.0813 | 8.385 | 9.6262 | 10.2789
South West | Bridgwater 132 kV | North Street Langport | Primary Substation | 11 | Hydrogen Evolution | 0.24035 | 0.29524 | 0.37504 | 0.47779 | 0.59933 | 0.75851 | 0.93596 | 1.161 | 1.4094 | 1.6931 | 1.9428 | 2.1735 | 2.3846 | 2.5798 | 2.7644 | 2.8886 | 3.3879 | 3.8016 | 0.57155 | 0.69132 | 0.86694 | 1.0967 | 1.3693 | 1.7216 | 2.1119 | 2.5979 | 3.1461 | 3.7759 | 4.3167 | 4.812 | 5.2627 | 5.6821 | 6.0791 | 6.3553 | 7.5212 | 8.4977
South West | Bridgwater 132 kV | Shapwick | Primary Substation | 11 | Counterfactual | 0.2164 | 0.24555 | 0.29612 | 0.35208 | 0.42466 | 0.52783 | 0.64604 | 0.79527 | 0.92642 | 1.0816 | 1.2132 | 1.3189 | 1.422 | 1.5297 | 1.6326 | 1.7354 | 2.2272 | 2.5888 | 0.5183 | 0.58242 | 0.69818 | 0.82655 | 0.99254 | 1.2251 | 1.4949 | 1.8313 | 2.1306 | 2.4901 | 2.7881 | 3.0209 | 3.2425 | 3.4752 | 3.6961 | 3.9166 | 5.01 | 5.8449
South West | Bridgwater 132 kV | Shapwick | Primary Substation | 11 | Electric Engagement | 0.24578 | 0.3147 | 0.48236 | 0.67621 | 0.86044 | 1.0798 | 1.3184 | 1.6056 | 1.8716 | 2.1291 | 2.3866 | 2.568 | 2.7519 | 2.9411 | 3.1354 | 3.3225 | 4.1722 | 4.7218 | 0.58362 | 0.73622 | 1.1286 | 1.5767 | 2.0022 | 2.4962 | 3.029 | 3.663 | 4.2538 | 4.8312 | 5.4125 | 5.8353 | 6.2653 | 6.7086 | 7.1597 | 7.5969 | 9.5605 | 10.8919
South West | Bridgwater 132 kV | Shapwick | Primary Substation | 11 | Holistic Transition | 0.23969 | 0.29955 | 0.47763 | 0.64808 | 0.84749 | 1.084 | 1.3678 | 1.7353 | 2.0597 | 2.3853 | 2.6418 | 2.8754 | 3.1024 | 3.2818 | 3.4603 | 3.5979 | 4.2268 | 4.5061 | 0.57475 | 0.71376 | 1.1403 | 1.5498 | 2.0292 | 2.5825 | 3.251 | 4.114 | 4.8737 | 5.6309 | 6.2095 | 6.7351 | 7.2457 | 7.64 | 8.0305 | 8.3394 | 9.7773 | 10.4258
South West | Bridgwater 132 kV | Shapwick | Primary Substation | 11 | Hydrogen Evolution | 0.22547 | 0.26476 | 0.32914 | 0.41692 | 0.51944 | 0.66359 | 0.81846 | 1.007 | 1.23 | 1.4934 | 1.7022 | 1.8891 | 2.0605 | 2.2322 | 2.4003 | 2.5292 | 3.1426 | 3.6526 | 0.53855 | 0.62594 | 0.77257 | 0.97328 | 1.2085 | 1.5336 | 1.8833 | 2.3028 | 2.8127 | 3.4199 | 3.8883 | 4.3018 | 4.6782 | 5.0584 | 5.4292 | 5.7223 | 7.1664 | 8.3795
South West | Bridgwater 132 kV | Somerton | Primary Substation | 11 | Counterfactual | 0.39923 | 0.45113 | 0.51523 | 0.59427 | 0.68035 | 0.79505 | 0.92442 | 1.1063 | 1.2594 | 1.4463 | 1.6225 | 1.781 | 1.9542 | 2.1307 | 2.2859 | 2.4511 | 3.1393 | 3.5747 | 0.96398 | 1.0764 | 1.2162 | 1.3875 | 1.5757 | 1.8245 | 2.1072 | 2.4977 | 2.8304 | 3.2398 | 3.6186 | 3.9526 | 4.315 | 4.6848 | 5.0083 | 5.3503 | 6.8018 | 7.7455
South West | Bridgwater 132 kV | Somerton | Primary Substation | 11 | Electric Engagement | 0.45331 | 0.57108 | 0.76394 | 0.97227 | 1.2021 | 1.4813 | 1.7885 | 2.1593 | 2.5196 | 2.8593 | 3.1605 | 3.3357 | 3.4972 | 3.6554 | 3.8114 | 3.9598 | 4.6467 | 5.07 | 1.0839 | 1.3415 | 1.7688 | 2.2304 | 2.738 | 3.3476 | 4.0098 | 4.794 | 5.562 | 6.2942 | 6.9452 | 7.3372 | 7.6995 | 8.0565 | 8.4084 | 8.7448 | 10.2958 | 11.2981
South West | Bridgwater 132 kV | Somerton | Primary Substation | 11 | Holistic Transition | 0.44139 | 0.53859 | 0.70166 | 0.87895 | 1.077 | 1.3202 | 1.6274 | 2.013 | 2.3387 | 2.671 | 2.9658 | 3.2405 | 3.5008 | 3.7258 | 3.9409 | 4.0946 | 4.6917 | 5.0144 | 1.0661 | 1.2894 | 1.6672 | 2.0759 | 2.5341 | 3.0833 | 3.7741 | 4.6337 | 5.3573 | 6.0897 | 6.726 | 7.3195 | 7.8806 | 8.3601 | 8.819 | 9.1551 | 10.4959 | 11.2379
South West | Bridgwater 132 kV | Somerton | Primary Substation | 11 | Hydrogen Evolution | 0.41631 | 0.48366 | 0.58379 | 0.69769 | 0.83285 | 1.0184 | 1.2208 | 1.4752 | 1.7429 | 2.0484 | 2.3403 | 2.6343 | 2.9095 | 3.1494 | 3.3765 | 3.5295 | 4.0718 | 4.4663 | 1.0019 | 1.1499 | 1.3677 | 1.6191 | 1.9187 | 2.3264 | 2.7673 | 3.3108 | 3.8891 | 4.5544 | 5.1766 | 5.7963 | 6.3736 | 6.8772 | 7.3547 | 7.6841 | 8.9062 | 9.8169
South West | Bridgwater 132 kV | Watchfield | Primary Substation | 11 | Counterfactual | 0.60967 | 0.6649 | 0.74245 | 0.83566 | 0.93821 | 1.0437 | 1.1623 | 1.2989 | 1.392 | 1.5003 | 1.6056 | 1.7938 | 1.914 | 2.028 | 2.1404 | 2.2374 | 2.6013 | 2.8143 | 1.4531 | 1.5715 | 1.7391 | 1.9395 | 2.1613 | 2.3913 | 2.6515 | 2.9492 | 3.156 | 3.3996 | 3.6342 | 4.0749 | 4.3406 | 4.5904 | 4.8366 | 5.0442 | 5.8392 | 6.3297
South West | Bridgwater 132 kV | Watchfield | Primary Substation | 11 | Electric Engagement | 0.64075 | 0.73927 | 0.90776 | 2.0243 | 2.2268 | 2.4307 | 2.6528 | 2.9014 | 3.2409 | 3.4564 | 3.6551 | 3.8058 | 3.938 | 4.0747 | 4.172 | 4.2677 | 4.7347 | 5.0564 | 1.522 | 1.7372 | 2.1148 | 4.8535 | 5.3029 | 5.7531 | 6.2397 | 6.7777 | 7.5662 | 8.0555 | 8.5098 | 8.8738 | 9.192 | 9.5208 | 9.7513 | 9.9787 | 11.0904 | 11.8695
South West | Bridgwater 132 kV | Watchfield | Primary Substation | 11 | Holistic Transition | 0.63399 | 0.72094 | 0.87714 | 1.0502 | 1.2451 | 1.4445 | 1.6722 | 1.9388 | 2.1808 | 2.5873 | 2.7946 | 3.0815 | 3.2904 | 3.4323 | 3.5576 | 3.6479 | 3.9973 | 4.1925 | 1.512 | 1.708 | 2.0678 | 2.4634 | 2.9107 | 3.366 | 3.888 | 4.4981 | 5.0632 | 6.0363 | 6.5073 | 7.1783 | 7.655 | 7.9668 | 8.2394 | 8.4423 | 9.2576 | 9.7149
South West | Bridgwater 132 kV | Watchfield | Primary Substation | 11 | Hydrogen Evolution | 0.61973 | 0.68936 | 0.78938 | 0.91333 | 1.052 | 1.1985 | 1.3591 | 1.5344 | 1.7826 | 2.0591 | 2.2435 | 2.426 | 2.6048 | 2.769 | 2.8891 | 2.9707 | 3.3489 | 3.6383 | 1.4755 | 1.6278 | 1.8468 | 2.1189 | 2.4249 | 2.7489 | 3.1032 | 3.4848 | 4.0637 | 4.7112 | 5.1265 | 5.5371 | 5.9393 | 6.3074 | 6.5682 | 6.7522 | 7.6551 | 8.3439
South West | Bridgwater 132 kV | Wedmore | Primary Substation | 11 | Counterfactual | 0.21186 | 0.22896 | 0.25308 | 0.27939 | 0.3103 | 0.35309 | 0.402 | 0.46884 | 0.52569 | 0.59048 | 0.64847 | 0.69803 | 0.74905 | 0.80204 | 0.85366 | 0.90493 | 1.1187 | 1.2541 | 0.51324 | 0.55062 | 0.60439 | 0.66311 | 0.73233 | 0.82704 | 0.93627 | 1.083 | 1.2095 | 1.3556 | 1.4836 | 1.5902 | 1.6979 | 1.8099 | 1.9188 | 2.0269 | 2.4931 | 2.8025
South West | Bridgwater 132 kV | Wedmore | Primary Substation | 11 | Electric Engagement | 0.22906 | 0.26898 | 0.34131 | 0.41835 | 0.49957 | 0.5951 | 0.70091 | 0.83081 | 0.94655 | 1.0532 | 1.1563 | 1.2204 | 1.2856 | 1.3531 | 1.4358 | 1.5029 | 1.8131 | 2.015 | 0.55146 | 0.63943 | 0.8045 | 0.97918 | 1.1619 | 1.3728 | 1.6042 | 1.8846 | 2.1362 | 2.3708 | 2.5993 | 2.7479 | 2.8995 | 3.0565 | 3.2509 | 3.4066 | 4.1183 | 4.6036
South West | Bridgwater 132 kV | Wedmore | Primary Substation | 11 | Holistic Transition | 0.22529 | 0.2592 | 0.32538 | 0.39318 | 0.47166 | 0.56484 | 0.67359 | 0.81529 | 0.93944 | 1.0964 | 1.2022 | 1.3002 | 1.3966 | 1.4775 | 1.5542 | 1.6124 | 1.8587 | 1.9836 | 0.54587 | 0.62425 | 0.78121 | 0.94135 | 1.1268 | 1.3415 | 1.5931 | 1.9189 | 2.204 | 2.5688 | 2.8032 | 3.0196 | 3.2326 | 3.4078 | 3.5742 | 3.7037 | 4.2641 | 4.5538
South West | Bridgwater 132 kV | Wedmore | Primary Substation | 11 | Hydrogen Evolution | 0.21725 | 0.24011 | 0.27159 | 0.30864 | 0.35197 | 0.41219 | 0.47922 | 0.5639 | 0.65439 | 0.75871 | 0.84723 | 0.92913 | 1.0061 | 1.0826 | 1.1713 | 1.2233 | 1.4464 | 1.6324 | 0.52523 | 0.57581 | 0.64577 | 0.72889 | 0.8262 | 0.9595 | 1.1077 | 1.2919 | 1.494 | 1.7289 | 1.9228 | 2.1002 | 2.2657 | 2.4312 | 2.6284 | 2.7447 | 3.2643 | 3.7025
South West | Bridgwater 132 kV | Wells | Primary Substation | 11 | Counterfactual | 0.33451 | 0.41143 | 0.51496 | 0.63051 | 0.76887 | 0.91576 | 1.092 | 1.343 | 1.545 | 1.7872 | 2.0169 | 2.2345 | 2.4643 | 2.6952 | 2.9159 | 3.1354 | 3.9284 | 4.3058 | 0.78198 | 0.94696 | 1.1701 | 1.4186 | 1.7173 | 2.0349 | 2.4165 | 2.9503 | 3.3853 | 3.9107 | 4.4009 | 4.8576 | 5.3345 | 5.8141 | 6.2714 | 6.7262 | 8.4113 | 9.2611
South West | Bridgwater 132 kV | Wells | Primary Substation | 11 | Electric Engagement | 0.42322 | 0.60489 | 0.87721 | 1.1888 | 1.5276 | 1.8745 | 2.2705 | 2.7758 | 3.2637 | 3.6462 | 3.9784 | 4.1304 | 4.2838 | 4.4431 | 4.6 | 4.7517 | 5.4344 | 5.9597 | 0.97896 | 1.3716 | 1.9688 | 2.6524 | 3.3901 | 4.1381 | 4.9833 | 6.0461 | 7.084 | 7.9035 | 8.6223 | 8.9759 | 9.3342 | 9.7066 | 10.0728 | 10.4285 | 12.027 | 13.2815
South West | Bridgwater 132 kV | Wells | Primary Substation | 11 | Holistic Transition | 0.40428 | 0.54823 | 0.77621 | 1.0164 | 1.2916 | 1.5842 | 1.9812 | 2.4453 | 2.8308 | 3.2219 | 3.5873 | 3.937 | 4.2805 | 4.5857 | 4.8721 | 5.0593 | 5.6955 | 6.1049 | 0.95113 | 1.2772 | 1.8005 | 2.3488 | 2.9761 | 3.6351 | 4.5248 | 5.555 | 6.4118 | 7.2745 | 8.0626 | 8.8161 | 9.5566 | 10.2082 | 10.8209 | 11.2348 | 12.708 | 13.6634
South West | Bridgwater 132 kV | Wells | Primary Substation | 11 | Hydrogen Evolution | 0.36187 | 0.4675 | 0.60807 | 0.78133 | 0.98066 | 1.1964 | 1.4433 | 1.7729 | 2.1096 | 2.4796 | 2.8255 | 3.1482 | 3.4546 | 3.7435 | 4.0147 | 4.1739 | 4.7087 | 5.1669 | 0.84291 | 1.0723 | 1.376 | 1.7558 | 2.1914 | 2.66 | 3.1923 | 3.8902 | 4.6157 | 5.4173 | 6.1522 | 6.8332 | 7.4773 | 8.0874 | 8.661 | 9.0107 | 10.2598 | 11.3341
South West | Exeter 132 kV | Athelstan Road | Primary Substation | 11 | Counterfactual | 0.17945 | 0.23291 | 0.3004 | 0.3718 | 0.46163 | 0.5576 | 0.65355 | 0.7971 | 0.91135 | 1.0328 | 1.158 | 1.2818 | 1.4175 | 1.5523 | 1.6834 | 1.8136 | 2.2307 | 2.414 | 0.39014 | 0.5043 | 0.64582 | 0.79516 | 0.98271 | 1.1828 | 1.3819 | 1.676 | 1.9117 | 2.1618 | 2.4195 | 2.6728 | 2.9491 | 3.2236 | 3.4905 | 3.7554 | 4.6116 | 5.0038
South West | Exeter 132 kV | Athelstan Road | Primary Substation | 11 | Electric Engagement | 0.23939 | 0.35908 | 0.50968 | 0.70824 | 0.89113 | 1.0839 | 1.311 | 1.6131 | 1.8619 | 2.0655 | 2.226 | 2.2728 | 2.3125 | 2.3502 | 2.3856 | 2.4161 | 2.5844 | 2.7813 | 0.52321 | 0.78067 | 1.0977 | 1.5163 | 1.8986 | 2.2997 | 2.7704 | 3.39 | 3.9029 | 4.3247 | 4.6576 | 4.7623 | 4.8524 | 4.9385 | 5.0195 | 5.0906 | 5.4881 | 5.9411
South West | Exeter 132 kV | Athelstan Road | Primary Substation | 11 | Holistic Transition | 0.22633 | 0.31983 | 0.45464 | 0.5682 | 0.69272 | 0.83617 | 0.99328 | 1.2036 | 1.3841 | 1.5615 | 1.748 | 1.9312 | 2.1145 | 2.2844 | 2.4403 | 2.5338 | 2.7912 | 3.0373 | 0.50365 | 0.71432 | 1.0082 | 1.2551 | 1.5241 | 1.832 | 2.166 | 2.6054 | 2.9845 | 3.3541 | 3.742 | 4.123 | 4.5052 | 4.8601 | 5.1862 | 5.3888 | 5.983 | 6.5519
South West | Exeter 132 kV | Athelstan Road | Primary Substation | 11 | Hydrogen Evolution | 0.19957 | 0.27001 | 0.36358 | 0.47579 | 0.60131 | 0.73046 | 0.87284 | 1.0743 | 1.2482 | 1.43 | 1.6122 | 1.7854 | 1.9526 | 2.1065 | 2.2472 | 2.3134 | 2.4369 | 2.615 | 0.43469 | 0.58665 | 0.78448 | 1.0222 | 1.2875 | 1.5586 | 1.8548 | 2.2689 | 2.6272 | 3.0007 | 3.3732 | 3.7266 | 4.0679 | 4.3823 | 4.6702 | 4.809 | 5.0885 | 5.484
South West | Exeter 132 kV | Bridge Mills | Primary Substation | 11 | Counterfactual | 0.20174 | 0.23201 | 0.27907 | 0.3335 | 0.39877 | 0.48407 | 0.58307 | 0.7181 | 0.83317 | 0.96599 | 1.0855 | 1.191 | 1.2978 | 1.4093 | 1.5174 | 1.6263 | 2.0975 | 2.4071 | 0.47757 | 0.5424 | 0.64695 | 0.76753 | 0.91242 | 1.1009 | 1.3213 | 1.6171 | 1.8722 | 2.1704 | 2.4332 | 2.6597 | 2.8846 | 3.121 | 3.3489 | 3.5781 | 4.6007 | 5.2988
South West | Exeter 132 kV | Bridge Mills | Primary Substation | 11 | Electric Engagement | 0.23656 | 0.30451 | 0.44748 | 1.1595 | 1.3272 | 1.5208 | 1.7371 | 2.0073 | 2.2491 | 2.474 | 2.6892 | 2.8243 | 2.9578 | 3.0976 | 3.2333 | 3.3662 | 3.9618 | 4.3723 | 0.55491 | 0.70151 | 1.0261 | 2.7669 | 3.1419 | 3.5679 | 4.04 | 4.6231 | 5.1489 | 5.6428 | 6.1199 | 6.432 | 6.7426 | 7.069 | 7.3848 | 7.6955 | 9.0798 | 10.0653
South West | Exeter 132 kV | Bridge Mills | Primary Substation | 11 | Holistic Transition | 0.22924 | 0.28222 | 0.41299 | 0.55146 | 0.71316 | 0.90354 | 1.1318 | 1.4297 | 1.692 | 1.9618 | 2.1878 | 2.3944 | 2.592 | 2.7597 | 2.9188 | 3.0374 | 3.5221 | 3.7743 | 0.54418 | 0.66417 | 0.97238 | 1.2965 | 1.6751 | 2.1114 | 2.6378 | 3.3207 | 3.9215 | 4.5348 | 5.0345 | 5.49 | 5.9259 | 6.2902 | 6.635 | 6.8989 | 8.0095 | 8.5904
South West | Exeter 132 kV | Bridge Mills | Primary Substation | 11 | Hydrogen Evolution | 0.21288 | 0.25132 | 0.31488 | 0.39646 | 0.492 | 0.61813 | 0.7621 | 0.94446 | 1.1477 | 1.3786 | 1.5743 | 1.7497 | 1.9123 | 2.0742 | 2.2284 | 2.3368 | 2.7934 | 3.1743 | 0.50233 | 0.58564 | 0.726 | 0.90689 | 1.1191 | 1.3972 | 1.7138 | 2.1086 | 2.5591 | 3.0756 | 3.5026 | 3.8815 | 4.2308 | 4.5824 | 4.9172 | 5.1605 | 6.2298 | 7.1279
South West | Exeter 132 kV | Budleigh Salterton | Primary Substation | 11 | Counterfactual | 0.081464 | 0.10022 | 0.12399 | 0.15179 | 0.18389 | 0.22062 | 0.26188 | 0.3218 | 0.37019 | 0.42053 | 0.47173 | 0.52511 | 0.5839 | 0.64198 | 0.69895 | 0.75491 | 0.94097 | 1.007 | 0.17956 | 0.21947 | 0.2693 | 0.32747 | 0.39449 | 0.47109 | 0.55694 | 0.68027 | 0.78049 | 0.88465 | 0.99041 | 1.1005 | 1.2213 | 1.3405 | 1.4575 | 1.5723 | 1.9582 | 2.1022
South West | Exeter 132 kV | Budleigh Salterton | Primary Substation | 11 | Electric Engagement | 0.10551 | 0.14911 | 0.20451 | 0.2702 | 0.34446 | 0.42646 | 0.52228 | 0.64652 | 0.74957 | 0.83451 | 0.90613 | 0.93093 | 0.95428 | 0.97655 | 0.99853 | 1.0193 | 1.1147 | 1.2032 | 0.23304 | 0.32619 | 0.44272 | 0.58058 | 0.73613 | 0.90785 | 1.1073 | 1.3634 | 1.5767 | 1.7536 | 1.9036 | 1.9596 | 2.0127 | 2.0634 | 2.1134 | 2.1608 | 2.3807 | 2.5829
South West | Exeter 132 kV | Budleigh Salterton | Primary Substation | 11 | Holistic Transition | 0.10066 | 0.1333 | 0.17351 | 0.22047 | 0.27424 | 0.33612 | 0.40479 | 0.49372 | 0.57158 | 0.65273 | 0.73644 | 0.81934 | 0.89996 | 0.97576 | 1.0462 | 1.0888 | 1.2108 | 1.3195 | 0.22607 | 0.29914 | 0.38695 | 0.48896 | 0.60529 | 0.73869 | 0.88547 | 1.0725 | 1.237 | 1.4079 | 1.5835 | 1.7576 | 1.927 | 2.0865 | 2.2351 | 2.3281 | 2.6079 | 2.8581
South West | Exeter 132 kV | Budleigh Salterton | Primary Substation | 11 | Hydrogen Evolution | 0.08897 | 0.1136 | 0.14593 | 0.18534 | 0.23097 | 0.28413 | 0.3452 | 0.42663 | 0.49778 | 0.57218 | 0.64901 | 0.72427 | 0.79737 | 0.86548 | 0.92874 | 0.96153 | 1.0445 | 1.1199 | 0.1963 | 0.24921 | 0.31768 | 0.40123 | 0.49781 | 0.61027 | 0.73859 | 0.90742 | 1.0554 | 1.2096 | 1.3684 | 1.524 | 1.6751 | 1.8161 | 1.9473 | 2.0173 | 2.2041 | 2.3733
South West | Exeter 132 kV | Burlescombe | Primary Substation | 11 | Counterfactual | 0.17581 | 0.18654 | 0.21138 | 0.23971 | 0.27458 | 0.33223 | 0.39864 | 0.48183 | 0.5572 | 0.64659 | 0.72114 | 0.7785 | 0.83106 | 0.88804 | 0.94162 | 0.99601 | 1.2958 | 1.5548 | 0.43107 | 0.45454 | 0.5127 | 0.57903 | 0.66092 | 0.79185 | 0.94498 | 1.135 | 1.3088 | 1.5184 | 1.6891 | 1.8172 | 1.9317 | 2.0567 | 2.1731 | 2.291 | 2.9603 | 3.5492
South West | Exeter 132 kV | Burlescombe | Primary Substation | 11 | Electric Engagement | 0.18593 | 0.21011 | 0.29992 | 0.39529 | 0.49288 | 0.62047 | 0.75659 | 0.91828 | 1.0748 | 1.2351 | 1.4007 | 1.5306 | 1.6617 | 1.8218 | 1.9555 | 2.0899 | 2.7048 | 3.0591 | 0.45352 | 0.50698 | 0.72114 | 0.94691 | 1.1767 | 1.4655 | 1.7717 | 2.133 | 2.4836 | 2.8445 | 3.2184 | 3.5164 | 3.8188 | 4.1936 | 4.5016 | 4.8116 | 6.2121 | 7.067
South West | Exeter 132 kV | Burlescombe | Primary Substation | 11 | Holistic Transition | 0.18381 | 0.20496 | 0.29903 | 0.39641 | 0.51164 | 0.65728 | 0.83552 | 1.0642 | 1.3172 | 1.5254 | 1.6852 | 1.8252 | 1.9591 | 2.0638 | 2.1648 | 2.2543 | 2.6983 | 2.8677 | 0.45038 | 0.49943 | 0.72865 | 0.96474 | 1.2445 | 1.5848 | 2.006 | 2.5466 | 3.1485 | 3.6347 | 3.9966 | 4.3135 | 4.6165 | 4.8476 | 5.0695 | 5.2688 | 6.2668 | 6.6525
South West | Exeter 132 kV | Burlescombe | Primary Substation | 11 | Hydrogen Evolution | 0.1791 | 0.19295 | 0.22422 | 0.26748 | 0.31924 | 0.4037 | 0.49593 | 0.6041 | 0.74353 | 0.90897 | 1.0356 | 1.1451 | 1.2441 | 1.3698 | 1.4692 | 1.5555 | 1.9859 | 2.3326 | 0.43839 | 0.46909 | 0.54166 | 0.64225 | 0.76303 | 0.95378 | 1.1628 | 1.4054 | 1.7258 | 2.1093 | 2.3955 | 2.6399 | 2.859 | 3.1465 | 3.3681 | 3.5643 | 4.5668 | 5.3848
South West | Exeter 132 kV | Clyst Honiton | Primary Substation | 11 | Counterfactual | 1.3777 | 1.4147 | 1.4654 | 1.5344 | 1.6275 | 1.7193 | 1.8242 | 1.969 | 2.172 | 2.4593 | 2.6581 | 2.7784 | 2.8173 | 2.8556 | 2.9177 | 3.1836 | 3.4986 | 3.6514 | 3.2665 | 3.3449 | 3.4529 | 3.599 | 3.8064 | 4.0205 | 4.2724 | 4.6192 | 5.1142 | 5.8193 | 6.3025 | 6.5899 | 6.6718 | 6.7531 | 6.8945 | 7.5379 | 8.2601 | 8.5929
South West | Exeter 132 kV | Clyst Honiton | Primary Substation | 11 | Electric Engagement | 1.3809 | 1.4344 | 1.5493 | 1.79 | 2.142 | 2.6121 | 3.1551 | 3.6482 | 3.9478 | 4.2127 | 4.4463 | 4.8551 | 4.9979 | 5.0882 | 5.1477 | 5.2126 | 5.3787 | 5.5201 | 3.2759 | 3.3925 | 3.6541 | 4.2253 | 5.0731 | 6.2239 | 7.5595 | 8.7629 | 9.4868 | 10.1266 | 10.6908 | 11.7027 | 12.051 | 12.2691 | 12.4103 | 12.5668 | 12.9588 | 13.2979
South West | Exeter 132 kV | Clyst Honiton | Primary Substation | 11 | Holistic Transition | 1.379 | 1.4291 | 1.5894 | 1.8315 | 2.1717 | 2.5892 | 3.0385 | 3.5989 | 3.9659 | 4.1957 | 4.2521 | 4.3103 | 4.6806 | 4.97 | 5.0535 | 5.0897 | 5.2241 | 5.3748 | 3.2732 | 3.3845 | 3.7643 | 4.3429 | 5.1667 | 6.1902 | 7.2978 | 8.6771 | 9.5756 | 10.1285 | 10.2475 | 10.3723 | 11.2788 | 11.9849 | 12.176 | 12.2559 | 12.562 | 12.9183
South West | Exeter 132 kV | Clyst Honiton | Primary Substation | 11 | Hydrogen Evolution | 1.3743 | 1.4185 | 1.4862 | 1.6669 | 1.9515 | 2.3402 | 2.7919 | 3.341 | 3.637 | 3.8922 | 4.0854 | 4.3006 | 4.662 | 4.7496 | 4.821 | 4.8741 | 4.9753 | 5.0678 | 3.2612 | 3.3576 | 3.505 | 3.9306 | 4.6144 | 5.5674 | 6.6805 | 8.0312 | 8.7479 | 9.3621 | 9.8218 | 10.3387 | 11.2219 | 11.4241 | 11.5859 | 11.71 | 11.9417 | 12.1524
South West | Exeter 132 kV | Core Hill | Primary Substation | 11 | Counterfactual | 0.15258 | 0.18197 | 0.21912 | 0.26252 | 0.31684 | 0.38164 | 0.45696 | 0.56255 | 0.65334 | 0.74841 | 0.8342 | 0.91917 | 1.0142 | 1.1078 | 1.1992 | 1.2894 | 1.6066 | 1.7414 | 0.35321 | 0.4158 | 0.49376 | 0.58462 | 0.69948 | 0.83747 | 0.99873 | 1.221 | 1.4152 | 1.6183 | 1.7975 | 1.9726 | 2.1682 | 2.361 | 2.549 | 2.7344 | 3.3908 | 3.6791
South West | Exeter 132 kV | Core Hill | Primary Substation | 11 | Electric Engagement | 0.18941 | 0.25709 | 0.34357 | 0.46412 | 0.61502 | 0.80505 | 1.0046 | 1.2207 | 1.3903 | 1.5366 | 1.6618 | 1.7134 | 1.7574 | 1.7977 | 1.8371 | 1.8728 | 2.0381 | 2.1838 | 0.43515 | 0.57996 | 0.7619 | 1.0213 | 1.3508 | 1.7718 | 2.206 | 2.6584 | 3.0093 | 3.3149 | 3.5769 | 3.6913 | 3.7894 | 3.8797 | 3.9681 | 4.0488 | 4.4264 | 4.7579
South West | Exeter 132 kV | Core Hill | Primary Substation | 11 | Holistic Transition | 0.18197 | 0.23306 | 0.304 | 0.39784 | 0.51688 | 0.65567 | 0.79889 | 0.97007 | 1.1065 | 1.2448 | 1.3893 | 1.53 | 1.6642 | 1.7874 | 1.9022 | 1.9723 | 2.1823 | 2.3622 | 0.42446 | 0.53908 | 0.69649 | 0.90612 | 1.1746 | 1.4857 | 1.8022 | 2.1716 | 2.462 | 2.7522 | 3.0554 | 3.351 | 3.6332 | 3.8924 | 4.1344 | 4.2867 | 4.7645 | 5.176
South West | Exeter 132 kV | Core Hill | Primary Substation | 11 | Hydrogen Evolution | 0.16393 | 0.20207 | 0.25302 | 0.33202 | 0.43588 | 0.57498 | 0.71858 | 0.88319 | 1.0078 | 1.1391 | 1.2734 | 1.4021 | 1.5245 | 1.634 | 1.7372 | 1.7911 | 1.9337 | 2.062 | 0.37852 | 0.46061 | 0.56851 | 0.74119 | 0.97213 | 1.2857 | 1.6038 | 1.9574 | 2.2163 | 2.4887 | 2.7665 | 3.033 | 3.2862 | 3.5129 | 3.7266 | 3.8416 | 4.1602 | 4.4457
South West | Exeter 132 kV | Countess Wear | Primary Substation | 11 | Counterfactual | 0.2285 | 0.2693 | 0.31746 | 0.3496 | 0.42087 | 0.49652 | 0.57711 | 0.67527 | 0.75936 | 0.85054 | 0.94273 | 1.036 | 1.1364 | 1.2361 | 1.3365 | 1.4421 | 1.7049 | 1.7849 | 0.53277 | 0.61913 | 0.72032 | 0.78794 | 0.93761 | 1.0966 | 1.266 | 1.4701 | 1.6464 | 1.8378 | 2.0308 | 2.2252 | 2.4332 | 2.6402 | 2.8493 | 3.0761 | 3.627 | 3.803
South West | Exeter 132 kV | Countess Wear | Primary Substation | 11 | Electric Engagement | 0.26219 | 0.3397 | 0.43662 | 0.60419 | 0.76663 | 0.92205 | 1.0855 | 1.2892 | 1.453 | 1.5924 | 1.7202 | 1.8267 | 1.8838 | 1.9048 | 1.9247 | 1.9431 | 2.0432 | 2.1536 | 0.60796 | 0.77391 | 0.98009 | 1.3386 | 1.6858 | 2.0171 | 2.3623 | 2.7879 | 3.1309 | 3.4247 | 3.6977 | 3.9492 | 4.0778 | 4.1273 | 4.1742 | 4.2179 | 4.4562 | 4.7134
South West | Exeter 132 kV | Countess Wear | Primary Substation | 11 | Holistic Transition | 0.25555 | 0.31758 | 0.4564 | 0.57754 | 0.69327 | 0.80803 | 0.93735 | 1.0855 | 1.2158 | 1.3508 | 1.4878 | 1.6218 | 1.7518 | 1.8628 | 1.9452 | 1.9928 | 2.1269 | 2.2484 | 0.59845 | 0.73584 | 1.0393 | 1.3035 | 1.5565 | 1.8068 | 2.0875 | 2.4042 | 2.6837 | 2.9719 | 3.2624 | 3.5466 | 3.8317 | 4.0725 | 4.2453 | 4.3491 | 4.6612 | 4.9434
South West | Exeter 132 kV | Countess Wear | Primary Substation | 11 | Hydrogen Evolution | 0.23929 | 0.29079 | 0.35374 | 0.44188 | 0.53852 | 0.64003 | 0.74311 | 0.87554 | 0.9991 | 1.1275 | 1.2578 | 1.4056 | 1.5592 | 1.6753 | 1.7712 | 1.8222 | 1.9213 | 2.0142 | 0.55709 | 0.66802 | 0.8024 | 0.99172 | 1.1994 | 1.4175 | 1.6369 | 1.9148 | 2.1755 | 2.4462 | 2.7195 | 3.0378 | 3.3719 | 3.6157 | 3.8161 | 3.9261 | 4.1537 | 4.365
South West | Exeter 132 kV | Cowley Road | Primary Substation | 11 | Counterfactual | 1.6064 | 1.6465 | 1.6951 | 1.7469 | 1.8057 | 1.8731 | 1.9521 | 2.0754 | 2.1744 | 2.3096 | 2.4457 | 2.5833 | 2.7251 | 2.8671 | 3.0059 | 3.1379 | 3.4876 | 3.6139 | 3.71 | 3.7947 | 3.8973 | 4.0066 | 4.1306 | 4.2721 | 4.4381 | 4.6934 | 4.9003 | 5.1847 | 5.4698 | 5.7564 | 6.0496 | 6.3432 | 6.63 | 6.9022 | 7.6251 | 7.9023
South West | Exeter 132 kV | Cowley Road | Primary Substation | 11 | Electric Engagement | 1.6588 | 1.7512 | 1.8743 | 2.0103 | 2.1598 | 2.3212 | 2.5201 | 2.7837 | 3.0661 | 3.2899 | 3.4893 | 3.579 | 3.6645 | 3.6947 | 3.7257 | 3.7539 | 3.9182 | 4.0913 | 3.8263 | 4.0227 | 4.2848 | 4.5729 | 4.8878 | 5.226 | 5.6411 | 6.1857 | 6.7801 | 7.253 | 7.6777 | 7.8785 | 8.0703 | 8.1397 | 8.2117 | 8.2773 | 8.6592 | 9.0615
South West | Exeter 132 kV | Cowley Road | Primary Substation | 11 | Holistic Transition | 1.6479 | 1.7153 | 1.8039 | 1.8966 | 2 | 2.1214 | 2.2594 | 2.507 | 2.707 | 2.9144 | 3.1234 | 3.3286 | 3.4822 | 3.6217 | 3.75 | 3.8242 | 3.5374 | 3.7251 | 3.8105 | 3.9606 | 4.1576 | 4.3627 | 4.5903 | 4.8549 | 5.1518 | 5.6811 | 6.1086 | 6.5497 | 6.9905 | 7.4242 | 7.745 | 8.0354 | 8.3037 | 8.4642 | 7.7078 | 8.1445
South West | Exeter 132 kV | Cowley Road | Primary Substation | 11 | Hydrogen Evolution | 1.6227 | 1.6746 | 1.7406 | 1.8128 | 1.8947 | 1.9904 | 2.1104 | 2.2777 | 2.4614 | 2.6566 | 2.8539 | 3.0338 | 3.2071 | 3.3681 | 3.5139 | 3.583 | 3.6958 | 3.84 | 3.7462 | 3.8571 | 3.9972 | 4.1506 | 4.3242 | 4.5259 | 4.7781 | 5.1251 | 5.5137 | 5.9264 | 6.3401 | 6.7143 | 7.0741 | 7.4082 | 7.7111 | 7.8578 | 8.1172 | 8.4448
South West | Exeter 132 kV | Crediton | Primary Substation | 11 | Counterfactual | 0.29748 | 0.35763 | 0.43036 | 0.51521 | 0.61997 | 0.7539 | 0.90075 | 1.0344 | 1.1332 | 1.2396 | 1.346 | 1.4534 | 1.5754 | 1.7038 | 1.8338 | 1.9613 | 2.4135 | 2.6157 | 0.69876 | 0.82697 | 0.9806 | 1.1592 | 1.3797 | 1.6616 | 1.9711 | 2.2484 | 2.4548 | 2.6776 | 2.8986 | 3.1197 | 3.3708 | 3.6356 | 3.9039 | 4.1656 | 5.1072 | 5.5443
South West | Exeter 132 kV | Crediton | Primary Substation | 11 | Electric Engagement | 0.34873 | 0.4681 | 0.62421 | 0.80359 | 1.0231 | 1.284 | 1.562 | 1.836 | 2.0636 | 2.263 | 2.4332 | 2.4963 | 2.5559 | 2.6255 | 2.6949 | 2.7591 | 3.0559 | 3.2765 | 0.81256 | 1.0702 | 1.4043 | 1.7865 | 2.2541 | 2.81 | 3.398 | 3.9636 | 4.4361 | 4.8555 | 5.2148 | 5.3558 | 5.4901 | 5.6474 | 5.8037 | 5.9496 | 6.6278 | 7.1406
South West | Exeter 132 kV | Crediton | Primary Substation | 11 | Holistic Transition | 0.33785 | 0.43505 | 0.55809 | 0.69504 | 0.87009 | 1.0888 | 1.3108 | 1.517 | 1.691 | 1.8812 | 2.0783 | 2.2662 | 2.4425 | 2.6157 | 2.78 | 2.8837 | 3.2071 | 3.4417 | 0.79653 | 1.0147 | 1.2873 | 1.5886 | 1.9732 | 2.4508 | 2.9331 | 3.3723 | 3.7437 | 4.1479 | 4.5647 | 4.9619 | 5.3332 | 5.6984 | 6.0455 | 6.271 | 7.0061 | 7.5459
South West | Exeter 132 kV | Crediton | Primary Substation | 11 | Hydrogen Evolution | 0.31356 | 0.38983 | 0.48787 | 0.60369 | 0.75659 | 0.95016 | 1.1496 | 1.3296 | 1.492 | 1.6717 | 1.8504 | 2.0174 | 2.1734 | 2.3324 | 2.4832 | 2.5661 | 2.8024 | 3.0021 | 0.73454 | 0.89993 | 1.1095 | 1.3568 | 1.6845 | 2.1001 | 2.5253 | 2.898 | 3.236 | 3.6129 | 3.9842 | 4.3293 | 4.65 | 4.98 | 5.2936 | 5.4712 | 6.0049 | 6.4563
South West | Exeter 132 kV | Cullompton | Primary Substation | 11 | Counterfactual | 0.47745 | 0.54564 | 0.62778 | 0.7475 | 0.90701 | 1.1234 | 1.3641 | 1.6522 | 1.8968 | 2.1438 | 2.3656 | 2.5814 | 2.8362 | 3.013 | 3.1755 | 3.3143 | 3.8468 | 4.1401 | 1.1228 | 1.2679 | 1.4435 | 1.6974 | 2.0359 | 2.495 | 3.0081 | 3.619 | 4.1414 | 4.6728 | 5.1462 | 5.6028 | 6.1502 | 6.5309 | 6.8783 | 7.1656 | 8.2926 | 8.9377
South West | Exeter 132 kV | Cullompton | Primary Substation | 11 | Electric Engagement | 0.52822 | 0.65568 | 0.84183 | 1.1027 | 1.8006 | 2.178 | 2.5918 | 3.075 | 3.509 | 3.9648 | 4.341 | 4.5534 | 4.7636 | 4.9052 | 5.0243 | 5.139 | 5.6643 | 6.0114 | 1.2356 | 1.5108 | 1.918 | 2.4843 | 4.1235 | 4.9405 | 5.8317 | 6.8633 | 7.8006 | 8.8141 | 9.645 | 10.1192 | 10.5901 | 10.9175 | 11.1883 | 11.4505 | 12.6477 | 13.4659
South West | Exeter 132 kV | Cullompton | Primary Substation | 11 | Holistic Transition | 0.51757 | 0.62314 | 0.79431 | 1.0201 | 1.3066 | 1.6525 | 2.0512 | 2.4976 | 2.9155 | 3.2951 | 3.6933 | 4.0724 | 4.3971 | 4.5972 | 4.7873 | 4.9193 | 5.401 | 5.682 | 1.22 | 1.4562 | 1.8424 | 2.3451 | 2.9837 | 3.7492 | 4.6326 | 5.6171 | 6.551 | 7.3892 | 8.2702 | 9.1088 | 9.8146 | 10.2406 | 10.6455 | 10.934 | 12.022 | 12.6661
South West | Exeter 132 kV | Cullompton | Primary Substation | 11 | Hydrogen Evolution | 0.49364 | 0.5789 | 0.68974 | 0.87316 | 1.1122 | 1.4093 | 1.7316 | 2.1045 | 2.4579 | 2.862 | 3.2382 | 3.5731 | 3.8665 | 4.0742 | 4.2523 | 4.3647 | 4.7595 | 5.0822 | 1.1588 | 1.3438 | 1.5831 | 1.9794 | 2.4985 | 3.1444 | 3.8435 | 4.6444 | 5.4098 | 6.3067 | 7.1334 | 7.86 | 8.4854 | 8.9322 | 9.3087 | 9.5538 | 10.4568 | 11.2003
South West | Exeter 132 kV | Dunkeswell 33/11kv | Primary Substation | 11 | Counterfactual | 0.28553 | 0.29929 | 0.31628 | 0.3365 | 0.36083 | 0.38939 | 0.42148 | 0.46696 | 0.50483 | 0.54534 | 0.58561 | 0.62567 | 0.66979 | 0.71264 | 0.7538 | 0.79598 | 0.96227 | 1.0588 | 0.70358 | 0.73327 | 0.76946 | 0.81234 | 0.86398 | 0.92446 | 0.99242 | 1.0875 | 1.1673 | 1.253 | 1.3374 | 1.4206 | 1.5115 | 1.6 | 1.6849 | 1.7718 | 2.12 | 2.3259
South West | Exeter 132 kV | Dunkeswell 33/11kv | Primary Substation | 11 | Electric Engagement | 0.29966 | 0.33006 | 0.37068 | 0.42065 | 0.47603 | 0.54021 | 0.61325 | 0.70455 | 0.78458 | 0.85473 | 0.91822 | 0.95236 | 0.98432 | 1.0141 | 1.0441 | 1.1154 | 1.2556 | 1.3488 | 0.73486 | 0.80105 | 0.88836 | 0.99573 | 1.1142 | 1.2504 | 1.4049 | 1.5957 | 1.7638 | 1.912 | 2.0471 | 2.1223 | 2.1934 | 2.2602 | 2.3271 | 2.4986 | 2.8178 | 3.0332
South West | Exeter 132 kV | Dunkeswell 33/11kv | Primary Substation | 11 | Holistic Transition | 0.29628 | 0.32133 | 0.35463 | 0.39387 | 0.43835 | 0.495 | 0.55516 | 0.63169 | 0.69912 | 0.77139 | 0.92978 | 0.99641 | 1.0605 | 1.1181 | 1.1756 | 1.2148 | 1.3639 | 1.468 | 0.7296 | 0.78699 | 0.86181 | 0.94916 | 1.0479 | 1.1717 | 1.3031 | 1.468 | 1.6137 | 1.7686 | 2.1381 | 2.2797 | 2.4163 | 2.5389 | 2.6614 | 2.747 | 3.0823 | 3.3177
South West | Exeter 132 kV | Dunkeswell 33/11kv | Primary Substation | 11 | Hydrogen Evolution | 0.29049 | 0.30829 | 0.33215 | 0.36539 | 0.40327 | 0.44828 | 0.50029 | 0.56765 | 0.63769 | 0.70897 | 0.777 | 0.83876 | 0.89986 | 0.95312 | 1.0064 | 1.0825 | 1.1964 | 1.2912 | 0.71447 | 0.75332 | 0.80429 | 0.87548 | 0.95651 | 1.0524 | 1.1628 | 1.3037 | 1.4505 | 1.6003 | 1.7423 | 1.8712 | 1.9985 | 2.1103 | 2.2221 | 2.4016 | 2.6568 | 2.8682
South West | Exeter 132 kV | East Budleigh | Primary Substation | 11 | Counterfactual | 0.099645 | 0.11707 | 0.13999 | 0.16624 | 0.19118 | 0.21939 | 0.25138 | 0.29787 | 0.33552 | 0.37492 | 0.41511 | 0.45668 | 0.50215 | 0.54733 | 0.59151 | 0.6351 | 0.77841 | 0.82963 | 0.23494 | 0.27176 | 0.31973 | 0.37452 | 0.42648 | 0.48521 | 0.55164 | 0.64706 | 0.7249 | 0.8062 | 0.88908 | 0.97464 | 1.0679 | 1.1605 | 1.251 | 1.3403 | 1.6367 | 1.7475
South West | Exeter 132 kV | East Budleigh | Primary Substation | 11 | Electric Engagement | 0.11867 | 0.15573 | 0.20393 | 0.2612 | 0.31917 | 0.38293 | 0.45796 | 0.5556 | 0.63679 | 0.70403 | 0.76132 | 0.7811 | 0.79884 | 0.81541 | 0.83174 | 0.84677 | 0.91629 | 0.9804 | 0.2773 | 0.35628 | 0.45781 | 0.5782 | 0.69937 | 0.83256 | 0.98839 | 1.1892 | 1.3569 | 1.4964 | 1.6159 | 1.6603 | 1.7003 | 1.738 | 1.7751 | 1.8094 | 1.9689 | 2.1153
South West | Exeter 132 kV | East Budleigh | Primary Substation | 11 | Holistic Transition | 0.11493 | 0.14292 | 0.17881 | 0.2209 | 0.26206 | 0.30973 | 0.36308 | 0.43239 | 0.49376 | 0.5582 | 0.62475 | 0.68839 | 0.74969 | 0.80683 | 0.86008 | 0.89125 | 0.98052 | 1.0604 | 0.27204 | 0.33415 | 0.41234 | 0.50353 | 0.5924 | 0.69485 | 0.80851 | 0.95391 | 1.0832 | 1.2183 | 1.3576 | 1.4908 | 1.6193 | 1.7393 | 1.8514 | 1.9193 | 2.1239 | 2.3073
South West | Exeter 132 kV | East Budleigh | Primary Substation | 11 | Hydrogen Evolution | 0.10542 | 0.12778 | 0.15778 | 0.19449 | 0.23002 | 0.27142 | 0.31957 | 0.38387 | 0.4408 | 0.50075 | 0.5628 | 0.62259 | 0.67981 | 0.73257 | 0.78181 | 0.80619 | 0.86632 | 0.92138 | 0.24787 | 0.2958 | 0.35953 | 0.43739 | 0.51238 | 0.59968 | 0.70053 | 0.83354 | 0.9515 | 1.0753 | 1.2032 | 1.3264 | 1.4444 | 1.5533 | 1.6552 | 1.7071 | 1.8422 | 1.9653
South West | Exeter 132 kV | Exeter Science Park | Primary Substation | 11 | Counterfactual | 1.0176 | 1.0413 | 1.0637 | 1.0777 | 1.1063 | 1.1368 | 1.1686 | 1.2051 | 1.2477 | 1.2926 | 1.3207 | 1.3422 | 1.3514 | 1.3583 | 1.3651 | 1.3721 | 1.3968 | 1.4085 | 2.5383 | 2.5883 | 2.635 | 2.6641 | 2.7287 | 2.7978 | 2.87 | 2.9527 | 3.0517 | 3.1558 | 3.2181 | 3.2634 | 3.2824 | 3.2967 | 3.3106 | 3.3247 | 3.3756 | 3.4004
South West | Exeter 132 kV | Exeter Science Park | Primary Substation | 11 | Electric Engagement | 1.0215 | 1.0525 | 1.0829 | 1.1836 | 1.2771 | 1.3769 | 1.4738 | 1.5564 | 1.569 | 1.5793 | 1.5878 | 1.5913 | 1.5944 | 1.5974 | 1.6004 | 1.603 | 1.6148 | 1.6249 | 2.5471 | 2.6145 | 2.6799 | 2.915 | 3.1366 | 3.3736 | 3.6024 | 3.7936 | 3.8198 | 3.8412 | 3.859 | 3.8665 | 3.8735 | 3.8801 | 3.8866 | 3.8925 | 3.9195 | 3.9426
South West | Exeter 132 kV | Exeter Science Park | Primary Substation | 11 | Holistic Transition | 1.0208 | 1.0507 | 1.1248 | 1.2033 | 1.2777 | 1.364 | 1.4509 | 1.5037 | 1.5253 | 1.5353 | 1.5455 | 1.5557 | 1.5656 | 1.575 | 1.5837 | 1.5894 | 1.6052 | 1.6177 | 2.5461 | 2.6113 | 2.7806 | 2.9619 | 3.137 | 3.3413 | 3.547 | 3.6746 | 3.725 | 3.7458 | 3.7673 | 3.7886 | 3.8093 | 3.8289 | 3.8473 | 3.8595 | 3.8953 | 3.9235
South West | Exeter 132 kV | Exeter Science Park | Primary Substation | 11 | Hydrogen Evolution | 1.0197 | 1.0489 | 1.0769 | 1.1596 | 1.235 | 1.317 | 1.3965 | 1.4802 | 1.5109 | 1.5384 | 1.5655 | 1.5772 | 1.5862 | 1.5943 | 1.6018 | 1.6061 | 1.6172 | 1.6284 | 2.5432 | 2.6066 | 2.667 | 2.862 | 3.0429 | 3.2399 | 3.4301 | 3.6294 | 3.6968 | 3.7559 | 3.814 | 3.8384 | 3.8569 | 3.8735 | 3.8891 | 3.898 | 3.9226 | 3.9471
South West | Exeter 132 kV | Exminster | Primary Substation | 11 | Counterfactual | 0.18818 | 0.26156 | 0.34462 | 0.43447 | 0.55791 | 0.68955 | 0.80075 | 0.93453 | 1.0514 | 1.2031 | 1.3786 | 1.5896 | 1.7473 | 1.9009 | 2.0245 | 2.1047 | 2.4311 | 2.6231 | 0.42572 | 0.5811 | 0.75848 | 0.94975 | 1.214 | 1.4977 | 1.7413 | 2.0329 | 2.2935 | 2.6363 | 3.0261 | 3.5028 | 3.8429 | 4.172 | 4.4328 | 4.6002 | 5.3021 | 5.735
South West | Exeter 132 kV | Exminster | Primary Substation | 11 | Electric Engagement | 0.22161 | 0.33386 | 0.49669 | 0.68198 | 0.91664 | 1.1746 | 1.4208 | 1.695 | 1.9963 | 2.2322 | 2.4839 | 2.65 | 2.81 | 2.9582 | 3.0837 | 3.158 | 3.4864 | 3.747 | 0.50089 | 0.74376 | 1.1033 | 1.5147 | 2.0364 | 2.6121 | 3.163 | 3.769 | 4.4594 | 4.9927 | 5.5609 | 5.9422 | 6.3103 | 6.6485 | 6.936 | 7.1113 | 7.8835 | 8.5065
South West | Exeter 132 kV | Exminster | Primary Substation | 11 | Holistic Transition | 0.21455 | 0.31334 | 0.4678 | 0.63202 | 0.85155 | 1.095 | 1.3328 | 1.621 | 1.8813 | 2.2272 | 2.4611 | 2.683 | 2.8863 | 3.0719 | 3.2297 | 3.3051 | 3.593 | 3.7565 | 0.48979 | 0.70815 | 1.0592 | 1.4326 | 1.9326 | 2.4883 | 3.0377 | 3.7038 | 4.3104 | 5.1242 | 5.6443 | 6.1354 | 6.5809 | 6.9837 | 7.3259 | 7.4932 | 8.158 | 8.5382
South West | Exeter 132 kV | Exminster | Primary Substation | 11 | Hydrogen Evolution | 0.2024 | 0.29126 | 0.40071 | 0.53106 | 0.71187 | 0.91876 | 1.107 | 1.3297 | 1.5707 | 1.8404 | 2.0879 | 2.2993 | 2.4998 | 2.6837 | 2.8395 | 2.9109 | 3.1891 | 3.4165 | 0.45836 | 0.65136 | 0.88887 | 1.1765 | 1.5782 | 2.0421 | 2.4673 | 2.9683 | 3.5252 | 4.1474 | 4.7006 | 5.164 | 5.6016 | 5.9998 | 6.3369 | 6.4953 | 7.1452 | 7.6834
South West | Exeter 132 kV | Exmouth Works | Primary Substation | 11 | Counterfactual | 0.18276 | 0.25284 | 0.33513 | 0.43996 | 0.55274 | 0.68231 | 0.82305 | 1.0276 | 1.1925 | 1.3684 | 1.5445 | 1.7288 | 1.9281 | 2.1287 | 2.3221 | 2.5165 | 3.1588 | 3.414 | 0.40932 | 0.55842 | 0.73106 | 0.95033 | 1.1858 | 1.4557 | 1.7485 | 2.1693 | 2.5107 | 2.8744 | 3.2381 | 3.6178 | 4.0269 | 4.4386 | 4.8356 | 5.2342 | 6.5663 | 7.1176
South West | Exeter 132 kV | Exmouth Works | Primary Substation | 11 | Electric Engagement | 0.26236 | 0.4193 | 0.61498 | 0.84432 | 1.0972 | 1.3769 | 1.7013 | 2.1247 | 2.4723 | 2.7602 | 3.0058 | 3.0965 | 3.1803 | 3.2647 | 3.3449 | 3.4228 | 3.7799 | 4.1027 | 0.58614 | 0.92228 | 1.3341 | 1.8158 | 2.3453 | 2.9304 | 3.606 | 4.4783 | 5.1982 | 5.7974 | 6.3118 | 6.5149 | 6.704 | 6.8938 | 7.075 | 7.2509 | 8.0675 | 8.8007
South West | Exeter 132 kV | Exmouth Works | Primary Substation | 11 | Holistic Transition | 0.24556 | 0.36613 | 0.50727 | 0.67712 | 0.85926 | 1.0717 | 1.3053 | 1.6104 | 1.8766 | 2.1514 | 2.4405 | 2.7167 | 2.9862 | 3.2436 | 3.4846 | 3.6323 | 4.0842 | 4.4766 | 0.56154 | 0.83152 | 1.1396 | 1.5084 | 1.9024 | 2.3596 | 2.859 | 3.5003 | 4.0624 | 4.6409 | 5.2472 | 5.8274 | 6.3938 | 6.9355 | 7.444 | 7.7656 | 8.7939 | 9.6897
South West | Exeter 132 kV | Exmouth Works | Primary Substation | 11 | Hydrogen Evolution | 0.20713 | 0.29915 | 0.41713 | 0.55853 | 0.71413 | 0.89798 | 1.1073 | 1.3892 | 1.6338 | 1.8912 | 2.1567 | 2.4159 | 2.6667 | 2.9038 | 3.1224 | 3.242 | 3.557 | 3.8393 | 0.46368 | 0.66185 | 0.91178 | 1.2113 | 1.5402 | 1.9281 | 2.3674 | 2.9512 | 3.4596 | 3.9926 | 4.5409 | 5.0762 | 5.5943 | 6.0846 | 6.5378 | 6.7925 | 7.4955 | 8.1234
South West | Exeter 132 kV | Folly Bridge | Primary Substation | 11 | Counterfactual | 0.27203 | 0.29766 | 0.32934 | 0.37685 | 0.4312 | 0.48934 | 0.54917 | 0.63588 | 0.70709 | 0.78509 | 0.85984 | 0.93028 | 1.005 | 1.0833 | 1.1624 | 1.2421 | 1.5718 | 1.7708 | 0.64829 | 0.70372 | 0.77248 | 0.87444 | 0.99124 | 1.1159 | 1.2451 | 1.4292 | 1.582 | 1.7511 | 1.9104 | 2.0577 | 2.212 | 2.374 | 2.5379 | 2.7028 | 3.3973 | 3.8291
South West | Exeter 132 kV | Folly Bridge | Primary Substation | 11 | Electric Engagement | 0.30019 | 0.35929 | 0.45076 | 0.57301 | 0.68894 | 0.81669 | 0.96425 | 1.1494 | 1.3132 | 1.4645 | 1.6057 | 1.6838 | 1.7582 | 1.8312 | 1.9142 | 1.9854 | 2.3211 | 2.5271 | 0.71075 | 0.8396 | 1.0411 | 1.3077 | 1.5594 | 1.8323 | 2.145 | 2.5326 | 2.877 | 3.1972 | 3.4978 | 3.6704 | 3.8359 | 3.9999 | 4.1839 | 4.3442 | 5.0959 | 5.5796
South West | Exeter 132 kV | Folly Bridge | Primary Substation | 11 | Holistic Transition | 0.29408 | 0.34195 | 0.42461 | 0.5182 | 0.61543 | 0.72623 | 0.85306 | 1.0193 | 1.1678 | 1.3277 | 1.4766 | 1.6136 | 1.7457 | 1.8627 | 1.9833 | 2.062 | 2.3624 | 2.5328 | 0.70175 | 0.81138 | 1.0005 | 1.2122 | 1.433 | 1.6791 | 1.9605 | 2.326 | 2.6518 | 2.9994 | 3.3164 | 3.6078 | 3.8896 | 4.1374 | 4.3925 | 4.5637 | 5.2341 | 5.6233
South West | Exeter 132 kV | Folly Bridge | Primary Substation | 11 | Hydrogen Evolution | 0.2809 | 0.31423 | 0.3611 | 0.43334 | 0.50706 | 0.58861 | 0.68294 | 0.80637 | 0.93074 | 1.0718 | 1.2033 | 1.325 | 1.4373 | 1.5448 | 1.6534 | 1.7194 | 1.9616 | 2.1565 | 0.66798 | 0.74101 | 0.84266 | 0.99908 | 1.1589 | 1.3334 | 1.5345 | 1.7939 | 2.059 | 2.3609 | 2.6372 | 2.8915 | 3.1252 | 3.3508 | 3.5787 | 3.7215 | 4.2685 | 4.7139
South West | Exeter 132 kV | Haven Road | Primary Substation | 11 | Counterfactual | 1.9357 | 2.0698 | 2.2097 | 2.3485 | 2.5175 | 2.6995 | 2.8805 | 3.1513 | 3.3519 | 3.678 | 4.01 | 4.345 | 4.7013 | 5.0554 | 5.3844 | 5.6901 | 6.7915 | 7.1343 | 4.7452 | 5.0305 | 5.3227 | 5.6128 | 5.9656 | 6.3453 | 6.7214 | 7.2781 | 7.6921 | 8.373 | 9.0667 | 9.7641 | 10.5033 | 11.2378 | 11.9189 | 12.5505 | 14.8477 | 15.5821
South West | Exeter 132 kV | Haven Road | Primary Substation | 11 | Electric Engagement | 2.0407 | 2.2956 | 2.5815 | 2.8857 | 3.236 | 3.6194 | 4.0437 | 4.5995 | 5.2144 | 5.7243 | 6.2054 | 6.4906 | 6.7581 | 6.6485 | 6.8498 | 7.0493 | 7.7716 | 8.2984 | 4.9793 | 5.5282 | 6.1297 | 6.7683 | 7.5037 | 8.3064 | 9.1885 | 10.3327 | 11.6246 | 12.6995 | 13.7167 | 14.3404 | 14.927 | 14.5889 | 15.031 | 15.469 | 17.0673 | 18.2244
South West | Exeter 132 kV | Haven Road | Primary Substation | 11 | Holistic Transition | 2.0193 | 2.2292 | 2.4434 | 2.656 | 2.9092 | 3.2097 | 3.5134 | 4.0876 | 4.5532 | 5.0394 | 5.5672 | 6.084 | 6.2269 | 6.6649 | 7.0827 | 7.3422 | 8.3146 | 8.8889 | 4.948 | 5.4162 | 5.8813 | 6.3434 | 6.8914 | 7.5378 | 8.1846 | 9.4069 | 10.3989 | 11.4311 | 12.546 | 13.6381 | 13.8121 | 14.7358 | 15.618 | 16.176 | 18.3759 | 19.6579
South West | Exeter 132 kV | Haven Road | Primary Substation | 11 | Hydrogen Evolution | 1.9704 | 2.1401 | 2.3311 | 2.5226 | 2.7522 | 3.0093 | 3.2859 | 3.6615 | 4.1046 | 4.5626 | 5.0315 | 5.4903 | 5.937 | 6.0207 | 6.3813 | 6.604 | 7.7015 | 8.1035 | 4.8233 | 5.1901 | 5.5927 | 5.9971 | 6.4829 | 7.0253 | 7.6036 | 8.3799 | 9.3116 | 10.2723 | 11.2521 | 12.2103 | 13.1441 | 13.1872 | 13.9394 | 14.4134 | 16.9312 | 17.8059
South West | Exeter 132 kV | Heavitree | Primary Substation | 11 | Counterfactual | 0.3581 | 0.41591 | 0.48375 | 0.55467 | 0.63489 | 0.72287 | 0.82634 | 0.99163 | 1.1229 | 1.2568 | 1.3943 | 1.536 | 1.6914 | 1.8461 | 1.997 | 2.146 | 2.5975 | 2.7334 | 0.81162 | 0.93391 | 1.0762 | 1.2248 | 1.3923 | 1.5755 | 1.7901 | 2.1289 | 2.4 | 2.6755 | 2.958 | 3.248 | 3.5646 | 3.8796 | 4.1868 | 4.4899 | 5.4158 | 5.716
South West | Exeter 132 kV | Heavitree | Primary Substation | 11 | Electric Engagement | 0.43653 | 0.57142 | 0.73606 | 0.92004 | 1.1245 | 1.3427 | 1.6159 | 1.9807 | 2.2837 | 2.512 | 2.6999 | 2.7372 | 2.7696 | 2.8007 | 2.8294 | 2.856 | 3.0138 | 3.2255 | 0.9863 | 1.2725 | 1.6179 | 2.0031 | 2.4288 | 2.8815 | 3.4464 | 4.1937 | 4.8171 | 5.2868 | 5.6757 | 5.7626 | 5.8394 | 5.9134 | 5.9819 | 6.046 | 6.4228 | 6.9107
South West | Exeter 132 kV | Heavitree | Primary Substation | 11 | Holistic Transition | 0.42101 | 0.51861 | 0.63177 | 0.74982 | 0.87963 | 1.0319 | 1.2148 | 1.4624 | 1.6592 | 1.8673 | 2.0878 | 2.3065 | 2.5267 | 2.73 | 2.913 | 3.0136 | 3.2617 | 3.5121 | 0.96433 | 1.1809 | 1.4283 | 1.6851 | 1.9652 | 2.2918 | 2.6807 | 3.198 | 3.6092 | 4.0423 | 4.4998 | 4.9536 | 5.4114 | 5.8343 | 6.2158 | 6.4338 | 7.0148 | 7.6004
South West | Exeter 132 kV | Heavitree | Primary Substation | 11 | Hydrogen Evolution | 0.38178 | 0.45738 | 0.54836 | 0.64749 | 0.75881 | 0.88344 | 1.0434 | 1.2691 | 1.455 | 1.6522 | 1.8572 | 2.0547 | 2.2452 | 2.4211 | 2.5813 | 2.6445 | 2.7363 | 2.894 | 0.86455 | 1.026 | 1.2183 | 1.4279 | 1.6621 | 1.9226 | 2.2559 | 2.7204 | 3.1029 | 3.5074 | 3.9261 | 4.329 | 4.7173 | 5.0762 | 5.4033 | 5.5361 | 5.7518 | 6.1101
South West | Exeter 132 kV | Hemyock | Primary Substation | 11 | Counterfactual | 2.0376 | 2.0601 | 2.0885 | 2.1195 | 2.1606 | 2.2123 | 2.2707 | 2.3471 | 2.4096 | 2.4787 | 2.5442 | 0.96857 | 1.0342 | 1.1036 | 1.1737 | 1.2434 | 1.5238 | 1.6821 | 5.0721 | 5.1205 | 5.1821 | 5.2493 | 5.3381 | 5.4493 | 5.5756 | 5.738 | 5.8725 | 6.0228 | 6.1626 | 2.1986 | 2.3345 | 2.4787 | 2.6241 | 2.7687 | 3.3622 | 3.7098
South West | Exeter 132 kV | Hemyock | Primary Substation | 11 | Electric Engagement | 2.0629 | 2.115 | 2.1935 | 2.2988 | 2.393 | 2.5035 | 2.6303 | 2.7922 | 2.9342 | 3.0622 | 3.1803 | 1.6048 | 1.6537 | 1.7259 | 1.7778 | 1.8254 | 2.0575 | 2.2284 | 5.1281 | 5.2413 | 5.4143 | 5.6441 | 5.8486 | 6.0853 | 6.3549 | 6.695 | 6.9949 | 7.2672 | 7.5206 | 3.5663 | 3.675 | 3.8418 | 3.9577 | 4.0643 | 4.5854 | 4.9881
South West | Exeter 132 kV | Hemyock | Primary Substation | 11 | Holistic Transition | 2.0576 | 2.099 | 2.1774 | 2.2466 | 2.3254 | 2.4208 | 2.5318 | 2.6781 | 2.8552 | 2.9932 | 3.1076 | 1.5793 | 1.6834 | 1.7786 | 1.8723 | 1.9341 | 2.1506 | 2.2901 | 5.1206 | 5.2148 | 5.3934 | 5.5515 | 5.7311 | 5.9441 | 6.1918 | 6.5151 | 6.92 | 7.2223 | 7.4627 | 3.5992 | 3.8193 | 4.0193 | 4.2174 | 4.3514 | 4.8353 | 5.1543
South West | Exeter 132 kV | Hemyock | Primary Substation | 11 | Hydrogen Evolution | 2.0454 | 2.0753 | 2.1136 | 2.1659 | 2.2254 | 2.3027 | 2.3834 | 2.4901 | 2.5985 | 2.7197 | 2.8315 | 1.2971 | 1.3871 | 1.4962 | 1.5804 | 1.6292 | 1.8598 | 2.0281 | 5.0894 | 5.1547 | 5.2377 | 5.3511 | 5.4801 | 5.6466 | 5.8192 | 6.0444 | 6.2767 | 6.5376 | 6.7739 | 2.8964 | 3.0825 | 3.3186 | 3.4943 | 3.5983 | 4.1335 | 4.5222
South West | Exeter 132 kV | Hill Barton Primary | Primary Substation | 11 | Counterfactual | 0.73405 | 0.73992 | 0.747 | 0.75578 | 0.76824 | 0.7843 | 0.802 | 0.82376 | 0.84423 | 0.86789 | 0.88835 | 0.90567 | 0.92305 | 0.93996 | 0.95534 | 0.97263 | 1.0645 | 1.1486 | 1.8319 | 1.8455 | 1.8624 | 1.8828 | 1.9118 | 1.9485 | 1.9892 | 2.0386 | 2.0854 | 2.14 | 2.1861 | 2.2242 | 2.2618 | 2.2987 | 2.3322 | 2.3695 | 2.572 | 2.7577
South West | Exeter 132 kV | Hill Barton Primary | Primary Substation | 11 | Electric Engagement | 0.7359 | 0.74496 | 0.77584 | 0.81872 | 0.86019 | 0.90761 | 0.95338 | 1.006 | 1.0573 | 1.0958 | 1.1322 | 1.1629 | 1.1963 | 1.2214 | 1.2427 | 1.2659 | 1.3949 | 1.4743 | 1.8359 | 1.8571 | 1.9311 | 2.0342 | 2.1333 | 2.2436 | 2.3492 | 2.4697 | 2.5873 | 2.6734 | 2.754 | 2.8227 | 2.8983 | 2.9537 | 2.999 | 3.0505 | 3.3409 | 3.5299
South West | Exeter 132 kV | Hill Barton Primary | Primary Substation | 11 | Holistic Transition | 0.73558 | 0.74551 | 0.78003 | 0.81596 | 0.85663 | 0.90264 | 0.94766 | 0.98653 | 1.0166 | 1.0456 | 1.0714 | 1.0984 | 1.1248 | 1.1475 | 1.1758 | 1.1998 | 1.3068 | 1.2682 | 1.8355 | 1.8594 | 1.9434 | 2.0304 | 2.1285 | 2.2357 | 2.341 | 2.4287 | 2.4954 | 2.558 | 2.6122 | 2.6704 | 2.7275 | 2.7761 | 2.837 | 2.8893 | 3.125 | 3.0137
South West | Exeter 132 kV | Hill Barton Primary | Primary Substation | 11 | Hydrogen Evolution | 0.73482 | 0.74027 | 0.74969 | 0.77058 | 0.79255 | 0.8201 | 0.84912 | 0.88195 | 0.92175 | 0.95384 | 0.98097 | 1.0041 | 1.0255 | 1.0393 | 1.0578 | 1.0702 | 1.1374 | 1.303 | 1.8335 | 1.8463 | 1.8677 | 1.9163 | 1.967 | 2.0295 | 2.095 | 2.1677 | 2.2554 | 2.3247 | 2.3824 | 2.4315 | 2.4761 | 2.5036 | 2.5418 | 2.5674 | 2.716 | 3.1144
South West | Exeter 132 kV | Honiton Heathfield | Primary Substation | 11 | Counterfactual | 0.34087 | 0.39898 | 0.47727 | 0.56872 | 0.67685 | 0.80482 | 0.94978 | 1.1547 | 1.3243 | 1.5079 | 1.6866 | 1.8643 | 2.0604 | 2.2556 | 2.4667 | 2.8574 | 3.6742 | 4.0004 | 0.79852 | 0.92251 | 1.0895 | 1.2838 | 1.5136 | 1.7855 | 2.0941 | 2.5242 | 2.8838 | 3.2749 | 3.6519 | 4.0225 | 4.4308 | 4.8378 | 5.2863 | 6.1838 | 7.9595 | 8.677
South West | Exeter 132 kV | Honiton Heathfield | Primary Substation | 11 | Electric Engagement | 0.41175 | 0.54753 | 0.7424 | 0.97364 | 1.229 | 1.5153 | 1.8445 | 2.2644 | 2.6271 | 2.9536 | 3.2668 | 3.7153 | 3.903 | 4.0872 | 4.2683 | 4.4434 | 4.9522 | 5.3617 | 0.95604 | 1.2483 | 1.6691 | 2.1665 | 2.7132 | 3.323 | 4.0197 | 4.8985 | 5.6636 | 6.3629 | 7.0467 | 8.1379 | 8.5809 | 9.0177 | 9.4468 | 9.8638 | 11.044 | 12.0005
South West | Exeter 132 kV | Honiton Heathfield | Primary Substation | 11 | Holistic Transition | 0.39683 | 0.50032 | 0.65645 | 0.83553 | 1.0419 | 1.2828 | 1.5578 | 1.9129 | 2.2251 | 2.5524 | 2.872 | 3.1791 | 3.7489 | 4.2585 | 4.5632 | 4.7201 | 5.2453 | 5.63 | 0.93409 | 1.1675 | 1.5191 | 1.9188 | 2.3788 | 2.9103 | 3.5168 | 4.2906 | 4.9726 | 5.684 | 6.3712 | 7.0305 | 8.351 | 9.529 | 10.201 | 10.5455 | 11.7486 | 12.631
South West | Exeter 132 kV | Honiton Heathfield | Primary Substation | 11 | Hydrogen Evolution | 0.3635 | 0.44263 | 0.54882 | 0.68583 | 0.84425 | 1.0342 | 1.2527 | 1.5375 | 1.8119 | 2.117 | 2.4097 | 2.826 | 3.3456 | 3.6453 | 3.9315 | 4.1246 | 4.548 | 4.9187 | 0.84898 | 1.0209 | 1.2483 | 1.5428 | 1.8832 | 2.2909 | 2.7571 | 3.356 | 3.9398 | 4.5951 | 5.2152 | 6.1486 | 7.3444 | 8.0002 | 8.6279 | 9.0691 | 10.0411 | 10.8907
South West | Exeter 132 kV | Lapford | Primary Substation | 11 | Counterfactual | 0.39095 | 0.41661 | 0.44781 | 0.48217 | 0.53636 | 0.60225 | 0.66421 | 0.75156 | 0.82368 | 0.9028 | 0.97887 | 1.0497 | 1.1248 | 1.2035 | 1.2825 | 1.3626 | 1.6873 | 1.8831 | 0.93237 | 0.98796 | 1.0558 | 1.1305 | 1.2471 | 1.3883 | 1.5223 | 1.7081 | 1.8632 | 2.035 | 2.1974 | 2.3457 | 2.501 | 2.6644 | 2.8282 | 2.9943 | 3.6809 | 4.1075
South West | Exeter 132 kV | Lapford | Primary Substation | 11 | Electric Engagement | 0.41799 | 0.47635 | 0.56376 | 0.6723 | 0.79181 | 0.92486 | 1.0712 | 1.2552 | 1.4188 | 1.5677 | 1.7081 | 1.7872 | 1.8637 | 1.962 | 2.0433 | 2.1212 | 2.5469 | 2.7614 | 0.99242 | 1.1199 | 1.3131 | 1.5507 | 1.811 | 2.096 | 2.407 | 2.7936 | 3.1389 | 3.4554 | 3.7557 | 3.9317 | 4.1027 | 4.3278 | 4.5095 | 4.6847 | 5.6239 | 6.1281
South West | Exeter 132 kV | Lapford | Primary Substation | 11 | Holistic Transition | 0.4122 | 0.46028 | 0.54236 | 0.62023 | 0.72384 | 0.84231 | 0.97095 | 1.1387 | 1.323 | 1.4819 | 1.6296 | 1.7661 | 1.8961 | 2.0163 | 2.1329 | 2.2161 | 2.5973 | 2.7776 | 0.98391 | 1.0942 | 1.2825 | 1.4609 | 1.6964 | 1.9596 | 2.246 | 2.6165 | 3.0331 | 3.3805 | 3.6964 | 3.9884 | 4.2669 | 4.5226 | 4.7706 | 4.9516 | 5.7883 | 6.1986
South West | Exeter 132 kV | Lapford | Primary Substation | 11 | Hydrogen Evolution | 0.39941 | 0.43276 | 0.47536 | 0.53328 | 0.61424 | 0.70089 | 0.79438 | 0.91678 | 1.0436 | 1.1829 | 1.3111 | 1.4289 | 1.5395 | 1.6667 | 1.7735 | 1.8424 | 2.1286 | 2.3382 | 0.95117 | 1.0243 | 1.1168 | 1.2425 | 1.4184 | 1.6044 | 1.8042 | 2.0622 | 2.3333 | 2.6329 | 2.9035 | 3.1506 | 3.3819 | 3.657 | 3.8823 | 4.032 | 4.6723 | 5.1501
South West | Exeter 132 kV | Marsh Barton | Primary Substation | 11 | Counterfactual | 1.8579 | 1.9083 | 1.9787 | 2.042 | 2.1089 | 2.1801 | 2.2753 | 2.4285 | 2.5769 | 2.7681 | 2.9605 | 3.1632 | 3.3303 | 3.4702 | 3.6069 | 3.7435 | 4.3469 | 4.5897 | 4.5938 | 4.7011 | 4.8482 | 4.9815 | 5.122 | 5.2712 | 5.4716 | 5.793 | 6.1058 | 6.5111 | 6.9182 | 7.3453 | 7.6949 | 7.9858 | 8.2699 | 8.5538 | 9.8214 | 10.3355
South West | Exeter 132 kV | Marsh Barton | Primary Substation | 11 | Electric Engagement | 1.8919 | 1.9714 | 2.0969 | 2.2303 | 2.3515 | 2.481 | 2.6612 | 2.9293 | 3.2096 | 3.4914 | 3.7971 | 4.0521 | 4.2499 | 4.4112 | 4.5745 | 4.7297 | 3.9867 | 4.3893 | 4.6704 | 4.8439 | 5.1116 | 5.3964 | 5.6542 | 5.9266 | 6.3088 | 6.876 | 7.4745 | 8.0794 | 8.7325 | 9.2822 | 9.7084 | 10.0554 | 10.4058 | 10.7404 | 8.6406 | 9.5054
South West | Exeter 132 kV | Marsh Barton | Primary Substation | 11 | Holistic Transition | 1.8862 | 1.9594 | 2.0707 | 2.1698 | 2.2711 | 2.3873 | 2.552 | 2.8267 | 3.1058 | 3.3925 | 3.7118 | 4.0716 | 4.3388 | 4.5597 | 4.7741 | 4.9551 | 4.1539 | 4.5251 | 4.6618 | 4.8267 | 5.0693 | 5.287 | 5.5097 | 5.7616 | 6.1192 | 6.7143 | 7.3205 | 7.9411 | 8.6221 | 9.4069 | 9.9742 | 10.4396 | 10.8913 | 11.277 | 9.0337 | 9.8278
South West | Exeter 132 kV | Marsh Barton | Primary Substation | 11 | Hydrogen Evolution | 1.8729 | 1.9341 | 2.0308 | 2.1251 | 2.2218 | 2.3204 | 2.462 | 2.684 | 2.954 | 3.2292 | 3.5245 | 3.813 | 4.051 | 4.2438 | 4.4344 | 4.5892 | 3.752 | 4.057 | 4.6284 | 4.7613 | 4.9647 | 5.1647 | 5.3701 | 5.5771 | 5.8777 | 6.3479 | 6.9253 | 7.5145 | 8.142 | 8.7545 | 9.256 | 9.6608 | 10.0608 | 10.3898 | 8.0789 | 8.7332
South West | Exeter 132 kV | Marsh Green | Primary Substation | 11 | Counterfactual | 0.72831 | 0.76383 | 0.816 | 0.87069 | 0.93795 | 1.0283 | 1.1346 | 1.2722 | 1.3941 | 1.5372 | 1.6597 | 1.7635 | 1.8645 | 1.9683 | 2.0648 | 2.1613 | 2.6193 | 2.9505 | 1.7849 | 1.8602 | 1.9769 | 2.0999 | 2.2519 | 2.4546 | 2.6954 | 3.0029 | 3.2785 | 3.6064 | 3.8814 | 4.1087 | 4.325 | 4.5491 | 4.7555 | 4.9617 | 5.9745 | 6.7339
South West | Exeter 132 kV | Marsh Green | Primary Substation | 11 | Electric Engagement | 0.75917 | 0.8259 | 0.98864 | 1.1655 | 1.3496 | 1.5609 | 1.7883 | 2.0667 | 2.3248 | 2.5693 | 2.8069 | 2.9764 | 3.1493 | 3.3994 | 3.5567 | 3.7192 | 4.433 | 4.9364 | 1.8544 | 1.9976 | 2.3758 | 2.7851 | 3.2081 | 3.6849 | 4.193 | 4.8099 | 5.3859 | 5.9352 | 6.4728 | 6.8694 | 7.2771 | 7.8792 | 8.2492 | 8.6332 | 10.3057 | 11.5223
South West | Exeter 132 kV | Marsh Green | Primary Substation | 11 | Holistic Transition | 0.75357 | 0.80762 | 0.96663 | 1.1298 | 1.322 | 1.5405 | 1.8032 | 2.1404 | 2.5974 | 2.8981 | 3.1373 | 3.3543 | 3.5618 | 3.7256 | 3.88 | 4.0012 | 4.5382 | 4.8033 | 1.8464 | 1.9663 | 2.346 | 2.734 | 3.1912 | 3.7001 | 4.3159 | 5.1037 | 6.1959 | 6.8921 | 7.4314 | 7.9187 | 8.3849 | 8.746 | 9.0854 | 9.3587 | 10.5975 | 11.2104
South West | Exeter 132 kV | Marsh Green | Primary Substation | 11 | Hydrogen Evolution | 0.74016 | 0.78493 | 0.85088 | 0.93498 | 1.0339 | 1.1677 | 1.3178 | 1.499 | 1.7129 | 1.9613 | 2.1614 | 2.3381 | 2.4998 | 2.7366 | 2.8867 | 3.0012 | 3.5318 | 3.9804 | 1.8122 | 1.9088 | 2.0565 | 2.2467 | 2.471 | 2.7719 | 3.1086 | 3.5094 | 3.9945 | 4.5627 | 5.0091 | 5.3987 | 5.7533 | 6.3007 | 6.6328 | 6.8947 | 8.1486 | 9.2153
South West | Exeter 132 kV | Newton Poppleford | Primary Substation | 11 | Counterfactual | 0.085196 | 0.10011 | 0.12026 | 0.14339 | 0.1707 | 0.20227 | 0.23843 | 0.28983 | 0.33234 | 0.37827 | 0.42353 | 0.46844 | 0.51673 | 0.56463 | 0.6111 | 0.65739 | 0.82055 | 0.89546 | 0.19798 | 0.22963 | 0.27235 | 0.3213 | 0.37899 | 0.44572 | 0.52218 | 0.62942 | 0.71887 | 0.8159 | 0.91078 | 1.0041 | 1.1037 | 1.2026 | 1.2985 | 1.3938 | 1.7359 | 1.8999
South West | Exeter 132 kV | Newton Poppleford | Primary Substation | 11 | Electric Engagement | 0.10379 | 0.13762 | 0.18631 | 0.24388 | 0.30774 | 0.37875 | 0.46123 | 0.5673 | 0.65736 | 0.73432 | 0.80245 | 0.83255 | 0.86068 | 0.88762 | 0.914 | 0.93868 | 1.0517 | 1.1434 | 0.23936 | 0.31149 | 0.41588 | 0.53875 | 0.67443 | 0.8248 | 0.99833 | 1.2192 | 1.4078 | 1.5702 | 1.7151 | 1.7832 | 1.8474 | 1.9093 | 1.9699 | 2.0269 | 2.2888 | 2.5024
South West | Exeter 132 kV | Newton Poppleford | Primary Substation | 11 | Holistic Transition | 0.099997 | 0.12523 | 0.16302 | 0.20668 | 0.25671 | 0.31502 | 0.38121 | 0.46702 | 0.54307 | 0.62243 | 0.69941 | 0.77123 | 0.83989 | 0.90187 | 0.96046 | 0.99748 | 1.1187 | 1.2118 | 0.23394 | 0.29033 | 0.37472 | 0.47145 | 0.5821 | 0.70984 | 0.85451 | 1.0398 | 1.2044 | 1.3752 | 1.5388 | 1.6915 | 1.8376 | 1.9691 | 2.0936 | 2.1748 | 2.4528 | 2.666
South West | Exeter 132 kV | Newton Poppleford | Primary Substation | 11 | Hydrogen Evolution | 0.090728 | 0.10972 | 0.13647 | 0.17055 | 0.20984 | 0.25662 | 0.31108 | 0.38251 | 0.45088 | 0.52395 | 0.59503 | 0.66194 | 0.72547 | 0.78366 | 0.83887 | 0.86917 | 0.96251 | 1.0454 | 0.21037 | 0.25108 | 0.30818 | 0.38098 | 0.46486 | 0.56466 | 0.68016 | 0.82961 | 0.97394 | 1.1285 | 1.2772 | 1.4168 | 1.5492 | 1.6711 | 1.7868 | 1.8526 | 2.0665 | 2.2557
South West | Exeter 132 kV | Newton St Cyres | Primary Substation | 11 | Counterfactual | 0.1486 | 0.16589 | 0.19446 | 0.2271 | 0.26613 | 0.31794 | 0.37778 | 0.45909 | 0.52958 | 0.61074 | 0.6823 | 0.74519 | 0.81023 | 0.87787 | 0.94292 | 1.0069 | 1.2955 | 1.4877 | 0.35503 | 0.39215 | 0.4558 | 0.52849 | 0.61555 | 0.73047 | 0.86443 | 1.0435 | 1.2005 | 1.3837 | 1.5419 | 1.6774 | 1.8156 | 1.9601 | 2.0982 | 2.2333 | 2.8607 | 3.2945
South West | Exeter 132 kV | Newton St Cyres | Primary Substation | 11 | Electric Engagement | 0.16905 | 0.20893 | 0.29569 | 0.39168 | 0.49367 | 0.61269 | 0.74542 | 0.91019 | 1.0606 | 1.2074 | 1.346 | 1.4335 | 1.5184 | 1.6053 | 1.6902 | 1.7739 | 2.1459 | 2.4029 | 0.40049 | 0.4867 | 0.68473 | 0.9018 | 1.1308 | 1.3936 | 1.684 | 2.0406 | 2.3687 | 2.693 | 3.0011 | 3.2028 | 3.4 | 3.6031 | 3.8006 | 3.9964 | 4.8606 | 5.4779
South West | Exeter 132 kV | Newton St Cyres | Primary Substation | 11 | Holistic Transition | 0.16511 | 0.19654 | 0.27693 | 0.36311 | 0.46366 | 0.58247 | 0.72587 | 0.91189 | 1.077 | 1.2479 | 1.3925 | 1.5255 | 1.6495 | 1.7515 | 1.8487 | 1.9204 | 2.2189 | 2.3745 | 0.39494 | 0.46619 | 0.65647 | 0.85864 | 1.0948 | 1.3677 | 1.6989 | 2.1263 | 2.505 | 2.894 | 3.2147 | 3.5091 | 3.783 | 4.0046 | 4.2154 | 4.3752 | 5.0593 | 5.4177
South West | Exeter 132 kV | Newton St Cyres | Primary Substation | 11 | Hydrogen Evolution | 0.15509 | 0.17773 | 0.21496 | 0.26439 | 0.32205 | 0.39964 | 0.48845 | 0.59928 | 0.72453 | 0.87176 | 0.99624 | 1.1063 | 1.2051 | 1.3019 | 1.3947 | 1.4604 | 1.7436 | 1.9826 | 0.36947 | 0.41867 | 0.50134 | 0.61146 | 0.74017 | 0.91184 | 1.1078 | 1.3486 | 1.6273 | 1.9583 | 2.2316 | 2.4704 | 2.6832 | 2.8942 | 3.0962 | 3.2444 | 3.9086 | 4.4723
South West | Exeter 132 kV | Offwell | Primary Substation | 11 | Counterfactual | 0.20792 | 0.22605 | 0.24729 | 0.274 | 0.30554 | 0.34168 | 0.38219 | 0.44188 | 0.49039 | 0.54116 | 0.593 | 0.64735 | 0.70902 | 0.76957 | 0.82811 | 0.88566 | 1.1095 | 1.2351 | 0.49363 | 0.53197 | 0.5765 | 0.63218 | 0.69782 | 0.77296 | 0.85709 | 0.97969 | 1.08 | 1.1849 | 1.2918 | 1.4034 | 1.5303 | 1.6548 | 1.7751 | 1.8927 | 2.3532 | 2.6155
South West | Exeter 132 kV | Offwell | Primary Substation | 11 | Electric Engagement | 0.22879 | 0.26729 | 0.31933 | 0.38314 | 0.45412 | 0.53573 | 0.63141 | 0.75524 | 0.8623 | 0.95966 | 1.0438 | 1.085 | 1.1191 | 1.1482 | 1.1772 | 1.2018 | 1.3117 | 1.4048 | 0.53969 | 0.62182 | 0.73118 | 0.86479 | 1.0131 | 1.1833 | 1.3819 | 1.6367 | 1.8582 | 2.0616 | 2.2375 | 2.326 | 2.4001 | 2.4642 | 2.5281 | 2.5829 | 2.8309 | 3.0413
South West | Exeter 132 kV | Offwell | Primary Substation | 11 | Holistic Transition | 0.22345 | 0.25165 | 0.28926 | 0.33506 | 0.38722 | 0.45212 | 0.52385 | 0.61723 | 0.70072 | 0.79224 | 0.88765 | 0.97894 | 1.0618 | 1.136 | 1.2066 | 1.2508 | 1.3895 | 1.4988 | 0.53119 | 0.59433 | 0.6763 | 0.77527 | 0.88771 | 1.0264 | 1.1789 | 1.3746 | 1.5502 | 1.7418 | 1.9418 | 2.1333 | 2.3066 | 2.4623 | 2.6105 | 2.7057 | 3.0159 | 3.2632
South West | Exeter 132 kV | Offwell | Primary Substation | 11 | Hydrogen Evolution | 0.21543 | 0.23777 | 0.27002 | 0.31229 | 0.36036 | 0.41828 | 0.48629 | 0.57771 | 0.6645 | 0.75938 | 0.85458 | 0.94292 | 1.0245 | 1.0959 | 1.1641 | 1.2026 | 1.312 | 1.3989 | 0.51003 | 0.55784 | 0.62564 | 0.71436 | 0.81523 | 0.93651 | 1.0782 | 1.2666 | 1.4457 | 1.6423 | 1.8391 | 2.0212 | 2.1888 | 2.3361 | 2.4769 | 2.5582 | 2.7975 | 2.9894
South West | Exeter 132 kV | Ottery St Mary | Primary Substation | 11 | Counterfactual | 0.25427 | 0.29165 | 0.34551 | 0.40846 | 0.48271 | 0.57252 | 0.67467 | 0.81836 | 0.9375 | 1.0673 | 1.1923 | 1.3132 | 1.4416 | 1.5704 | 1.6985 | 1.8507 | 2.312 | 2.5298 | 0.57548 | 0.6546 | 0.76987 | 0.90421 | 1.0628 | 1.2544 | 1.4731 | 1.7765 | 2.0305 | 2.3092 | 2.5744 | 2.8278 | 3.0943 | 3.3621 | 3.6292 | 3.957 | 4.9401 | 5.4259
South West | Exeter 132 kV | Ottery St Mary | Primary Substation | 11 | Electric Engagement | 0.30241 | 0.38789 | 0.52597 | 0.68594 | 0.8622 | 1.0598 | 1.2867 | 1.5764 | 1.824 | 2.0383 | 2.2388 | 2.4009 | 2.4957 | 2.5861 | 2.6741 | 2.7597 | 3.144 | 3.4419 | 0.68248 | 0.86437 | 1.1648 | 1.5109 | 1.8902 | 2.3132 | 2.7952 | 3.4041 | 3.9281 | 4.386 | 4.821 | 5.2071 | 5.4249 | 5.6346 | 5.8384 | 6.0373 | 6.9274 | 7.6281
South West | Exeter 132 kV | Ottery St Mary | Primary Substation | 11 | Holistic Transition | 0.29236 | 0.35498 | 0.4666 | 0.59219 | 0.73784 | 0.90669 | 1.1034 | 1.3578 | 1.5818 | 1.8117 | 2.025 | 2.2244 | 2.4674 | 2.6694 | 2.8294 | 2.9351 | 3.3022 | 3.5523 | 0.66793 | 0.80756 | 1.0608 | 1.3434 | 1.6708 | 2.046 | 2.4838 | 3.0442 | 3.5387 | 4.0432 | 4.5025 | 4.9312 | 5.4691 | 5.9114 | 6.2528 | 6.4858 | 7.3276 | 7.9027
South West | Exeter 132 kV | Ottery St Mary | Primary Substation | 11 | Hydrogen Evolution | 0.26898 | 0.31691 | 0.38903 | 0.48002 | 0.58539 | 0.71521 | 0.86404 | 1.0571 | 1.2446 | 1.4488 | 1.6409 | 1.8536 | 2.0722 | 2.2352 | 2.3881 | 2.4796 | 2.79 | 3.0563 | 0.60831 | 0.71085 | 0.8659 | 1.0621 | 1.2894 | 1.5691 | 1.8882 | 2.2961 | 2.699 | 3.1397 | 3.547 | 4.0079 | 4.4852 | 4.83 | 5.1536 | 5.3545 | 6.0713 | 6.6882
South West | Exeter 132 kV | Pinhoe | Primary Substation | 11 | Counterfactual | 0.53156 | 0.65604 | 0.79559 | 0.97044 | 1.1317 | 1.2811 | 1.4401 | 1.6763 | 1.8694 | 2.0529 | 2.2369 | 2.4205 | 2.6249 | 2.8286 | 3.027 | 3.2227 | 3.8459 | 4.0822 | 1.1698 | 1.433 | 1.726 | 2.0918 | 2.4295 | 2.7419 | 3.0736 | 3.5607 | 3.9622 | 4.3422 | 4.722 | 5.0982 | 5.5157 | 5.9313 | 6.3359 | 6.7348 | 8.0178 | 8.5331
South West | Exeter 132 kV | Pinhoe | Primary Substation | 11 | Electric Engagement | 0.63064 | 0.86014 | 1.1397 | 1.4961 | 1.8394 | 2.1757 | 2.547 | 3.0312 | 3.4175 | 3.7326 | 3.9956 | 4.0639 | 4.1246 | 4.1837 | 4.2396 | 4.2909 | 4.559 | 4.8726 | 1.3909 | 1.8818 | 2.4745 | 3.2303 | 3.955 | 4.6601 | 5.4324 | 6.4292 | 7.2259 | 7.8794 | 8.4278 | 8.5841 | 8.7247 | 8.862 | 8.9921 | 9.1126 | 9.744 | 10.4667
South West | Exeter 132 kV | Pinhoe | Primary Substation | 11 | Holistic Transition | 0.61035 | 0.79385 | 1.0248 | 1.2988 | 1.55 | 1.7886 | 2.0531 | 2.3807 | 2.6617 | 2.9575 | 3.26 | 3.5516 | 3.8433 | 4.1121 | 4.3569 | 4.4979 | 4.8792 | 5.222 | 1.3612 | 1.7665 | 2.2707 | 2.8664 | 3.4124 | 3.9276 | 4.4946 | 5.1839 | 5.7773 | 6.3992 | 7.031 | 7.6385 | 8.2472 | 8.808 | 9.3195 | 9.6249 | 10.5061 | 11.3038
South West | Exeter 132 kV | Pinhoe | Primary Substation | 11 | Hydrogen Evolution | 0.5641 | 0.71975 | 0.90747 | 1.1484 | 1.3681 | 1.579 | 1.8198 | 2.1433 | 2.4026 | 2.6771 | 2.9577 | 3.2219 | 3.4766 | 3.7131 | 3.9294 | 4.0269 | 4.2156 | 4.4595 | 1.2431 | 1.5783 | 1.9781 | 2.493 | 2.9612 | 3.4076 | 3.9138 | 4.5846 | 5.1217 | 5.6893 | 6.2661 | 6.807 | 7.3283 | 7.8131 | 8.257 | 8.4629 | 8.897 | 9.4512
South West | Exeter 132 kV | Sidmouth Town | Primary Substation | 11 | Counterfactual | 0.18068 | 0.22393 | 0.27798 | 0.34101 | 0.41406 | 0.49757 | 0.59066 | 0.72657 | 0.83606 | 0.95045 | 1.0671 | 1.1883 | 1.3209 | 1.4531 | 1.5823 | 1.7093 | 2.1295 | 2.2847 | 0.40174 | 0.49381 | 0.60717 | 0.73899 | 0.89142 | 1.0655 | 1.2591 | 1.5386 | 1.7653 | 2.0018 | 2.2427 | 2.4925 | 2.765 | 3.0363 | 3.3014 | 3.5619 | 4.433 | 4.77
South West | Exeter 132 kV | Sidmouth Town | Primary Substation | 11 | Electric Engagement | 0.23478 | 0.33466 | 0.46045 | 0.61004 | 0.77834 | 0.96297 | 1.1793 | 1.4601 | 1.6924 | 1.8834 | 2.0451 | 2.1031 | 2.1558 | 2.2065 | 2.2565 | 2.3033 | 2.5153 | 2.7158 | 0.52206 | 0.73603 | 1.0006 | 1.3147 | 1.6672 | 2.0538 | 2.5041 | 3.0829 | 3.5639 | 3.9615 | 4.2999 | 4.4305 | 4.5502 | 4.6656 | 4.7795 | 4.8864 | 5.3755 | 5.8338
South West | Exeter 132 kV | Sidmouth Town | Primary Substation | 11 | Holistic Transition | 0.22357 | 0.29888 | 0.39027 | 0.49686 | 0.61807 | 0.75649 | 0.91118 | 1.1115 | 1.2869 | 1.4696 | 1.6585 | 1.8434 | 2.0229 | 2.192 | 2.3486 | 2.4437 | 2.7173 | 2.9591 | 0.50581 | 0.67495 | 0.87468 | 1.1063 | 1.3686 | 1.667 | 1.9977 | 2.419 | 2.7896 | 3.1742 | 3.5706 | 3.9591 | 4.3363 | 4.6923 | 5.023 | 5.2302 | 5.8589 | 6.4163
South West | Exeter 132 kV | Sidmouth Town | Primary Substation | 11 | Hydrogen Evolution | 0.19755 | 0.2539 | 0.32798 | 0.41826 | 0.52221 | 0.64266 | 0.78174 | 0.96775 | 1.1292 | 1.2982 | 1.4731 | 1.6449 | 1.8103 | 1.965 | 2.1082 | 2.1837 | 2.3725 | 2.5403 | 0.43935 | 0.56067 | 0.71752 | 0.90873 | 1.1286 | 1.3831 | 1.6751 | 2.0605 | 2.396 | 2.7462 | 3.1074 | 3.4623 | 3.804 | 4.1239 | 4.4209 | 4.582 | 5.0065 | 5.3831
South West | Exeter 132 kV | Sowton | Primary Substation | 11 | Counterfactual | 0.19375 | 0.21619 | 0.24704 | 0.27354 | 0.30486 | 0.32739 | 0.35296 | 0.39054 | 0.42174 | 0.45301 | 0.48475 | 0.5177 | 0.55169 | 0.58793 | 0.62389 | 0.68091 | 0.88272 | 1.0204 | 0.45156 | 0.49908 | 0.56334 | 0.61876 | 0.68429 | 0.73122 | 0.78433 | 0.86157 | 0.92617 | 0.99067 | 1.0558 | 1.123 | 1.1923 | 1.266 | 1.3396 | 1.4587 | 1.8708 | 2.1528
South West | Exeter 132 kV | Sowton | Primary Substation | 11 | Electric Engagement | 0.20768 | 0.24634 | 0.29996 | 0.3543 | 0.41365 | 0.46395 | 0.52303 | 0.59845 | 0.65889 | 0.70968 | 0.76492 | 0.81277 | 0.84847 | 0.88076 | 0.91037 | 0.93806 | 1.0802 | 1.1969 | 0.48259 | 0.56602 | 0.6791 | 0.79512 | 0.92105 | 1.0262 | 1.1494 | 1.3044 | 1.4288 | 1.5337 | 1.6486 | 1.7564 | 1.8306 | 1.8981 | 1.96 | 2.0181 | 2.33 | 2.5793
South West | Exeter 132 kV | Sowton | Primary Substation | 11 | Holistic Transition | 0.20467 | 0.23804 | 0.28159 | 0.32592 | 0.36919 | 0.40882 | 0.45236 | 0.50592 | 0.55124 | 0.59922 | 0.65812 | 0.71673 | 0.79003 | 0.85339 | 0.90647 | 0.98336 | 1.1292 | 1.2462 | 0.47793 | 0.55229 | 0.6471 | 0.74332 | 0.83768 | 0.92261 | 1.0153 | 1.1271 | 1.2219 | 1.3217 | 1.4433 | 1.5644 | 1.7213 | 1.8561 | 1.9662 | 2.1418 | 2.4556 | 2.7092
South West | Exeter 132 kV | Sowton | Primary Substation | 11 | Hydrogen Evolution | 0.19892 | 0.22602 | 0.26998 | 0.3099 | 0.35426 | 0.38856 | 0.43225 | 0.48738 | 0.53804 | 0.5865 | 0.65423 | 0.74743 | 0.84224 | 0.91555 | 0.98619 | 1.0358 | 1.1992 | 1.2862 | 0.46313 | 0.52161 | 0.61415 | 0.7 | 0.79474 | 0.86683 | 0.95793 | 1.0716 | 1.1752 | 1.2743 | 1.4119 | 1.6046 | 1.8023 | 1.9509 | 2.0941 | 2.1952 | 2.5414 | 2.7261
South West | Exeter 132 kV | Sowton B | Primary Substation | 11 | Counterfactual | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9835 | 5.9836 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9587 | 14.9589
South West | Exeter 132 kV | Sowton B | Primary Substation | 11 | Electric Engagement | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 0 | 0 | 0 | 0 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 0 | 0 | 0 | 0
South West | Exeter 132 kV | Sowton B | Primary Substation | 11 | Holistic Transition | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 0 | 0 | 0 | 0 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 0 | 0 | 0 | 0
South West | Exeter 132 kV | Sowton B | Primary Substation | 11 | Hydrogen Evolution | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 5.9834 | 0 | 0 | 0 | 5.7735e-05 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 14.9586 | 0 | 0 | 0 | 0.00011547
South West | Exeter 132 kV | St Thomas | Primary Substation | 11 | Counterfactual | 0.3984 | 0.46875 | 0.58195 | 0.70885 | 0.85704 | 1.0253 | 1.1932 | 1.4393 | 1.6429 | 1.8544 | 2.0591 | 2.2554 | 2.4623 | 2.6713 | 2.8736 | 3.0759 | 3.8086 | 4.1827 | 0.90884 | 1.0584 | 1.3004 | 1.5712 | 1.8876 | 2.2466 | 2.6066 | 3.1263 | 3.5608 | 4.0154 | 4.4493 | 4.8591 | 5.2865 | 5.7191 | 6.1363 | 6.5536 | 8.0987 | 8.9328
South West | Exeter 132 kV | St Thomas | Primary Substation | 11 | Electric Engagement | 0.48807 | 0.65018 | 0.92125 | 1.2395 | 1.5842 | 1.9507 | 2.3435 | 2.8532 | 3.2955 | 3.6612 | 3.9909 | 4.135 | 4.2742 | 4.4162 | 4.5547 | 4.6929 | 5.3692 | 5.8886 | 1.1083 | 1.4543 | 2.0445 | 2.7336 | 3.4765 | 4.2585 | 5.0891 | 6.1559 | 7.088 | 7.864 | 8.5701 | 8.901 | 9.223 | 9.5524 | 9.8724 | 10.1926 | 11.744 | 12.9661
South West | Exeter 132 kV | St Thomas | Primary Substation | 11 | Holistic Transition | 0.46986 | 0.59059 | 0.82464 | 1.0754 | 1.3426 | 1.646 | 1.9776 | 2.4185 | 2.7861 | 3.1682 | 3.5262 | 3.8679 | 4.2066 | 4.5061 | 4.7829 | 4.9649 | 5.6111 | 6.0283 | 1.0822 | 1.352 | 1.8801 | 2.4431 | 3.0441 | 3.7174 | 4.4544 | 5.4238 | 6.2334 | 7.0691 | 7.8354 | 8.5643 | 9.287 | 9.9201 | 10.5057 | 10.9032 | 12.3731 | 13.3364
South West | Exeter 132 kV | St Thomas | Primary Substation | 11 | Hydrogen Evolution | 0.42595 | 0.51745 | 0.66939 | 0.84942 | 1.0521 | 1.2883 | 1.536 | 1.8671 | 2.1727 | 2.5108 | 2.8289 | 3.125 | 3.4058 | 3.6733 | 3.9232 | 4.0641 | 4.5295 | 4.9846 | 0.97024 | 1.1667 | 1.4937 | 1.8827 | 2.3212 | 2.8291 | 3.3586 | 4.0559 | 4.7105 | 5.438 | 6.109 | 6.7289 | 7.3147 | 7.8758 | 8.4003 | 8.7072 | 9.7842 | 10.8377
South West | Exeter 132 kV | Tiverton Junction | Primary Substation | 11 | Counterfactual | 1.184 | 1.2673 | 1.3957 | 1.5282 | 1.6661 | 1.8877 | 2.1418 | 2.4102 | 2.6197 | 2.8418 | 3.0443 | 3.2314 | 3.4299 | 3.6221 | 3.7789 | 3.9408 | 4.6331 | 5.0894 | 2.9129 | 3.0899 | 3.3658 | 3.6503 | 3.9482 | 4.4245 | 4.9741 | 5.5527 | 6.0094 | 6.4993 | 6.9392 | 7.3386 | 7.7619 | 8.1725 | 8.5054 | 8.8431 | 10.3239 | 11.3305
South West | Exeter 132 kV | Tiverton Junction | Primary Substation | 11 | Electric Engagement | 1.2348 | 1.3808 | 1.6769 | 2.0038 | 2.3384 | 2.7601 | 3.1934 | 3.6857 | 4.1609 | 4.5849 | 4.9604 | 5.1812 | 5.3964 | 5.6205 | 5.7895 | 6.0286 | 6.7859 | 7.3323 | 3.0254 | 3.3415 | 4.0078 | 4.7398 | 5.4873 | 6.4204 | 7.3718 | 8.4448 | 9.4915 | 10.438 | 11.2767 | 11.7866 | 12.2881 | 12.817 | 13.2089 | 13.7802 | 15.5564 | 16.8726
South West | Exeter 132 kV | Tiverton Junction | Primary Substation | 11 | Holistic Transition | 1.2236 | 1.3482 | 1.625 | 1.9145 | 2.2121 | 2.6054 | 3.0754 | 3.612 | 4.1138 | 4.4992 | 4.9606 | 5.273 | 5.5495 | 5.7734 | 5.9867 | 6.1428 | 6.7566 | 7.0973 | 3.0084 | 3.2864 | 3.9229 | 4.5851 | 5.2719 | 6.1608 | 7.2222 | 8.4326 | 9.5801 | 10.4503 | 11.5119 | 12.206 | 12.8157 | 13.3015 | 13.7639 | 14.1119 | 15.526 | 16.3184
South West | Exeter 132 kV | Tiverton Junction | Primary Substation | 11 | Hydrogen Evolution | 1.2003 | 1.3022 | 1.4784 | 1.6736 | 1.8789 | 2.1912 | 2.5057 | 2.8531 | 3.2126 | 3.5902 | 3.9328 | 4.26 | 4.5528 | 4.8229 | 5.0504 | 5.2734 | 5.872 | 6.32 | 2.949 | 3.1704 | 3.554 | 3.9798 | 4.4303 | 5.1158 | 5.8047 | 6.5567 | 7.3476 | 8.1918 | 8.9413 | 9.646 | 10.2699 | 10.8575 | 11.3439 | 11.8531 | 13.2354 | 14.2926
South West | Exeter 132 kV | Tiverton Moorhayes | Primary Substation | 11 | Counterfactual | 0.55062 | 0.59718 | 0.66176 | 0.7319 | 0.81865 | 0.94452 | 1.0847 | 1.2695 | 1.4237 | 1.5928 | 1.7522 | 1.8972 | 2.0483 | 2.21 | 2.3717 | 2.5329 | 3.1884 | 3.5806 | 1.3336 | 1.4335 | 1.5747 | 1.7282 | 1.9179 | 2.1894 | 2.4942 | 2.8904 | 3.2248 | 3.5964 | 3.9394 | 4.2457 | 4.5604 | 4.8983 | 5.2355 | 5.5713 | 6.9698 | 7.8401
South West | Exeter 132 kV | Tiverton Moorhayes | Primary Substation | 11 | Electric Engagement | 0.60601 | 0.71428 | 0.90087 | 1.1219 | 1.3392 | 1.6154 | 1.9263 | 2.3168 | 2.6657 | 2.9859 | 3.2925 | 3.4701 | 3.6487 | 3.8688 | 4.0816 | 4.2763 | 5.1991 | 5.7092 | 1.4567 | 1.6902 | 2.1067 | 2.5957 | 3.0737 | 3.6682 | 4.3325 | 5.1589 | 5.9011 | 6.5877 | 7.2496 | 7.649 | 8.0519 | 8.5549 | 9.0382 | 9.4768 | 11.5306 | 12.7327
South West | Exeter 132 kV | Tiverton Moorhayes | Primary Substation | 11 | Holistic Transition | 0.5943 | 0.67861 | 0.85002 | 1.0143 | 1.2027 | 1.4495 | 1.7376 | 2.1122 | 2.4941 | 2.8802 | 3.1971 | 3.4875 | 3.7691 | 4.0279 | 4.2737 | 4.4562 | 5.2131 | 5.5792 | 1.4395 | 1.6304 | 2.0274 | 2.4077 | 2.8438 | 3.3965 | 4.0458 | 4.8845 | 5.7506 | 6.6173 | 7.3024 | 7.9289 | 8.5362 | 9.0876 | 9.611 | 10.0079 | 11.6848 | 12.5173
South West | Exeter 132 kV | Tiverton Moorhayes | Primary Substation | 11 | Hydrogen Evolution | 0.56755 | 0.62886 | 0.71389 | 0.82105 | 0.94455 | 1.1253 | 1.3169 | 1.5624 | 1.8181 | 2.1067 | 2.365 | 2.6051 | 2.8314 | 3.0918 | 3.3361 | 3.4927 | 4.1161 | 4.6082 | 1.3713 | 1.5043 | 1.6904 | 1.9257 | 2.1971 | 2.5879 | 3.0009 | 3.5229 | 4.0792 | 4.7112 | 5.2637 | 5.7723 | 6.2493 | 6.8123 | 7.3386 | 7.6807 | 9.093 | 10.2232
South West | Exeter 132 kV | Tiverton South | Primary Substation | 11 | Counterfactual | 0.3376 | 0.40334 | 0.47298 | 0.5542 | 0.6559 | 0.78561 | 0.91518 | 1.1001 | 1.246 | 1.4105 | 1.5766 | 1.7437 | 1.9415 | 2.1501 | 2.3492 | 2.5368 | 3.2012 | 3.5199 | 0.7948 | 0.93486 | 1.0825 | 1.2539 | 1.4679 | 1.7401 | 2.0119 | 2.3943 | 2.6983 | 3.0424 | 3.3875 | 3.7319 | 4.1437 | 4.5788 | 4.9926 | 5.3775 | 6.7591 | 7.4435
South West | Exeter 132 kV | Tiverton South | Primary Substation | 11 | Electric Engagement | 0.41029 | 0.55472 | 0.739 | 0.96109 | 1.1975 | 1.4695 | 1.7675 | 2.1599 | 2.5124 | 2.8495 | 3.1312 | 3.2318 | 3.3265 | 3.4385 | 3.549 | 3.6525 | 4.127 | 4.4542 | 0.95581 | 1.2664 | 1.6589 | 2.1301 | 2.6291 | 3.2 | 3.8199 | 4.6285 | 5.3636 | 6.0862 | 6.6877 | 6.9102 | 7.1217 | 7.372 | 7.6186 | 7.8509 | 8.9207 | 9.6769
South West | Exeter 132 kV | Tiverton South | Primary Substation | 11 | Holistic Transition | 0.39391 | 0.50561 | 0.65444 | 0.79627 | 0.96725 | 1.1765 | 1.4124 | 1.7239 | 1.9935 | 2.2742 | 2.5789 | 2.8687 | 3.1279 | 3.3812 | 3.6205 | 3.7775 | 4.2863 | 4.6254 | 0.93107 | 1.1828 | 1.5129 | 1.8264 | 2.2024 | 2.656 | 3.1657 | 3.8299 | 4.4062 | 5.0048 | 5.656 | 6.2754 | 6.8223 | 7.3554 | 7.8601 | 8.1997 | 9.3419 | 10.1192
South West | Exeter 132 kV | Tiverton South | Primary Substation | 11 | Hydrogen Evolution | 0.36105 | 0.44547 | 0.54814 | 0.66849 | 0.81748 | 1.0014 | 1.1872 | 1.4451 | 1.6917 | 1.9827 | 2.2716 | 2.5368 | 2.7773 | 3.0152 | 3.2392 | 3.3698 | 3.7477 | 4.0464 | 0.84666 | 1.0291 | 1.2466 | 1.5018 | 1.8177 | 2.206 | 2.5941 | 3.1262 | 3.6402 | 4.2593 | 4.8685 | 5.4219 | 5.9174 | 6.4113 | 6.8764 | 7.1548 | 7.9981 | 8.6701
South West | Exeter 132 kV | Topsham | Primary Substation | 11 | Counterfactual | 0.21657 | 0.26459 | 0.30816 | 0.36671 | 0.42176 | 0.48025 | 0.53659 | 0.61327 | 0.67507 | 0.74437 | 0.8148 | 0.87899 | 0.94981 | 1.0208 | 1.0904 | 1.1675 | 1.3993 | 1.5025 | 0.50522 | 0.60675 | 0.69857 | 0.82124 | 0.93712 | 1.0603 | 1.1788 | 1.3378 | 1.4671 | 1.6124 | 1.7591 | 1.8912 | 2.0362 | 2.1816 | 2.3244 | 2.4862 | 2.9681 | 3.1922
South West | Exeter 132 kV | Topsham | Primary Substation | 11 | Electric Engagement | 0.25393 | 0.3393 | 0.44276 | 0.55105 | 0.66929 | 0.77126 | 0.89345 | 1.0533 | 1.1962 | 1.3 | 1.3913 | 1.4431 | 1.4697 | 1.4959 | 1.5207 | 1.5434 | 1.6498 | 1.769 | 0.58863 | 0.77206 | 0.99289 | 1.2242 | 1.4759 | 1.6906 | 1.9462 | 2.2766 | 2.5746 | 2.7912 | 2.984 | 3.1067 | 3.1683 | 3.2292 | 3.2867 | 3.3402 | 3.5935 | 3.8705
South West | Exeter 132 kV | Topsham | Primary Substation | 11 | Holistic Transition | 0.24706 | 0.31767 | 0.39688 | 0.48506 | 0.57452 | 0.65139 | 0.74267 | 0.87314 | 0.97047 | 1.0719 | 1.1738 | 1.2735 | 1.3863 | 1.4854 | 1.5677 | 1.6171 | 1.759 | 1.8808 | 0.57836 | 0.73452 | 0.90914 | 1.1026 | 1.299 | 1.4668 | 1.6649 | 1.9442 | 2.1522 | 2.3679 | 2.5822 | 2.7917 | 3.0345 | 3.246 | 3.4189 | 3.5264 | 3.8551 | 4.1379
South West | Exeter 132 kV | Topsham | Primary Substation | 11 | Hydrogen Evolution | 0.22865 | 0.29112 | 0.36219 | 0.4292 | 0.50343 | 0.58606 | 0.67239 | 0.78019 | 0.87758 | 0.98287 | 1.0802 | 1.1843 | 1.288 | 1.3719 | 1.4488 | 1.4878 | 1.5792 | 1.675 | 0.53256 | 0.66758 | 0.81943 | 0.96332 | 1.1224 | 1.2992 | 1.482 | 1.706 | 1.9097 | 2.1302 | 2.3312 | 2.5499 | 2.7692 | 2.9423 | 3.1011 | 3.1841 | 3.3936 | 3.6135
South West | Exeter 132 kV | Witheridge | Primary Substation | 11 | Counterfactual | 1.2289 | 1.2549 | 1.2866 | 1.3238 | 1.3517 | 1.3986 | 1.4481 | 1.517 | 1.574 | 1.6336 | 1.694 | 1.7516 | 1.8126 | 1.8755 | 1.9385 | 2.0024 | 2.2832 | 2.4759 | 3.0409 | 3.0966 | 3.1646 | 3.2441 | 3.3041 | 3.4031 | 3.5083 | 3.6529 | 3.7735 | 3.901 | 4.0282 | 4.1481 | 4.2737 | 4.4036 | 4.5336 | 4.6651 | 5.2512 | 5.66
South West | Exeter 132 kV | Witheridge | Primary Substation | 11 | Electric Engagement | 1.2483 | 1.2993 | 1.4318 | 1.5861 | 1.7261 | 1.8965 | 2.0685 | 2.2901 | 2.51 | 2.6949 | 2.8656 | 2.9981 | 3.1516 | 3.2801 | 3.3754 | 3.4913 | 4.0572 | 4.3494 | 3.084 | 3.1951 | 3.5037 | 3.8615 | 4.1861 | 4.5691 | 4.9493 | 5.4385 | 5.9291 | 6.3358 | 6.7088 | 7.0093 | 7.3646 | 7.6583 | 7.864 | 8.1261 | 9.3814 | 10.0732
South West | Exeter 132 kV | Witheridge | Primary Substation | 11 | Holistic Transition | 1.2443 | 1.2875 | 1.3999 | 1.5189 | 1.6332 | 1.7595 | 1.8731 | 2.0208 | 2.1568 | 2.2976 | 2.444 | 2.5773 | 2.7041 | 2.8203 | 2.9435 | 3.0345 | 3.4666 | 3.689 | 3.0782 | 3.1759 | 3.4427 | 3.7223 | 3.9936 | 4.2775 | 4.5279 | 4.8519 | 5.1493 | 5.4525 | 5.7656 | 6.0511 | 6.3234 | 6.5718 | 6.834 | 7.0317 | 7.9758 | 8.4843
South West | Exeter 132 kV | Witheridge | Primary Substation | 11 | Hydrogen Evolution | 1.2349 | 1.2681 | 1.3098 | 1.3632 | 1.4055 | 1.4769 | 1.5548 | 1.6547 | 1.7603 | 1.8769 | 1.9877 | 2.0915 | 2.1893 | 2.2818 | 2.3785 | 2.4434 | 2.7142 | 2.911 | 3.0543 | 3.1268 | 3.217 | 3.3322 | 3.4232 | 3.5734 | 3.7372 | 3.9453 | 4.1677 | 4.4143 | 4.6452 | 4.8606 | 5.063 | 5.2561 | 5.4575 | 5.5951 | 6.1812 | 6.6136
South West | Exeter 132 kV | Withycombe Raleigh | Primary Substation | 11 | Counterfactual | 0.43355 | 0.51955 | 0.62677 | 0.75135 | 0.89905 | 1.0677 | 1.2561 | 1.5298 | 1.7515 | 1.9836 | 2.2178 | 2.4593 | 2.7381 | 3.0151 | 3.2888 | 3.5867 | 4.4381 | 4.7264 | 1.0099 | 1.1915 | 1.416 | 1.6762 | 1.9852 | 2.3374 | 2.7297 | 3.293 | 3.7529 | 4.2337 | 4.7171 | 5.2143 | 5.7923 | 6.3663 | 6.9346 | 7.5646 | 9.3362 | 9.9629
South West | Exeter 132 kV | Withycombe Raleigh | Primary Substation | 11 | Electric Engagement | 0.54482 | 0.74003 | 0.99033 | 1.3013 | 1.6485 | 2.0292 | 2.4712 | 3.0388 | 3.5174 | 3.9414 | 4.2943 | 4.4772 | 4.5944 | 4.7084 | 4.8101 | 4.9016 | 5.3243 | 5.7073 | 1.2575 | 1.6718 | 2.1973 | 2.8546 | 3.5853 | 4.3851 | 5.3065 | 6.4755 | 7.4688 | 8.3664 | 9.1147 | 9.5448 | 9.8134 | 10.0753 | 10.3066 | 10.5147 | 11.4817 | 12.3546
South West | Exeter 132 kV | Withycombe Raleigh | Primary Substation | 11 | Holistic Transition | 0.52182 | 0.66333 | 0.84916 | 1.0651 | 1.3107 | 1.5947 | 1.9096 | 2.3156 | 2.6669 | 3.0401 | 3.445 | 3.8383 | 4.2667 | 4.6526 | 4.9665 | 5.1531 | 5.6859 | 6.1459 | 1.2242 | 1.5384 | 1.9456 | 2.416 | 2.9489 | 3.5625 | 4.2365 | 5.0906 | 5.8319 | 6.6182 | 7.4768 | 8.311 | 9.237 | 10.0666 | 10.7274 | 11.1326 | 12.3505 | 13.408
South West | Exeter 132 kV | Withycombe Raleigh | Primary Substation | 11 | Hydrogen Evolution | 0.46763 | 0.57797 | 0.72346 | 0.91388 | 1.1295 | 1.379 | 1.6632 | 2.0385 | 2.3632 | 2.7287 | 3.1042 | 3.4933 | 3.8857 | 4.2091 | 4.5003 | 4.6461 | 5.0085 | 5.3282 | 1.0861 | 1.3218 | 1.6293 | 2.0369 | 2.4966 | 3.0267 | 3.6256 | 4.4046 | 5.0786 | 5.8464 | 6.6318 | 7.455 | 8.2909 | 8.9654 | 9.5696 | 9.8801 | 10.6931 | 11.4095
South West | Exeter 132 kV | Woodbury | Primary Substation | 11 | Counterfactual | 0.23731 | 0.27842 | 0.32071 | 0.36109 | 0.4089 | 0.46847 | 0.53556 | 0.62928 | 0.70738 | 0.79197 | 0.87423 | 0.9551 | 1.0417 | 1.128 | 1.211 | 1.2946 | 1.6161 | 1.7929 | 0.54043 | 0.62793 | 0.7182 | 0.80424 | 0.90617 | 1.0328 | 1.1759 | 1.3731 | 1.539 | 1.7198 | 1.8937 | 2.0626 | 2.242 | 2.4209 | 2.5928 | 2.7655 | 3.4422 | 3.827
South West | Exeter 132 kV | Woodbury | Primary Substation | 11 | Electric Engagement | 0.26934 | 0.34758 | 0.44473 | 0.54728 | 0.66012 | 0.79296 | 0.94495 | 1.1379 | 1.3053 | 1.454 | 1.5899 | 1.6628 | 1.7326 | 1.8014 | 1.8686 | 1.9329 | 2.2308 | 2.4308 | 0.61205 | 0.78172 | 0.99247 | 1.2138 | 1.4562 | 1.7392 | 2.0609 | 2.4654 | 2.8181 | 3.1339 | 3.4245 | 3.5875 | 3.7445 | 3.9002 | 4.0519 | 4.1978 | 4.8722 | 5.3376
South West | Exeter 132 kV | Woodbury | Primary Substation | 11 | Holistic Transition | 0.26291 | 0.32723 | 0.40816 | 0.48861 | 0.58191 | 0.69683 | 0.82768 | 0.99593 | 1.1459 | 1.3021 | 1.4496 | 1.5892 | 1.7235 | 1.8438 | 1.9581 | 2.0367 | 2.3225 | 2.5022 | 0.60258 | 0.74676 | 0.92884 | 1.1091 | 1.3181 | 1.5712 | 1.8602 | 2.2282 | 2.5565 | 2.8963 | 3.2119 | 3.5101 | 3.7971 | 4.0524 | 4.295 | 4.4663 | 5.1082 | 5.5169
South West | Exeter 132 kV | Woodbury | Primary Substation | 11 | Hydrogen Evolution | 0.24901 | 0.30355 | 0.36056 | 0.42154 | 0.49189 | 0.58159 | 0.68355 | 0.8156 | 0.94567 | 1.0864 | 1.2195 | 1.345 | 1.4644 | 1.5759 | 1.6816 | 1.748 | 1.9765 | 2.1627 | 0.56686 | 0.68621 | 0.80866 | 0.93979 | 1.0911 | 1.2831 | 1.5005 | 1.7782 | 2.0554 | 2.3565 | 2.6372 | 2.9006 | 3.1507 | 3.3856 | 3.6084 | 3.7525 | 4.2703 | 4.695
South West | Indian Queens 132 kV | Blackpool | Primary Substation | 11 | Counterfactual | 0.22618 | 0.24027 | 0.25855 | 0.27808 | 0.30055 | 0.3296 | 0.36311 | 0.41212 | 0.45264 | 0.4965 | 0.53941 | 0.5815 | 0.62724 | 0.67335 | 0.71777 | 0.76164 | 0.92145 | 0.99054 | 0.4878 | 0.5177 | 0.55691 | 0.5988 | 0.64696 | 0.70887 | 0.78048 | 0.88366 | 0.96978 | 1.0638 | 1.1544 | 1.2423 | 1.3369 | 1.4325 | 1.5242 | 1.6147 | 1.9517 | 2.1065
South West | Indian Queens 132 kV | Blackpool | Primary Substation | 11 | Electric Engagement | 0.24459 | 0.27723 | 0.32649 | 0.3798 | 0.43901 | 0.50879 | 0.58996 | 0.69578 | 0.78672 | 0.86566 | 0.9378 | 0.97087 | 1.0126 | 1.0637 | 1.0972 | 1.1309 | 1.3923 | 1.4897 | 0.52871 | 0.59823 | 0.70531 | 0.82056 | 0.94767 | 1.0959 | 1.2671 | 1.4883 | 1.6795 | 1.8469 | 2.0012 | 2.0767 | 2.1698 | 2.2819 | 2.3584 | 2.4353 | 2.9989 | 3.2291
South West | Indian Queens 132 kV | Blackpool | Primary Substation | 11 | Holistic Transition | 0.24072 | 0.26486 | 0.30409 | 0.3447 | 0.39274 | 0.4513 | 0.52086 | 0.61322 | 0.69458 | 0.77861 | 0.85763 | 0.93319 | 1.0161 | 1.0992 | 1.1608 | 1.2008 | 1.4479 | 1.5284 | 0.52301 | 0.57686 | 0.66638 | 0.75859 | 0.8673 | 0.9971 | 1.1518 | 1.3552 | 1.5346 | 1.7186 | 1.8881 | 2.0497 | 2.2258 | 2.3998 | 2.5301 | 2.6174 | 3.1486 | 3.3342
South West | Indian Queens 132 kV | Blackpool | Primary Substation | 11 | Hydrogen Evolution | 0.23195 | 0.25029 | 0.27469 | 0.30214 | 0.33462 | 0.37699 | 0.42599 | 0.492 | 0.55631 | 0.62687 | 0.69448 | 0.75892 | 0.82551 | 0.89369 | 0.94956 | 0.98266 | 1.1443 | 1.2339 | 0.50069 | 0.53997 | 0.59246 | 0.65167 | 0.72167 | 0.81221 | 0.91654 | 1.0551 | 1.1927 | 1.3443 | 1.4871 | 1.6222 | 1.7611 | 1.9036 | 2.0211 | 2.0931 | 2.4477 | 2.6544
South West | Indian Queens 132 kV | Bodmin | Primary Substation | 11 | Counterfactual | 0.6805 | 0.75777 | 0.86845 | 1.0072 | 1.1477 | 1.3175 | 1.5105 | 1.7806 | 2.0087 | 2.2582 | 2.505 | 2.743 | 2.9788 | 3.2047 | 3.4206 | 3.6369 | 4.4456 | 4.8414 | 1.5395 | 1.7036 | 1.9405 | 2.236 | 2.5367 | 2.8993 | 3.3132 | 3.8848 | 4.3723 | 4.9094 | 5.4354 | 5.9351 | 6.4244 | 6.8936 | 7.3404 | 7.7874 | 9.4983 | 10.3791
South West | Indian Queens 132 kV | Bodmin | Primary Substation | 11 | Electric Engagement | 0.76577 | 0.93192 | 1.2041 | 1.5205 | 1.8468 | 2.2181 | 2.6423 | 3.1906 | 3.6612 | 4.0759 | 4.4573 | 4.6633 | 4.8459 | 5.017 | 5.1833 | 5.3613 | 6.1296 | 6.6422 | 1.7287 | 2.0845 | 2.6782 | 3.3647 | 4.0692 | 4.8644 | 5.7666 | 6.9239 | 7.9219 | 8.8094 | 9.6328 | 10.101 | 10.5197 | 10.9147 | 11.2972 | 11.7114 | 13.4706 | 14.6849
South West | Indian Queens 132 kV | Bodmin | Primary Substation | 11 | Holistic Transition | 0.7471 | 0.87414 | 1.1028 | 1.3623 | 1.6419 | 1.9694 | 2.3514 | 2.8475 | 3.2926 | 3.7446 | 4.1981 | 4.5999 | 4.9723 | 5.2889 | 5.5855 | 5.7825 | 6.5045 | 6.9137 | 1.7006 | 1.985 | 2.5052 | 3.0903 | 3.7227 | 4.4525 | 5.3064 | 6.4052 | 7.3945 | 8.3912 | 9.3828 | 10.2485 | 11.0496 | 11.7232 | 12.3544 | 12.7864 | 14.4249 | 15.3693
South West | Indian Queens 132 kV | Bodmin | Primary Substation | 11 | Hydrogen Evolution | 0.70827 | 0.80667 | 0.9582 | 1.1492 | 1.3492 | 1.5951 | 1.8754 | 2.2407 | 2.6111 | 3.0057 | 3.3785 | 3.7328 | 4.0542 | 4.3469 | 4.6216 | 4.8041 | 5.3857 | 5.8558 | 1.6013 | 1.8131 | 2.1393 | 2.5518 | 2.9841 | 3.5135 | 4.115 | 4.8878 | 5.6868 | 6.5403 | 7.3328 | 8.082 | 8.7579 | 9.3758 | 9.9558 | 10.3595 | 11.6942 | 12.7836
South West | Indian Queens 132 kV | Bugle | Primary Substation | 11 | Counterfactual | 6.3618 | 6.3954 | 6.4531 | 6.5196 | 6.6078 | 6.7294 | 6.8505 | 7.0097 | 7.145 | 7.2989 | 7.4403 | 7.567 | 7.6978 | 7.8319 | 7.9583 | 8.0857 | 8.5227 | 8.7645 | 15.7818 | 15.8508 | 15.9756 | 16.1191 | 16.3103 | 16.5721 | 16.8365 | 17.1803 | 17.4757 | 17.817 | 18.1232 | 18.3915 | 18.664 | 18.9452 | 19.2082 | 19.4731 | 20.3728 | 20.8837
South West | Indian Queens 132 kV | Bugle | Primary Substation | 11 | Electric Engagement | 6.3858 | 6.4544 | 6.6168 | 6.8088 | 7.0162 | 7.2604 | 7.5188 | 7.7878 | 8.0215 | 8.2301 | 8.4268 | 8.5212 | 8.6024 | 3.3535 | 3.5751 | 3.7972 | 6.1962 | 6.6374 | 15.8299 | 15.9711 | 16.3327 | 16.758 | 17.215 | 17.7431 | 18.2977 | 18.8499 | 19.3302 | 19.761 | 20.1685 | 20.3655 | 20.5301 | 7.3651 | 7.8531 | 8.3432 | 14.1391 | 15.1838
South West | Indian Queens 132 kV | Bugle | Primary Substation | 11 | Holistic Transition | 6.3672 | 6.4114 | 6.5694 | 6.7383 | 6.9274 | 7.1677 | 7.3504 | 7.5897 | 7.7774 | 7.9667 | 8.1272 | 8.2979 | 3.462 | 3.6758 | 3.9231 | 4.1213 | 6.3165 | 12.3934 | 15.7926 | 15.8863 | 16.2519 | 16.6407 | 17.0785 | 17.6198 | 18.0167 | 18.534 | 18.931 | 19.3253 | 19.6412 | 19.9867 | 7.8169 | 8.2707 | 8.7888 | 9.2093 | 14.519 | 29.6425
South West | Indian Queens 132 kV | Bugle | Primary Substation | 11 | Hydrogen Evolution | 6.3694 | 6.4098 | 6.4866 | 6.5935 | 6.7193 | 6.8868 | 7.0552 | 7.2664 | 7.4443 | 7.6384 | 7.8204 | 7.9904 | 8.1464 | 2.7801 | 2.9945 | 3.1562 | 3.7555 | 10.0313 | 15.7971 | 15.8807 | 16.0459 | 16.2794 | 16.5551 | 16.9187 | 17.2837 | 17.7354 | 18.109 | 18.52 | 18.8979 | 19.2474 | 19.5621 | 6.0742 | 6.5293 | 6.8799 | 8.2574 | 23.8636
South West | Indian Queens 132 kV | Callywith | Primary Substation | 11 | Counterfactual | 0.69402 | 0.70625 | 0.73061 | 0.77544 | 0.82622 | 0.88304 | 0.9401 | 1.0041 | 1.0547 | 1.1127 | 1.165 | 1.2116 | 1.2589 | 1.3069 | 1.352 | 1.3981 | 1.5997 | 1.7387 | 1.5753 | 1.6014 | 1.6549 | 1.7513 | 1.8614 | 1.9846 | 2.1098 | 2.2494 | 2.3615 | 2.4915 | 2.6062 | 2.706 | 2.8056 | 2.9074 | 3.0022 | 3.0989 | 3.5359 | 3.8471
South West | Indian Queens 132 kV | Callywith | Primary Substation | 11 | Electric Engagement | 0.70736 | 0.73398 | 0.79976 | 0.89436 | 0.9948 | 1.1052 | 1.2172 | 1.3409 | 1.446 | 1.5445 | 1.6414 | 1.7066 | 1.8284 | 1.8964 | 1.9706 | 2.0556 | 2.4638 | 2.6421 | 1.6047 | 1.6621 | 1.8108 | 2.0224 | 2.2464 | 2.4892 | 2.7338 | 3.0014 | 3.2298 | 3.4461 | 3.6602 | 3.8087 | 4.0714 | 4.2275 | 4.3949 | 4.5842 | 5.5079 | 5.9338
South West | Indian Queens 132 kV | Callywith | Primary Substation | 11 | Holistic Transition | 0.7043 | 0.72514 | 0.79056 | 0.87949 | 0.98158 | 1.0953 | 1.2184 | 1.3617 | 1.4815 | 1.6029 | 1.7044 | 1.9004 | 2.0469 | 2.1223 | 2.2025 | 2.2785 | 2.5832 | 2.6967 | 1.6 | 1.6472 | 1.8008 | 2.005 | 2.2404 | 2.4986 | 2.7811 | 3.1101 | 3.3857 | 3.6627 | 3.8878 | 4.3513 | 4.6631 | 4.8264 | 4.9983 | 5.1619 | 5.8337 | 6.0917
South West | Indian Queens 132 kV | Callywith | Primary Substation | 11 | Hydrogen Evolution | 0.69868 | 0.71388 | 0.74722 | 0.81093 | 0.88264 | 0.96434 | 1.0451 | 1.1311 | 1.2207 | 1.3205 | 1.405 | 1.4813 | 1.5825 | 1.6536 | 1.7263 | 1.7875 | 2.0838 | 2.2609 | 1.5855 | 1.6184 | 1.6916 | 1.832 | 1.9908 | 2.1707 | 2.3484 | 2.5349 | 2.7331 | 2.9563 | 3.1409 | 3.3058 | 3.519 | 3.6732 | 3.8297 | 3.9636 | 4.6465 | 5.0582
South West | Indian Queens 132 kV | Camborne Carn Brea | Primary Substation | 11 | Counterfactual | 1.1439 | 0.93004 | 1.0152 | 1.1087 | 1.2077 | 1.338 | 1.4863 | 1.7006 | 1.8699 | 2.0503 | 2.2292 | 2.4071 | 2.6015 | 2.7957 | 2.9823 | 3.1696 | 3.8631 | 4.1962 | 2.6182 | 2.2003 | 2.382 | 2.5813 | 2.7923 | 3.0689 | 3.3846 | 3.8342 | 4.1926 | 4.5768 | 4.9533 | 5.3236 | 5.7251 | 6.1265 | 6.5115 | 6.8975 | 8.3539 | 9.0845
South West | Indian Queens 132 kV | Camborne Carn Brea | Primary Substation | 11 | Electric Engagement | 1.224 | 1.0925 | 1.305 | 1.5389 | 1.787 | 2.0845 | 2.4295 | 2.8766 | 4.8259 | 5.1479 | 5.4399 | 5.5793 | 5.715 | 5.8501 | 5.9879 | 6.1144 | 6.7153 | 7.113 | 2.7977 | 2.5586 | 3.0182 | 3.5213 | 4.0516 | 4.683 | 5.4108 | 6.3452 | 11.0685 | 11.7496 | 12.3725 | 12.6867 | 12.9946 | 13.3026 | 13.6139 | 13.9029 | 15.2708 | 16.2046
South West | Indian Queens 132 kV | Camborne Carn Brea | Primary Substation | 11 | Holistic Transition | 1.2087 | 1.0447 | 1.2153 | 1.3965 | 1.5965 | 1.8493 | 2.1413 | 2.5252 | 4.429 | 4.7684 | 5.0928 | 5.4034 | 5.7062 | 5.9778 | 6.2406 | 6.4085 | 6.9989 | 7.3619 | 2.7755 | 2.4779 | 2.8634 | 3.2705 | 3.7193 | 4.2769 | 4.9217 | 5.7603 | 10.4174 | 11.1554 | 11.8485 | 12.5106 | 13.1566 | 13.7321 | 14.2883 | 14.6546 | 15.9905 | 16.8247
South West | Indian Queens 132 kV | Camborne Carn Brea | Primary Substation | 11 | Hydrogen Evolution | 1.1732 | 0.98073 | 1.0976 | 1.2307 | 1.3749 | 1.567 | 1.7893 | 2.0854 | 2.3662 | 2.6646 | 2.9523 | 3.2249 | 3.4885 | 3.7351 | 3.9709 | 4.1075 | 4.5543 | 4.9253 | 2.6849 | 2.3155 | 2.566 | 2.8514 | 3.1603 | 3.5701 | 4.0425 | 4.6633 | 5.2592 | 5.8947 | 6.4985 | 7.0682 | 7.6181 | 8.1355 | 8.6296 | 8.9258 | 9.9427 | 10.7906
South West | Indian Queens 132 kV | Camborne Holmans | Primary Substation | 11 | Counterfactual | 0.2706 | 0.36656 | 0.47933 | 0.59748 | 0.71322 | 0.86282 | 1.0184 | 1.2346 | 1.4094 | 1.5981 | 1.789 | 1.9806 | 2.1908 | 2.4019 | 2.6058 | 2.8085 | 3.5323 | 3.8365 | 0.61432 | 0.81805 | 1.0568 | 1.3065 | 1.5515 | 1.8672 | 2.1961 | 2.6464 | 3.0137 | 3.4119 | 3.8119 | 4.2092 | 4.6419 | 5.0769 | 5.4963 | 5.9129 | 7.4246 | 8.0926
South West | Indian Queens 132 kV | Camborne Holmans | Primary Substation | 11 | Electric Engagement | 0.3582 | 0.55053 | 0.80184 | 1.0736 | 1.3543 | 1.6884 | 2.0595 | 2.5329 | 2.9319 | 3.2734 | 3.577 | 3.7051 | 3.828 | 3.9487 | 4.0664 | 4.1793 | 4.6968 | 5.0738 | 0.8094 | 1.2222 | 1.7619 | 2.3424 | 2.9387 | 3.6451 | 4.4233 | 5.4064 | 6.2381 | 6.9551 | 7.5976 | 7.8865 | 8.1661 | 8.442 | 8.7103 | 8.969 | 10.1516 | 11.034
South West | Indian Queens 132 kV | Camborne Holmans | Primary Substation | 11 | Holistic Transition | 0.34031 | 0.49293 | 0.69178 | 0.89904 | 1.1164 | 1.3879 | 1.6852 | 2.0621 | 2.3979 | 2.7472 | 3.0893 | 3.4198 | 3.7415 | 4.0319 | 4.3017 | 4.4692 | 4.9991 | 5.3565 | 0.78335 | 1.1234 | 1.5671 | 2.0272 | 2.5098 | 3.1047 | 3.7553 | 4.5696 | 5.2981 | 6.0498 | 6.7752 | 7.4747 | 8.1562 | 8.7684 | 9.3379 | 9.7026 | 10.9103 | 11.7366
South West | Indian Queens 132 kV | Camborne Holmans | Primary Substation | 11 | Hydrogen Evolution | 0.29852 | 0.42177 | 0.57141 | 0.73284 | 0.89803 | 1.1148 | 1.348 | 1.6467 | 1.932 | 2.2379 | 2.5412 | 2.8328 | 3.1129 | 3.3751 | 3.619 | 3.7526 | 4.1413 | 4.4742 | 0.67693 | 0.94312 | 1.2635 | 1.609 | 1.9616 | 2.4235 | 2.9166 | 3.538 | 4.1404 | 4.7862 | 5.4185 | 6.0243 | 6.6057 | 7.1521 | 7.6606 | 7.9485 | 8.8351 | 9.5969
South West | Indian Queens 132 kV | Camborne Treswithian | Primary Substation | 11 | Counterfactual | 0.23239 | 0.2648 | 0.3077 | 0.35451 | 0.40991 | 0.48304 | 0.56663 | 0.68758 | 0.78779 | 0.89788 | 1.0049 | 1.1081 | 1.2187 | 1.3303 | 1.4369 | 1.5438 | 1.9581 | 2.1807 | 0.54897 | 0.61768 | 0.71016 | 0.81102 | 0.93038 | 1.087 | 1.2667 | 1.5228 | 1.7371 | 1.9747 | 2.2023 | 2.4184 | 2.6477 | 2.8796 | 3.1002 | 3.3213 | 4.1967 | 4.6869
South West | Indian Queens 132 kV | Camborne Treswithian | Primary Substation | 11 | Electric Engagement | 0.2734 | 0.34737 | 0.46647 | 0.5972 | 0.74152 | 0.91382 | 1.1133 | 1.3716 | 1.5975 | 1.8002 | 1.9891 | 2.0948 | 2.1926 | 2.2897 | 2.3843 | 2.4774 | 2.9074 | 3.1739 | 0.64004 | 0.79778 | 1.0586 | 1.3432 | 1.6551 | 2.0227 | 2.4451 | 2.9876 | 3.4644 | 3.8959 | 4.301 | 4.5374 | 4.7589 | 4.9802 | 5.1948 | 5.4069 | 6.3789 | 7.0072
South West | Indian Queens 132 kV | Camborne Treswithian | Primary Substation | 11 | Holistic Transition | 0.26476 | 0.31957 | 0.41823 | 0.52234 | 0.64463 | 0.79663 | 0.97736 | 1.2159 | 1.4288 | 1.6505 | 1.855 | 2.0509 | 2.2345 | 2.3944 | 2.5449 | 2.6475 | 3.0303 | 3.2393 | 0.62739 | 0.74996 | 0.97667 | 1.2144 | 1.4929 | 1.8313 | 2.2353 | 2.764 | 3.2356 | 3.7233 | 4.1632 | 4.5826 | 4.977 | 5.3168 | 5.6364 | 5.8602 | 6.7218 | 7.2001
South West | Indian Queens 132 kV | Camborne Treswithian | Primary Substation | 11 | Hydrogen Evolution | 0.24517 | 0.2867 | 0.34512 | 0.41338 | 0.49466 | 0.60341 | 0.7296 | 0.89691 | 1.0666 | 1.2555 | 1.4324 | 1.6008 | 1.7584 | 1.9069 | 2.0468 | 2.1341 | 2.4431 | 2.6942 | 0.57742 | 0.66646 | 0.79235 | 0.94006 | 1.1158 | 1.3488 | 1.6182 | 1.9706 | 2.3345 | 2.7421 | 3.1163 | 3.47 | 3.8005 | 4.1142 | 4.4093 | 4.5997 | 5.3046 | 5.8827
South West | Indian Queens 132 kV | Constantine 33kv | Primary Substation | 11 | Counterfactual | 0.41347 | 0.44167 | 0.47703 | 0.51716 | 0.56542 | 0.6405 | 0.7254 | 0.8403 | 0.93923 | 1.0501 | 1.1527 | 1.2455 | 1.3403 | 1.4378 | 1.5291 | 1.6216 | 2.0531 | 2.3701 | 0.99173 | 1.0518 | 1.1304 | 1.2193 | 1.3266 | 1.4903 | 1.6772 | 1.9267 | 2.1438 | 2.3907 | 2.6142 | 2.8123 | 3.0114 | 3.2172 | 3.4086 | 3.6022 | 4.5271 | 5.2225
South West | Indian Queens 132 kV | Constantine 33kv | Primary Substation | 11 | Electric Engagement | 0.44012 | 0.49765 | 0.60819 | 0.72968 | 0.85922 | 1.0306 | 1.2227 | 1.4636 | 1.6872 | 1.904 | 2.1191 | 2.266 | 2.4102 | 2.5544 | 4.2753 | 4.4387 | 5.0899 | 5.4723 | 1.0508 | 1.1747 | 1.4253 | 1.6985 | 1.9876 | 2.3598 | 2.7739 | 3.2897 | 3.7704 | 4.2393 | 4.707 | 5.0349 | 5.3587 | 5.6849 | 9.9492 | 10.312 | 11.7658 | 12.6739
South West | Indian Queens 132 kV | Constantine 33kv | Primary Substation | 11 | Holistic Transition | 0.43415 | 0.47979 | 0.58504 | 0.69628 | 0.82814 | 1.003 | 1.2133 | 1.4851 | 1.7321 | 1.9889 | 2.2097 | 2.4084 | 2.5983 | 2.7552 | 4.4859 | 4.6282 | 5.2248 | 5.4541 | 1.0418 | 1.1444 | 1.3933 | 1.6544 | 1.9637 | 2.3592 | 2.8398 | 3.4585 | 4.0189 | 4.5963 | 5.0793 | 5.5128 | 5.9274 | 6.2644 | 10.5342 | 10.8403 | 12.1819 | 12.6985
South West | Indian Queens 132 kV | Constantine 33kv | Primary Substation | 11 | Hydrogen Evolution | 0.42226 | 0.45775 | 0.50631 | 0.56831 | 0.64225 | 0.75627 | 0.88363 | 1.0446 | 1.2273 | 1.436 | 1.6177 | 1.7826 | 1.9365 | 2.0835 | 2.2275 | 2.3454 | 2.7934 | 3.1765 | 1.0111 | 1.0879 | 1.1949 | 1.3321 | 1.496 | 1.7436 | 2.0201 | 2.3651 | 2.7658 | 3.2271 | 3.6189 | 3.9716 | 4.2992 | 4.6156 | 4.9241 | 5.1811 | 6.1987 | 7.0867
South West | Indian Queens 132 kV | Davidstow | Primary Substation | 11 | Counterfactual | 0.32333 | 0.33805 | 0.37015 | 0.40627 | 0.45093 | 0.52839 | 0.6166 | 0.72698 | 0.82655 | 0.94155 | 1.0407 | 1.1203 | 1.196 | 1.276 | 1.349 | 1.4226 | 1.8023 | 2.1148 | 0.69789 | 0.7298 | 0.80407 | 0.8877 | 0.99154 | 1.165 | 1.3655 | 1.6143 | 1.8407 | 2.1072 | 2.3312 | 2.5072 | 2.6706 | 2.8447 | 3.002 | 3.1601 | 4.0031 | 4.7133
South West | Indian Queens 132 kV | Davidstow | Primary Substation | 11 | Electric Engagement | 0.33915 | 0.37353 | 0.48585 | 0.60536 | 0.7291 | 0.89781 | 1.0787 | 1.2964 | 1.5049 | 1.7139 | 1.931 | 2.0964 | 2.3442 | 2.5461 | 2.7487 | 2.9425 | 3.7853 | 4.2258 | 0.73304 | 0.80819 | 1.0733 | 1.3542 | 1.6429 | 2.0206 | 2.4229 | 2.9047 | 3.3674 | 3.8344 | 4.3205 | 4.6985 | 5.2437 | 5.7001 | 6.1545 | 6.5925 | 8.4833 | 9.5397
South West | Indian Queens 132 kV | Davidstow | Primary Substation | 11 | Holistic Transition | 0.33581 | 0.36397 | 0.48709 | 0.61296 | 0.7638 | 0.95985 | 1.2001 | 1.5071 | 1.7832 | 2.0607 | 2.2771 | 2.4674 | 2.731 | 2.9026 | 3.0723 | 3.2128 | 3.8504 | 4.0797 | 0.72815 | 0.79269 | 1.0919 | 1.3968 | 1.7622 | 2.2178 | 2.7837 | 3.5066 | 4.1544 | 4.8008 | 5.2901 | 5.7193 | 6.2934 | 6.6651 | 7.03 | 7.3369 | 8.7543 | 9.2732
South West | Indian Queens 132 kV | Davidstow | Primary Substation | 11 | Hydrogen Evolution | 0.32836 | 0.34861 | 0.38915 | 0.44367 | 0.50939 | 0.6205 | 0.73981 | 0.88031 | 1.0572 | 1.2644 | 1.4271 | 1.5705 | 1.7442 | 1.8941 | 2.042 | 2.1656 | 2.7347 | 3.1766 | 0.70906 | 0.75362 | 0.84667 | 0.973 | 1.1255 | 1.3742 | 1.6424 | 1.955 | 2.3593 | 2.8373 | 3.2029 | 3.5209 | 3.8949 | 4.225 | 4.5486 | 4.8245 | 6.1326 | 7.1658
South West | Indian Queens 132 kV | Delabole | Primary Substation | 11 | Counterfactual | 0.57334 | 0.61878 | 0.70677 | 0.78125 | 0.86552 | 0.98271 | 1.1176 | 1.3048 | 1.4634 | 1.6413 | 1.8076 | 1.9607 | 2.1199 | 2.2823 | 2.4359 | 2.5902 | 3.224 | 3.6074 | 1.2773 | 1.3748 | 1.5657 | 1.729 | 1.9144 | 2.1695 | 2.4654 | 2.8696 | 3.2158 | 3.6093 | 3.97 | 4.2956 | 4.6291 | 4.9709 | 5.2922 | 5.6147 | 6.9778 | 7.8388
South West | Indian Queens 132 kV | Delabole | Primary Substation | 11 | Electric Engagement | 0.62563 | 0.72932 | 0.94859 | 1.1562 | 2.9195 | 3.1877 | 3.4899 | 3.874 | 4.2166 | 4.5301 | 4.8304 | 5.0114 | 5.2027 | 5.4075 | 5.6264 | 5.8486 | 6.7141 | 7.2504 | 1.3932 | 1.6172 | 2.1066 | 2.5687 | 6.9133 | 7.4953 | 8.1463 | 8.9666 | 9.7032 | 10.3841 | 11.0413 | 11.4552 | 11.8915 | 12.358 | 12.849 | 13.3478 | 15.3094 | 16.5788
South West | Indian Queens 132 kV | Delabole | Primary Substation | 11 | Holistic Transition | 0.61418 | 0.69535 | 0.89731 | 1.0797 | 2.834 | 3.0949 | 3.4078 | 3.8163 | 4.1789 | 4.5491 | 4.869 | 5.1658 | 5.4641 | 5.7286 | 5.9981 | 6.21 | 6.9417 | 7.3133 | 1.3761 | 1.5602 | 2.0285 | 2.4535 | 6.8036 | 7.3957 | 8.1112 | 9.0396 | 9.8636 | 10.6989 | 11.4017 | 12.051 | 12.7018 | 13.2681 | 13.8417 | 14.3003 | 15.9466 | 16.7923
South West | Indian Queens 132 kV | Delabole | Primary Substation | 11 | Hydrogen Evolution | 0.59006 | 0.64895 | 0.76594 | 0.87285 | 0.99564 | 1.1665 | 1.3597 | 1.609 | 1.879 | 2.1811 | 2.4472 | 2.6928 | 2.9329 | 3.1705 | 3.406 | 3.5769 | 4.1955 | 4.7003 | 1.3144 | 1.4423 | 1.6976 | 1.933 | 2.2035 | 2.5754 | 2.9956 | 3.5296 | 4.1225 | 4.7914 | 5.3666 | 5.8926 | 6.4036 | 6.9126 | 7.415 | 7.789 | 9.2097 | 10.3799
South West | Indian Queens 132 kV | Devoran | Primary Substation | 11 | Counterfactual | 0.19294 | 0.22068 | 0.25381 | 0.29107 | 0.32893 | 0.37452 | 0.42717 | 0.50652 | 0.5706 | 0.64023 | 0.70999 | 0.78039 | 0.85772 | 0.93502 | 1.01 | 1.0845 | 1.351 | 1.4693 | 0.45198 | 0.51078 | 0.58109 | 0.65989 | 0.74002 | 0.83623 | 0.94745 | 1.1127 | 1.2473 | 1.3942 | 1.54 | 1.6858 | 1.8448 | 2.004 | 2.1582 | 2.311 | 2.8672 | 3.1253
South West | Indian Queens 132 kV | Devoran | Primary Substation | 11 | Electric Engagement | 0.2241 | 0.28337 | 0.36664 | 0.45887 | 0.55547 | 0.66517 | 0.79419 | 0.96425 | 1.1083 | 1.2312 | 1.341 | 1.3885 | 1.4339 | 1.4787 | 1.5227 | 1.5647 | 1.7568 | 1.8937 | 0.5211 | 0.64783 | 0.82637 | 1.0233 | 1.2282 | 1.4592 | 1.7292 | 2.0819 | 2.3822 | 2.6403 | 2.8729 | 2.9796 | 3.0827 | 3.1847 | 3.2847 | 3.3804 | 3.819 | 4.139
South West | Indian Queens 132 kV | Devoran | Primary Substation | 11 | Holistic Transition | 0.21733 | 0.2621 | 0.3266 | 0.39474 | 0.46818 | 0.55566 | 0.65791 | 0.79512 | 0.91525 | 1.0409 | 1.1638 | 1.2822 | 1.3975 | 1.5019 | 1.5998 | 1.6611 | 1.858 | 1.9847 | 0.51097 | 0.61102 | 0.75549 | 0.9072 | 1.0705 | 1.2621 | 1.4859 | 1.7825 | 2.0428 | 2.3134 | 2.5741 | 2.825 | 3.0691 | 3.2891 | 3.4956 | 3.629 | 4.0759 | 4.3684
South West | Indian Queens 132 kV | Devoran | Primary Substation | 11 | Hydrogen Evolution | 0.20295 | 0.23783 | 0.28476 | 0.33752 | 0.39292 | 0.46125 | 0.54164 | 0.65226 | 0.75675 | 0.86955 | 0.9811 | 1.0881 | 1.1913 | 1.2879 | 1.3783 | 1.4289 | 1.5782 | 1.6979 | 0.4742 | 0.54923 | 0.64926 | 0.76199 | 0.8799 | 1.0246 | 1.194 | 1.4241 | 1.644 | 1.882 | 2.1145 | 2.3368 | 2.5507 | 2.7519 | 2.9403 | 3.049 | 3.3876 | 3.662
South West | Indian Queens 132 kV | Drinnick. | Primary Substation | 11 | Counterfactual | 6.625 | 6.6609 | 6.7055 | 6.7556 | 6.8149 | 6.8977 | 6.9908 | 7.1245 | 7.2345 | 7.3531 | 7.4708 | 7.5772 | 7.6908 | 4.8738 | 4.9934 | 5.1133 | 5.5677 | 5.7605 | 16.4798 | 16.5558 | 16.6516 | 16.7587 | 16.8855 | 17.0609 | 17.259 | 17.5399 | 17.773 | 18.0266 | 18.2748 | 18.4933 | 18.7234 | 11.6274 | 11.8741 | 12.1209 | 13.0756 | 13.4807
South West | Indian Queens 132 kV | Drinnick. | Primary Substation | 11 | Electric Engagement | 6.6696 | 6.7503 | 6.8759 | 7.0129 | 7.1647 | 7.3553 | 7.5747 | 7.8329 | 8.0583 | 8.2497 | 8.4248 | 8.5027 | 8.5786 | 2.9589 | 3.0695 | 3.1794 | 3.8656 | 4.1468 | 16.5786 | 16.7507 | 17.0236 | 17.3197 | 17.6454 | 18.0488 | 18.5102 | 19.0388 | 19.503 | 19.8969 | 20.2581 | 20.4224 | 20.5798 | 6.4967 | 6.7427 | 6.9876 | 8.5177 | 9.1728
South West | Indian Queens 132 kV | Drinnick. | Primary Substation | 11 | Holistic Transition | 6.6595 | 6.7185 | 6.8191 | 6.9243 | 7.0484 | 7.212 | 7.3601 | 7.5559 | 7.7208 | 7.8944 | 8.0622 | 8.3562 | 5.6565 | 3.2271 | 3.3997 | 3.5209 | 4.0538 | 7.2493 | 16.5632 | 16.6952 | 16.9245 | 17.163 | 17.4435 | 17.8034 | 18.1192 | 18.5321 | 18.8765 | 19.2368 | 19.5768 | 20.236 | 13.4093 | 7.2604 | 7.6244 | 7.8854 | 9.0478 | 16.9814
South West | Indian Queens 132 kV | Drinnick. | Primary Substation | 11 | Hydrogen Evolution | 6.6394 | 6.6852 | 6.749 | 6.8217 | 6.9081 | 7.0296 | 7.1671 | 7.3495 | 7.5076 | 7.6738 | 7.8402 | 8.0013 | 8.1578 | 2.5269 | 2.6859 | 2.7886 | 3.2789 | 6.5165 | 16.5118 | 16.6101 | 16.7468 | 16.9031 | 17.0887 | 17.3467 | 17.6381 | 18.0199 | 18.3479 | 18.6927 | 19.0344 | 19.364 | 19.6817 | 5.5349 | 5.8682 | 6.0892 | 7.2019 | 15.231
South West | Indian Queens 132 kV | Falmouth Bickland Hl | Primary Substation | 11 | Counterfactual | 0.67821 | 0.82179 | 0.98166 | 1.1334 | 1.3031 | 1.4947 | 1.7121 | 2.0389 | 2.3066 | 2.5665 | 2.8519 | 3.1324 | 3.4464 | 3.7583 | 4.0614 | 4.3643 | 5.3902 | 5.7776 | 1.4962 | 1.802 | 2.138 | 2.4562 | 2.8114 | 3.2114 | 3.6644 | 4.337 | 4.8925 | 5.4299 | 6.0258 | 6.602 | 7.245 | 7.8837 | 8.5039 | 9.1234 | 11.2447 | 12.0791
South West | Indian Queens 132 kV | Falmouth Bickland Hl | Primary Substation | 11 | Electric Engagement | 0.80927 | 1.1005 | 1.4479 | 1.8406 | 2.2529 | 2.8981 | 3.4184 | 4.1182 | 4.8501 | 5.3087 | 5.7057 | 5.8481 | 5.9817 | 6.1112 | 6.2371 | 6.3533 | 6.9447 | 7.3807 | 1.7874 | 2.4144 | 3.1491 | 3.9779 | 4.8437 | 6.1762 | 7.2577 | 8.7106 | 10.2092 | 11.1605 | 11.989 | 12.3064 | 12.6064 | 12.8983 | 13.182 | 13.4456 | 14.7872 | 15.7933
South West | Indian Queens 132 kV | Falmouth Bickland Hl | Primary Substation | 11 | Holistic Transition | 0.78184 | 1.0155 | 1.3011 | 1.5854 | 1.8828 | 2.2136 | 2.5659 | 3.042 | 3.6695 | 4.1091 | 4.5671 | 5.0176 | 5.4576 | 5.8692 | 6.2541 | 6.4847 | 7.1969 | 7.7234 | 1.747 | 2.2704 | 2.8959 | 3.5161 | 4.1624 | 4.8745 | 5.627 | 6.6278 | 7.9455 | 8.8693 | 9.8278 | 10.7705 | 11.6926 | 12.5559 | 13.3648 | 13.8646 | 15.4772 | 16.693
South West | Indian Queens 132 kV | Falmouth Bickland Hl | Primary Substation | 11 | Hydrogen Evolution | 0.72012 | 0.90383 | 1.1215 | 1.3584 | 1.6028 | 1.8861 | 2.219 | 2.6789 | 3.1906 | 3.5988 | 4.0216 | 4.4329 | 4.8343 | 5.2048 | 5.5506 | 5.7276 | 6.1841 | 6.568 | 1.5896 | 1.9871 | 2.4497 | 2.953 | 3.4697 | 4.0662 | 4.7632 | 5.7146 | 6.7808 | 7.623 | 8.4928 | 9.3386 | 10.1645 | 10.9286 | 11.6425 | 12.0186 | 13.0377 | 13.8962
South West | Indian Queens 132 kV | Falmouth Docks | Primary Substation | 11 | Counterfactual | 0.8483 | 0.87872 | 0.91283 | 0.94873 | 0.9902 | 1.0396 | 1.0932 | 1.1769 | 1.243 | 1.3131 | 1.3864 | 1.463 | 1.5492 | 1.3356 | 1.4189 | 1.5045 | 1.7721 | 2.7495 | 1.903 | 1.968 | 2.0396 | 2.1148 | 2.2014 | 2.304 | 2.4149 | 2.5864 | 2.7227 | 2.8672 | 3.0179 | 3.1752 | 3.3517 | 2.7789 | 2.9493 | 3.1241 | 3.6769 | 5.6467
South West | Indian Queens 132 kV | Falmouth Docks | Primary Substation | 11 | Electric Engagement | 0.8636 | 0.93421 | 1.0171 | 1.1079 | 1.212 | 1.3275 | 1.463 | 1.6449 | 1.794 | 1.915 | 2.0176 | 2.0503 | 2.0787 | 1.8072 | 1.8364 | 1.9228 | 2.0425 | 2.1558 | 1.942 | 2.0935 | 2.2678 | 2.4576 | 2.6746 | 2.9145 | 3.1949 | 3.5679 | 3.8749 | 4.1256 | 4.3393 | 4.4132 | 4.4783 | 3.7937 | 3.8601 | 4.0407 | 4.3185 | 4.5792
South West | Indian Queens 132 kV | Falmouth Docks | Primary Substation | 11 | Holistic Transition | 0.85594 | 0.90994 | 0.96688 | 1.027 | 1.0968 | 1.1795 | 1.2713 | 1.3959 | 1.5045 | 1.6187 | 1.7392 | 1.8601 | 1.9763 | 1.7893 | 1.89 | 2.0119 | 2.1684 | 2.309 | 1.9309 | 2.0525 | 2.1772 | 2.308 | 2.459 | 2.6361 | 2.8315 | 3.0921 | 3.3204 | 3.5595 | 3.8115 | 4.0641 | 4.3073 | 3.7945 | 4.0064 | 4.2604 | 4.6224 | 4.9483
South West | Indian Queens 132 kV | Falmouth Docks | Primary Substation | 11 | Hydrogen Evolution | 0.83795 | 0.87785 | 0.92452 | 0.97396 | 1.0327 | 1.1031 | 1.1845 | 1.2994 | 1.399 | 1.5043 | 1.6156 | 1.7276 | 1.8341 | 1.6343 | 1.7284 | 1.8341 | 1.9338 | 2.0262 | 1.885 | 1.9711 | 2.0697 | 2.174 | 2.2973 | 2.4443 | 2.6138 | 2.8501 | 3.0555 | 3.2722 | 3.5007 | 3.7305 | 3.9497 | 3.4062 | 3.6001 | 3.8168 | 4.0416 | 4.2489
South West | Indian Queens 132 kV | Fowey | Primary Substation | 11 | Counterfactual | 0.1127 | 0.13421 | 0.15796 | 0.1844 | 0.21488 | 0.25181 | 0.29455 | 0.35814 | 0.40991 | 0.46571 | 0.52154 | 0.57777 | 0.63928 | 0.70104 | 0.76072 | 0.82002 | 1.4362 | 1.5435 | 0.26288 | 0.30921 | 0.35995 | 0.41626 | 0.48104 | 0.55923 | 0.64981 | 0.78257 | 0.89166 | 1.0097 | 1.1267 | 1.2435 | 1.3703 | 1.4978 | 1.6208 | 1.7428 | 2.9952 | 3.2285
South West | Indian Queens 132 kV | Fowey | Primary Substation | 11 | Electric Engagement | 0.13641 | 0.18508 | 0.24847 | 0.31763 | 0.39455 | 1.1171 | 1.2194 | 1.3543 | 1.4679 | 1.6804 | 1.7674 | 1.8064 | 1.844 | 1.8816 | 1.9179 | 1.9529 | 2.1134 | 2.24 | 0.31537 | 0.42102 | 0.55755 | 0.70567 | 0.86943 | 2.3244 | 2.5393 | 2.8198 | 3.0576 | 3.4931 | 3.6781 | 3.7664 | 3.8524 | 3.9385 | 4.0212 | 4.1015 | 4.4695 | 4.7636
South West | Indian Queens 132 kV | Fowey | Primary Substation | 11 | Holistic Transition | 0.13107 | 0.16995 | 0.21879 | 0.27001 | 0.33002 | 1.0361 | 1.1189 | 1.2291 | 1.3259 | 1.5422 | 1.6401 | 1.7342 | 1.8263 | 1.9095 | 1.9872 | 2.0372 | 2.2019 | 2.323 | 0.30727 | 0.39593 | 0.50615 | 0.62114 | 0.75521 | 2.1816 | 2.3637 | 2.603 | 2.8139 | 3.2633 | 3.472 | 3.6724 | 3.8685 | 4.0446 | 4.2091 | 4.3185 | 4.6945 | 4.9716
South West | Indian Queens 132 kV | Fowey | Primary Substation | 11 | Hydrogen Evolution | 0.12048 | 0.14841 | 0.18237 | 0.21984 | 0.26424 | 0.8387 | 0.90287 | 0.99055 | 1.137 | 1.2263 | 1.3142 | 1.3988 | 1.4805 | 1.5578 | 1.6293 | 1.6709 | 1.7944 | 1.9091 | 0.28008 | 0.34099 | 0.41356 | 0.49366 | 0.58838 | 1.744 | 1.8796 | 2.0623 | 2.3644 | 2.5536 | 2.7375 | 2.9138 | 3.0838 | 3.2451 | 3.3947 | 3.4844 | 3.7656 | 4.0253
South West | Indian Queens 132 kV | Fraddon | Primary Substation | 11 | Counterfactual | 1.5822 | 1.6315 | 1.9854 | 2.0722 | 2.1752 | 2.3309 | 2.4908 | 2.7052 | 2.8906 | 3.0995 | 3.2911 | 3.4327 | 3.5734 | 3.4978 | 3.6637 | 3.8314 | 4.583 | 5.1175 | 3.7162 | 3.8219 | 4.5452 | 4.7368 | 4.9653 | 5.305 | 5.6589 | 6.1269 | 6.5361 | 7.004 | 7.4237 | 7.7173 | 8.0013 | 7.7449 | 8.0938 | 8.446 | 10.0709 | 11.2611
South West | Indian Queens 132 kV | Fraddon | Primary Substation | 11 | Electric Engagement | 1.6303 | 2.0251 | 2.2411 | 2.4909 | 2.7551 | 3.0959 | 3.4492 | 3.8091 | 4.1368 | 4.4329 | 4.7502 | 5.025 | 5.4539 | 5.8075 | 6.1524 | 6.4689 | 7.7736 | 8.4542 | 3.8225 | 4.6311 | 5.1238 | 5.6894 | 6.2837 | 7.031 | 7.7995 | 8.549 | 9.2353 | 9.8546 | 10.5337 | 11.1523 | 12.1238 | 12.9072 | 13.6664 | 14.3718 | 17.2979 | 18.9161
South West | Indian Queens 132 kV | Fraddon | Primary Substation | 11 | Holistic Transition | 1.6191 | 1.9926 | 2.2022 | 2.4323 | 2.7031 | 3.051 | 3.3089 | 3.8193 | 4.2657 | 4.7332 | 5.1205 | 5.5416 | 5.9672 | 6.3373 | 6.6964 | 6.9688 | 8.0083 | 8.4301 | 3.8053 | 4.5759 | 5.0737 | 5.6151 | 6.2524 | 7.0444 | 7.6124 | 8.7852 | 9.8069 | 10.8705 | 11.7265 | 12.6677 | 13.5876 | 14.3735 | 15.133 | 15.7198 | 18.0237 | 18.9807
South West | Indian Queens 132 kV | Fraddon | Primary Substation | 11 | Hydrogen Evolution | 1.5981 | 1.9523 | 2.0441 | 2.174 | 2.3266 | 2.5542 | 2.7843 | 3.0722 | 3.3194 | 3.5885 | 3.8353 | 4.0713 | 4.4624 | 4.7722 | 5.0717 | 5.2958 | 6.1975 | 6.8596 | 3.7513 | 4.4727 | 4.6754 | 4.9646 | 5.3047 | 5.8031 | 6.3067 | 6.9285 | 7.4535 | 8.028 | 8.5442 | 9.0323 | 9.8918 | 10.5552 | 11.1944 | 11.6842 | 13.7406 | 15.2749
South West | Indian Queens 132 kV | Geevor | Primary Substation | 11 | Counterfactual | 0.17315 | 0.1995 | 0.22798 | 0.25913 | 0.29514 | 0.33569 | 0.38215 | 0.45532 | 0.51343 | 0.57517 | 0.63934 | 0.7073 | 0.78339 | 0.85912 | 0.93253 | 1.0061 | 1.2606 | 1.3619 | 0.40534 | 0.46163 | 0.52149 | 0.58671 | 0.6618 | 0.74615 | 0.84244 | 0.99237 | 1.1122 | 1.2393 | 1.3712 | 1.5106 | 1.6662 | 1.8211 | 1.9711 | 2.1216 | 2.6459 | 2.8616
South West | Indian Queens 132 kV | Geevor | Primary Substation | 11 | Electric Engagement | 0.20485 | 0.2652 | 0.33672 | 0.41655 | 0.50742 | 2.1824 | 2.3028 | 2.4647 | 2.5993 | 2.7124 | 2.81 | 2.8451 | 2.8763 | 2.9141 | 2.942 | 2.9665 | 3.0784 | 3.1784 | 0.47575 | 0.6055 | 0.75572 | 0.92261 | 1.1119 | 5.2568 | 5.5057 | 5.8375 | 6.1145 | 6.3483 | 6.551 | 6.6284 | 6.6981 | 6.7808 | 6.8436 | 6.8994 | 7.1582 | 7.3881
South West | Indian Queens 132 kV | Geevor | Primary Substation | 11 | Holistic Transition | 0.19812 | 0.24437 | 0.29378 | 0.34734 | 0.40955 | 2.0571 | 2.1408 | 2.2546 | 2.3543 | 2.4617 | 2.5745 | 2.6848 | 2.7911 | 2.8988 | 2.991 | 3.0444 | 3.1923 | 3.3165 | 0.46583 | 0.57018 | 0.67825 | 0.79463 | 0.9289 | 5.0214 | 5.1989 | 5.4367 | 5.6458 | 5.87 | 6.105 | 6.3351 | 6.5571 | 6.7816 | 6.9751 | 7.0909 | 7.4299 | 7.7173
South West | Indian Queens 132 kV | Geevor | Primary Substation | 11 | Hydrogen Evolution | 0.18311 | 0.21723 | 0.25787 | 0.30298 | 0.35625 | 0.41817 | 0.49308 | 0.59887 | 0.69487 | 0.79697 | 0.90326 | 1.0058 | 1.1045 | 1.1984 | 1.2821 | 1.3234 | 1.4198 | 1.505 | 0.42753 | 0.50128 | 0.58707 | 0.68188 | 0.79353 | 0.92272 | 1.0782 | 1.2955 | 1.493 | 1.7025 | 1.9203 | 2.1305 | 2.333 | 2.5261 | 2.6983 | 2.7859 | 3.0016 | 3.1916
South West | Indian Queens 132 kV | Hayle | Primary Substation | 11 | Counterfactual | 1.7495 | 1.8912 | 2.0654 | 2.2307 | 2.406 | 2.6234 | 2.8622 | 3.1674 | 3.4122 | 3.6766 | 3.9423 | 4.1937 | 4.469 | 3.6491 | 3.928 | 4.2067 | 5.2122 | 5.6996 | 4.2562 | 4.5591 | 4.9291 | 5.28 | 5.6525 | 6.113 | 6.6197 | 7.2577 | 7.7739 | 8.3342 | 8.8921 | 9.409 | 9.971 | 7.7957 | 8.3704 | 8.9444 | 11.0519 | 12.1169
South West | Indian Queens 132 kV | Hayle | Primary Substation | 11 | Electric Engagement | 1.8626 | 2.1412 | 2.5154 | 2.9068 | 3.3084 | 3.7776 | 4.3193 | 4.9385 | 5.4531 | 5.8895 | 6.2776 | 6.4315 | 6.5759 | 5.8958 | 6.0829 | 6.2834 | 7.1271 | 7.6909 | 4.5073 | 5.1117 | 5.9206 | 6.762 | 7.6211 | 8.6185 | 9.7624 | 11.0388 | 12.101 | 13.006 | 13.8146 | 14.1502 | 14.4632 | 12.7112 | 13.1353 | 13.5864 | 15.5005 | 16.8229
South West | Indian Queens 132 kV | Hayle | Primary Substation | 11 | Holistic Transition | 1.8387 | 2.0702 | 2.3872 | 2.6845 | 3.0071 | 3.4011 | 3.7947 | 4.2594 | 4.6522 | 5.0609 | 5.4682 | 5.8719 | 6.274 | 6.0173 | 6.3918 | 6.6558 | 7.4892 | 8.0203 | 4.4723 | 4.9939 | 5.7033 | 6.3679 | 7.089 | 7.957 | 8.8069 | 9.7929 | 10.6232 | 11.4796 | 12.3215 | 13.1619 | 14.0003 | 13.1975 | 13.9908 | 14.5632 | 16.4522 | 17.6784
South West | Indian Queens 132 kV | Hayle | Primary Substation | 11 | Hydrogen Evolution | 1.7849 | 1.9661 | 2.1995 | 2.4345 | 2.6858 | 2.997 | 3.3522 | 3.7743 | 4.1394 | 4.5259 | 4.919 | 5.2971 | 5.6605 | 5.0604 | 5.4028 | 5.6205 | 6.2365 | 6.7462 | 4.3349 | 4.73 | 5.2325 | 5.738 | 6.2785 | 6.9447 | 7.7013 | 8.5832 | 9.3423 | 10.1448 | 10.9553 | 11.7328 | 12.477 | 10.8233 | 11.5394 | 12.0061 | 13.4049 | 14.57
South West | Indian Queens 132 kV | Helston | Primary Substation | 11 | Counterfactual | 0.52269 | 0.62116 | 0.74407 | 0.87399 | 1.0222 | 1.207 | 1.4121 | 1.7017 | 1.9448 | 2.2108 | 2.4724 | 2.7208 | 2.9762 | 3.2245 | 3.4659 | 3.7043 | 4.615 | 5.0877 | 1.2453 | 1.4549 | 1.7171 | 1.9937 | 2.3094 | 2.7018 | 3.1388 | 3.7478 | 4.2639 | 4.8321 | 5.3909 | 5.9107 | 6.4391 | 6.9534 | 7.4514 | 7.9431 | 9.8562 | 10.8884
South West | Indian Queens 132 kV | Helston | Primary Substation | 11 | Electric Engagement | 0.61509 | 0.81685 | 1.1101 | 1.4257 | 1.7745 | 2.1822 | 2.6465 | 3.2758 | 3.8032 | 4.2641 | 4.675 | 4.8927 | 5.0956 | 5.2878 | 5.475 | 5.6565 | 6.4904 | 7.0457 | 1.4503 | 1.8846 | 2.5214 | 3.2031 | 3.9528 | 4.821 | 5.8037 | 7.1357 | 8.2504 | 9.2299 | 10.108 | 10.5956 | 11.0536 | 11.4902 | 11.9141 | 12.3268 | 14.2155 | 15.5158
South West | Indian Queens 132 kV | Helston | Primary Substation | 11 | Holistic Transition | 0.5951 | 0.75523 | 0.9957 | 1.2445 | 1.5336 | 1.8844 | 2.2873 | 2.8127 | 3.3163 | 3.811 | 4.2588 | 4.6852 | 5.0916 | 5.4444 | 5.7762 | 5.999 | 6.7952 | 7.2713 | 1.4206 | 1.7796 | 2.3231 | 2.8825 | 3.5317 | 4.3062 | 5.1984 | 6.3499 | 7.4654 | 8.5459 | 9.5045 | 10.4155 | 11.2836 | 12.0311 | 12.7339 | 13.2189 | 15.0116 | 16.1017
South West | Indian Queens 132 kV | Helston | Primary Substation | 11 | Hydrogen Evolution | 0.55223 | 0.67843 | 0.84616 | 1.0294 | 1.2431 | 1.5141 | 1.82 | 2.2226 | 2.6555 | 3.0859 | 3.4825 | 3.8596 | 4.2135 | 4.5375 | 4.8419 | 5.0283 | 5.6489 | 6.1585 | 1.3109 | 1.584 | 1.9445 | 2.3388 | 2.7988 | 3.3785 | 4.0307 | 4.8773 | 5.8143 | 6.7369 | 7.5723 | 8.3629 | 9.1027 | 9.783 | 10.4222 | 10.8255 | 12.2326 | 13.3967
South West | Indian Queens 132 kV | Isles Of Scilly | Primary Substation | 11 | Counterfactual | 1.0155 | 1.0334 | 1.0497 | 1.069 | 1.0906 | 1.1145 | 1.1408 | 1.1822 | 1.2143 | 1.2485 | 1.284 | 1.321 | 1.3624 | 0.45855 | 0.49817 | 0.54143 | 0.69033 | 0.80122 | 2.5292 | 2.568 | 2.6024 | 2.6427 | 2.6879 | 2.7376 | 2.7921 | 2.8767 | 2.9428 | 3.0131 | 3.086 | 3.1617 | 3.246 | 0.96746 | 1.0482 | 1.1361 | 1.4419 | 1.6698
South West | Indian Queens 132 kV | Isles Of Scilly | Primary Substation | 11 | Electric Engagement | 1.0313 | 1.0693 | 1.1106 | 1.1563 | 1.2061 | 1.2605 | 1.3244 | 1.9646 | 2.0352 | 2.095 | 2.1478 | 2.1711 | 2.1903 | 1.263 | 1.2801 | 1.3119 | 1.4222 | 1.5451 | 2.5637 | 2.6475 | 2.7346 | 2.8304 | 2.9343 | 3.0473 | 3.1795 | 4.4643 | 4.6097 | 4.7333 | 4.8431 | 4.8932 | 4.9353 | 2.6119 | 2.6495 | 2.7168 | 2.9577 | 3.2187
South West | Indian Queens 132 kV | Isles Of Scilly | Primary Substation | 11 | Holistic Transition | 1.0277 | 1.0606 | 1.0909 | 1.1225 | 1.1574 | 1.1978 | 1.2422 | 1.8575 | 1.9104 | 1.9675 | 2.0274 | 2.0846 | 2.1393 | 1.2452 | 1.2934 | 1.3416 | 1.4749 | 1.6139 | 2.558 | 2.6342 | 2.7004 | 2.7695 | 2.845 | 2.9313 | 3.0255 | 4.2612 | 4.3719 | 4.4911 | 4.6159 | 4.735 | 4.8494 | 2.5938 | 2.695 | 2.7963 | 3.087 | 3.3851
South West | Indian Queens 132 kV | Isles Of Scilly | Primary Substation | 11 | Hydrogen Evolution | 1.0218 | 1.0444 | 1.0701 | 1.098 | 1.1296 | 1.1655 | 1.2082 | 1.2693 | 1.4512 | 1.5091 | 1.5694 | 1.626 | 1.6801 | 0.78386 | 0.82945 | 0.87266 | 0.97747 | 1.0981 | 2.5426 | 2.5925 | 2.6466 | 2.7051 | 2.7711 | 2.8456 | 2.9339 | 3.0587 | 3.4251 | 3.5434 | 3.6664 | 3.7819 | 3.8926 | 1.63 | 1.7235 | 1.8122 | 2.033 | 2.2825
South West | Indian Queens 132 kV | Laneast | Primary Substation | 11 | Counterfactual | 0.36177 | 0.38182 | 0.4049 | 0.43328 | 0.46667 | 0.52096 | 0.57999 | 0.66224 | 0.73129 | 0.80113 | 0.87191 | 0.9406 | 1.015 | 1.0901 | 1.1622 | 1.2346 | 1.5219 | 1.7015 | 0.78627 | 0.82854 | 0.87813 | 0.9386 | 1.0098 | 1.1238 | 1.2484 | 1.4202 | 1.5656 | 1.714 | 1.8622 | 2.0048 | 2.1581 | 2.3132 | 2.4615 | 2.6101 | 3.2096 | 3.5927
South West | Indian Queens 132 kV | Laneast | Primary Substation | 11 | Electric Engagement | 0.38586 | 0.42824 | 0.4978 | 0.575 | 0.65989 | 0.97427 | 1.1099 | 1.283 | 1.4377 | 1.5758 | 1.7091 | 1.7899 | 1.8782 | 1.9752 | 2.088 | 2.2978 | 2.7014 | 2.877 | 0.83944 | 0.92973 | 1.0802 | 1.2466 | 1.4284 | 2.0695 | 2.3532 | 2.7137 | 3.0369 | 3.3268 | 3.6078 | 3.7827 | 3.9734 | 4.1823 | 4.4216 | 4.8554 | 5.7222 | 6.1239
South West | Indian Queens 132 kV | Laneast | Primary Substation | 11 | Holistic Transition | 0.37964 | 0.41018 | 0.46548 | 0.52378 | 0.59245 | 0.69712 | 0.81553 | 0.96851 | 1.2025 | 1.3455 | 1.4828 | 1.6085 | 1.7406 | 1.8686 | 2.0089 | 2.2199 | 2.5761 | 2.7272 | 0.82947 | 0.89783 | 1.0234 | 1.155 | 1.3096 | 1.5369 | 1.7966 | 2.1299 | 2.6228 | 2.9323 | 3.2236 | 3.4901 | 3.7687 | 4.0358 | 4.3265 | 4.7585 | 5.523 | 5.8583
South West | Indian Queens 132 kV | Laneast | Primary Substation | 11 | Hydrogen Evolution | 0.36977 | 0.39354 | 0.42971 | 0.47266 | 0.52334 | 0.60413 | 0.69257 | 0.80755 | 0.92551 | 1.0493 | 1.1671 | 1.2788 | 1.3932 | 1.5061 | 1.6235 | 1.7598 | 2.0295 | 2.2169 | 0.80388 | 0.85479 | 0.93181 | 1.0237 | 1.132 | 1.3023 | 1.4884 | 1.7279 | 1.9773 | 2.2403 | 2.4866 | 2.7191 | 2.9562 | 3.1912 | 3.4346 | 3.7158 | 4.3011 | 4.7162
South West | Indian Queens 132 kV | Lanner | Primary Substation | 11 | Counterfactual | 0.28038 | 0.32705 | 0.38717 | 0.45337 | 0.53158 | 0.63412 | 0.75219 | 0.92316 | 1.0647 | 1.2208 | 1.3709 | 1.5162 | 1.6718 | 1.8291 | 1.9798 | 2.13 | 2.7173 | 3.03 | 0.65741 | 0.75673 | 0.88682 | 1.0296 | 1.1984 | 1.4184 | 1.6728 | 2.0354 | 2.3389 | 2.6765 | 2.9961 | 3.3008 | 3.6236 | 3.9508 | 4.263 | 4.5739 | 5.8158 | 6.5064
South West | Indian Queens 132 kV | Lanner | Primary Substation | 11 | Electric Engagement | 0.33863 | 0.44849 | 0.61706 | 0.80369 | 1.009 | 1.2515 | 1.5316 | 1.8948 | 2.2116 | 2.495 | 2.7583 | 2.8978 | 3.0332 | 3.1697 | 3.3016 | 3.4308 | 5.5939 | 5.9757 | 0.7867 | 1.0233 | 1.3928 | 1.7999 | 2.2444 | 2.7629 | 3.3569 | 4.1203 | 4.7898 | 5.3939 | 5.9597 | 6.2745 | 6.5828 | 6.8947 | 7.1953 | 7.4909 | 12.7637 | 13.6646
South West | Indian Queens 132 kV | Lanner | Primary Substation | 11 | Holistic Transition | 0.32603 | 0.40785 | 0.54808 | 0.69631 | 0.87123 | 1.0847 | 1.3405 | 1.6785 | 1.9792 | 2.291 | 2.5771 | 2.8462 | 3.1066 | 3.3344 | 3.546 | 3.6894 | 5.792 | 6.0798 | 0.76798 | 0.95247 | 1.2753 | 1.6142 | 2.0132 | 2.4899 | 3.0631 | 3.814 | 4.4818 | 5.1692 | 5.7855 | 6.3635 | 6.923 | 7.407 | 7.8565 | 8.1697 | 13.2983 | 13.9591
South West | Indian Queens 132 kV | Lanner | Primary Substation | 11 | Hydrogen Evolution | 0.29866 | 0.36356 | 0.446 | 0.5435 | 0.659 | 0.81268 | 0.9897 | 1.2252 | 1.4625 | 1.7271 | 1.9746 | 2.2071 | 2.428 | 2.6383 | 2.8353 | 2.9587 | 3.3939 | 3.7437 | 0.69801 | 0.83961 | 1.0173 | 1.2289 | 1.4792 | 1.8094 | 2.1881 | 2.6848 | 3.1953 | 3.7672 | 4.2918 | 4.7812 | 5.2448 | 5.6892 | 6.1052 | 6.3745 | 7.3697 | 8.1791
South West | Indian Queens 132 kV | Lostwithiel | Primary Substation | 11 | Counterfactual | 0.50929 | 0.53111 | 0.56849 | 0.61243 | 0.66565 | 0.74475 | 0.83659 | 0.95786 | 1.0641 | 1.187 | 1.2957 | 1.3884 | 1.4803 | 1.5756 | 1.6639 | 1.7529 | 2.1645 | 2.465 | 1.2438 | 1.2902 | 1.3749 | 1.4739 | 1.5943 | 1.7701 | 1.9766 | 2.2455 | 2.4837 | 2.7636 | 3.0054 | 3.2068 | 3.4024 | 3.6065 | 3.794 | 3.9826 | 4.8858 | 5.5671
South West | Indian Queens 132 kV | Lostwithiel | Primary Substation | 11 | Electric Engagement | 0.53441 | 0.58183 | 0.70838 | 0.84293 | 0.98483 | 1.1606 | 1.3532 | 1.5924 | 1.8118 | 2.0222 | 2.2322 | 2.3792 | 2.5282 | 2.6824 | 2.8371 | 3.0584 | 3.7412 | 4.1537 | 1.2993 | 1.4012 | 1.6932 | 2.0017 | 2.3247 | 2.7146 | 3.1387 | 3.6614 | 4.1437 | 4.6108 | 5.0801 | 5.4186 | 5.7632 | 6.1209 | 6.4763 | 7.0015 | 8.563 | 9.5548
South West | Indian Queens 132 kV | Lostwithiel | Primary Substation | 11 | Holistic Transition | 0.52826 | 0.56416 | 0.69188 | 0.82335 | 0.98038 | 1.1725 | 1.4073 | 1.7123 | 1.9831 | 2.256 | 2.6291 | 2.825 | 3.0156 | 3.1686 | 3.3193 | 3.4369 | 3.9723 | 4.1932 | 1.2896 | 1.3706 | 1.6765 | 1.9903 | 2.3648 | 2.8095 | 3.3588 | 4.0699 | 4.7005 | 5.3315 | 6.2089 | 6.6471 | 7.073 | 7.4071 | 7.734 | 7.995 | 9.2061 | 9.7123
South West | Indian Queens 132 kV | Lostwithiel | Primary Substation | 11 | Hydrogen Evolution | 0.51771 | 0.54452 | 0.59646 | 0.66136 | 0.73957 | 0.85468 | 0.98261 | 1.1413 | 1.3285 | 1.5441 | 1.7206 | 1.8788 | 2.0275 | 2.1752 | 2.3187 | 2.5001 | 2.9978 | 3.394 | 1.2624 | 1.3203 | 1.4362 | 1.5824 | 1.7589 | 2.0143 | 2.2984 | 2.6458 | 3.0676 | 3.558 | 3.9488 | 4.2949 | 4.618 | 4.942 | 5.2551 | 5.6805 | 6.8363 | 7.7692
South West | Indian Queens 132 kV | Marazion | Primary Substation | 11 | Counterfactual | 0.33682 | 0.37873 | 0.42725 | 0.48147 | 0.54335 | 0.61089 | 0.6798 | 0.78383 | 0.86708 | 0.9549 | 1.0466 | 1.1405 | 1.2455 | 1.3497 | 1.4508 | 1.5525 | 1.9079 | 2.0671 | 0.79737 | 0.88701 | 0.98911 | 1.1027 | 1.2324 | 1.373 | 1.5161 | 1.7297 | 1.9017 | 2.0832 | 2.2722 | 2.465 | 2.68 | 2.8935 | 3.1003 | 3.3081 | 4.0426 | 4.3812
South West | Indian Queens 132 kV | Marazion | Primary Substation | 11 | Electric Engagement | 0.37752 | 0.46734 | 0.57499 | 0.69831 | 0.8363 | 0.99051 | 1.1619 | 1.3869 | 1.578 | 1.7399 | 1.8851 | 1.9475 | 2.0082 | 2.0771 | 2.1454 | 2.2191 | 2.5059 | 2.6682 | 0.88779 | 1.0822 | 1.3098 | 1.5704 | 1.861 | 2.1827 | 2.5379 | 3.0004 | 3.3943 | 3.7298 | 4.0319 | 4.1678 | 4.3004 | 4.4499 | 4.5974 | 4.7556 | 5.3852 | 5.7551
South West | Indian Queens 132 kV | Marazion | Primary Substation | 11 | Holistic Transition | 0.36887 | 0.4411 | 0.52206 | 0.61077 | 0.71251 | 0.83282 | 0.95657 | 1.1212 | 1.2666 | 1.4213 | 1.5827 | 1.7374 | 1.8892 | 2.0407 | 2.1855 | 2.2905 | 2.592 | 2.7887 | 0.87505 | 1.0382 | 1.2161 | 1.4099 | 1.6313 | 1.8891 | 2.153 | 2.4991 | 2.8058 | 3.1306 | 3.468 | 3.7916 | 4.1094 | 4.4261 | 4.7287 | 4.9518 | 5.6186 | 6.0656
South West | Indian Queens 132 kV | Marazion | Primary Substation | 11 | Hydrogen Evolution | 0.34983 | 0.40547 | 0.47166 | 0.54892 | 0.63767 | 0.73829 | 0.84527 | 0.99144 | 1.1281 | 1.2699 | 1.4152 | 1.5557 | 1.6942 | 1.8267 | 1.9529 | 2.0296 | 2.226 | 2.3853 | 0.82625 | 0.94748 | 1.0881 | 1.2524 | 1.4408 | 1.6521 | 1.8749 | 2.1759 | 2.4581 | 2.7507 | 3.0494 | 3.3384 | 3.6232 | 3.8964 | 4.1566 | 4.3178 | 4.7478 | 5.0976
South West | Indian Queens 132 kV | Mevagissey | Primary Substation | 11 | Counterfactual | 0.22298 | 0.24968 | 0.2786 | 0.30961 | 0.34527 | 0.38733 | 0.43519 | 0.50906 | 0.56817 | 0.63063 | 0.69539 | 0.7631 | 0.83859 | 0.91403 | 0.98735 | 1.0604 | 1.3092 | 1.4069 | 0.49896 | 0.55637 | 0.61729 | 0.68246 | 0.75707 | 0.84471 | 0.94417 | 1.0958 | 1.218 | 1.3471 | 1.4806 | 1.6198 | 1.7745 | 1.9291 | 2.0793 | 2.2287 | 2.7431 | 2.9533
South West | Indian Queens 132 kV | Mevagissey | Primary Substation | 11 | Electric Engagement | 0.25397 | 0.31613 | 0.3877 | 0.46682 | 0.55692 | 0.65881 | 0.78012 | 0.94202 | 1.0776 | 1.1914 | 1.2907 | 1.328 | 1.3742 | 1.407 | 1.4397 | 1.47 | 1.6679 | 1.7752 | 0.56781 | 0.70239 | 0.85346 | 1.0197 | 1.2081 | 1.4203 | 1.6715 | 2.0041 | 2.2838 | 2.5197 | 2.7267 | 2.8093 | 2.9098 | 2.9836 | 3.057 | 3.1253 | 3.5585 | 3.8063
South West | Indian Queens 132 kV | Mevagissey | Primary Substation | 11 | Holistic Transition | 0.24739 | 0.29668 | 0.34694 | 0.40094 | 0.46354 | 0.53873 | 0.62512 | 0.74109 | 0.8432 | 0.9521 | 1.0658 | 1.1755 | 1.2938 | 1.3928 | 1.4856 | 1.5414 | 1.762 | 1.8929 | 0.55815 | 0.67015 | 0.78088 | 0.89912 | 1.0352 | 1.1967 | 1.3811 | 1.625 | 1.8406 | 2.0694 | 2.3074 | 2.5372 | 2.7841 | 2.9917 | 3.1871 | 3.3081 | 3.7948 | 4.0972
South West | Indian Queens 132 kV | Mevagissey | Primary Substation | 11 | Hydrogen Evolution | 0.23282 | 0.26826 | 0.30838 | 0.35233 | 0.40421 | 0.4668 | 0.54128 | 0.64542 | 0.73976 | 0.84034 | 0.94441 | 1.0451 | 1.1488 | 1.2386 | 1.3229 | 1.3662 | 1.503 | 1.5992 | 0.52087 | 0.59797 | 0.68298 | 0.77579 | 0.88501 | 1.016 | 1.171 | 1.3854 | 1.5803 | 1.7878 | 2.0018 | 2.2088 | 2.4217 | 2.607 | 2.7809 | 2.8728 | 3.1715 | 3.3862
South West | Indian Queens 132 kV | Mousehole | Primary Substation | 11 | Counterfactual | 0.050597 | 0.064075 | 0.079643 | 0.096449 | 0.11561 | 0.14064 | 0.16917 | 0.21097 | 0.24547 | 0.28236 | 0.31891 | 0.35543 | 0.39524 | 0.43523 | 0.47396 | 0.51225 | 0.65509 | 0.72413 | 0.11552 | 0.14472 | 0.17815 | 0.21422 | 0.25528 | 0.30853 | 0.36933 | 0.45709 | 0.53022 | 0.60891 | 0.68593 | 0.76213 | 0.84455 | 0.9275 | 1.0076 | 1.0867 | 1.3872 | 1.5395
South West | Indian Queens 132 kV | Mousehole | Primary Substation | 11 | Electric Engagement | 0.065891 | 0.097315 | 0.13854 | 0.18346 | 0.23336 | 0.2933 | 0.3629 | 0.4533 | 0.53143 | 0.59976 | 0.66298 | 0.69399 | 0.72477 | 0.75573 | 0.78624 | 0.81654 | 0.95902 | 1.047 | 0.14954 | 0.21803 | 0.30759 | 0.40459 | 0.51164 | 0.63876 | 0.78537 | 0.97419 | 1.1382 | 1.2828 | 1.4175 | 1.4873 | 1.5568 | 1.627 | 1.6959 | 1.7644 | 2.0841 | 2.2904
South West | Indian Queens 132 kV | Mousehole | Primary Substation | 11 | Holistic Transition | 0.062653 | 0.088182 | 0.12104 | 0.15522 | 0.19561 | 0.24609 | 0.30499 | 0.38251 | 0.4515 | 0.52332 | 0.59225 | 0.65823 | 0.72301 | 0.78129 | 0.83571 | 0.87244 | 1.0076 | 1.0888 | 0.14477 | 0.20316 | 0.27804 | 0.35553 | 0.44667 | 0.55809 | 0.68843 | 0.85807 | 1.0094 | 1.1659 | 1.3134 | 1.4542 | 1.5925 | 1.7162 | 1.8316 | 1.9117 | 2.2156 | 2.4024
South West | Indian Queens 132 kV | Mousehole | Primary Substation | 11 | Hydrogen Evolution | 0.055462 | 0.073413 | 0.09457 | 0.11828 | 0.14624 | 0.18328 | 0.22612 | 0.28335 | 0.33905 | 0.39959 | 0.45857 | 0.51482 | 0.56936 | 0.62097 | 0.66967 | 0.69947 | 0.79845 | 0.87965 | 0.12639 | 0.16572 | 0.21131 | 0.26245 | 0.32258 | 0.40151 | 0.49249 | 0.61237 | 0.73085 | 0.86009 | 0.98416 | 1.1019 | 1.2158 | 1.3242 | 1.4264 | 1.4909 | 1.7147 | 1.8999
South West | Indian Queens 132 kV | Mullion | Primary Substation | 11 | Counterfactual | 0.1996 | 0.22596 | 0.25195 | 0.27966 | 0.31144 | 0.34682 | 0.38742 | 0.45078 | 0.50133 | 0.55501 | 0.61065 | 0.66957 | 0.73542 | 0.80061 | 0.86435 | 0.92754 | 1.1493 | 1.2409 | 0.47825 | 0.53604 | 0.59112 | 0.64971 | 0.7165 | 0.79067 | 0.87539 | 1.0058 | 1.1105 | 1.2216 | 1.3366 | 1.4581 | 1.5934 | 1.7273 | 1.8582 | 1.988 | 2.4476 | 2.645
South West | Indian Queens 132 kV | Mullion | Primary Substation | 11 | Electric Engagement | 0.22628 | 0.28804 | 0.35155 | 0.42222 | 0.502 | 0.58986 | 0.69505 | 0.83485 | 0.95251 | 1.0517 | 1.1375 | 1.1701 | 1.1989 | 1.2246 | 1.2502 | 1.2729 | 1.38 | 1.4792 | 0.53752 | 0.67377 | 0.80845 | 0.9574 | 1.1248 | 1.3085 | 1.5271 | 1.8149 | 2.0581 | 2.2642 | 2.4436 | 2.5163 | 2.5813 | 2.6401 | 2.6986 | 2.7511 | 3.0012 | 3.2316
South West | Indian Queens 132 kV | Mullion | Primary Substation | 11 | Holistic Transition | 0.22054 | 0.27337 | 0.319 | 0.36797 | 0.42471 | 0.49043 | 0.56514 | 0.66529 | 0.75366 | 0.84891 | 0.94904 | 1.0467 | 1.1407 | 1.2274 | 1.3089 | 1.3571 | 1.4977 | 1.6231 | 0.52904 | 0.65132 | 0.75241 | 0.86012 | 0.98393 | 1.1258 | 1.2857 | 1.4962 | 1.6829 | 1.883 | 2.093 | 2.2981 | 2.496 | 2.6791 | 2.8516 | 2.9574 | 3.2842 | 3.577
South West | Indian Queens 132 kV | Mullion | Primary Substation | 11 | Hydrogen Evolution | 0.20776 | 0.24298 | 0.27893 | 0.31882 | 0.36536 | 0.41938 | 0.48442 | 0.57571 | 0.65873 | 0.74701 | 0.83897 | 0.92759 | 1.0127 | 1.0893 | 1.1613 | 1.1971 | 1.2855 | 1.3681 | 0.49643 | 0.57448 | 0.65115 | 0.7357 | 0.83401 | 0.94751 | 1.0833 | 1.2715 | 1.443 | 1.6248 | 1.8139 | 1.9963 | 2.1716 | 2.3299 | 2.4788 | 2.5553 | 2.7551 | 2.9409
South West | Indian Queens 132 kV | Newlyn | Primary Substation | 11 | Counterfactual | 0.11982 | 0.15199 | 0.18657 | 0.2185 | 0.25562 | 0.31517 | 0.37319 | 0.45187 | 0.51324 | 0.57943 | 0.64692 | 0.71548 | 0.7916 | 0.86735 | 0.94025 | 1.0141 | 1.2712 | 1.7848 | 0.28199 | 0.35093 | 0.42426 | 0.49192 | 0.57029 | 0.69564 | 0.81775 | 0.98102 | 1.1093 | 1.248 | 1.3885 | 1.5303 | 1.6868 | 1.8427 | 1.9925 | 2.144 | 2.6806 | 3.7271
South West | Indian Queens 132 kV | Newlyn | Primary Substation | 11 | Electric Engagement | 0.1501 | 0.2178 | 0.29901 | 0.3811 | 0.47398 | 0.59949 | 0.73307 | 1.5353 | 1.6726 | 1.7888 | 1.8914 | 1.9338 | 1.9752 | 2.1315 | 2.1716 | 2.2093 | 2.3919 | 2.5231 | 0.34933 | 0.49604 | 0.66948 | 0.84367 | 1.0398 | 1.3054 | 1.5856 | 3.2023 | 3.4882 | 3.7318 | 3.9488 | 4.0442 | 4.1377 | 4.4612 | 4.552 | 4.6379 | 5.0564 | 5.3619
South West | Indian Queens 132 kV | Newlyn | Primary Substation | 11 | Holistic Transition | 0.14403 | 0.19925 | 0.2618 | 0.3213 | 0.39082 | 0.49484 | 0.59954 | 1.3646 | 1.4748 | 1.5907 | 1.7072 | 1.8207 | 1.9319 | 2.1503 | 2.2484 | 2.3102 | 2.5109 | 2.6545 | 0.34063 | 0.46543 | 0.60453 | 0.73659 | 0.89001 | 1.1169 | 1.3445 | 2.8931 | 3.1298 | 3.3776 | 3.6241 | 3.8642 | 4.0995 | 4.5479 | 4.7554 | 4.8902 | 5.3472 | 5.6779
South West | Indian Queens 132 kV | Newlyn | Primary Substation | 11 | Hydrogen Evolution | 0.12924 | 0.17126 | 0.21867 | 0.26449 | 0.31892 | 0.40437 | 0.72211 | 0.8318 | 1.2216 | 1.3276 | 1.4335 | 1.5982 | 1.6977 | 1.7895 | 1.8768 | 1.9242 | 2.0622 | 2.1814 | 0.30297 | 0.39457 | 0.49573 | 0.59314 | 0.70848 | 0.89064 | 1.536 | 1.764 | 2.5528 | 2.7747 | 2.9947 | 3.3318 | 3.538 | 3.7292 | 3.9111 | 4.0131 | 4.3261 | 4.5955
South West | Indian Queens 132 kV | Newquay Trencreek Ln | Primary Substation | 11 | Counterfactual | 0.31397 | 0.4099 | 0.53255 | 0.66018 | 0.78334 | 0.9085 | 1.05 | 1.2444 | 1.4111 | 1.586 | 1.7673 | 1.9429 | 2.1123 | 2.2709 | 2.4224 | 2.5759 | 3.0844 | 3.2795 | 0.73609 | 0.93957 | 1.1968 | 1.4633 | 1.7211 | 1.9829 | 2.2782 | 2.68 | 3.0271 | 3.391 | 3.7685 | 4.1319 | 4.4799 | 4.8041 | 5.1139 | 5.4276 | 6.477 | 6.8945
South West | Indian Queens 132 kV | Newquay Trencreek Ln | Primary Substation | 11 | Electric Engagement | 0.38186 | 0.55778 | 0.78304 | 1.0286 | 1.2809 | 1.5467 | 1.8499 | 2.2438 | 2.574 | 2.8574 | 3.1101 | 3.2202 | 3.2969 | 3.3594 | 3.4206 | 3.5062 | 3.7865 | 4.0285 | 0.88704 | 1.2656 | 1.7438 | 2.264 | 2.7974 | 3.3573 | 3.9925 | 4.8094 | 5.4965 | 6.0894 | 6.6213 | 6.8646 | 7.0361 | 7.1759 | 7.3128 | 7.4983 | 8.132 | 8.6781
South West | Indian Queens 132 kV | Newquay Trencreek Ln | Primary Substation | 11 | Holistic Transition | 0.36757 | 0.51327 | 0.69695 | 0.8814 | 1.0714 | 1.2776 | 1.504 | 1.7906 | 2.0482 | 2.3178 | 2.6024 | 2.8753 | 3.1147 | 3.3286 | 3.5278 | 3.6742 | 4.019 | 4.3043 | 0.86593 | 1.1897 | 1.5901 | 1.9912 | 2.4038 | 2.8493 | 3.3348 | 3.9402 | 4.4875 | 5.0567 | 5.656 | 6.2294 | 6.731 | 7.1783 | 7.5957 | 7.9072 | 8.6875 | 9.3391
South West | Indian Queens 132 kV | Newquay Trencreek Ln | Primary Substation | 11 | Hydrogen Evolution | 0.33567 | 0.45665 | 0.61974 | 0.78832 | 0.96308 | 1.1464 | 1.3543 | 1.6232 | 1.8713 | 2.1261 | 2.3909 | 2.6378 | 2.8565 | 3.0452 | 3.2209 | 3.3407 | 3.5646 | 3.76 | 0.78458 | 1.0461 | 1.3944 | 1.7551 | 2.1282 | 2.5183 | 2.958 | 3.5192 | 4.0385 | 4.5698 | 5.1208 | 5.6333 | 6.0847 | 6.4728 | 6.8345 | 7.0844 | 7.5799 | 8.0117
South West | Indian Queens 132 kV | Newquay Trevemper | Primary Substation | 11 | Counterfactual | 1.0948 | 1.2096 | 1.3534 | 1.5011 | 1.6591 | 1.8334 | 2.0238 | 2.3034 | 2.5156 | 2.7455 | 2.9753 | 3.2096 | 3.4638 | 3.7219 | 3.9683 | 4.2168 | 5.0984 | 5.4955 | 2.6513 | 2.8973 | 3.2025 | 3.5149 | 3.8491 | 4.2164 | 4.6185 | 5.2009 | 5.6467 | 6.1316 | 6.6122 | 7.098 | 7.6219 | 8.1545 | 8.6619 | 9.173 | 11.0168 | 11.8859
South West | Indian Queens 132 kV | Newquay Trevemper | Primary Substation | 11 | Electric Engagement | 1.1933 | 1.4294 | 1.7434 | 2.0725 | 2.4289 | 2.82 | 3.2705 | 3.856 | 4.3369 | 4.7533 | 5.1383 | 5.3172 | 5.4972 | 5.6793 | 5.8665 | 6.0593 | 6.9002 | 7.4435 | 2.8699 | 3.3833 | 4.0601 | 4.7644 | 5.5244 | 6.3496 | 7.2944 | 8.512 | 9.516 | 10.3911 | 11.2047 | 11.6035 | 12.0057 | 12.4134 | 12.8291 | 13.2561 | 15.1255 | 16.3745
South West | Indian Queens 132 kV | Newquay Trevemper | Primary Substation | 11 | Holistic Transition | 1.1719 | 1.3678 | 1.6216 | 1.874 | 2.1611 | 2.4776 | 2.8417 | 3.3151 | 3.7201 | 4.1401 | 4.5656 | 4.9756 | 5.3791 | 5.748 | 6.105 | 6.3555 | 7.1775 | 7.6955 | 2.8379 | 3.2813 | 3.8488 | 4.4105 | 5.0478 | 5.7404 | 6.5369 | 7.5613 | 8.4392 | 9.3447 | 10.2477 | 11.1163 | 11.9709 | 12.7489 | 13.501 | 14.0402 | 15.8739 | 17.0547
South West | Indian Queens 132 kV | Newquay Trevemper | Primary Substation | 11 | Hydrogen Evolution | 1.126 | 1.276 | 1.4737 | 1.6738 | 1.896 | 2.1472 | 2.4314 | 2.8118 | 3.1531 | 3.52 | 3.886 | 4.2401 | 4.5886 | 4.9176 | 5.2301 | 5.4256 | 6.0218 | 6.4976 | 2.7207 | 3.0483 | 3.4731 | 3.9018 | 4.3781 | 4.9108 | 5.5113 | 6.305 | 7.0243 | 7.7994 | 8.563 | 9.2991 | 10.0225 | 10.7082 | 11.3593 | 11.7766 | 13.1056 | 14.1772
South West | Indian Queens 132 kV | Padstow | Primary Substation | 11 | Counterfactual | 0.43886 | 0.49759 | 0.55086 | 0.60993 | 0.68586 | 0.76433 | 0.85335 | 0.99027 | 1.0994 | 1.2146 | 1.3345 | 1.4603 | 1.6017 | 1.7415 | 1.8775 | 2.014 | 2.4854 | 2.7059 | 0.95125 | 1.0785 | 1.1912 | 1.3156 | 1.4748 | 1.6385 | 1.8235 | 2.1047 | 2.3303 | 2.5683 | 2.8154 | 3.0743 | 3.3641 | 3.6509 | 3.9297 | 4.2091 | 5.1847 | 5.6539
South West | Indian Queens 132 kV | Padstow | Primary Substation | 11 | Electric Engagement | 0.49554 | 0.62442 | 0.75815 | 0.9065 | 1.0847 | 1.2742 | 1.499 | 1.7979 | 2.0488 | 2.2587 | 2.9965 | 3.068 | 3.1349 | 3.2603 | 3.3242 | 3.4364 | 3.7592 | 3.9679 | 1.077 | 1.3591 | 1.6417 | 1.9537 | 2.3279 | 2.7226 | 3.189 | 3.8035 | 4.3216 | 4.7572 | 6.2486 | 6.4069 | 6.556 | 6.822 | 6.9649 | 7.2039 | 7.9244 | 8.4058
South West | Indian Queens 132 kV | Padstow | Primary Substation | 11 | Holistic Transition | 0.48331 | 0.59109 | 0.68649 | 0.78858 | 0.9167 | 1.0585 | 1.2177 | 1.4308 | 1.6187 | 1.8188 | 2.5832 | 2.7887 | 2.9896 | 3.2391 | 3.4169 | 3.5794 | 3.9561 | 4.217 | 1.0588 | 1.3058 | 1.5163 | 1.7401 | 2.019 | 2.3236 | 2.6633 | 3.1108 | 3.5072 | 3.9277 | 5.4764 | 5.9073 | 6.3289 | 6.8476 | 7.2224 | 7.5662 | 8.4112 | 9.0151
South West | Indian Queens 132 kV | Padstow | Primary Substation | 11 | Hydrogen Evolution | 0.4569 | 0.53327 | 0.6099 | 0.69449 | 0.80408 | 0.92162 | 1.0605 | 1.2544 | 1.5588 | 1.7439 | 1.9362 | 2.1228 | 2.3054 | 2.504 | 2.6626 | 2.7729 | 3.01 | 3.1944 | 0.99134 | 1.1592 | 1.3219 | 1.5008 | 1.7326 | 1.9785 | 2.2677 | 2.667 | 3.2872 | 3.6684 | 4.0637 | 4.4475 | 4.8234 | 5.2312 | 5.5588 | 5.7896 | 6.3121 | 6.7226
South West | Indian Queens 132 kV | Par Harbour | Primary Substation | 11 | Counterfactual | 7.6585 | 7.7808 | 7.9567 | 8.0511 | 8.1585 | 8.2785 | 8.414 | 8.6073 | 8.7688 | 8.9422 | 9.1001 | 9.2477 | 9.4107 | 6.078 | 6.2354 | 6.3927 | 6.9208 | 7.1595 | 18.837 | 19.0886 | 19.4475 | 19.6461 | 19.8722 | 20.1249 | 20.4103 | 20.8127 | 21.1519 | 21.5171 | 21.8481 | 22.1528 | 22.4873 | 14.0828 | 14.4056 | 14.7279 | 15.8177 | 16.3251
South West | Indian Queens 132 kV | Par Harbour | Primary Substation | 11 | Electric Engagement | 7.7237 | 8.029 | 8.1934 | 8.41 | 8.65 | 5.4166 | 5.7186 | 6.1035 | 6.4215 | 6.6911 | 6.9043 | 6.9774 | 7.0423 | 3.891 | 3.9683 | 4.0683 | 4.3877 | 4.6522 | 18.9813 | 19.6096 | 19.9604 | 20.4229 | 20.9338 | 12.7507 | 13.3867 | 14.1876 | 14.8492 | 15.4138 | 15.8609 | 16.0235 | 16.1685 | 8.2742 | 8.4517 | 8.6746 | 9.4204 | 10.0409
South West | Indian Queens 132 kV | Par Harbour | Primary Substation | 11 | Holistic Transition | 7.7086 | 7.9828 | 8.1051 | 8.2655 | 8.4498 | 5.1641 | 5.3842 | 5.6701 | 5.9257 | 6.1826 | 6.416 | 6.6387 | 3.6909 | 3.9026 | 4.1001 | 4.2485 | 4.6044 | 4.8611 | 18.9579 | 19.5291 | 19.8022 | 20.1566 | 20.5632 | 12.2835 | 12.7581 | 13.3662 | 13.9129 | 14.4559 | 14.9421 | 15.4065 | 7.9473 | 8.393 | 8.8096 | 9.1277 | 9.946 | 10.5413
South West | Indian Queens 132 kV | Par Harbour | Primary Substation | 11 | Hydrogen Evolution | 7.6796 | 7.9331 | 8.0229 | 8.1576 | 8.3123 | 4.994 | 5.197 | 5.4651 | 5.714 | 5.9656 | 6.1965 | 6.4096 | 6.6146 | 3.5558 | 3.7409 | 3.8693 | 4.1423 | 9.3275 | 18.8835 | 19.4021 | 19.5924 | 19.8808 | 20.2115 | 11.851 | 12.2817 | 12.8426 | 13.3666 | 13.8924 | 14.3693 | 14.8076 | 15.228 | 7.4969 | 7.8816 | 8.153 | 8.775 | 21.6912
South West | Indian Queens 132 kV | Penryn | Primary Substation | 11 | Counterfactual | 0.26234 | 0.29799 | 0.33824 | 0.3828 | 0.43477 | 0.4963 | 0.56695 | 0.67533 | 0.76167 | 0.85463 | 0.94927 | 1.0466 | 1.1546 | 1.2623 | 1.3669 | 1.4711 | 1.8395 | 2.0004 | 0.61995 | 0.69556 | 0.78063 | 0.8745 | 0.9837 | 1.1125 | 1.2605 | 1.4844 | 1.6642 | 1.8581 | 2.0545 | 2.2551 | 2.4766 | 2.6976 | 2.9118 | 3.1253 | 3.8894 | 4.2357
South West | Indian Queens 132 kV | Penryn | Primary Substation | 11 | Electric Engagement | 0.30578 | 0.3853 | 0.48967 | 0.60448 | 0.73396 | 0.8807 | 1.0549 | 1.2862 | 1.474 | 1.6311 | 1.7681 | 1.8201 | 1.8659 | 1.9067 | 1.9605 | 2.0081 | 2.2367 | 2.4051 | 0.71626 | 0.88617 | 1.1078 | 1.3503 | 1.6225 | 1.9293 | 2.2917 | 2.7687 | 3.1552 | 3.4799 | 3.7645 | 3.8778 | 3.9782 | 4.0669 | 4.1828 | 4.2902 | 4.8106 | 5.2009
South West | Indian Queens 132 kV | Penryn | Primary Substation | 11 | Holistic Transition | 0.29619 | 0.35531 | 0.43103 | 0.51119 | 0.60503 | 0.71762 | 0.8368 | 0.9983 | 1.1371 | 1.2842 | 1.4384 | 1.5976 | 1.7526 | 1.895 | 2.0388 | 2.1211 | 2.374 | 2.5491 | 0.7019 | 0.83439 | 1.0024 | 1.1792 | 1.3852 | 1.6291 | 1.8828 | 2.2218 | 2.513 | 2.8201 | 3.1408 | 3.4756 | 3.8018 | 4.1011 | 4.4024 | 4.5805 | 5.1534 | 5.5571
South West | Indian Queens 132 kV | Penryn | Primary Substation | 11 | Hydrogen Evolution | 0.27682 | 0.32209 | 0.38027 | 0.44419 | 0.51976 | 0.61213 | 0.72143 | 0.87335 | 1.0075 | 1.1493 | 1.2955 | 1.4375 | 1.5737 | 1.6963 | 1.8179 | 1.8774 | 2.0483 | 2.2619 | 0.65192 | 0.74908 | 0.87227 | 1.0074 | 1.1669 | 1.3609 | 1.5895 | 1.9034 | 2.1802 | 2.4725 | 2.7725 | 3.0637 | 3.3422 | 3.5923 | 3.8411 | 3.965 | 4.3455 | 4.8446
South West | Indian Queens 132 kV | Penzance Causewayhead | Primary Substation | 11 | Counterfactual | 0.22041 | 0.26751 | 0.3225 | 0.37097 | 0.42635 | 0.49135 | 0.56269 | 0.67477 | 0.76337 | 0.85746 | 0.9549 | 1.0574 | 1.1722 | 1.2868 | 1.4009 | 1.5114 | 1.8818 | 2.0252 | 0.52553 | 0.62663 | 0.74231 | 0.84395 | 0.95962 | 1.0948 | 1.2428 | 1.4726 | 1.6556 | 1.8495 | 2.0502 | 2.2606 | 2.4957 | 2.7303 | 2.9637 | 3.1897 | 3.9549 | 4.2629
South West | Indian Queens 132 kV | Penzance Causewayhead | Primary Substation | 11 | Electric Engagement | 0.26762 | 0.37082 | 0.49322 | 0.61442 | 0.75121 | 0.90326 | 1.0814 | 1.3207 | 1.5172 | 1.6779 | 1.8153 | 1.8648 | 1.9071 | 1.9507 | 1.9899 | 2.0287 | 2.1955 | 2.3515 | 0.63025 | 0.85412 | 1.1125 | 1.3664 | 1.6518 | 1.9679 | 2.3369 | 2.8282 | 3.2334 | 3.5665 | 3.8533 | 3.9634 | 4.0591 | 4.1571 | 4.2463 | 4.3343 | 4.7217 | 5.0808
South West | Indian Queens 132 kV | Penzance Causewayhead | Primary Substation | 11 | Holistic Transition | 0.2574 | 0.34032 | 0.43002 | 0.51127 | 0.6056 | 0.71623 | 0.83937 | 1.0062 | 1.1505 | 1.3026 | 1.4656 | 1.6236 | 1.7816 | 1.9273 | 2.0655 | 2.1456 | 2.2525 | 2.445 | 0.61505 | 0.80312 | 0.99936 | 1.1765 | 1.3807 | 1.6179 | 1.8801 | 2.2293 | 2.5328 | 2.8516 | 3.1922 | 3.5228 | 3.8533 | 4.159 | 4.4496 | 4.6237 | 4.8452 | 5.2911
South West | Indian Queens 132 kV | Penzance Causewayhead | Primary Substation | 11 | Hydrogen Evolution | 0.23562 | 0.29814 | 0.37427 | 0.44217 | 0.52243 | 0.61718 | 0.72738 | 0.88376 | 1.0208 | 1.1647 | 1.3152 | 1.4654 | 1.6085 | 1.7439 | 1.8663 | 1.932 | 2.0775 | 2.2778 | 0.55922 | 0.69571 | 0.85716 | 1.0002 | 1.1688 | 1.3667 | 1.5959 | 1.9176 | 2.2005 | 2.4966 | 2.8057 | 3.114 | 3.408 | 3.6865 | 3.9387 | 4.0775 | 4.4036 | 4.8689
South West | Indian Queens 132 kV | Penzance Heamoor | Primary Substation | 11 | Counterfactual | 0.20039 | 0.24395 | 0.30174 | 0.36687 | 0.43398 | 0.50823 | 0.5936 | 0.72455 | 0.82976 | 0.94253 | 1.0571 | 1.1743 | 1.304 | 1.4336 | 1.5593 | 1.6843 | 2.128 | 2.3175 | 0.47103 | 0.56355 | 0.68567 | 0.82289 | 0.96421 | 1.1202 | 1.2994 | 1.5707 | 1.7904 | 2.0265 | 2.2648 | 2.5069 | 2.7732 | 3.0394 | 3.2973 | 3.5537 | 4.4757 | 4.8863
South West | Indian Queens 132 kV | Penzance Heamoor | Primary Substation | 11 | Electric Engagement | 0.25342 | 0.35155 | 0.49002 | 0.64549 | 0.81084 | 0.99101 | 1.2049 | 1.4891 | 1.7291 | 1.934 | 2.1149 | 2.1895 | 3.8336 | 3.8997 | 3.964 | 4.0241 | 4.2979 | 4.5078 | 0.58872 | 0.79836 | 1.0936 | 1.4234 | 1.7723 | 2.1498 | 2.5953 | 3.1823 | 3.6803 | 4.1082 | 4.4887 | 4.6553 | 8.7486 | 8.8989 | 9.0448 | 9.1822 | 9.8093 | 10.2979
South West | Indian Queens 132 kV | Penzance Heamoor | Primary Substation | 11 | Holistic Transition | 0.24194 | 0.31517 | 0.41922 | 0.53275 | 0.65573 | 0.79517 | 0.9578 | 1.1773 | 1.3711 | 1.5759 | 1.7804 | 1.9774 | 3.7426 | 3.9154 | 4.0762 | 4.1742 | 4.4724 | 4.6831 | 0.57167 | 0.73558 | 0.96677 | 1.2173 | 1.488 | 1.7912 | 2.1438 | 2.6132 | 3.0289 | 3.4657 | 3.8968 | 4.3116 | 8.6499 | 9.0133 | 9.352 | 9.5648 | 10.2446 | 10.7313
South West | Indian Queens 132 kV | Penzance Heamoor | Primary Substation | 11 | Hydrogen Evolution | 0.217 | 0.27282 | 0.35229 | 0.44306 | 0.53992 | 0.65138 | 0.78408 | 0.96796 | 1.139 | 1.3246 | 1.5111 | 1.6907 | 1.8626 | 2.0217 | 2.1696 | 2.2489 | 2.4655 | 2.6486 | 0.50797 | 0.62791 | 0.79701 | 0.99008 | 1.1954 | 1.4302 | 1.7084 | 2.0891 | 2.4465 | 2.8349 | 3.2214 | 3.5926 | 3.9479 | 4.2779 | 4.5849 | 4.7549 | 5.2455 | 5.662
South West | Indian Queens 132 kV | Perranporth | Primary Substation | 11 | Counterfactual | 0.70611 | 0.75427 | 0.82648 | 0.89031 | 0.96627 | 1.075 | 1.1978 | 1.3671 | 1.5109 | 1.6697 | 1.8195 | 1.9582 | 2.1028 | 2.2508 | 2.3911 | 2.5314 | 3.0213 | 3.3224 | 1.6141 | 1.7194 | 1.877 | 2.0174 | 2.1849 | 2.421 | 2.6897 | 3.0544 | 3.3676 | 3.7179 | 4.0418 | 4.3366 | 4.6396 | 4.9511 | 5.2446 | 5.5379 | 6.5564 | 7.209
South West | Indian Queens 132 kV | Perranporth | Primary Substation | 11 | Electric Engagement | 0.75235 | 0.86101 | 1.0487 | 3.2809 | 3.4801 | 3.7275 | 4.0049 | 4.3547 | 4.6667 | 4.9545 | 5.2321 | 5.3509 | 5.4561 | 5.6388 | 5.8455 | 6.0272 | 6.8668 | 7.3384 | 1.7165 | 1.9567 | 2.3759 | 7.9071 | 8.3481 | 8.8848 | 9.4818 | 10.2277 | 10.8969 | 11.5196 | 12.1244 | 12.3774 | 12.5981 | 13.0016 | 13.462 | 13.8729 | 15.7555 | 16.8739
South West | Indian Queens 132 kV | Perranporth | Primary Substation | 11 | Holistic Transition | 0.74198 | 0.83534 | 1.0094 | 3.2169 | 3.4054 | 3.643 | 3.8453 | 4.1322 | 4.4575 | 4.79 | 5.0835 | 5.3605 | 5.6317 | 5.8893 | 6.1395 | 6.3122 | 7.0343 | 7.3755 | 1.7008 | 1.9173 | 2.3222 | 7.8145 | 8.2539 | 8.7916 | 9.2351 | 9.8665 | 10.6025 | 11.3495 | 11.9925 | 12.5962 | 13.1868 | 13.7366 | 14.2689 | 14.6464 | 16.2589 | 17.0428
South West | Indian Queens 132 kV | Perranporth | Primary Substation | 11 | Hydrogen Evolution | 0.72107 | 0.78421 | 0.8827 | 0.97882 | 1.092 | 3.2992 | 3.4776 | 3.7056 | 3.9466 | 4.2159 | 4.4566 | 4.6495 | 4.8286 | 4.9846 | 5.1841 | 5.3305 | 5.9119 | 6.36 | 1.6472 | 1.7875 | 2.0029 | 2.216 | 2.4664 | 7.9323 | 8.3197 | 8.8076 | 9.3348 | 9.9284 | 10.4469 | 10.8458 | 11.2114 | 11.5192 | 11.9379 | 12.2589 | 13.5807 | 14.617
South West | Indian Queens 132 kV | Polzeath | Primary Substation | 11 | Counterfactual | 0.53189 | 0.56823 | 0.60337 | 0.64209 | 0.6871 | 0.74021 | 0.80023 | 0.89139 | 0.96439 | 1.0415 | 1.122 | 1.2063 | 1.3006 | 1.3942 | 1.485 | 1.5759 | 1.8907 | 2.0209 | 1.2967 | 1.3762 | 1.4509 | 1.5327 | 1.6274 | 1.7385 | 1.8637 | 2.0514 | 2.2028 | 2.3627 | 2.5292 | 2.7028 | 2.8966 | 3.0889 | 3.2755 | 3.4619 | 4.115 | 4.3962
South West | Indian Queens 132 kV | Polzeath | Primary Substation | 11 | Electric Engagement | 0.5692 | 0.65301 | 0.74334 | 0.84202 | 0.9537 | 1.0812 | 1.2319 | 1.4314 | 1.5981 | 1.7382 | 1.8611 | 1.9105 | 1.9575 | 2.0038 | 2.0491 | 2.1677 | 2.3717 | 2.5198 | 1.3795 | 1.5643 | 1.756 | 1.9644 | 2.1991 | 2.4655 | 2.779 | 3.19 | 3.5352 | 3.8269 | 4.0845 | 4.1943 | 4.2997 | 4.4035 | 4.5051 | 4.791 | 5.2524 | 5.5956
South West | Indian Queens 132 kV | Polzeath | Primary Substation | 11 | Holistic Transition | 0.56105 | 0.63205 | 0.6977 | 0.76655 | 0.84575 | 0.94205 | 1.0506 | 1.1949 | 1.3221 | 1.4566 | 1.7633 | 1.9017 | 2.0376 | 2.1656 | 2.2857 | 2.3614 | 2.5995 | 2.7781 | 1.3672 | 1.5317 | 1.6773 | 1.8292 | 2.0025 | 2.2104 | 2.4435 | 2.7481 | 3.0182 | 3.3023 | 4.0134 | 4.3046 | 4.5908 | 4.8606 | 5.1144 | 5.2792 | 5.8201 | 6.2352
South West | Indian Queens 132 kV | Polzeath | Primary Substation | 11 | Hydrogen Evolution | 0.54404 | 0.59172 | 0.64329 | 0.69856 | 0.76389 | 0.84285 | 0.9358 | 1.0649 | 1.1813 | 1.3037 | 1.4306 | 1.5546 | 1.6764 | 1.7899 | 1.8959 | 2.03 | 2.1846 | 2.3119 | 1.3237 | 1.4293 | 1.5391 | 1.6564 | 1.7945 | 1.9602 | 2.1544 | 2.4207 | 2.6619 | 2.9153 | 3.177 | 3.4324 | 3.6837 | 3.9184 | 4.1378 | 4.451 | 4.7951 | 5.0808
South West | Indian Queens 132 kV | Probus 33 | Primary Substation | 11 | Counterfactual | 0.1831 | 0.20481 | 0.23008 | 0.25997 | 0.29461 | 0.34523 | 0.40111 | 0.48142 | 0.54715 | 0.61697 | 0.68757 | 0.75696 | 0.83258 | 0.90905 | 0.98242 | 1.0562 | 1.3365 | 1.4951 | 0.41825 | 0.46414 | 0.51811 | 0.58159 | 0.65509 | 0.76136 | 0.87912 | 1.0464 | 1.1845 | 1.3322 | 1.4798 | 1.6237 | 1.7793 | 1.9371 | 2.0878 | 2.2394 | 2.824 | 3.164
South West | Indian Queens 132 kV | Probus 33 | Primary Substation | 11 | Electric Engagement | 0.20967 | 0.25657 | 0.32864 | 0.40776 | 0.49538 | 0.60983 | 0.74148 | 0.91207 | 1.0614 | 1.1943 | 1.3192 | 1.3884 | 1.4563 | 1.5261 | 1.5947 | 1.6968 | 2.0249 | 2.1873 | 0.477 | 0.57686 | 0.73201 | 0.90137 | 1.0878 | 1.3279 | 1.6029 | 1.957 | 2.2683 | 2.5471 | 2.8104 | 2.9614 | 3.1103 | 3.2638 | 3.4138 | 3.6312 | 4.3441 | 4.7173
South West | Indian Queens 132 kV | Probus 33 | Primary Substation | 11 | Holistic Transition | 0.20333 | 0.23739 | 0.29304 | 0.3517 | 0.42092 | 0.51738 | 0.62804 | 0.77308 | 0.90316 | 1.0393 | 1.1714 | 1.2948 | 1.416 | 1.5268 | 1.6326 | 1.7424 | 2.0415 | 2.1863 | 0.46715 | 0.5432 | 0.66871 | 0.80026 | 0.95502 | 1.1645 | 1.4065 | 1.721 | 2.0034 | 2.2972 | 2.5772 | 2.8385 | 3.095 | 3.3277 | 3.5496 | 3.7794 | 4.4297 | 4.7545
South West | Indian Queens 132 kV | Probus 33 | Primary Substation | 11 | Hydrogen Evolution | 0.19171 | 0.21825 | 0.25641 | 0.29966 | 0.35133 | 0.42591 | 0.50926 | 0.62081 | 0.73113 | 0.84947 | 0.96362 | 1.0728 | 1.1798 | 1.2825 | 1.38 | 1.4622 | 1.6875 | 1.8515 | 0.43723 | 0.49408 | 0.57523 | 0.66736 | 0.7774 | 0.93423 | 1.1093 | 1.3411 | 1.5737 | 1.8244 | 2.0627 | 2.2896 | 2.5115 | 2.7256 | 2.9287 | 3.1013 | 3.595 | 3.9606
South West | Indian Queens 132 kV | Redruth | Primary Substation | 11 | Counterfactual | 0.73457 | 0.84026 | 0.95535 | 1.0792 | 1.221 | 1.395 | 1.5671 | 1.8121 | 2.0101 | 2.2251 | 2.449 | 2.6666 | 2.8933 | 2.9306 | 3.1552 | 3.3821 | 4.2234 | 4.6521 | 1.7604 | 1.9859 | 2.2304 | 2.4923 | 2.7938 | 3.1625 | 3.5277 | 4.0395 | 4.4575 | 4.9131 | 5.3865 | 5.8389 | 6.3017 | 6.292 | 6.7536 | 7.2196 | 8.9762 | 9.9
South West | Indian Queens 132 kV | Redruth | Primary Substation | 11 | Electric Engagement | 0.8212 | 1.0285 | 1.2966 | 1.603 | 1.932 | 2.3146 | 2.7194 | 3.226 | 3.6607 | 4.0049 | 5.8839 | 6.0156 | 6.1328 | 6.2109 | 6.3575 | 6.4944 | 7.129 | 7.5653 | 1.9522 | 2.4017 | 2.9775 | 3.6391 | 4.3454 | 5.1606 | 6.0146 | 7.0675 | 7.9787 | 8.693 | 13.2645 | 13.5498 | 13.8039 | 13.9626 | 14.2926 | 14.6033 | 16.0509 | 17.0687
South West | Indian Queens 132 kV | Redruth | Primary Substation | 11 | Holistic Transition | 0.80138 | 0.97078 | 1.1958 | 1.4262 | 1.687 | 2.009 | 2.3014 | 2.6762 | 3.0122 | 3.3633 | 5.2693 | 5.6258 | 5.9732 | 6.2887 | 6.5891 | 6.7873 | 7.4538 | 7.8789 | 1.9218 | 2.3036 | 2.8083 | 3.3232 | 3.9048 | 4.613 | 5.244 | 6.0402 | 6.7601 | 7.5059 | 12.1317 | 12.8878 | 13.6253 | 14.2918 | 14.9265 | 15.357 | 16.8617 | 17.8359
South West | Indian Queens 132 kV | Redruth | Primary Substation | 11 | Hydrogen Evolution | 0.76382 | 0.89933 | 1.0636 | 1.2575 | 1.4726 | 1.7378 | 2.0087 | 2.3601 | 2.707 | 3.0412 | 3.3649 | 3.6737 | 3.9722 | 4.1365 | 4.4148 | 4.5796 | 5.0856 | 5.493 | 1.825 | 2.1207 | 2.4713 | 2.891 | 3.3551 | 3.9242 | 4.4999 | 5.2337 | 5.9691 | 6.6664 | 7.3331 | 7.968 | 8.5797 | 8.8693 | 9.45 | 9.8037 | 10.9444 | 11.8677
South West | Indian Queens 132 kV | Roseland | Primary Substation | 11 | Counterfactual | 0.15036 | 0.1759 | 0.20229 | 0.23122 | 0.26506 | 0.30248 | 0.34553 | 0.41303 | 0.46668 | 0.52386 | 0.58299 | 0.64492 | 0.71446 | 0.78329 | 0.85043 | 0.91708 | 1.1405 | 1.2248 | 0.35413 | 0.40914 | 0.46472 | 0.52539 | 0.59621 | 0.67428 | 0.76372 | 0.90217 | 1.013 | 1.131 | 1.2528 | 1.38 | 1.5223 | 1.6632 | 1.8005 | 1.9368 | 2.3981 | 2.5791
South West | Indian Queens 132 kV | Roseland | Primary Substation | 11 | Electric Engagement | 0.17913 | 0.23804 | 0.30379 | 0.37866 | 0.46284 | 0.55473 | 0.66417 | 0.80932 | 0.92952 | 1.0282 | 1.1128 | 1.1414 | 1.1673 | 1.1916 | 1.2154 | 1.2367 | 1.3371 | 1.4273 | 0.41799 | 0.54603 | 0.68439 | 0.842 | 1.0183 | 1.21 | 1.437 | 1.7349 | 1.9826 | 2.187 | 2.3632 | 2.4271 | 2.4857 | 2.5409 | 2.5951 | 2.644 | 2.8771 | 3.0857
South West | Indian Queens 132 kV | Roseland | Primary Substation | 11 | Holistic Transition | 0.17285 | 0.21968 | 0.26632 | 0.31597 | 0.3738 | 0.44073 | 0.51624 | 0.61826 | 0.70638 | 0.80017 | 0.89886 | 0.99485 | 1.0884 | 1.1757 | 1.2577 | 1.3055 | 1.4385 | 1.552 | 0.40869 | 0.5155 | 0.61811 | 0.72677 | 0.85235 | 0.99635 | 1.1573 | 1.3711 | 1.5565 | 1.7528 | 1.959 | 2.1598 | 2.3559 | 2.5392 | 2.7119 | 2.8158 | 3.1225 | 3.3866
South West | Indian Queens 132 kV | Roseland | Primary Substation | 11 | Hydrogen Evolution | 0.15947 | 0.19345 | 0.231 | 0.27385 | 0.32386 | 0.38086 | 0.44904 | 0.54465 | 0.62997 | 0.7194 | 0.8128 | 0.9032 | 0.99117 | 1.0715 | 1.1467 | 1.1839 | 1.2709 | 1.3462 | 0.37436 | 0.44875 | 0.52817 | 0.61909 | 0.72471 | 0.84439 | 0.98657 | 1.1834 | 1.3591 | 1.5428 | 1.7344 | 1.92 | 2.1007 | 2.266 | 2.4209 | 2.4996 | 2.6947 | 2.8638
South West | Indian Queens 132 kV | Sawles Road | Primary Substation | 11 | Counterfactual | 0.14741 | 0.202 | 0.27472 | 0.34086 | 0.40386 | 0.47576 | 0.54658 | 0.64607 | 0.72675 | 0.81343 | 0.91916 | 1.0123 | 1.1139 | 1.2134 | 1.3098 | 1.4056 | 1.7454 | 1.8939 | 0.33781 | 0.45407 | 0.60767 | 0.74676 | 0.8794 | 1.0307 | 1.1797 | 1.3862 | 1.5551 | 1.7371 | 1.965 | 2.1592 | 2.3692 | 2.5742 | 2.7725 | 2.9697 | 3.6783 | 4.0025
South West | Indian Queens 132 kV | Sawles Road | Primary Substation | 11 | Electric Engagement | 0.18757 | 0.29063 | 0.43077 | 0.56643 | 0.7046 | 0.8582 | 1.0229 | 1.2582 | 1.4402 | 1.5952 | 1.7313 | 1.7902 | 1.8435 | 1.8964 | 1.9476 | 1.9971 | 2.2205 | 2.4016 | 0.42732 | 0.6508 | 0.95174 | 1.2408 | 1.5339 | 1.8586 | 2.2034 | 2.7014 | 3.0825 | 3.41 | 3.6993 | 3.833 | 3.954 | 4.0745 | 4.1911 | 4.3042 | 4.8153 | 5.2347
South West | Indian Queens 132 kV | Sawles Road | Primary Substation | 11 | Holistic Transition | 0.17904 | 0.26438 | 0.37955 | 0.4848 | 0.59186 | 0.71522 | 0.84279 | 1.0064 | 1.1858 | 1.3409 | 1.4937 | 1.6403 | 1.7843 | 1.917 | 2.0403 | 2.118 | 2.3619 | 2.5422 | 0.41452 | 0.6057 | 0.86025 | 1.0919 | 1.3277 | 1.5972 | 1.875 | 2.2263 | 2.6252 | 2.9597 | 3.2847 | 3.5946 | 3.8992 | 4.179 | 4.4392 | 4.6084 | 5.1636 | 5.579
South West | Indian Queens 132 kV | Sawles Road | Primary Substation | 11 | Hydrogen Evolution | 0.16126 | 0.23323 | 0.33052 | 0.41862 | 0.5068 | 0.61027 | 0.71557 | 0.85299 | 1.0087 | 1.1492 | 1.2895 | 1.425 | 1.5535 | 1.6748 | 1.7874 | 1.8517 | 2.0377 | 2.1969 | 0.36895 | 0.52624 | 0.73536 | 0.92369 | 1.112 | 1.3323 | 1.5546 | 1.8401 | 2.1793 | 2.4768 | 2.7708 | 3.0537 | 3.3202 | 3.5728 | 3.8073 | 3.9453 | 4.3654 | 4.7271
South West | Indian Queens 132 kV | St Agnes | Primary Substation | 11 | Counterfactual | 0.28491 | 0.31581 | 0.36207 | 0.40416 | 0.45091 | 0.50846 | 0.57473 | 0.67342 | 0.75359 | 0.84067 | 0.92709 | 1.0132 | 1.1072 | 1.2014 | 1.2925 | 1.3829 | 1.7081 | 1.8548 | 0.67248 | 0.73854 | 0.837 | 0.92676 | 1.0264 | 1.1485 | 1.2894 | 1.4961 | 1.6656 | 1.8508 | 2.0325 | 2.2116 | 2.4056 | 2.6003 | 2.7881 | 2.9745 | 3.6573 | 3.9812
South West | Indian Queens 132 kV | St Agnes | Primary Substation | 11 | Electric Engagement | 0.32214 | 0.39296 | 0.5026 | 0.61219 | 0.7318 | 0.86863 | 1.0284 | 1.2387 | 1.4177 | 1.5716 | 1.7102 | 1.7727 | 1.8587 | 1.9196 | 1.9786 | 2.0362 | 2.3004 | 2.4849 | 0.75518 | 0.90748 | 1.1444 | 1.3797 | 1.635 | 1.9247 | 2.2607 | 2.6987 | 3.0739 | 3.3991 | 3.6944 | 3.8363 | 4.0257 | 4.1653 | 4.3001 | 4.4324 | 5.0367 | 5.4711
South West | Indian Queens 132 kV | St Agnes | Primary Substation | 11 | Holistic Transition | 0.31417 | 0.36852 | 0.45667 | 0.53931 | 0.63335 | 0.74519 | 0.87707 | 1.0529 | 1.208 | 1.3693 | 1.5242 | 1.6716 | 1.8405 | 1.9699 | 2.0905 | 2.1679 | 2.4283 | 2.594 | 0.74345 | 0.86609 | 1.0646 | 1.2506 | 1.4616 | 1.7085 | 1.9997 | 2.3834 | 2.7226 | 3.0732 | 3.4039 | 3.7181 | 4.0749 | 4.349 | 4.6048 | 4.774 | 5.3673 | 5.7511
South West | Indian Queens 132 kV | St Agnes | Primary Substation | 11 | Hydrogen Evolution | 0.2966 | 0.33665 | 0.39913 | 0.45841 | 0.5259 | 0.61061 | 0.70947 | 0.84488 | 0.97418 | 1.1148 | 1.2517 | 1.3824 | 1.5209 | 1.6399 | 1.7506 | 1.8145 | 2.0126 | 2.1762 | 0.69848 | 0.78503 | 0.9191 | 1.0462 | 1.1907 | 1.3709 | 1.5803 | 1.8634 | 2.1377 | 2.437 | 2.724 | 2.9969 | 3.2845 | 3.5337 | 3.7656 | 3.9041 | 4.3569 | 4.7335
South West | Indian Queens 132 kV | St Austell | Primary Substation | 11 | Counterfactual | 0.68318 | 0.79018 | 0.93006 | 1.0811 | 1.2494 | 1.4444 | 1.6628 | 1.9734 | 2.235 | 2.514 | 2.8204 | 3.0956 | 3.3529 | 3.6078 | 3.8571 | 4.1023 | 4.9777 | 5.3369 | 1.5388 | 1.7657 | 2.0614 | 2.3798 | 2.7347 | 3.1456 | 3.6063 | 4.2537 | 4.8037 | 5.3924 | 6.0454 | 6.6183 | 7.1473 | 7.6721 | 8.184 | 8.6875 | 10.5124 | 11.2994
South West | Indian Queens 132 kV | St Austell | Primary Substation | 11 | Electric Engagement | 0.78693 | 1.0109 | 1.3162 | 1.6519 | 2.0248 | 2.4434 | 2.9292 | 5.1776 | 5.7096 | 6.1767 | 6.5943 | 6.7924 | 6.9347 | 7.0761 | 7.1932 | 7.3257 | 8.0936 | 8.5425 | 1.7691 | 2.2501 | 2.9041 | 3.6201 | 4.4127 | 5.2984 | 6.32 | 11.6815 | 12.7948 | 13.7801 | 14.6679 | 15.1124 | 15.4358 | 15.7582 | 16.0202 | 16.323 | 18.0302 | 19.0763
South West | Indian Queens 132 kV | St Austell | Primary Substation | 11 | Holistic Transition | 0.76477 | 0.93972 | 1.1799 | 1.436 | 1.7306 | 2.0719 | 2.4613 | 4.5427 | 5.0482 | 5.5215 | 5.9888 | 6.4144 | 6.7997 | 7.1509 | 7.477 | 7.6819 | 8.4743 | 8.9127 | 1.7364 | 2.1268 | 2.6609 | 3.2273 | 3.8782 | 4.6252 | 5.4745 | 10.5055 | 11.6167 | 12.6361 | 13.6304 | 14.5263 | 15.3408 | 16.08 | 16.7672 | 17.2119 | 18.9697 | 19.9776
South West | Indian Queens 132 kV | St Austell | Primary Substation | 11 | Hydrogen Evolution | 0.71593 | 0.85803 | 1.0436 | 1.2488 | 1.4845 | 1.7642 | 2.0863 | 2.5072 | 2.9515 | 3.378 | 3.8029 | 4.2034 | 4.5413 | 4.8588 | 5.1337 | 5.2966 | 5.8465 | 6.2729 | 1.6116 | 1.9192 | 2.3158 | 2.7543 | 3.2583 | 3.8549 | 4.5384 | 5.4201 | 6.3789 | 7.2826 | 8.1742 | 9.0118 | 9.7121 | 10.3727 | 10.9367 | 11.2867 | 12.5129 | 13.4882
South West | Indian Queens 132 kV | St Buryan | Primary Substation | 11 | Counterfactual | 0.381 | 0.39877 | 0.41982 | 0.44357 | 0.47127 | 0.51064 | 0.5544 | 0.61632 | 0.66819 | 0.72371 | 0.77883 | 0.82719 | 0.87936 | 0.74846 | 0.80386 | 0.86109 | 1.0876 | 1.225 | 0.92506 | 0.96327 | 1.0088 | 1.0599 | 1.1194 | 1.2031 | 1.2966 | 1.427 | 1.5374 | 1.6565 | 1.7731 | 1.8722 | 1.9781 | 1.6264 | 1.7409 | 1.8591 | 2.3354 | 2.6324
South West | Indian Queens 132 kV | St Buryan | Primary Substation | 11 | Electric Engagement | 0.40053 | 0.44051 | 0.49918 | 0.56381 | 0.63458 | 0.72544 | 0.82968 | 0.95051 | 1.0566 | 1.1513 | 1.239 | 1.2826 | 1.3211 | 1.2803 | 1.3374 | 1.4086 | 1.7204 | 1.932 | 0.96837 | 1.0551 | 1.1833 | 1.3236 | 1.4762 | 1.6689 | 1.8886 | 2.1363 | 2.3541 | 2.5491 | 2.7299 | 2.8214 | 2.9013 | 2.7794 | 2.9062 | 3.0613 | 3.74 | 4.2102
South West | Indian Queens 132 kV | St Buryan | Primary Substation | 11 | Holistic Transition | 0.39621 | 0.42811 | 0.47654 | 0.52793 | 0.58802 | 0.66815 | 0.74039 | 0.83508 | 0.91575 | 1.0009 | 1.0844 | 1.1675 | 1.2492 | 1.316 | 1.3986 | 1.4734 | 1.7568 | 1.9472 | 0.96188 | 1.0345 | 1.1455 | 1.2624 | 1.3987 | 1.5751 | 1.7293 | 1.9293 | 2.0977 | 2.2737 | 2.443 | 2.6139 | 2.7824 | 2.912 | 3.0866 | 3.2457 | 3.8617 | 4.275
South West | Indian Queens 132 kV | St Buryan | Primary Substation | 11 | Hydrogen Evolution | 0.38734 | 0.41019 | 0.4401 | 0.47494 | 0.51564 | 0.57427 | 0.6407 | 0.72798 | 0.80458 | 0.88664 | 0.9685 | 1.0466 | 1.1199 | 1.0645 | 1.1399 | 1.2051 | 1.4323 | 1.6419 | 0.93911 | 0.98886 | 1.0533 | 1.1284 | 1.216 | 1.3406 | 1.4815 | 1.6644 | 1.823 | 1.9928 | 2.1609 | 2.3207 | 2.4697 | 2.2976 | 2.4562 | 2.5942 | 3.0906 | 3.5467
South West | Indian Queens 132 kV | St Columb Major | Primary Substation | 11 | Counterfactual | 0.59811 | 0.62754 | 0.6762 | 0.72442 | 0.7809 | 0.86824 | 0.96606 | 1.0945 | 1.2062 | 1.3306 | 1.447 | 1.5466 | 1.6484 | 1.7526 | 1.8505 | 1.9633 | 2.417 | 2.7483 | 1.3285 | 1.3918 | 1.4988 | 1.6054 | 1.731 | 1.9213 | 2.1366 | 2.416 | 2.6617 | 2.9392 | 3.1933 | 3.4068 | 3.6211 | 3.8421 | 4.048 | 4.2833 | 5.2616 | 5.9942
South West | Indian Queens 132 kV | St Columb Major | Primary Substation | 11 | Electric Engagement | 0.60523 | 0.66815 | 0.79823 | 0.93508 | 1.0781 | 1.2677 | 1.4764 | 1.7366 | 1.9738 | 2.1987 | 2.4231 | 2.5746 | 2.7376 | 2.9353 | 3.1386 | 3.5999 | 4.8524 | 5.9704 | 1.349 | 1.4866 | 1.7816 | 2.0916 | 2.4131 | 2.827 | 3.2793 | 3.8397 | 4.3521 | 4.8423 | 5.3339 | 5.6754 | 6.0419 | 6.4906 | 6.9375 | 7.9011 | 10.5795 | 12.9615
South West | Indian Queens 132 kV | St Columb Major | Primary Substation | 11 | Holistic Transition | 0.59929 | 0.65069 | 0.77805 | 0.90356 | 1.0501 | 1.2444 | 1.4748 | 1.7706 | 2.0833 | 2.3526 | 2.5821 | 2.7907 | 3.0039 | 3.1941 | 3.407 | 3.6812 | 4.3084 | 4.5706 | 1.3404 | 1.4582 | 1.7587 | 2.0547 | 2.4004 | 2.8418 | 3.3714 | 4.0487 | 4.7735 | 5.3845 | 5.8907 | 6.349 | 6.8154 | 7.2225 | 7.6726 | 8.2458 | 9.6315 | 10.2236
South West | Indian Queens 132 kV | St Columb Major | Primary Substation | 11 | Hydrogen Evolution | 0.58574 | 0.62335 | 0.68409 | 0.75425 | 0.83463 | 0.95825 | 1.093 | 1.2602 | 1.4515 | 1.6634 | 1.8449 | 2.011 | 2.1752 | 2.3621 | 2.5377 | 2.7244 | 3.2414 | 3.6433 | 1.3058 | 1.3887 | 1.5228 | 1.6799 | 1.86 | 2.1304 | 2.4254 | 2.7865 | 3.2102 | 3.6835 | 4.0789 | 4.4372 | 4.7882 | 5.1979 | 5.5724 | 5.9701 | 7.1428 | 8.0675
South West | Indian Queens 132 kV | St Ives | Primary Substation | 11 | Counterfactual | 0.76878 | 0.83026 | 0.89297 | 0.95992 | 1.0367 | 1.1235 | 1.2233 | 1.3772 | 1.4998 | 1.6305 | 1.7653 | 1.9049 | 2.0605 | 1.6479 | 1.7997 | 1.951 | 2.4649 | 2.6804 | 1.8853 | 2.0196 | 2.1527 | 2.2944 | 2.4562 | 2.6386 | 2.8475 | 3.1651 | 3.4202 | 3.6919 | 3.9713 | 4.2592 | 4.5787 | 3.4779 | 3.79 | 4.1007 | 5.1698 | 5.6376
South West | Indian Queens 132 kV | St Ives | Primary Substation | 11 | Electric Engagement | 0.83305 | 0.9772 | 1.1327 | 1.3032 | 1.496 | 1.7079 | 1.9599 | 2.2914 | 2.5671 | 2.7955 | 2.9924 | 3.0625 | 3.1276 | 2.6436 | 2.7086 | 2.789 | 3.0726 | 3.318 | 2.0281 | 2.345 | 2.6757 | 3.0361 | 3.442 | 3.8861 | 4.4115 | 5.0944 | 5.6651 | 6.1405 | 6.5531 | 6.7112 | 6.859 | 5.6352 | 5.7844 | 5.9642 | 6.6254 | 7.1986
South West | Indian Queens 132 kV | St Ives | Primary Substation | 11 | Holistic Transition | 0.81977 | 0.94195 | 1.0558 | 1.1757 | 1.3143 | 1.4744 | 1.6517 | 1.8891 | 2.0959 | 2.3144 | 2.542 | 2.7673 | 2.9882 | 2.6653 | 2.8608 | 2.9993 | 3.3524 | 3.648 | 2.0088 | 2.2907 | 2.5437 | 2.8086 | 3.1126 | 3.4601 | 3.8407 | 4.3412 | 4.7792 | 5.2395 | 5.7171 | 6.1908 | 6.6557 | 5.7675 | 6.1819 | 6.4817 | 7.3006 | 7.9916
South West | Indian Queens 132 kV | St Ives | Primary Substation | 11 | Hydrogen Evolution | 0.78883 | 0.87114 | 0.95828 | 1.0526 | 1.1637 | 1.2924 | 1.4463 | 1.661 | 1.852 | 2.0525 | 2.2612 | 2.464 | 2.6618 | 2.2891 | 2.4611 | 2.5695 | 2.7928 | 2.9998 | 1.93 | 2.1118 | 2.2976 | 2.4983 | 2.7335 | 3.0047 | 3.3273 | 3.7714 | 4.1671 | 4.5815 | 5.0116 | 5.4296 | 5.8376 | 4.8269 | 5.1838 | 5.4132 | 5.9218 | 6.3905
South West | Indian Queens 132 kV | St Keverne | Primary Substation | 11 | Counterfactual | 0.20144 | 0.22595 | 0.25024 | 0.27855 | 0.31127 | 0.35081 | 0.39554 | 0.46368 | 0.51856 | 0.57743 | 0.63763 | 0.69982 | 0.76921 | 0.83804 | 0.90455 | 0.97174 | 1.2252 | 1.3626 | 0.46787 | 0.5209 | 0.57254 | 0.63232 | 0.70118 | 0.78404 | 0.87761 | 1.0183 | 1.1324 | 1.2551 | 1.3798 | 1.508 | 1.6503 | 1.7917 | 1.9281 | 2.0658 | 2.5907 | 2.8816
South West | Indian Queens 132 kV | St Keverne | Primary Substation | 11 | Electric Engagement | 0.22658 | 0.28074 | 0.34568 | 0.41857 | 0.49988 | 0.59456 | 0.70664 | 0.8544 | 0.9813 | 1.092 | 1.1914 | 1.2399 | 1.2835 | 1.3241 | 1.371 | 1.5332 | 1.7002 | 1.8158 | 0.52355 | 0.64195 | 0.78013 | 0.93424 | 1.1053 | 1.3032 | 1.5364 | 1.8412 | 2.1041 | 2.3346 | 2.5426 | 2.6481 | 2.744 | 2.8341 | 2.9367 | 3.2696 | 3.6454 | 3.9119
South West | Indian Queens 132 kV | St Keverne | Primary Substation | 11 | Holistic Transition | 0.22093 | 0.26522 | 0.31319 | 0.36515 | 0.42552 | 0.50109 | 0.5868 | 0.70105 | 0.80336 | 0.9137 | 1.0251 | 1.1305 | 1.231 | 1.3219 | 1.4164 | 1.5983 | 1.7852 | 1.9153 | 0.51501 | 0.61682 | 0.72354 | 0.83826 | 0.97071 | 1.1338 | 1.3183 | 1.5609 | 1.7788 | 2.0123 | 2.2462 | 2.4676 | 2.6792 | 2.8707 | 3.0691 | 3.4423 | 3.8621 | 4.16
South West | Indian Queens 132 kV | St Keverne | Primary Substation | 11 | Hydrogen Evolution | 0.20981 | 0.24072 | 0.27768 | 0.32022 | 0.37026 | 0.43242 | 0.50597 | 0.60757 | 0.7059 | 0.81083 | 0.9157 | 1.0145 | 1.1728 | 1.258 | 1.3426 | 1.3944 | 1.5284 | 1.6355 | 0.48635 | 0.55422 | 0.63267 | 0.72258 | 0.82807 | 0.95829 | 1.1117 | 1.3212 | 1.5251 | 1.7427 | 1.9588 | 2.1624 | 2.4848 | 2.6612 | 2.8361 | 2.9455 | 3.242 | 3.4811
South West | Indian Queens 132 kV | St Mawgan | Primary Substation | 11 | Counterfactual | 0.42984 | 0.4721 | 0.52166 | 0.58281 | 0.64865 | 0.71808 | 0.78523 | 0.87139 | 0.94745 | 1.0262 | 1.185 | 1.2417 | 1.3028 | 1.3605 | 1.4165 | 1.4722 | 1.6771 | 1.7783 | 1.0233 | 1.1137 | 1.2182 | 1.3464 | 1.4848 | 1.6305 | 1.7716 | 1.9513 | 2.1112 | 2.2772 | 2.6499 | 2.769 | 2.8961 | 3.015 | 3.1298 | 3.244 | 3.67 | 3.8869
South West | Indian Queens 132 kV | St Mawgan | Primary Substation | 11 | Electric Engagement | 0.4515 | 0.52432 | 0.61398 | 0.7209 | 0.83791 | 0.96636 | 1.099 | 1.4417 | 1.5951 | 1.7312 | 1.8317 | 1.8832 | 1.9307 | 2.0398 | 2.0817 | 2.1308 | 2.3435 | 2.4526 | 1.0716 | 1.2308 | 1.4232 | 1.6522 | 1.9031 | 2.1767 | 2.457 | 3.2482 | 3.5749 | 3.8657 | 4.0793 | 4.1929 | 4.2987 | 4.5461 | 4.6379 | 4.7439 | 5.2068 | 5.457
South West | Indian Queens 132 kV | St Mawgan | Primary Substation | 11 | Holistic Transition | 0.44693 | 0.51167 | 0.58788 | 0.67753 | 0.77721 | 0.88851 | 0.99907 | 1.1326 | 1.5419 | 1.6786 | 1.7867 | 1.8858 | 1.975 | 2.0834 | 2.1623 | 2.2243 | 2.4341 | 2.5511 | 1.0647 | 1.2103 | 1.3781 | 1.5745 | 1.7933 | 2.0354 | 2.2757 | 2.563 | 3.544 | 3.8408 | 4.0716 | 4.282 | 4.4699 | 4.6953 | 4.8612 | 4.9931 | 5.4529 | 5.7192
South West | Indian Queens 132 kV | St Mawgan | Primary Substation | 11 | Hydrogen Evolution | 0.43742 | 0.49116 | 0.55675 | 0.63739 | 0.7269 | 0.82485 | 0.92089 | 1.0379 | 1.3325 | 1.4567 | 1.5525 | 1.6391 | 1.7229 | 1.8565 | 1.9265 | 1.9738 | 2.1171 | 2.2241 | 1.0403 | 1.1581 | 1.2991 | 1.4724 | 1.6655 | 1.8757 | 2.0806 | 2.3272 | 3.0213 | 3.2879 | 3.4899 | 3.671 | 3.8467 | 4.1429 | 4.288 | 4.3878 | 4.7007 | 4.9376
South West | Indian Queens 132 kV | St Tudy | Primary Substation | 11 | Counterfactual | 0.54227 | 0.564 | 0.60893 | 0.6521 | 0.70446 | 0.78606 | 0.88026 | 1.0031 | 1.1111 | 1.2357 | 1.3458 | 1.4395 | 1.5316 | 1.6278 | 1.7168 | 1.8065 | 2.229 | 2.544 | 1.31 | 1.3567 | 1.4574 | 1.5552 | 1.6741 | 1.8554 | 2.0672 | 2.3399 | 2.5824 | 2.8667 | 3.1119 | 3.3157 | 3.5123 | 3.7188 | 3.908 | 4.0987 | 5.0259 | 5.7393
South West | Indian Queens 132 kV | St Tudy | Primary Substation | 11 | Electric Engagement | 0.56664 | 0.61593 | 0.75273 | 0.88816 | 1.0308 | 1.2131 | 1.412 | 1.6576 | 1.8865 | 2.1082 | 2.3307 | 2.4889 | 2.658 | 2.825 | 2.9872 | 3.1934 | 4.0095 | 4.4472 | 1.364 | 1.4711 | 1.7868 | 2.0987 | 2.4247 | 2.8294 | 3.2675 | 3.8044 | 4.3077 | 4.7994 | 5.2955 | 5.6583 | 6.0451 | 6.4306 | 6.8032 | 7.2648 | 9.1316 | 10.1813
South West | Indian Queens 132 kV | St Tudy | Primary Substation | 11 | Holistic Transition | 0.56113 | 0.60002 | 0.73832 | 0.87121 | 1.0303 | 1.2296 | 1.4734 | 1.788 | 2.0697 | 2.3539 | 2.5816 | 2.9272 | 3.1345 | 3.2947 | 3.4475 | 3.6146 | 4.1984 | 4.4388 | 1.3556 | 1.4443 | 1.7743 | 2.0923 | 2.4725 | 2.9333 | 3.5031 | 4.2369 | 4.892 | 5.5487 | 6.0592 | 6.8692 | 7.3299 | 7.6796 | 8.0116 | 8.3727 | 9.685 | 10.2337
South West | Indian Queens 132 kV | St Tudy | Primary Substation | 11 | Hydrogen Evolution | 0.55024 | 0.57886 | 0.6388 | 0.70276 | 0.78005 | 0.89891 | 1.0294 | 1.19 | 1.3813 | 1.6024 | 1.7827 | 1.9441 | 2.1001 | 2.2526 | 2.3983 | 2.5357 | 3.1315 | 3.5547 | 1.3277 | 1.3904 | 1.5243 | 1.6693 | 1.8446 | 2.1084 | 2.3984 | 2.7507 | 3.1822 | 3.6856 | 4.0852 | 4.4386 | 4.7772 | 5.1118 | 5.4307 | 5.7337 | 7.1226 | 8.1149
South West | Indian Queens 132 kV | Trebal | Primary Substation | 11 | Counterfactual | 0.062984 | 0.062984 | 0.063047 | 0.06311 | 0.063236 | 0.063467 | 0.06376 | 0.064054 | 0.064348 | 0.064705 | 0.064999 | 0.06523 | 0.065335 | 0.0025193 | 0.0026243 | 0.0027293 | 0.0038368 | 0.0048865 | 0.15746 | 0.15746 | 0.15762 | 0.15777 | 0.15809 | 0.15861 | 0.1593 | 0.15998 | 0.16066 | 0.1615 | 0.16218 | 0.16271 | 0.16292 | 0.005826 | 0.0060359 | 0.0062459 | 0.0087757 | 0.01119
South West | Indian Queens 132 kV | Trebal | Primary Substation | 11 | Electric Engagement | 0.062984 | 0.062984 | 0.063299 | 0.063614 | 0.063928 | 0.06439 | 0.064915 | 1.6398 | 1.64 | 1.6403 | 1.6406 | 1.6409 | 1.6411 | 1.5808 | 1.5815 | 1.5822 | 1.5855 | 1.5871 | 0.15746 | 0.15746 | 0.15825 | 0.15903 | 0.15982 | 0.16087 | 0.16208 | 4.0991 | 4.0996 | 4.1001 | 4.1009 | 4.1013 | 4.1019 | 3.9509 | 3.9525 | 3.9541 | 3.9615 | 3.9653
South West | Indian Queens 132 kV | Trebal | Primary Substation | 11 | Holistic Transition | 0.062984 | 0.062984 | 0.063362 | 0.063739 | 0.064243 | 0.064957 | 0.065377 | 1.6404 | 1.6407 | 1.641 | 1.6409 | 1.6411 | 1.6414 | 1.5822 | 1.5826 | 1.583 | 1.5854 | 1.5862 | 0.15746 | 0.15746 | 0.1584 | 0.15935 | 0.16061 | 0.16229 | 0.16329 | 4.1007 | 4.1014 | 4.102 | 4.1018 | 4.1022 | 4.1026 | 3.9547 | 3.9556 | 3.9565 | 3.9617 | 3.9634
South West | Indian Queens 132 kV | Trebal | Primary Substation | 11 | Hydrogen Evolution | 0.062984 | 0.062984 | 0.063047 | 0.063173 | 0.063299 | 0.063593 | 0.063886 | 0.064243 | 0.064469 | 0.064821 | 0.064926 | 0.064968 | 1.6395 | 1.5784 | 1.5788 | 1.5792 | 1.5814 | 1.5832 | 0.15746 | 0.15746 | 0.15762 | 0.15793 | 0.15825 | 0.15893 | 0.15961 | 0.16045 | 0.16093 | 0.16173 | 0.16194 | 0.16199 | 4.0984 | 3.9455 | 3.9464 | 3.9473 | 3.9524 | 3.9565
South West | Indian Queens 132 kV | Truro Shortlanesend | Primary Substation | 11 | Counterfactual | 0.55084 | 0.62546 | 0.72204 | 0.82872 | 0.95962 | 1.1356 | 1.3387 | 1.633 | 1.878 | 2.1461 | 2.4005 | 2.6368 | 2.8907 | 3.148 | 3.394 | 3.6393 | 4.544 | 5.0033 | 1.252 | 1.408 | 1.6133 | 1.8401 | 2.1205 | 2.496 | 2.9322 | 3.555 | 4.0794 | 4.6587 | 5.1975 | 5.6874 | 6.2083 | 6.7376 | 7.2413 | 7.7435 | 9.6355 | 10.6469
South West | Indian Queens 132 kV | Truro Shortlanesend | Primary Substation | 11 | Electric Engagement | 0.65024 | 0.83159 | 1.1204 | 1.4548 | 1.8331 | 2.2925 | 2.8112 | 3.4493 | 3.9796 | 4.446 | 4.8782 | 5.1008 | 5.3232 | 5.5501 | 5.7955 | 6.0145 | 7.0314 | 7.667 | 1.4725 | 1.8592 | 2.4911 | 3.2253 | 4.0536 | 5.0522 | 6.1689 | 7.5191 | 8.6403 | 9.6352 | 10.5648 | 11.0702 | 11.5774 | 12.0962 | 12.6479 | 13.1476 | 15.4478 | 16.9474
South West | Indian Queens 132 kV | Truro Shortlanesend | Primary Substation | 11 | Holistic Transition | 0.6283 | 0.76215 | 1.0092 | 1.2748 | 1.5963 | 1.9905 | 2.4447 | 3.0303 | 3.5408 | 4.0501 | 4.5195 | 4.9603 | 5.3925 | 5.7745 | 6.1572 | 6.4026 | 7.313 | 7.8096 | 1.4397 | 1.7387 | 2.3079 | 2.9184 | 3.657 | 4.5455 | 5.5699 | 6.8759 | 8.0138 | 9.1374 | 10.1497 | 11.0976 | 12.0266 | 12.8385 | 13.6485 | 14.1842 | 16.2346 | 17.3738
South West | Indian Queens 132 kV | Truro Shortlanesend | Primary Substation | 11 | Hydrogen Evolution | 0.58277 | 0.68589 | 0.82902 | 1.0097 | 1.2325 | 1.5341 | 1.8724 | 2.296 | 2.6979 | 3.1294 | 3.5342 | 3.9174 | 4.2867 | 4.6426 | 4.9883 | 5.1981 | 5.9342 | 6.5293 | 1.3228 | 1.5436 | 1.8515 | 2.2486 | 2.7397 | 3.4018 | 4.14 | 5.044 | 5.9117 | 6.8446 | 7.7027 | 8.5096 | 9.2847 | 10.036 | 10.7643 | 11.2211 | 12.8993 | 14.2702
South West | Indian Queens 132 kV | Truro Treyew Road | Primary Substation | 11 | Counterfactual | 0.68229 | 0.76075 | 0.85833 | 0.97399 | 1.0916 | 1.2133 | 1.3492 | 1.5379 | 1.6911 | 1.8248 | 1.9919 | 2.131 | 2.2829 | 2.4351 | 2.5823 | 2.7289 | 3.2433 | 3.5284 | 1.6534 | 1.8203 | 2.0263 | 2.2694 | 2.5168 | 2.7728 | 3.0587 | 3.4519 | 3.7737 | 4.0545 | 4.4158 | 4.7042 | 5.0167 | 5.3299 | 5.6323 | 5.9333 | 7.006 | 7.6165
South West | Indian Queens 132 kV | Truro Treyew Road | Primary Substation | 11 | Electric Engagement | 0.74349 | 0.89265 | 1.091 | 1.3162 | 1.5553 | 1.8074 | 2.0976 | 2.5314 | 2.8458 | 3.0784 | 3.2845 | 3.373 | 3.4386 | 3.4975 | 3.5609 | 3.6794 | 3.9718 | 4.1892 | 1.7896 | 2.1113 | 2.5365 | 3.0163 | 3.525 | 4.0582 | 4.6691 | 5.6004 | 6.2608 | 6.7488 | 7.1847 | 7.3837 | 7.5276 | 7.6553 | 7.7945 | 8.0424 | 8.6931 | 9.1933
South West | Indian Queens 132 kV | Truro Treyew Road | Primary Substation | 11 | Holistic Transition | 0.73067 | 0.85361 | 1.0132 | 1.1939 | 1.3881 | 1.5964 | 1.8315 | 2.1326 | 2.458 | 2.6958 | 2.9036 | 3.1124 | 3.3183 | 3.5088 | 3.6915 | 3.8651 | 4.1998 | 4.4531 | 1.7705 | 2.0453 | 2.3984 | 2.7958 | 3.2236 | 3.6785 | 4.1915 | 4.841 | 5.5667 | 6.0781 | 6.5088 | 6.9437 | 7.373 | 7.7695 | 8.1522 | 8.5158 | 9.2644 | 9.8459
South West | Indian Queens 132 kV | Truro Treyew Road | Primary Substation | 11 | Hydrogen Evolution | 0.70333 | 0.80319 | 0.93338 | 1.0846 | 1.2459 | 1.4189 | 1.6155 | 1.8722 | 2.1711 | 2.3833 | 2.5936 | 2.7978 | 2.9857 | 3.1551 | 3.3161 | 3.461 | 3.69 | 4.0393 | 1.7004 | 1.9167 | 2.1954 | 2.5183 | 2.863 | 3.2313 | 3.6485 | 4.1866 | 4.8436 | 5.2905 | 5.728 | 6.1517 | 6.5369 | 6.8821 | 7.2119 | 7.5086 | 8.0138 | 8.831
South West | Indian Queens 132 kV | Twelveheads. | Primary Substation | 11 | Counterfactual | 0.33102 | 0.36038 | 0.39499 | 0.43293 | 0.47864 | 0.5331 | 0.59606 | 0.68967 | 0.76652 | 0.84842 | 0.93306 | 1.0156 | 1.1063 | 1.1962 | 1.2828 | 1.3704 | 1.6935 | 1.8523 | 0.80007 | 0.86275 | 0.93663 | 1.0175 | 1.115 | 1.2308 | 1.3648 | 1.5608 | 1.7233 | 1.8965 | 2.0749 | 2.2462 | 2.433 | 2.6186 | 2.7969 | 2.9771 | 3.6542 | 3.9994
South West | Indian Queens 132 kV | Twelveheads. | Primary Substation | 11 | Electric Engagement | 0.36619 | 0.4322 | 0.52354 | 0.62947 | 0.74648 | 0.87927 | 1.0312 | 1.2281 | 1.398 | 1.5452 | 1.6782 | 1.7403 | 1.8218 | 1.8814 | 1.9395 | 1.9941 | 3.8242 | 4.0005 | 0.87844 | 1.0203 | 1.2169 | 1.4455 | 1.6962 | 1.9781 | 2.2979 | 2.707 | 3.0627 | 3.3731 | 3.6558 | 3.7952 | 3.9844 | 4.1196 | 4.2511 | 4.3756 | 8.8973 | 9.31
South West | Indian Queens 132 kV | Twelveheads. | Primary Substation | 11 | Holistic Transition | 0.35927 | 0.41052 | 0.48507 | 0.56393 | 0.65581 | 0.76687 | 0.89389 | 1.1078 | 1.2519 | 1.4056 | 1.5543 | 1.6964 | 1.8339 | 1.9582 | 2.0768 | 2.1538 | 3.9896 | 4.1639 | 0.86848 | 0.98397 | 1.1527 | 1.3301 | 1.5359 | 1.7806 | 2.0604 | 2.5404 | 2.853 | 3.1853 | 3.5018 | 3.8037 | 4.0964 | 4.3596 | 4.6108 | 4.7787 | 9.3081 | 9.7071
South West | Indian Queens 132 kV | Twelveheads. | Primary Substation | 11 | Hydrogen Evolution | 0.34276 | 0.38036 | 0.42879 | 0.48908 | 0.55909 | 0.64383 | 0.74263 | 0.87304 | 1.0069 | 1.1455 | 1.2798 | 1.4061 | 1.5497 | 1.6624 | 1.7698 | 1.8312 | 2.0229 | 2.1889 | 0.82645 | 0.90764 | 1.011 | 1.1413 | 1.292 | 1.4731 | 1.6829 | 1.9544 | 2.238 | 2.5313 | 2.8121 | 3.0754 | 3.383 | 3.619 | 3.8439 | 3.9768 | 4.414 | 4.7915
South West | Indian Queens 132 kV | Wadebridge | Primary Substation | 11 | Counterfactual | 0.54636 | 0.60056 | 0.78641 | 0.87989 | 0.98576 | 1.1145 | 1.252 | 1.427 | 1.5754 | 1.7385 | 1.8815 | 2.0181 | 2.1642 | 2.3109 | 2.4505 | 2.5916 | 3.1469 | 3.4534 | 1.2702 | 1.3862 | 1.7691 | 1.9693 | 2.1966 | 2.4727 | 2.7691 | 3.1421 | 3.4618 | 3.8161 | 4.1224 | 4.4099 | 4.7137 | 5.0198 | 5.31 | 5.6027 | 6.7844 | 7.4654
South West | Indian Queens 132 kV | Wadebridge | Primary Substation | 11 | Electric Engagement | 0.59702 | 0.82583 | 1.0047 | 1.2172 | 1.4489 | 1.7172 | 2.0092 | 2.3616 | 2.6719 | 2.9503 | 3.1943 | 3.3288 | 3.4938 | 3.6289 | 3.7689 | 3.9501 | 4.5485 | 4.9354 | 1.3825 | 1.8588 | 2.2528 | 2.7177 | 3.2224 | 3.8011 | 4.4264 | 5.1729 | 5.8347 | 6.4341 | 6.9632 | 7.2696 | 7.6541 | 7.9647 | 8.2828 | 8.684 | 10.053 | 10.9713
South West | Indian Queens 132 kV | Wadebridge | Primary Substation | 11 | Holistic Transition | 0.58593 | 0.79325 | 0.94923 | 1.1311 | 1.3417 | 1.5923 | 1.8709 | 2.2829 | 2.5869 | 2.899 | 3.1648 | 3.4163 | 3.6618 | 3.8756 | 4.0869 | 4.281 | 4.8213 | 5.1216 | 1.3658 | 1.8043 | 2.1626 | 2.576 | 3.0549 | 3.6154 | 4.2426 | 5.182 | 5.8624 | 6.5561 | 7.1334 | 7.6777 | 8.2091 | 8.6663 | 9.1168 | 9.5327 | 10.7582 | 11.4477
South West | Indian Queens 132 kV | Wadebridge | Primary Substation | 11 | Hydrogen Evolution | 0.56283 | 0.74795 | 0.8444 | 0.97402 | 1.1235 | 1.3093 | 1.5083 | 1.7465 | 1.9947 | 2.2639 | 2.4947 | 2.7096 | 2.9486 | 3.1451 | 3.3363 | 3.4828 | 3.9291 | 4.2982 | 1.3067 | 1.6892 | 1.898 | 2.1792 | 2.5042 | 2.9065 | 3.3359 | 3.8421 | 4.3791 | 4.9655 | 5.4579 | 5.9132 | 6.4298 | 6.8478 | 7.2533 | 7.5698 | 8.5954 | 9.4484
South West | Indian Queens 132 kV | Wheal Reeth | Primary Substation | 11 | Counterfactual | 0.47731 | 0.49847 | 0.52781 | 0.55607 | 0.58763 | 0.62651 | 0.67135 | 0.73876 | 0.79387 | 0.8534 | 0.91288 | 0.97306 | 1.0388 | 1.1046 | 1.1683 | 1.2316 | 1.4899 | 1.6409 | 1.1717 | 1.217 | 1.2795 | 1.3397 | 1.4068 | 1.4892 | 1.5845 | 1.7255 | 1.8418 | 1.9682 | 2.0931 | 2.218 | 2.3536 | 2.4894 | 2.6204 | 2.7507 | 3.289 | 3.6113
South West | Indian Queens 132 kV | Wheal Reeth | Primary Substation | 11 | Electric Engagement | 0.50101 | 0.54789 | 0.64189 | 0.74179 | 0.84695 | 0.96455 | 1.0948 | 1.2669 | 1.4255 | 1.5606 | 1.6818 | 1.7567 | 1.8342 | 1.8982 | 1.9453 | 1.9996 | 2.2325 | 2.4062 | 1.2241 | 1.3255 | 1.5359 | 1.7589 | 1.9917 | 2.2485 | 2.5288 | 2.8968 | 3.2394 | 3.5301 | 3.7913 | 3.9608 | 4.1403 | 4.2889 | 4.395 | 4.5214 | 5.0613 | 5.4734
South West | Indian Queens 132 kV | Wheal Reeth | Primary Substation | 11 | Holistic Transition | 0.49544 | 0.53197 | 0.60844 | 0.68319 | 0.76758 | 0.85861 | 0.95625 | 1.0868 | 1.2062 | 1.331 | 1.4533 | 1.5684 | 1.6767 | 1.7707 | 1.8594 | 1.9184 | 2.127 | 2.2661 | 1.2156 | 1.2986 | 1.4754 | 1.6475 | 1.8412 | 2.0442 | 2.2593 | 2.544 | 2.8043 | 3.0735 | 3.3342 | 3.5794 | 3.8106 | 4.0109 | 4.1999 | 4.3295 | 4.8056 | 5.1289
South West | Indian Queens 132 kV | Wheal Reeth | Primary Substation | 11 | Hydrogen Evolution | 0.4852 | 0.51188 | 0.5538 | 0.59638 | 0.64464 | 0.70705 | 0.78123 | 0.88205 | 0.98281 | 1.0946 | 1.2036 | 1.3058 | 1.4009 | 1.4859 | 1.5659 | 1.6134 | 1.762 | 1.8814 | 1.1891 | 1.247 | 1.3368 | 1.4276 | 1.5304 | 1.6624 | 1.8185 | 2.0281 | 2.2401 | 2.4759 | 2.7028 | 2.9148 | 3.1119 | 3.2896 | 3.4564 | 3.5584 | 3.8936 | 4.166
South West | Iron Acton 132 kV | Abbeywood Primary | Primary Substation | 11 | Counterfactual | 0.095987 | 0.10307 | 0.10864 | 0.1146 | 0.12131 | 0.12836 | 0.13698 | 0.15111 | 0.16241 | 0.17426 | 0.18649 | 0.19947 | 0.2139 | 0.22838 | 0.24252 | 0.25713 | 0.31453 | 0.35478 | 0.22992 | 0.24569 | 0.25772 | 0.27004 | 0.28391 | 0.29841 | 0.31619 | 0.34511 | 0.36841 | 0.39286 | 0.41801 | 0.44464 | 0.47416 | 0.50375 | 0.53265 | 0.56256 | 0.68105 | 0.76523
South West | Iron Acton 132 kV | Abbeywood Primary | Primary Substation | 11 | Electric Engagement | 0.10021 | 0.11946 | 0.13089 | 0.14358 | 0.15749 | 0.17249 | 0.19093 | 0.21639 | 0.23752 | 0.25536 | 0.27106 | 0.27981 | 0.28712 | 0.29407 | 0.30079 | 0.30724 | 0.3368 | 0.36831 | 0.23909 | 0.28398 | 0.30784 | 0.33424 | 0.36307 | 0.39407 | 0.43221 | 0.48454 | 0.5283 | 0.56545 | 0.59837 | 0.61722 | 0.63319 | 0.64842 | 0.66319 | 0.6775 | 0.74414 | 0.8145
South West | Iron Acton 132 kV | Abbeywood Primary | Primary Substation | 11 | Holistic Transition | 0.09848 | 0.11506 | 0.12283 | 0.13107 | 0.14024 | 0.15098 | 0.16399 | 0.18354 | 0.20048 | 0.21793 | 0.23575 | 0.25358 | 0.2707 | 0.28713 | 0.30246 | 0.31376 | 0.30924 | 0.3448 | 0.23601 | 0.27582 | 0.29262 | 0.31035 | 0.33006 | 0.35294 | 0.38054 | 0.4217 | 0.45749 | 0.49424 | 0.53159 | 0.56894 | 0.60482 | 0.63936 | 0.67162 | 0.69592 | 0.67343 | 0.75335
South West | Iron Acton 132 kV | Abbeywood Primary | Primary Substation | 11 | Hydrogen Evolution | 0.098045 | 0.11441 | 0.1223 | 0.13072 | 0.14036 | 0.15102 | 0.16485 | 0.18541 | 0.20339 | 0.222 | 0.24146 | 0.26069 | 0.27958 | 0.29718 | 0.31364 | 0.32543 | 0.3618 | 0.38971 | 0.23426 | 0.27303 | 0.28942 | 0.30689 | 0.32686 | 0.34881 | 0.37742 | 0.41967 | 0.45685 | 0.4953 | 0.53536 | 0.57491 | 0.61386 | 0.6501 | 0.68419 | 0.70889 | 0.78784 | 0.84986
South West | Iron Acton 132 kV | Almondsbury | Primary Substation | 11 | Counterfactual | 0.54391 | 0.59289 | 0.66264 | 0.74233 | 0.8389 | 0.95004 | 1.3883 | 1.5546 | 1.6926 | 1.8492 | 1.9928 | 2.1252 | 2.2622 | 2.4009 | 2.5332 | 2.668 | 3.2132 | 3.5353 | 1.1723 | 1.279 | 1.4358 | 1.6143 | 1.8306 | 2.0771 | 3.1384 | 3.4991 | 3.8013 | 4.148 | 4.46 | 4.7413 | 5.0281 | 5.3189 | 5.5954 | 5.8771 | 7.0501 | 7.7756
South West | Iron Acton 132 kV | Almondsbury | Primary Substation | 11 | Electric Engagement | 0.59205 | 0.71576 | 0.92429 | 1.1581 | 1.6677 | 2.2476 | 2.5262 | 2.8546 | 3.1319 | 3.3786 | 3.6146 | 3.7529 | 3.889 | 4.0219 | 4.1506 | 4.2764 | 4.8291 | 5.2644 | 1.2789 | 1.5539 | 2.0294 | 2.5617 | 3.7761 | 5.1542 | 5.7643 | 6.4687 | 7.0663 | 7.6046 | 8.1253 | 8.446 | 8.7635 | 9.0753 | 9.3769 | 9.6731 | 10.9724 | 12.0137
South West | Iron Acton 132 kV | Almondsbury | Primary Substation | 11 | Holistic Transition | 0.58088 | 0.68303 | 0.86582 | 1.6361 | 1.8737 | 2.1224 | 2.3899 | 2.7232 | 3.0039 | 3.2916 | 3.5466 | 3.7871 | 4.0231 | 4.2237 | 4.4093 | 4.5436 | 5.0356 | 5.312 | 1.2619 | 1.4982 | 1.9297 | 3.8262 | 4.3863 | 4.961 | 5.578 | 6.3345 | 6.9716 | 7.6196 | 8.1793 | 8.7053 | 9.2207 | 9.652 | 10.0516 | 10.3487 | 11.4829 | 12.1255
South West | Iron Acton 132 kV | Almondsbury | Primary Substation | 11 | Hydrogen Evolution | 0.55991 | 0.64384 | 0.76243 | 0.91043 | 1.0845 | 1.8405 | 2.0303 | 2.2592 | 2.4837 | 2.7383 | 2.9628 | 3.1677 | 3.3629 | 3.5471 | 3.7224 | 3.8401 | 4.2994 | 4.6821 | 1.2074 | 1.3973 | 1.6672 | 2.006 | 2.4054 | 4.2485 | 4.67 | 5.1635 | 5.6568 | 6.2202 | 6.705 | 7.144 | 7.5594 | 7.954 | 8.3296 | 8.5906 | 9.6644 | 10.5679
South West | Iron Acton 132 kV | Bedminster | Primary Substation | 11 | Counterfactual | 0.46214 | 0.71085 | 0.92938 | 1.1309 | 1.4133 | 1.7227 | 2.0396 | 2.4645 | 2.8116 | 3.1551 | 3.5057 | 3.8754 | 4.2804 | 4.6691 | 5.0499 | 5.4311 | 6.789 | 7.3849 | 1.054 | 1.5704 | 2.0237 | 2.4449 | 3.0353 | 3.6808 | 4.3407 | 5.216 | 5.9357 | 6.6455 | 7.369 | 8.1291 | 8.9595 | 9.7546 | 10.5338 | 11.3129 | 14.1137 | 15.3777
South West | Iron Acton 132 kV | Bedminster | Primary Substation | 11 | Electric Engagement | 0.61169 | 1.0217 | 1.4464 | 2.0324 | 2.6094 | 3.208 | 3.8501 | 4.678 | 5.3485 | 5.9142 | 6.491 | 6.7996 | 7.0938 | 7.3805 | 7.6611 | 7.9134 | 9.1203 | 10.2408 | 1.3868 | 2.2525 | 3.1403 | 4.3818 | 5.5995 | 6.8561 | 8.1924 | 9.8985 | 11.2824 | 12.455 | 13.65 | 14.3066 | 14.9346 | 15.5464 | 16.1447 | 16.6856 | 19.2882 | 21.6889
South West | Iron Acton 132 kV | Bedminster | Primary Substation | 11 | Holistic Transition | 0.589 | 0.94142 | 1.368 | 1.7659 | 2.1697 | 2.6261 | 3.0924 | 3.679 | 4.1932 | 4.7295 | 5.3858 | 6.056 | 6.7179 | 7.3458 | 7.9468 | 8.3518 | 9.7199 | 10.8399 | 1.3626 | 2.1294 | 3.0578 | 3.9251 | 4.8024 | 5.7871 | 6.7811 | 8.0113 | 9.0927 | 10.2157 | 11.5781 | 12.9689 | 14.3436 | 15.6484 | 16.8982 | 17.7555 | 20.6897 | 23.1324
South West | Iron Acton 132 kV | Bedminster | Primary Substation | 11 | Hydrogen Evolution | 0.51062 | 0.79913 | 1.0879 | 1.4417 | 1.827 | 2.2426 | 2.6966 | 3.2889 | 3.7844 | 4.3005 | 4.883 | 5.4553 | 6.0035 | 6.5144 | 7.0009 | 7.3076 | 8.2769 | 9.0174 | 1.162 | 1.7688 | 2.3715 | 3.1245 | 3.9436 | 4.823 | 5.7764 | 7.0041 | 8.0279 | 9.0917 | 10.2883 | 11.4646 | 12.5887 | 13.6374 | 14.6369 | 15.2768 | 17.3421 | 18.9312
South West | Iron Acton 132 kV | Bishopsworth | Primary Substation | 11 | Counterfactual | 0.29733 | 0.37228 | 0.45879 | 0.55792 | 0.65998 | 0.77381 | 0.90067 | 1.1064 | 1.2689 | 1.4442 | 1.6259 | 1.8172 | 2.0305 | 2.2418 | 2.449 | 2.6558 | 3.363 | 3.6255 | 0.68123 | 0.84055 | 1.0227 | 1.2307 | 1.4447 | 1.683 | 1.9474 | 2.3707 | 2.7078 | 3.0712 | 3.4463 | 3.8396 | 4.2766 | 4.7094 | 5.1337 | 5.5569 | 7.0194 | 7.5855
South West | Iron Acton 132 kV | Bishopsworth | Primary Substation | 11 | Electric Engagement | 0.38854 | 0.56198 | 0.76738 | 1.0017 | 1.2625 | 1.5484 | 1.8871 | 2.3351 | 2.7182 | 3.0327 | 3.302 | 3.3995 | 3.4905 | 3.5761 | 3.6588 | 3.7354 | 4.0758 | 4.3888 | 0.88403 | 1.2541 | 1.6863 | 2.1802 | 2.7282 | 3.3257 | 4.0294 | 4.9494 | 5.7405 | 6.3933 | 6.9559 | 7.1738 | 7.379 | 7.5724 | 7.7595 | 7.9337 | 8.7208 | 9.4378
South West | Iron Acton 132 kV | Bishopsworth | Primary Substation | 11 | Holistic Transition | 0.3741 | 0.50924 | 0.65811 | 0.81594 | 0.99347 | 1.2063 | 1.4399 | 1.7732 | 2.0595 | 2.3584 | 2.6713 | 2.9892 | 3.3023 | 3.5938 | 3.8648 | 4.0274 | 4.4837 | 4.8437 | 0.86794 | 1.17 | 1.498 | 1.8448 | 2.232 | 2.6922 | 3.1912 | 3.8929 | 4.4971 | 5.1249 | 5.7798 | 6.4448 | 7.1004 | 7.7115 | 8.2807 | 8.6325 | 9.6739 | 10.5084
South West | Iron Acton 132 kV | Bishopsworth | Primary Substation | 11 | Hydrogen Evolution | 0.32564 | 0.42413 | 0.54796 | 0.68061 | 0.83181 | 1.0053 | 1.2123 | 1.5031 | 1.7606 | 2.0299 | 2.3121 | 2.59 | 2.8607 | 3.1109 | 3.3441 | 3.4649 | 3.756 | 3.999 | 0.74417 | 0.95537 | 1.2175 | 1.5 | 1.8211 | 2.1871 | 2.621 | 3.2214 | 3.7538 | 4.3092 | 4.8899 | 5.4619 | 6.0191 | 6.5351 | 7.0165 | 7.2731 | 7.9274 | 8.475
South West | Iron Acton 132 kV | Bower Ashton | Primary Substation | 11 | Counterfactual | 0.69782 | 0.75802 | 0.82267 | 0.89772 | 0.66672 | 0.77996 | 0.90616 | 1.0905 | 1.2434 | 1.4039 | 1.5544 | 1.7093 | 1.8788 | 2.0477 | 2.2122 | 2.3769 | 2.9722 | 3.2623 | 1.665 | 1.7922 | 1.9287 | 2.0868 | 1.4689 | 1.706 | 1.97 | 2.3514 | 2.6703 | 3.0059 | 3.318 | 3.6377 | 3.9855 | 4.3325 | 4.6699 | 5.0075 | 6.2431 | 6.8628
South West | Iron Acton 132 kV | Bower Ashton | Primary Substation | 11 | Electric Engagement | 0.76386 | 0.88908 | 1.0493 | 1.2509 | 1.1406 | 1.3956 | 1.6886 | 2.0667 | 2.3711 | 2.6284 | 2.8688 | 2.9846 | 3.0924 | 3.2013 | 3.305 | 3.4068 | 3.8933 | 4.2616 | 1.8122 | 2.0789 | 2.418 | 2.8444 | 2.4823 | 3.0173 | 3.6295 | 4.4124 | 5.0441 | 5.581 | 6.0845 | 6.3377 | 6.5747 | 6.8144 | 7.0424 | 7.2668 | 8.3407 | 9.1626
South West | Iron Acton 132 kV | Bower Ashton | Primary Substation | 11 | Holistic Transition | 0.75201 | 0.84884 | 0.9843 | 1.1341 | 0.97266 | 1.1775 | 1.4016 | 1.6769 | 1.922 | 2.1744 | 2.4423 | 2.7071 | 2.9636 | 3.2059 | 3.4339 | 3.5889 | 4.1244 | 4.4906 | 1.7968 | 2.0123 | 2.3099 | 2.6378 | 2.1804 | 2.6234 | 3.106 | 3.6902 | 4.212 | 4.7475 | 5.3097 | 5.865 | 6.4034 | 6.9108 | 7.3887 | 7.7206 | 8.9002 | 9.7222
South West | Iron Acton 132 kV | Bower Ashton | Primary Substation | 11 | Hydrogen Evolution | 0.72109 | 0.79574 | 0.89452 | 1.0162 | 0.82525 | 0.99553 | 1.186 | 1.4441 | 1.6829 | 1.9149 | 2.1555 | 2.388 | 2.6133 | 2.8244 | 3.0227 | 3.1496 | 3.535 | 3.8399 | 1.7171 | 1.8765 | 2.0844 | 2.3428 | 1.8117 | 2.1707 | 2.5711 | 3.107 | 3.6071 | 4.0904 | 4.588 | 5.0682 | 5.5335 | 5.9705 | 6.3813 | 6.6495 | 7.4929 | 8.1647
South West | Iron Acton 132 kV | Bradley Stoke | Primary Substation | 11 | Counterfactual | 0.76507 | 0.81053 | 0.86136 | 0.91745 | 0.97656 | 1.042 | 1.1194 | 1.2495 | 1.3575 | 1.471 | 1.5902 | 1.7154 | 1.8554 | 1.9979 | 2.1362 | 2.281 | 2.8687 | 3.2462 | 1.5906 | 1.6875 | 1.7962 | 1.9159 | 2.0403 | 2.177 | 2.3387 | 2.6081 | 2.8336 | 3.0707 | 3.3187 | 3.5784 | 3.8675 | 4.1618 | 4.4474 | 4.7468 | 5.9746 | 6.7827
South West | Iron Acton 132 kV | Bradley Stoke | Primary Substation | 11 | Electric Engagement | 0.81194 | 0.91111 | 1.0368 | 1.1792 | 1.3222 | 1.4745 | 1.6657 | 1.9334 | 2.1701 | 2.3724 | 2.5515 | 2.6469 | 2.7366 | 2.8261 | 2.9127 | 3.0039 | 3.4547 | 3.9316 | 1.6943 | 1.9081 | 2.1782 | 2.4839 | 2.7849 | 3.1017 | 3.4999 | 4.054 | 4.5475 | 4.9716 | 5.3496 | 5.5604 | 5.7597 | 5.9585 | 6.1511 | 6.3544 | 7.3619 | 8.4219
South West | Iron Acton 132 kV | Bradley Stoke | Primary Substation | 11 | Holistic Transition | 0.80127 | 0.87728 | 0.97327 | 1.0747 | 1.1736 | 1.287 | 1.435 | 1.6557 | 1.8552 | 2.0609 | 2.2717 | 2.4941 | 2.711 | 2.918 | 3.1145 | 3.2591 | 3.8266 | 4.3605 | 1.6782 | 1.8487 | 2.0624 | 2.2888 | 2.505 | 2.7495 | 3.0678 | 3.5369 | 3.963 | 4.4005 | 4.8464 | 5.3161 | 5.7742 | 6.2116 | 6.6274 | 6.9405 | 8.2003 | 9.3901
South West | Iron Acton 132 kV | Bradley Stoke | Primary Substation | 11 | Hydrogen Evolution | 0.78058 | 0.84425 | 0.92614 | 1.0145 | 1.1004 | 1.1908 | 1.3156 | 1.5024 | 1.6736 | 1.8521 | 2.0363 | 2.2243 | 2.4099 | 2.585 | 2.7533 | 2.8695 | 3.3074 | 3.7444 | 1.6245 | 1.7636 | 1.941 | 2.134 | 2.3164 | 2.5059 | 2.7679 | 3.1573 | 3.5164 | 3.8904 | 4.2742 | 4.6659 | 5.0528 | 5.4189 | 5.7708 | 6.0201 | 6.9852 | 7.9499
South West | Iron Acton 132 kV | Broadweir Primary | Primary Substation | 11 | Counterfactual | 0.15265 | 0.15772 | 0.16304 | 0.16959 | 0.19022 | 0.21482 | 0.24286 | 0.27943 | 0.32031 | 0.35972 | 0.38164 | 0.39473 | 0.40915 | 0.42355 | 0.43756 | 0.45168 | 0.49934 | 0.52184 | 0.30703 | 0.31776 | 0.32886 | 0.34246 | 0.38658 | 0.44028 | 0.50216 | 0.58274 | 0.67557 | 0.76878 | 0.81812 | 0.84489 | 0.87429 | 0.90364 | 0.93218 | 0.96095 | 1.0589 | 1.1062
South West | Iron Acton 132 kV | Broadweir Primary | Primary Substation | 11 | Electric Engagement | 0.15809 | 0.1689 | 0.18227 | 0.2248 | 0.28458 | 0.36053 | 0.44793 | 0.52304 | 0.57047 | 0.59291 | 0.6094 | 0.61643 | 0.62265 | 0.6284 | 0.63355 | 0.63795 | 0.65619 | 0.67276 | 0.31905 | 0.34212 | 0.37008 | 0.46506 | 0.60241 | 0.77949 | 0.98363 | 1.1571 | 1.2653 | 1.3131 | 1.3473 | 1.3627 | 1.3764 | 1.3892 | 1.4006 | 1.4105 | 1.4526 | 1.4906
South West | Iron Acton 132 kV | Broadweir Primary | Primary Substation | 11 | Holistic Transition | 0.15694 | 0.16549 | 0.19356 | 0.23584 | 0.29053 | 0.3607 | 0.42089 | 0.49429 | 0.53072 | 0.54917 | 0.56837 | 0.58693 | 0.60534 | 0.62234 | 0.638 | 0.64778 | 0.67414 | 0.69717 | 0.31744 | 0.33665 | 0.39982 | 0.49694 | 0.62443 | 0.78984 | 0.93327 | 1.1082 | 1.1921 | 1.2306 | 1.2706 | 1.3093 | 1.3478 | 1.3833 | 1.4161 | 1.4372 | 1.4971 | 1.5497
South West | Iron Acton 132 kV | Broadweir Primary | Primary Substation | 11 | Hydrogen Evolution | 0.15462 | 0.16112 | 0.16945 | 0.20262 | 0.25106 | 0.31428 | 0.38657 | 0.47499 | 0.51909 | 0.54095 | 0.56003 | 0.57859 | 0.59633 | 0.61287 | 0.62807 | 0.63664 | 0.6551 | 0.67191 | 0.31135 | 0.32527 | 0.34267 | 0.41752 | 0.52999 | 0.6786 | 0.84888 | 1.0564 | 1.159 | 1.2054 | 1.2444 | 1.2824 | 1.3187 | 1.3526 | 1.3838 | 1.4018 | 1.4425 | 1.4793
South West | Iron Acton 132 kV | Clifton | Primary Substation | 11 | Counterfactual | 1.3415 | 1.4553 | 1.6006 | 1.7514 | 1.9241 | 2.1139 | 2.3132 | 2.6209 | 2.8711 | 3.137 | 3.4122 | 3.6982 | 4.0176 | 3.2694 | 3.5822 | 3.8923 | 4.9868 | 5.4709 | 3.2655 | 3.5079 | 3.811 | 4.1264 | 4.4865 | 4.8819 | 5.2958 | 5.9279 | 6.4467 | 6.9981 | 7.5654 | 8.1527 | 8.8063 | 6.7893 | 7.4294 | 8.0636 | 10.3211 | 11.3492
South West | Iron Acton 132 kV | Clifton | Primary Substation | 11 | Electric Engagement | 1.4629 | 1.708 | 2.0248 | 2.3904 | 2.7701 | 3.1793 | 3.6699 | 4.3234 | 4.8672 | 5.3202 | 5.7489 | 5.9565 | 6.1452 | 5.2621 | 5.4419 | 5.609 | 6.3689 | 7.1011 | 3.5345 | 4.0611 | 4.7241 | 5.4925 | 6.2874 | 7.1412 | 8.163 | 9.5102 | 10.6327 | 11.5716 | 12.462 | 12.9094 | 13.3189 | 11.0514 | 11.4416 | 11.8058 | 13.4717 | 15.066
South West | Iron Acton 132 kV | Clifton | Primary Substation | 11 | Holistic Transition | 1.4419 | 1.6407 | 1.895 | 2.1341 | 2.3893 | 2.6999 | 3.0489 | 3.54 | 3.9606 | 4.3946 | 4.8894 | 5.396 | 5.8924 | 5.2987 | 5.7363 | 6.0283 | 6.9717 | 7.7385 | 3.5096 | 3.9571 | 4.5109 | 5.0322 | 5.5859 | 6.2565 | 7.0022 | 8.0363 | 8.9222 | 9.8312 | 10.8615 | 11.9155 | 12.9494 | 11.2695 | 12.1832 | 12.805 | 14.8729 | 16.5724
South West | Iron Acton 132 kV | Clifton | Primary Substation | 11 | Hydrogen Evolution | 1.381 | 1.5293 | 1.7354 | 1.9495 | 2.1893 | 2.4609 | 2.7803 | 3.2313 | 3.6084 | 4.0073 | 4.4436 | 4.8807 | 5.3073 | 4.6372 | 5.0121 | 5.2411 | 5.9055 | 6.45 | 3.3525 | 3.6724 | 4.1035 | 4.5559 | 5.0616 | 5.633 | 6.302 | 7.2381 | 8.0168 | 8.8372 | 9.7323 | 10.6291 | 11.5043 | 9.6522 | 10.4236 | 10.9028 | 12.3316 | 13.509
South West | Iron Acton 132 kV | Cotham Primary | Primary Substation | 11 | Counterfactual | 4.0151 | 4.0152 | 4.0153 | 4.0153 | 4.0154 | 4.0155 | 4.0156 | 4.0158 | 4.0159 | 4.0161 | 4.0162 | 4.0164 | 4.0166 | 4.0168 | 4.0169 | 4.0171 | 4.0176 | 4.0176 | 10.0378 | 10.0379 | 10.0381 | 10.0382 | 10.0383 | 10.0385 | 10.0387 | 10.0391 | 10.0393 | 10.0397 | 10.04 | 10.0404 | 10.0407 | 10.0411 | 10.0414 | 10.0417 | 10.0428 | 10.0428
South West | Iron Acton 132 kV | Cotham Primary | Primary Substation | 11 | Electric Engagement | 4.0153 | 4.0154 | 4.0156 | 4.0158 | 4.016 | 4.0162 | 4.0165 | 4.0169 | 4.0173 | 4.0175 | 4.0177 | 4.0177 | 4.0177 | 4.0177 | 4.0177 | 4.0177 | 4.0178 | 4.0179 | 10.0383 | 10.0385 | 10.0388 | 10.0392 | 10.0396 | 10.0401 | 10.0407 | 10.0415 | 10.0422 | 10.0426 | 10.043 | 10.043 | 10.043 | 10.043 | 10.043 | 10.043 | 10.0433 | 10.0436
South West | Iron Acton 132 kV | Cotham Primary | Primary Substation | 11 | Holistic Transition | 4.0153 | 4.0153 | 4.0154 | 4.0156 | 4.0157 | 4.0158 | 4.016 | 4.0162 | 4.0164 | 4.0167 | 4.0169 | 4.0171 | 4.0173 | 4.0175 | 4.0177 | 4.0177 | 1.069 | 1.0691 | 10.0381 | 10.0383 | 10.0385 | 10.0387 | 10.0389 | 10.0392 | 10.0395 | 10.04 | 10.0404 | 10.0409 | 10.0414 | 10.0418 | 10.0423 | 10.0426 | 10.043 | 10.0431 | 2.6712 | 2.6715
South West | Iron Acton 132 kV | Cotham Primary | Primary Substation | 11 | Hydrogen Evolution | 4.0151 | 4.0152 | 4.0153 | 4.0154 | 4.0155 | 4.0157 | 4.0158 | 4.0161 | 4.0163 | 4.0165 | 4.0168 | 4.017 | 4.0172 | 4.0174 | 4.0176 | 4.0177 | 4.0177 | 4.0177 | 10.0378 | 10.0379 | 10.0382 | 10.0384 | 10.0386 | 10.0389 | 10.0392 | 10.0397 | 10.0401 | 10.0406 | 10.0411 | 10.0415 | 10.042 | 10.0424 | 10.0428 | 10.0429 | 10.0431 | 10.0431
South West | Iron Acton 132 kV | Cribbs Causeway | Primary Substation | 11 | Counterfactual | 0.37952 | 0.38847 | 0.39362 | 0.39997 | 0.40645 | 0.41372 | 0.42378 | 0.43914 | 0.45424 | 0.47034 | 0.48609 | 0.50221 | 0.52423 | 0.54365 | 0.56221 | 0.58345 | 0.68486 | 0.79104 | 0.92166 | 0.94203 | 0.95442 | 0.9692 | 0.98434 | 1.0012 | 1.0242 | 1.0584 | 1.0921 | 1.1283 | 1.1634 | 1.199 | 1.2476 | 1.291 | 1.3323 | 1.3781 | 1.5983 | 1.828
South West | Iron Acton 132 kV | Cribbs Causeway | Primary Substation | 11 | Electric Engagement | 0.38697 | 0.40406 | 0.41729 | 0.43135 | 0.44569 | 0.46045 | 0.48053 | 0.50665 | 0.53706 | 0.57212 | 0.60652 | 0.63247 | 0.66003 | 0.68451 | 0.71182 | 0.73813 | 0.89071 | 1.0348 | 0.94002 | 0.98082 | 1.0125 | 1.0461 | 1.0801 | 1.1147 | 1.161 | 1.2204 | 1.2899 | 1.3714 | 1.4498 | 1.5082 | 1.5697 | 1.6247 | 1.6855 | 1.7447 | 2.0856 | 2.409
South West | Iron Acton 132 kV | Cribbs Causeway | Primary Substation | 11 | Holistic Transition | 0.38991 | 0.41001 | 0.42526 | 0.44092 | 0.45751 | 0.47823 | 0.50261 | 0.53593 | 0.56787 | 0.60314 | 0.63834 | 0.67707 | 0.70869 | 0.7413 | 0.77469 | 0.80958 | 0.76336 | 0.93593 | 0.9476 | 0.99618 | 1.0333 | 1.0713 | 1.1115 | 1.1604 | 1.2171 | 1.2933 | 1.3662 | 1.446 | 1.5268 | 1.6148 | 1.6866 | 1.7594 | 1.8339 | 1.9117 | 1.749 | 2.1358
South West | Iron Acton 132 kV | Cribbs Causeway | Primary Substation | 11 | Hydrogen Evolution | 0.38251 | 0.39497 | 0.40318 | 0.41278 | 0.42263 | 0.43345 | 0.45093 | 0.4748 | 0.50073 | 0.53212 | 0.56413 | 0.59062 | 0.61717 | 0.63994 | 0.66594 | 0.6931 | 0.82958 | 0.96583 | 0.92897 | 0.95833 | 0.97762 | 0.99999 | 1.023 | 1.048 | 1.0877 | 1.1412 | 1.1994 | 1.2715 | 1.3438 | 1.4033 | 1.4614 | 1.5117 | 1.5686 | 1.6281 | 1.9302 | 2.2316
South West | Iron Acton 132 kV | Eastville | Primary Substation | 11 | Counterfactual | 0.34328 | 0.44575 | 0.56043 | 0.69943 | 0.83867 | 0.99278 | 1.1646 | 1.4438 | 1.6638 | 1.9017 | 2.151 | 2.4145 | 2.7081 | 2.9982 | 3.2821 | 3.5662 | 4.5498 | 4.9461 | 0.77241 | 0.99149 | 1.2338 | 1.5261 | 1.818 | 2.1401 | 2.4979 | 3.072 | 3.5276 | 4.0199 | 4.5352 | 5.078 | 5.6804 | 6.2755 | 6.858 | 7.4403 | 9.4789 | 10.3318
South West | Iron Acton 132 kV | Eastville | Primary Substation | 11 | Electric Engagement | 0.47033 | 0.70083 | 0.9841 | 1.296 | 1.64 | 2.0212 | 2.477 | 3.0868 | 3.6125 | 4.0472 | 4.4215 | 4.5682 | 4.7049 | 4.8331 | 4.9564 | 5.0703 | 5.5767 | 6.0482 | 1.0565 | 1.5509 | 2.148 | 2.8021 | 3.5203 | 4.313 | 5.2578 | 6.5103 | 7.598 | 8.502 | 9.2858 | 9.6124 | 9.9195 | 10.2085 | 10.4864 | 10.745 | 11.9153 | 12.9919
South West | Iron Acton 132 kV | Eastville | Primary Substation | 11 | Holistic Transition | 0.45437 | 0.63599 | 0.83943 | 1.0509 | 1.2892 | 1.5774 | 1.8951 | 2.3522 | 2.749 | 3.1649 | 3.6006 | 4.0433 | 4.4797 | 4.8873 | 5.2676 | 5.5024 | 6.1874 | 6.7218 | 1.0432 | 1.4524 | 1.8997 | 2.3622 | 2.8797 | 3.5001 | 4.177 | 5.1378 | 5.976 | 6.8507 | 7.7641 | 8.6921 | 9.6075 | 10.4637 | 11.2639 | 11.7727 | 13.3318 | 14.5683
South West | Iron Acton 132 kV | Eastville | Primary Substation | 11 | Hydrogen Evolution | 0.38443 | 0.51576 | 0.68016 | 0.85313 | 1.0491 | 1.2767 | 1.5528 | 1.9453 | 2.3011 | 2.6717 | 3.0585 | 3.4391 | 3.8111 | 4.1534 | 4.4736 | 4.645 | 5.0739 | 5.4437 | 0.86497 | 1.1483 | 1.4967 | 1.862 | 2.2739 | 2.7503 | 3.3261 | 4.1351 | 4.8714 | 5.6367 | 6.4337 | 7.2187 | 7.9858 | 8.693 | 9.3558 | 9.7207 | 10.6849 | 11.5149
South West | Iron Acton 132 kV | Emersons Green | Primary Substation | 11 | Counterfactual | 0.81092 | 0.83906 | 0.85671 | 0.87106 | 0.8871 | 0.9008 | 0.9157 | 0.93432 | 0.95116 | 0.97023 | 0.98746 | 1.0026 | 1.0188 | 1.0296 | 1.0398 | 1.0501 | 1.0962 | 1.1291 | 1.6418 | 1.7048 | 1.7465 | 1.7796 | 1.8165 | 1.8466 | 1.8796 | 1.9205 | 1.9579 | 2.0008 | 2.0389 | 2.0716 | 2.1061 | 2.1293 | 2.1509 | 2.1729 | 2.2745 | 2.3498
South West | Iron Acton 132 kV | Emersons Green | Primary Substation | 11 | Electric Engagement | 0.81965 | 0.88341 | 0.93236 | 0.97279 | 1.0145 | 1.0416 | 1.0689 | 1.1013 | 1.1309 | 1.1593 | 1.1879 | 1.2094 | 1.2325 | 1.2493 | 1.2657 | 1.2822 | 1.3573 | 1.4067 | 1.6628 | 1.8137 | 1.932 | 2.0283 | 2.1273 | 2.1879 | 2.2483 | 2.3192 | 2.3846 | 2.4478 | 2.5121 | 2.5613 | 2.6142 | 2.6535 | 2.6916 | 2.7299 | 2.9032 | 3.0222
South West | Iron Acton 132 kV | Emersons Green | Primary Substation | 11 | Holistic Transition | 0.81901 | 0.88169 | 0.92968 | 0.9687 | 1.0111 | 1.0385 | 1.069 | 1.1069 | 1.141 | 1.1748 | 1.2034 | 1.2299 | 1.2574 | 1.2743 | 1.2903 | 1.3032 | 1.3611 | 1.3876 | 1.6618 | 1.811 | 1.9282 | 2.0225 | 2.1249 | 2.188 | 2.2586 | 2.3463 | 2.4249 | 2.5026 | 2.5667 | 2.6257 | 2.6872 | 2.7242 | 2.759 | 2.7878 | 2.9196 | 2.9805
South West | Iron Acton 132 kV | Emersons Green | Primary Substation | 11 | Hydrogen Evolution | 0.81773 | 0.87876 | 0.91881 | 0.95094 | 0.98532 | 1.0052 | 1.0251 | 1.0487 | 1.0747 | 1.104 | 1.1286 | 1.1512 | 1.1742 | 1.1904 | 1.2057 | 1.2176 | 1.2739 | 1.3214 | 1.6585 | 1.8035 | 1.9007 | 1.9776 | 2.0598 | 2.1042 | 2.1487 | 2.2005 | 2.259 | 2.3253 | 2.38 | 2.4296 | 2.48 | 2.5154 | 2.5491 | 2.5757 | 2.7072 | 2.8192
South West | Iron Acton 132 kV | Feeder Rd 11kv | Primary Substation | 11 | Counterfactual | 1.1298 | 1.3968 | 1.9427 | 2.25 | 3.1129 | 3.5501 | 4.0245 | 4.7125 | 5.2506 | 5.8099 | 6.3828 | 6.9807 | 7.6474 | 8.309 | 8.9406 | 9.5679 | 11.5574 | 12.1447 | 2.5415 | 3.1107 | 4.2342 | 4.8811 | 6.8736 | 7.7896 | 8.781 | 10.1966 | 11.3111 | 12.4673 | 13.6481 | 14.8753 | 16.2383 | 17.5904 | 18.8795 | 20.1588 | 24.2474 | 25.5076
South West | Iron Acton 132 kV | Feeder Rd 11kv | Primary Substation | 11 | Electric Engagement | 1.8846 | 2.4669 | 3.4211 | 4.3578 | 5.3119 | 6.3273 | 7.4761 | 8.9677 | 10.1091 | 11.0369 | 11.8186 | 12.0506 | 12.2468 | 12.431 | 12.6301 | 12.8304 | 13.6981 | 14.4825 | 4.347 | 5.5989 | 7.5835 | 9.5638 | 11.5731 | 13.7051 | 16.1 | 19.1688 | 21.5141 | 23.4296 | 25.0531 | 25.5715 | 26.0173 | 26.4376 | 26.8867 | 27.3371 | 29.3308 | 31.109
South West | Iron Acton 132 kV | Feeder Rd 11kv | Primary Substation | 11 | Holistic Transition | 1.8423 | 2.3064 | 3.2078 | 3.8434 | 4.5211 | 5.2555 | 6.0472 | 7.0097 | 7.8219 | 8.6822 | 9.5837 | 10.49 | 11.371 | 12.1935 | 12.9867 | 13.4546 | 14.6432 | 15.4669 | 4.3055 | 5.3516 | 7.2795 | 8.6723 | 10.1521 | 11.7439 | 13.4391 | 15.4512 | 17.1539 | 18.9495 | 20.8239 | 22.7077 | 24.5398 | 26.2522 | 27.905 | 28.9058 | 31.5968 | 33.5157
South West | Iron Acton 132 kV | Feeder Rd 11kv | Primary Substation | 11 | Hydrogen Evolution | 1.6821 | 2.0324 | 2.7009 | 3.2144 | 3.7954 | 4.427 | 5.124 | 6.0703 | 6.8781 | 7.7245 | 8.6019 | 9.456 | 10.2813 | 11.0263 | 11.7107 | 12.0343 | 12.7085 | 13.1741 | 3.8959 | 4.655 | 6.0411 | 7.1341 | 8.3691 | 9.7068 | 11.1699 | 13.1208 | 14.7863 | 16.5275 | 18.3267 | 20.0767 | 21.7675 | 23.2935 | 24.6969 | 25.374 | 26.8671 | 27.9092
South West | Iron Acton 132 kV | Feeder Road B | Primary Substation | 11 | Counterfactual | 0.072961 | 0.21677 | 0.24692 | 0.28147 | 0.32272 | 0.36931 | 0.42231 | 0.50238 | 0.57106 | 0.6547 | 0.7367 | 0.81553 | 0.88955 | 0.96292 | 1.0341 | 1.1058 | 1.3683 | 1.5094 | 0.16246 | 0.4549 | 0.51937 | 0.59179 | 0.67861 | 0.77701 | 0.88927 | 1.0571 | 1.2051 | 1.3883 | 1.5659 | 1.7335 | 1.8851 | 2.0353 | 2.1811 | 2.3278 | 2.8703 | 3.1675
South West | Iron Acton 132 kV | Feeder Road B | Primary Substation | 11 | Electric Engagement | 0.21273 | 0.27576 | 0.35028 | 0.45211 | 0.54712 | 0.6624 | 0.80512 | 0.9859 | 1.1326 | 1.2598 | 1.3693 | 1.4137 | 1.4532 | 1.4905 | 1.5257 | 1.5565 | 1.6885 | 1.8045 | 0.44677 | 0.5856 | 0.74524 | 0.96266 | 1.1668 | 1.4171 | 1.7286 | 2.1172 | 2.4317 | 2.707 | 2.9445 | 3.0411 | 3.1282 | 3.2106 | 3.2887 | 3.3578 | 3.662 | 3.9275
South West | Iron Acton 132 kV | Feeder Road B | Primary Substation | 11 | Holistic Transition | 0.20934 | 0.26504 | 0.34284 | 0.40321 | 0.47716 | 0.57461 | 0.68395 | 0.8414 | 0.97553 | 1.1003 | 1.2035 | 1.3079 | 1.4098 | 1.5053 | 1.5952 | 1.6553 | 1.8341 | 1.977 | 0.4439 | 0.57252 | 0.74632 | 0.88084 | 1.0463 | 1.2652 | 1.51 | 1.8593 | 2.1576 | 2.43 | 2.6465 | 2.8653 | 3.0794 | 3.2802 | 3.4696 | 3.5994 | 4.0039 | 4.3309
South West | Iron Acton 132 kV | Feeder Road B | Primary Substation | 11 | Hydrogen Evolution | 0.19744 | 0.23794 | 0.28818 | 0.34506 | 0.41509 | 0.50355 | 0.60997 | 0.75808 | 0.87759 | 0.99789 | 1.1163 | 1.2132 | 1.3064 | 1.3924 | 1.4726 | 1.5213 | 1.6468 | 1.7593 | 0.41284 | 0.50261 | 0.61112 | 0.7333 | 0.88549 | 1.0799 | 1.3147 | 1.6395 | 1.8983 | 2.1573 | 2.4097 | 2.6092 | 2.8013 | 2.9787 | 3.1444 | 3.2472 | 3.5252 | 3.773
South West | Iron Acton 132 kV | Filton Dc | Primary Substation | 11 | Counterfactual | 2.9764 | 3.3584 | 3.5723 | 3.8475 | 4.0508 | 4.2751 | 4.5394 | 4.9787 | 5.3348 | 5.7018 | 6.0807 | 6.4829 | 6.9271 | 7.3752 | 7.8126 | 8.2571 | 9.8832 | 10.7177 | 6.8904 | 7.6716 | 8.1136 | 8.7245 | 9.1464 | 9.6111 | 10.1597 | 11.0651 | 11.8047 | 12.5664 | 13.3509 | 14.1809 | 15.0945 | 16.0157 | 16.9149 | 17.8293 | 21.211 | 23.0045
South West | Iron Acton 132 kV | Filton Dc | Primary Substation | 11 | Electric Engagement | 3.1581 | 3.7203 | 4.2697 | 4.7307 | 5.24 | 5.7897 | 6.4509 | 7.3446 | 8.1123 | 8.7504 | 9.3021 | 9.5395 | 9.7554 | 9.9647 | 10.1663 | 8.8316 | 9.7991 | 10.8175 | 7.2952 | 8.4651 | 9.6554 | 10.6241 | 11.6907 | 12.8374 | 14.2106 | 16.0509 | 17.6426 | 18.9729 | 20.1308 | 20.6601 | 21.1461 | 21.618 | 22.0728 | 18.6868 | 20.8875 | 23.1814
South West | Iron Acton 132 kV | Filton Dc | Primary Substation | 11 | Holistic Transition | 3.126 | 3.6989 | 4.0512 | 4.3637 | 4.7111 | 5.1088 | 5.5794 | 6.2635 | 6.8661 | 7.4903 | 8.1392 | 8.8021 | 7.9127 | 8.5255 | 9.0929 | 9.4724 | 12.288 | 13.4408 | 7.2547 | 8.5052 | 9.2698 | 9.9522 | 10.7067 | 11.5644 | 12.571 | 14.0164 | 15.2951 | 16.614 | 17.9793 | 19.3735 | 16.8923 | 18.183 | 19.3808 | 20.2047 | 26.9335 | 29.55
South West | Iron Acton 132 kV | Filton Dc | Primary Substation | 11 | Hydrogen Evolution | 3.0388 | 3.4729 | 3.861 | 4.1232 | 4.4204 | 4.757 | 5.1828 | 5.7981 | 6.3276 | 6.8849 | 7.4663 | 8.0515 | 8.6199 | 9.1562 | 9.6514 | 10.7477 | 11.6766 | 12.5406 | 7.0292 | 7.929 | 8.7812 | 9.336 | 9.9634 | 10.6702 | 11.5625 | 12.8385 | 13.9407 | 15.0978 | 16.3004 | 17.5119 | 18.6888 | 19.8014 | 20.8305 | 23.4612 | 25.5281 | 27.4599
South West | Iron Acton 132 kV | Hewlett Packard | Primary Substation | 11 | Counterfactual | 0.44775 | 0.5007 | 0.59575 | 0.69126 | 0.81572 | 0.92123 | 1.0194 | 1.1313 | 1.2337 | 1.34 | 1.4451 | 1.5635 | 1.6657 | 1.7698 | 1.8721 | 1.9734 | 2.3207 | 2.4609 | 1.0618 | 1.1737 | 1.3733 | 1.5727 | 1.8337 | 2.0556 | 2.2623 | 2.4967 | 2.7126 | 2.9376 | 3.16 | 3.4181 | 3.6327 | 3.8505 | 4.0645 | 4.2767 | 5.0086 | 5.3116
South West | Iron Acton 132 kV | Hewlett Packard | Primary Substation | 11 | Electric Engagement | 0.46967 | 0.55475 | 0.6966 | 0.83928 | 1.0286 | 1.2006 | 1.3646 | 1.5502 | 1.7588 | 1.9236 | 2.0646 | 2.1506 | 2.2353 | 2.319 | 2.4046 | 2.4866 | 2.7936 | 2.9738 | 1.1104 | 1.2943 | 1.5995 | 1.9051 | 2.3129 | 2.6834 | 3.0345 | 3.427 | 3.8839 | 4.2409 | 4.5455 | 4.7356 | 4.9233 | 5.1088 | 5.298 | 5.4789 | 6.1586 | 6.5613
South West | Iron Acton 132 kV | Hewlett Packard | Primary Substation | 11 | Holistic Transition | 0.46497 | 0.5391 | 0.66616 | 0.79335 | 0.96296 | 1.1191 | 1.2665 | 1.4304 | 1.5961 | 1.7995 | 1.9491 | 2.0901 | 2.2261 | 2.3598 | 2.4917 | 2.5954 | 2.9419 | 3.1448 | 1.1037 | 1.2671 | 1.5444 | 1.8206 | 2.1913 | 2.5331 | 2.8546 | 3.2093 | 3.5713 | 4.0261 | 4.3471 | 4.6482 | 4.9389 | 5.2242 | 5.5062 | 5.732 | 6.4974 | 6.9504
South West | Iron Acton 132 kV | Hewlett Packard | Primary Substation | 11 | Hydrogen Evolution | 0.45469 | 0.52279 | 0.64119 | 0.75985 | 0.92065 | 1.0652 | 1.2003 | 1.3468 | 1.5116 | 1.6836 | 1.8276 | 1.9576 | 2.0884 | 2.2125 | 2.3339 | 2.4315 | 2.7349 | 2.9091 | 1.0772 | 1.2253 | 1.4805 | 1.7351 | 2.0835 | 2.3969 | 2.6885 | 3.0011 | 3.3623 | 3.7399 | 4.0484 | 4.3245 | 4.6016 | 4.8656 | 5.124 | 5.3352 | 6.0043 | 6.3906
South West | Iron Acton 132 kV | Keynsham West | Primary Substation | 11 | Counterfactual | 0.1637 | 0.20765 | 0.25294 | 0.29884 | 0.35044 | 0.41312 | 0.48231 | 0.5964 | 0.6841 | 0.77713 | 0.86598 | 0.95779 | 1.0594 | 1.1631 | 1.2635 | 1.3555 | 1.6702 | 1.7719 | 0.37117 | 0.46402 | 0.55926 | 0.65591 | 0.76421 | 0.89499 | 1.0391 | 1.2746 | 1.4569 | 1.65 | 1.8332 | 2.0214 | 2.2302 | 2.4433 | 2.6491 | 2.837 | 3.4866 | 3.7067
South West | Iron Acton 132 kV | Keynsham West | Primary Substation | 11 | Electric Engagement | 0.20673 | 0.29348 | 0.39671 | 0.50727 | 0.63242 | 0.76791 | 0.95419 | 1.1656 | 1.3418 | 1.4908 | 1.6172 | 1.6569 | 1.6923 | 1.7235 | 1.7566 | 1.7869 | 1.9149 | 2.0247 | 0.46702 | 0.65253 | 0.87107 | 1.1043 | 1.3667 | 1.6493 | 2.0401 | 2.4748 | 2.8397 | 3.1533 | 3.4196 | 3.5094 | 3.5905 | 3.663 | 3.7392 | 3.8094 | 4.1154 | 4.3744
South West | Iron Acton 132 kV | Keynsham West | Primary Substation | 11 | Holistic Transition | 0.1982 | 0.26058 | 0.33293 | 0.40842 | 0.49237 | 0.61808 | 0.72566 | 0.87365 | 1.0001 | 1.1354 | 1.2783 | 1.421 | 1.5556 | 1.679 | 1.7935 | 1.8578 | 2.015 | 2.1198 | 0.45495 | 0.59542 | 0.75538 | 0.92149 | 1.105 | 1.378 | 1.6092 | 1.9219 | 2.1904 | 2.4767 | 2.7786 | 3.0796 | 3.3619 | 3.6202 | 3.8605 | 4 | 4.3692 | 4.6221
South West | Iron Acton 132 kV | Keynsham West | Primary Substation | 11 | Hydrogen Evolution | 0.17703 | 0.23166 | 0.29319 | 0.35676 | 0.42851 | 0.51521 | 0.62937 | 0.7787 | 0.91099 | 1.0459 | 1.1857 | 1.3184 | 1.4441 | 1.5572 | 1.6654 | 1.7147 | 1.8235 | 1.9104 | 0.40088 | 0.51752 | 0.64745 | 0.78182 | 0.93292 | 1.1142 | 1.3533 | 1.6619 | 1.9362 | 2.2178 | 2.5077 | 2.7811 | 3.0387 | 3.2712 | 3.4938 | 3.5983 | 3.8462 | 4.0434
South West | Iron Acton 132 kV | Lockleaze | Primary Substation | 11 | Counterfactual | 0.3489 | 0.44871 | 0.55171 | 0.68739 | 0.83415 | 0.98846 | 1.1539 | 1.3964 | 1.5886 | 1.7956 | 2.0095 | 2.2274 | 2.4611 | 2.6942 | 2.923 | 3.1498 | 3.9334 | 4.2316 | 0.77165 | 0.98326 | 1.2004 | 1.4832 | 1.7909 | 2.1141 | 2.4597 | 2.9602 | 3.36 | 3.7903 | 4.2342 | 4.684 | 5.1637 | 5.6418 | 6.1112 | 6.5762 | 8.2005 | 8.8481
South West | Iron Acton 132 kV | Lockleaze | Primary Substation | 11 | Electric Engagement | 0.45176 | 0.65757 | 0.89936 | 1.2511 | 1.5743 | 1.9033 | 2.2944 | 2.8122 | 3.2323 | 3.5786 | 3.8747 | 3.9843 | 4.0854 | 4.1839 | 4.2755 | 4.3635 | 4.7465 | 5.131 | 1.0011 | 1.4413 | 1.9524 | 2.6947 | 3.375 | 4.0638 | 4.8782 | 5.9464 | 6.8156 | 7.5362 | 8.1566 | 8.4036 | 8.6335 | 8.8574 | 9.0666 | 9.2684 | 10.1557 | 11.0357
South West | Iron Acton 132 kV | Lockleaze | Primary Substation | 11 | Holistic Transition | 0.43687 | 0.60022 | 0.8343 | 1.0691 | 1.2915 | 1.5423 | 1.824 | 2.1921 | 2.5119 | 2.845 | 3.1904 | 3.5404 | 3.8884 | 4.2087 | 4.5028 | 4.6846 | 5.194 | 5.6124 | 0.98591 | 1.3505 | 1.8649 | 2.3749 | 2.8603 | 3.4042 | 4.0089 | 4.7863 | 5.4645 | 6.1675 | 6.8928 | 7.6268 | 8.3569 | 9.0294 | 9.6482 | 10.0421 | 11.2074 | 12.1769
South West | Iron Acton 132 kV | Lockleaze | Primary Substation | 11 | Hydrogen Evolution | 0.38233 | 0.51081 | 0.65511 | 0.85801 | 1.0596 | 1.2747 | 1.5159 | 1.8471 | 2.1409 | 2.4513 | 2.767 | 3.0722 | 3.3682 | 3.6474 | 3.9021 | 4.0381 | 4.3817 | 4.6774 | 0.84648 | 1.1233 | 1.4297 | 1.8592 | 2.2878 | 2.7431 | 3.2498 | 3.9359 | 4.5483 | 5.1939 | 5.8468 | 6.4765 | 7.0871 | 7.6638 | 8.1912 | 8.481 | 9.2552 | 9.9256
South West | Iron Acton 132 kV | Mangotsfield | Primary Substation | 11 | Counterfactual | 2.0487 | 2.1361 | 2.2356 | 2.3442 | 2.4749 | 2.6219 | 2.7865 | 3.0382 | 3.2403 | 3.4548 | 3.6724 | 3.8972 | 4.1457 | 4.3929 | 4.6334 | 3.8434 | 4.6798 | 4.9886 | 4.7501 | 4.9357 | 5.1459 | 5.3747 | 5.649 | 5.9569 | 6.301 | 6.82 | 7.2402 | 7.6863 | 8.1369 | 8.5997 | 9.1091 | 9.6154 | 10.1077 | 8.0223 | 9.7583 | 10.4311
South West | Iron Acton 132 kV | Mangotsfield | Primary Substation | 11 | Electric Engagement | 2.1596 | 2.3639 | 2.6163 | 2.8975 | 3.212 | 3.5576 | 3.9636 | 4.5051 | 4.9514 | 5.3183 | 5.6472 | 5.7665 | 5.874 | 5.9796 | 6.0794 | 5.1396 | 5.5731 | 5.9668 | 4.9969 | 5.4317 | 5.9657 | 6.5572 | 7.2161 | 7.9378 | 8.7809 | 9.8942 | 10.8166 | 11.5795 | 12.2696 | 12.5386 | 12.7836 | 13.0244 | 13.2527 | 10.8841 | 11.8897 | 12.7983
South West | Iron Acton 132 kV | Mangotsfield | Primary Substation | 11 | Holistic Transition | 2.1364 | 2.2918 | 2.469 | 2.6592 | 2.8794 | 3.1326 | 3.4188 | 3.8053 | 4.1422 | 4.5001 | 4.8813 | 5.2564 | 5.6226 | 5.9637 | 6.2809 | 5.4381 | 5.9931 | 6.4066 | 4.9633 | 5.3083 | 5.6987 | 6.1151 | 6.5947 | 7.1411 | 7.7545 | 8.57 | 9.2843 | 10.0392 | 10.8394 | 11.6269 | 12.3956 | 13.1112 | 13.7783 | 11.6076 | 12.8758 | 13.8376
South West | Iron Acton 132 kV | Mangotsfield | Primary Substation | 11 | Hydrogen Evolution | 2.0827 | 2.2031 | 2.3427 | 2.5009 | 2.6862 | 2.9014 | 3.152 | 3.5008 | 3.8136 | 4.1465 | 4.4859 | 4.8134 | 5.1307 | 5.425 | 5.6976 | 4.806 | 5.1853 | 5.4919 | 4.8258 | 5.0829 | 5.3786 | 5.7131 | 6.1046 | 6.5571 | 7.0811 | 7.8012 | 8.451 | 9.1416 | 9.8414 | 10.516 | 11.1691 | 11.7759 | 12.3387 | 10.0569 | 10.912 | 11.6095
South West | Iron Acton 132 kV | Patchway Primary | Primary Substation | 11 | Counterfactual | 0.25992 | 0.28457 | 0.31356 | 0.3416 | 0.37577 | 0.41201 | 0.4566 | 0.52991 | 0.59188 | 0.65601 | 0.7251 | 0.79728 | 0.87585 | 0.95883 | 1.037 | 1.1212 | 1.4562 | 1.6641 | 0.56068 | 0.61272 | 0.67358 | 0.73261 | 0.80404 | 0.87963 | 0.97253 | 1.124 | 1.2531 | 1.3865 | 1.5299 | 1.6796 | 1.842 | 2.0132 | 2.1747 | 2.3488 | 3.0484 | 3.4941
South West | Iron Acton 132 kV | Patchway Primary | Primary Substation | 11 | Electric Engagement | 0.28806 | 0.34075 | 0.40356 | 0.47361 | 0.5537 | 0.63722 | 0.74491 | 0.89884 | 1.0349 | 1.1486 | 1.2508 | 1.3031 | 1.3543 | 1.4023 | 1.452 | 1.5023 | 1.7659 | 2.043 | 0.62336 | 0.7352 | 0.86767 | 1.0148 | 1.182 | 1.3558 | 1.5798 | 1.898 | 2.1813 | 2.4195 | 2.6348 | 2.7504 | 2.8638 | 2.9706 | 3.0807 | 3.1927 | 3.7791 | 4.3935
South West | Iron Acton 132 kV | Patchway Primary | Primary Substation | 11 | Holistic Transition | 0.28253 | 0.32218 | 0.36962 | 0.41653 | 0.47091 | 0.53637 | 0.62114 | 0.74772 | 0.86076 | 0.98042 | 1.1052 | 1.2371 | 1.3663 | 1.4899 | 1.609 | 1.695 | 2.0309 | 2.3545 | 0.61552 | 0.70303 | 0.80648 | 0.90877 | 1.0261 | 1.1666 | 1.3478 | 1.6156 | 1.8561 | 2.1093 | 2.3725 | 2.6505 | 2.9226 | 3.1833 | 3.4348 | 3.6211 | 4.3655 | 5.0858
South West | Iron Acton 132 kV | Patchway Primary | Primary Substation | 11 | Hydrogen Evolution | 0.26867 | 0.30008 | 0.33909 | 0.37827 | 0.42493 | 0.47592 | 0.54653 | 0.65098 | 0.74825 | 0.84608 | 0.95085 | 1.0592 | 1.1652 | 1.2664 | 1.361 | 1.4266 | 1.6793 | 1.9314 | 0.58014 | 0.64707 | 0.72955 | 0.81264 | 0.91083 | 1.0175 | 1.1658 | 1.3836 | 1.5871 | 1.7915 | 2.0094 | 2.2352 | 2.4561 | 2.6673 | 2.8652 | 3.0059 | 3.5611 | 4.1161
South West | Iron Acton 132 kV | St Pauls Bsp 11kv | Bulk Supply Point | 11 | Counterfactual | 0.71492 | 0.88075 | 1.197 | 1.4137 | 1.7273 | 2.0546 | 2.3828 | 2.8378 | 3.2058 | 3.5909 | 3.986 | 4.3877 | 4.8204 | 5.2464 | 5.6626 | 6.0793 | 7.5252 | 8.1892 | 1.6148 | 1.9732 | 2.6328 | 3.0927 | 3.754 | 4.4426 | 5.1319 | 6.0702 | 6.8349 | 7.634 | 8.4516 | 9.2791 | 10.1663 | 11.0391 | 11.8922 | 12.7455 | 15.7283 | 17.1321
South West | Iron Acton 132 kV | St Pauls Bsp 11kv | Bulk Supply Point | 11 | Electric Engagement | 0.88967 | 1.2803 | 1.8665 | 2.5678 | 3.2539 | 3.9412 | 4.7038 | 5.6417 | 6.3425 | 6.9205 | 7.4202 | 7.6517 | 7.8779 | 8.0948 | 8.3038 | 8.4911 | 9.3239 | 10.0934 | 2.0057 | 2.8661 | 4.1085 | 5.6181 | 7.0877 | 8.5518 | 10.1628 | 12.1042 | 13.5508 | 14.7499 | 15.7927 | 16.2969 | 16.7912 | 17.2652 | 17.7224 | 18.1352 | 19.998 | 21.7053
South West | Iron Acton 132 kV | St Pauls Bsp 11kv | Bulk Supply Point | 11 | Holistic Transition | 0.86564 | 1.1998 | 1.8492 | 2.3625 | 2.8648 | 3.412 | 3.9887 | 4.6161 | 5.1494 | 5.7045 | 6.2858 | 6.8851 | 7.4953 | 8.0716 | 8.6114 | 8.9616 | 10.0424 | 10.9088 | 1.9812 | 2.7508 | 4.1675 | 5.308 | 6.4192 | 7.6188 | 8.8672 | 10.1854 | 11.3086 | 12.4718 | 13.6875 | 14.9395 | 16.2137 | 17.4183 | 18.5484 | 19.2986 | 21.7001 | 23.648
South West | Iron Acton 132 kV | St Pauls Bsp 11kv | Bulk Supply Point | 11 | Hydrogen Evolution | 0.78303 | 1.0387 | 1.4735 | 1.9122 | 2.3843 | 2.8555 | 3.3638 | 4.0046 | 4.5592 | 5.131 | 5.7124 | 6.2898 | 6.8537 | 7.38 | 7.8726 | 8.1705 | 8.9158 | 9.5401 | 1.7685 | 2.34 | 3.2656 | 4.2224 | 5.2463 | 6.2609 | 7.3443 | 8.6746 | 9.825 | 11.0077 | 12.2067 | 13.3952 | 14.5557 | 15.64 | 16.6568 | 17.2839 | 18.9063 | 20.2683
South West | Iron Acton 132 kV | Western Approach | Primary Substation | 11 | Counterfactual | 1.7712 | 1.8157 | 1.8928 | 1.9726 | 2.0668 | 2.1741 | 2.2983 | 2.4477 | 2.5957 | 2.6462 | 2.6949 | 2.7398 | 2.7873 | 2.8333 | 2.8807 | 2.9297 | 3.1316 | 3.2733 | 4.371 | 4.4765 | 4.6626 | 4.8562 | 5.0835 | 5.3434 | 5.6429 | 5.9983 | 6.3534 | 6.4645 | 6.57 | 6.6651 | 6.7649 | 6.8609 | 6.961 | 7.0641 | 7.4962 | 7.8081
South West | Iron Acton 132 kV | Western Approach | Primary Substation | 11 | Electric Engagement | 1.7852 | 1.9372 | 2.1518 | 2.417 | 2.7211 | 3.0715 | 3.4186 | 3.7727 | 4.1042 | 4.1763 | 4.2445 | 4.2812 | 4.3174 | 4.3508 | 4.3838 | 4.042 | 4.287 | 4.4875 | 4.4022 | 4.7714 | 5.2948 | 5.9433 | 6.6856 | 7.5421 | 8.3854 | 9.2362 | 10.034 | 10.1897 | 10.3374 | 10.4203 | 10.5016 | 10.5758 | 10.6504 | 9.7694 | 10.3359 | 10.8002
South West | Iron Acton 132 kV | Western Approach | Primary Substation | 11 | Holistic Transition | 1.7823 | 1.9284 | 2.1389 | 2.3945 | 2.6909 | 3.0367 | 3.3738 | 3.7239 | 4.0491 | 4.1244 | 4.1953 | 4.3786 | 4.4494 | 4.5161 | 4.5801 | 4.2638 | 4.5156 | 4.6968 | 4.398 | 4.7568 | 5.2744 | 5.9054 | 6.6359 | 7.4874 | 8.3128 | 9.1624 | 9.951 | 10.115 | 10.2665 | 10.6991 | 10.8509 | 10.9923 | 11.1294 | 10.3043 | 10.8788 | 11.2883
South West | Iron Acton 132 kV | Western Approach | Primary Substation | 11 | Hydrogen Evolution | 1.7757 | 1.9144 | 2.1074 | 2.3478 | 2.6272 | 2.9538 | 3.2791 | 3.6133 | 3.9256 | 3.995 | 4.0644 | 4.1284 | 4.1882 | 4.2421 | 4.2981 | 3.9335 | 4.1783 | 4.3764 | 4.381 | 4.7213 | 5.1948 | 5.7874 | 6.475 | 7.2797 | 8.0762 | 8.8868 | 9.645 | 9.7952 | 9.9429 | 10.0784 | 10.204 | 10.3164 | 10.4338 | 9.5004 | 10.069 | 10.524
South West | Iron Acton 132 kV | Whitchurch | Primary Substation | 11 | Counterfactual | 0.82853 | 1.0306 | 1.3102 | 1.5533 | 1.8082 | 2.0928 | 2.4064 | 2.8648 | 3.2524 | 3.6495 | 4.05 | 4.4613 | 4.9285 | 5.3829 | 5.7963 | 6.1864 | 7.5678 | 8.1587 | 1.9268 | 2.3532 | 2.9358 | 3.4458 | 3.9809 | 4.5772 | 5.2326 | 6.1809 | 6.9887 | 7.8172 | 8.6493 | 9.5005 | 10.4702 | 11.4151 | 12.2713 | 13.0703 | 15.9299 | 17.1981
South West | Iron Acton 132 kV | Whitchurch | Primary Substation | 11 | Electric Engagement | 1.0012 | 1.386 | 1.9236 | 2.5707 | 3.152 | 3.7461 | 4.4396 | 5.3429 | 6.142 | 6.8506 | 7.5441 | 7.9152 | 8.2165 | 8.4931 | 8.7619 | 9.0195 | 10.2162 | 11.2323 | 2.3123 | 3.135 | 4.2701 | 5.6809 | 6.9102 | 8.1568 | 9.6018 | 11.4683 | 13.1318 | 14.6262 | 16.0908 | 16.9 | 17.5591 | 18.1622 | 18.7454 | 19.3059 | 21.9117 | 24.1402
South West | Iron Acton 132 kV | Whitchurch | Primary Substation | 11 | Holistic Transition | 0.98077 | 1.2974 | 1.7585 | 2.1752 | 2.6003 | 3.0523 | 3.5547 | 4.2537 | 4.8838 | 5.5494 | 6.3213 | 7.0914 | 7.7622 | 8.3771 | 8.9555 | 9.3416 | 10.7059 | 11.6558 | 2.2967 | 2.9975 | 3.9989 | 4.9111 | 5.8407 | 6.8201 | 7.9009 | 9.3854 | 10.7271 | 12.1412 | 13.776 | 15.4068 | 16.8102 | 18.0922 | 19.2989 | 20.1206 | 23.1083 | 25.2134
South West | Iron Acton 132 kV | Whitchurch | Primary Substation | 11 | Hydrogen Evolution | 0.88577 | 1.1371 | 1.5002 | 1.8299 | 2.183 | 2.6 | 3.0733 | 3.7089 | 4.2847 | 4.9097 | 5.573 | 6.2298 | 6.8536 | 7.4146 | 7.8989 | 8.2026 | 9.1357 | 9.8576 | 2.0556 | 2.5954 | 3.3611 | 4.0646 | 4.8162 | 5.6982 | 6.6944 | 8.0167 | 9.2215 | 10.536 | 11.9228 | 13.2958 | 14.5933 | 15.7566 | 16.7559 | 17.3943 | 19.4128 | 21.0001
South West | Iron Acton 132 kV | Winterbourne | Primary Substation | 11 | Counterfactual | 0.77875 | 0.88159 | 0.98512 | 1.0655 | 1.1849 | 1.321 | 1.4777 | 1.657 | 1.8054 | 1.9639 | 2.1224 | 2.2824 | 2.4472 | 2.6047 | 2.7578 | 2.9136 | 3.4453 | 3.6471 | 1.6951 | 1.913 | 2.1316 | 2.3015 | 2.5531 | 2.8402 | 3.171 | 3.5444 | 3.856 | 4.1899 | 4.5216 | 4.8538 | 5.193 | 5.5166 | 5.8311 | 6.1509 | 7.2616 | 7.7085
South West | Iron Acton 132 kV | Winterbourne | Primary Substation | 11 | Electric Engagement | 0.8479 | 1.0347 | 1.2477 | 1.4693 | 1.7299 | 2.0193 | 2.3557 | 2.7344 | 3.0229 | 3.2604 | 3.4743 | 3.5547 | 3.6326 | 3.706 | 3.7773 | 3.8457 | 4.153 | 4.4271 | 1.8489 | 2.25 | 2.7062 | 3.1785 | 3.7328 | 4.348 | 5.0589 | 5.8464 | 6.4464 | 6.9444 | 7.3975 | 7.5821 | 7.7616 | 7.932 | 8.0974 | 8.2569 | 8.9768 | 9.6176
South West | Iron Acton 132 kV | Winterbourne | Primary Substation | 11 | Holistic Transition | 0.83347 | 0.98789 | 1.1754 | 1.3416 | 1.5465 | 1.78 | 2.0525 | 2.3144 | 2.5419 | 2.7789 | 3.0228 | 3.2635 | 3.4952 | 3.7073 | 3.9067 | 4.0253 | 4.3762 | 4.6389 | 1.828 | 2.1694 | 2.5833 | 2.9498 | 3.4006 | 3.9119 | 4.5062 | 5.0676 | 5.5574 | 6.0648 | 6.5812 | 7.0899 | 7.58 | 8.0271 | 8.4479 | 8.707 | 9.5176 | 10.1298
South West | Iron Acton 132 kV | Winterbourne | Primary Substation | 11 | Hydrogen Evolution | 0.80003 | 0.9329 | 1.0686 | 1.1967 | 1.36 | 1.5509 | 1.7763 | 2.0174 | 2.2384 | 2.4744 | 2.7094 | 2.9293 | 3.13 | 3.3173 | 3.4901 | 3.5853 | 3.8413 | 4.0614 | 1.7424 | 2.0294 | 2.3199 | 2.5936 | 2.9434 | 3.3524 | 3.8328 | 4.3358 | 4.8019 | 5.3001 | 5.7911 | 6.2476 | 6.663 | 7.0517 | 7.4107 | 7.6153 | 8.2044 | 8.7124
South West | Iron Acton 132 kV | Woodland Way | Primary Substation | 11 | Counterfactual | 1.6185 | 1.9132 | 2.2346 | 2.6176 | 3.0726 | 3.5744 | 4.0864 | 4.8858 | 5.5229 | 6.1998 | 6.8922 | 7.6157 | 8.4223 | 9.2245 | 10.0094 | 10.7865 | 13.4482 | 14.4398 | 3.4559 | 4.0826 | 4.7596 | 5.5635 | 6.5154 | 7.5632 | 8.6285 | 10.2712 | 11.5901 | 12.9901 | 14.4186 | 15.907 | 17.5601 | 19.2032 | 20.8108 | 22.4014 | 27.9046 | 30.0429
South West | Iron Acton 132 kV | Woodland Way | Primary Substation | 11 | Electric Engagement | 1.9692 | 2.6202 | 3.4081 | 4.3146 | 5.3557 | 6.4983 | 7.786 | 9.4993 | 10.9235 | 12.0951 | 13.115 | 13.4965 | 13.8413 | 14.1717 | 14.4897 | 14.7726 | 16.0043 | 17.2185 | 4.2374 | 5.6284 | 7.2865 | 9.1881 | 11.3667 | 13.7514 | 16.4201 | 19.938 | 22.8761 | 25.3051 | 27.4361 | 28.2872 | 29.0642 | 29.8103 | 30.5293 | 31.1738 | 34.0248 | 36.7956
South West | Iron Acton 132 kV | Woodland Way | Primary Substation | 11 | Holistic Transition | 1.9084 | 2.4065 | 2.9756 | 3.596 | 4.3339 | 5.1852 | 6.0788 | 7.2899 | 8.3463 | 9.4587 | 10.649 | 11.8497 | 13.0266 | 14.136 | 15.1585 | 15.7657 | 17.4715 | 18.8334 | 4.1609 | 5.2751 | 6.5221 | 7.8738 | 9.473 | 11.3062 | 13.2099 | 15.7492 | 17.9751 | 20.3088 | 22.8005 | 25.3129 | 27.777 | 30.102 | 32.2506 | 33.5646 | 37.455 | 40.611
South West | Iron Acton 132 kV | Woodland Way | Primary Substation | 11 | Hydrogen Evolution | 1.7276 | 2.1058 | 2.5613 | 3.0853 | 3.7187 | 4.4412 | 5.2326 | 6.3376 | 7.3172 | 8.3315 | 9.3885 | 10.4334 | 11.4433 | 12.3835 | 13.2537 | 13.7053 | 14.7941 | 15.7265 | 3.6993 | 4.5124 | 5.4761 | 6.5841 | 7.9219 | 9.4431 | 11.0949 | 13.3733 | 15.4015 | 17.4939 | 19.6684 | 21.818 | 23.896 | 25.833 | 27.6286 | 28.5859 | 31.0272 | 33.1226
South West | Landulph 132 kV | Adelaide Road | Primary Substation | 11 | Counterfactual | 0.097357 | 0.13632 | 0.24168 | 0.30707 | 0.36607 | 0.47346 | 0.62681 | 0.81779 | 1.0315 | 1.2063 | 1.364 | 1.4632 | 1.5769 | 1.6871 | 1.7981 | 1.9044 | 2.2068 | 2.3138 | 0.22044 | 0.30389 | 0.51977 | 0.65797 | 0.78148 | 1.0067 | 1.329 | 1.7286 | 2.1799 | 2.5484 | 2.8797 | 3.0848 | 3.3192 | 3.5465 | 3.7753 | 3.9945 | 4.6169 | 4.8456
South West | Landulph 132 kV | Adelaide Road | Primary Substation | 11 | Electric Engagement | 0.13301 | 0.21461 | 0.37836 | 0.51248 | 0.63701 | 0.86658 | 1.1241 | 1.4288 | 1.7476 | 1.9845 | 2.191 | 2.2715 | 2.3524 | 2.4339 | 2.5111 | 2.5819 | 2.8104 | 3.0326 | 0.29952 | 0.47744 | 0.81816 | 1.1054 | 1.3673 | 1.8587 | 2.408 | 3.0516 | 3.7325 | 4.2383 | 4.6777 | 4.8508 | 5.0258 | 5.2017 | 5.3688 | 5.5227 | 6.0198 | 6.4978
South West | Landulph 132 kV | Adelaide Road | Primary Substation | 11 | Holistic Transition | 0.12548 | 0.19511 | 0.33156 | 0.4349 | 0.52536 | 0.7206 | 0.93394 | 1.182 | 1.4601 | 1.6888 | 1.9061 | 2.075 | 2.2483 | 2.4134 | 2.5696 | 2.6796 | 2.9562 | 3.1799 | 0.28854 | 0.44611 | 0.73477 | 0.96289 | 1.159 | 1.5843 | 2.0471 | 2.5794 | 3.1807 | 3.6719 | 4.1349 | 4.4871 | 4.8495 | 5.1951 | 5.5229 | 5.7579 | 6.3611 | 6.8529
South West | Landulph 132 kV | Adelaide Road | Primary Substation | 11 | Hydrogen Evolution | 0.10873 | 0.16268 | 0.28872 | 0.3821 | 0.46284 | 0.64773 | 0.85231 | 1.0926 | 1.3631 | 1.5902 | 1.8063 | 1.9534 | 2.1 | 2.2413 | 2.3742 | 2.4597 | 2.6452 | 2.7826 | 0.24562 | 0.36372 | 0.62588 | 0.8287 | 1 | 1.3994 | 1.8398 | 2.3518 | 2.9335 | 3.4167 | 3.8725 | 4.1762 | 4.4799 | 4.773 | 5.0488 | 5.2295 | 5.6254 | 5.9204
South West | Landulph 132 kV | Alexandra Road | Primary Substation | 11 | Counterfactual | 0.37142 | 0.43455 | 0.53923 | 0.63657 | 0.74082 | 0.855 | 0.9959 | 1.188 | 1.3585 | 1.5212 | 1.6684 | 1.9412 | 2.0575 | 2.1748 | 2.2895 | 2.4001 | 2.7655 | 2.8697 | 0.89117 | 1.0255 | 1.245 | 1.4479 | 1.6654 | 1.9035 | 2.1976 | 2.5964 | 2.9528 | 3.2925 | 3.5984 | 4.1767 | 4.4145 | 4.6536 | 4.8872 | 5.1125 | 5.8637 | 6.0889
South West | Landulph 132 kV | Alexandra Road | Primary Substation | 11 | Electric Engagement | 0.42241 | 0.56542 | 0.75691 | 0.93989 | 1.1428 | 1.3628 | 1.6094 | 1.945 | 2.2727 | 2.5195 | 2.7449 | 3.0037 | 3.0728 | 3.1398 | 3.2087 | 3.2755 | 3.5928 | 3.884 | 1.0046 | 1.3166 | 1.7255 | 2.1138 | 2.5436 | 3.0091 | 3.5275 | 4.2287 | 4.9276 | 5.4492 | 5.9219 | 6.4881 | 6.6384 | 6.7845 | 6.9339 | 7.0788 | 7.7675 | 8.3985
South West | Landulph 132 kV | Alexandra Road | Primary Substation | 11 | Holistic Transition | 0.41201 | 0.53376 | 0.68455 | 0.82135 | 0.97307 | 1.1421 | 1.3284 | 1.5838 | 1.833 | 2.0874 | 2.3336 | 2.7055 | 2.8927 | 3.0715 | 3.2352 | 3.3417 | 3.6873 | 3.9498 | 0.98966 | 1.2625 | 1.5914 | 1.8884 | 2.217 | 2.582 | 2.9815 | 3.524 | 4.0582 | 4.6058 | 5.1208 | 5.9146 | 6.3027 | 6.6732 | 7.0131 | 7.2382 | 7.9891 | 8.5669
South West | Landulph 132 kV | Alexandra Road | Primary Substation | 11 | Hydrogen Evolution | 0.38758 | 0.49471 | 0.64052 | 0.76734 | 0.90973 | 1.069 | 1.2436 | 1.4902 | 1.7426 | 1.9798 | 2.2042 | 2.5528 | 2.7139 | 2.8675 | 3.0074 | 3.0886 | 3.328 | 3.5049 | 0.92722 | 1.1632 | 1.4747 | 1.7448 | 2.0481 | 2.3869 | 2.7563 | 3.2746 | 3.814 | 4.3165 | 4.782 | 5.5233 | 5.853 | 6.1671 | 6.4539 | 6.6228 | 7.1338 | 7.5155
South West | Landulph 132 kV | Alma Road | Primary Substation | 11 | Counterfactual | 0.43783 | 0.50486 | 0.57944 | 0.66197 | 0.75458 | 0.85714 | 0.9712 | 1.1523 | 1.2915 | 1.438 | 1.5889 | 1.7497 | 1.9397 | 2.1278 | 2.3115 | 2.4931 | 3.1014 | 3.2829 | 0.94441 | 1.0864 | 1.2432 | 1.416 | 1.6091 | 1.8224 | 2.0587 | 2.4291 | 2.7156 | 3.0164 | 3.3256 | 3.6544 | 4.0424 | 4.4263 | 4.8011 | 5.1715 | 6.4219 | 6.8132
South West | Landulph 132 kV | Alma Road | Primary Substation | 11 | Electric Engagement | 0.52444 | 0.67616 | 0.86472 | 1.074 | 1.3066 | 1.5587 | 1.8567 | 2.2603 | 2.5871 | 2.8515 | 3.0703 | 3.1277 | 3.1868 | 3.2409 | 3.2928 | 3.3402 | 3.5341 | 3.7456 | 1.1368 | 1.4592 | 1.8543 | 2.291 | 2.7741 | 3.2959 | 3.9094 | 4.7334 | 5.4028 | 5.9463 | 6.3987 | 6.5275 | 6.6621 | 6.786 | 6.905 | 7.0144 | 7.4756 | 7.9632
South West | Landulph 132 kV | Alma Road | Primary Substation | 11 | Holistic Transition | 0.5059 | 0.61612 | 0.74459 | 0.87934 | 1.0286 | 1.1961 | 1.3873 | 1.6546 | 1.8825 | 2.1243 | 2.3807 | 2.6428 | 2.9139 | 3.1659 | 3.3963 | 3.5246 | 3.8309 | 4.0596 | 1.1096 | 1.3547 | 1.6345 | 1.9266 | 2.2476 | 2.605 | 3.0089 | 3.5644 | 4.04 | 4.5426 | 5.0743 | 5.6172 | 6.1807 | 6.7052 | 7.186 | 7.4623 | 8.1706 | 8.7149
South West | Landulph 132 kV | Alma Road | Primary Substation | 11 | Hydrogen Evolution | 0.46485 | 0.55037 | 0.6579 | 0.77265 | 0.90262 | 1.05 | 1.2224 | 1.4726 | 1.6829 | 1.9065 | 2.1425 | 2.3749 | 2.6113 | 2.8299 | 3.0287 | 3.1236 | 3.301 | 3.4328 | 1.0043 | 1.1872 | 1.4139 | 1.6553 | 1.9275 | 2.2343 | 2.5912 | 3.1029 | 3.5341 | 3.9909 | 4.472 | 4.9455 | 5.4292 | 5.8767 | 6.2841 | 6.4835 | 6.8841 | 7.1863
South West | Landulph 132 kV | Armada Street | Primary Substation | 11 | Counterfactual | 0.13389 | 0.19464 | 0.2631 | 0.33667 | 0.41915 | 0.51021 | 0.6243 | 0.79459 | 0.92538 | 1.0627 | 1.2283 | 1.37 | 1.538 | 1.7045 | 1.8667 | 2.0268 | 2.5533 | 2.7196 | 0.29514 | 0.42432 | 0.56815 | 0.72228 | 0.89439 | 1.0838 | 1.3208 | 1.6698 | 1.9394 | 2.222 | 2.5645 | 2.8543 | 3.1975 | 3.5376 | 3.8687 | 4.1953 | 5.2796 | 5.6381
South West | Landulph 132 kV | Armada Street | Primary Substation | 11 | Electric Engagement | 0.20942 | 0.34926 | 0.52393 | 0.70986 | 0.91633 | 1.1462 | 1.417 | 1.7799 | 2.075 | 2.3137 | 2.5415 | 2.5893 | 2.6405 | 2.6875 | 2.7326 | 2.79 | 2.9698 | 3.1542 | 0.46293 | 0.76135 | 1.1282 | 1.5164 | 1.9457 | 2.4228 | 2.9817 | 3.7242 | 4.3301 | 4.8225 | 5.2987 | 5.4069 | 5.5242 | 5.6325 | 5.7365 | 5.8649 | 6.2929 | 6.7208
South West | Landulph 132 kV | Armada Street | Primary Substation | 11 | Holistic Transition | 0.19338 | 0.29772 | 0.41291 | 0.54237 | 0.67556 | 0.83172 | 1.0086 | 1.2516 | 1.4597 | 1.6796 | 1.941 | 2.1689 | 2.4055 | 2.6253 | 2.8261 | 2.9536 | 3.2259 | 3.4392 | 0.43953 | 0.67256 | 0.92379 | 1.2046 | 1.4914 | 1.8255 | 2.2002 | 2.7062 | 3.1417 | 3.6001 | 4.147 | 4.6199 | 5.1125 | 5.571 | 5.9908 | 6.264 | 6.8971 | 7.4029
South West | Landulph 132 kV | Armada Street | Primary Substation | 11 | Hydrogen Evolution | 0.15703 | 0.23639 | 0.33861 | 0.44 | 0.5547 | 0.69145 | 0.85093 | 1.0777 | 1.2698 | 1.4727 | 1.7155 | 1.9189 | 2.1269 | 2.3188 | 2.4935 | 2.5921 | 2.7474 | 2.8763 | 0.3466 | 0.5169 | 0.73296 | 0.94651 | 1.1869 | 1.4727 | 1.8039 | 2.2691 | 2.6642 | 3.08 | 3.5809 | 3.9957 | 4.4217 | 4.8151 | 5.1736 | 5.3796 | 5.7328 | 6.0258
South West | Landulph 132 kV | Buckwell Street | Primary Substation | 11 | Counterfactual | 0.19943 | 0.2235 | 0.25983 | 0.28692 | 0.31968 | 0.37609 | 0.457 | 0.55433 | 0.62471 | 0.67502 | 0.76312 | 0.81731 | 0.87946 | 0.93811 | 0.99831 | 1.055 | 1.2581 | 1.3424 | 0.45958 | 0.5115 | 0.58668 | 0.64335 | 0.71141 | 0.82873 | 0.99768 | 1.1999 | 1.3462 | 1.4494 | 1.6338 | 1.7445 | 1.8714 | 1.9911 | 2.1138 | 2.2296 | 2.6473 | 2.8255
South West | Landulph 132 kV | Buckwell Street | Primary Substation | 11 | Electric Engagement | 0.22039 | 0.27057 | 0.33759 | 0.39941 | 0.46948 | 0.56802 | 0.70524 | 0.86978 | 0.99252 | 1.0691 | 1.1983 | 1.2434 | 1.2902 | 1.3321 | 1.373 | 1.4119 | 1.5959 | 1.7703 | 0.506 | 0.61613 | 0.75595 | 0.88538 | 1.0313 | 1.2387 | 1.529 | 1.8737 | 2.1298 | 2.2879 | 2.5604 | 2.6552 | 2.7541 | 2.843 | 2.9298 | 3.0124 | 3.4063 | 3.7771
South West | Landulph 132 kV | Buckwell Street | Primary Substation | 11 | Holistic Transition | 0.21563 | 0.26019 | 0.30696 | 0.34974 | 0.39645 | 0.47743 | 0.59135 | 0.72254 | 0.82192 | 0.89454 | 1.0372 | 1.1373 | 1.237 | 1.334 | 1.4025 | 1.464 | 1.6815 | 1.88 | 0.49875 | 0.60028 | 0.70112 | 0.79396 | 0.89465 | 1.0686 | 1.3135 | 1.5926 | 1.8032 | 1.9546 | 2.2553 | 2.4615 | 2.6679 | 2.8685 | 3.0018 | 3.1314 | 3.5984 | 4.036
South West | Landulph 132 kV | Buckwell Street | Primary Substation | 11 | Hydrogen Evolution | 0.20653 | 0.23993 | 0.28943 | 0.32907 | 0.37017 | 0.44849 | 0.55797 | 0.68888 | 0.78776 | 0.8597 | 0.98987 | 1.0725 | 1.156 | 1.237 | 1.3097 | 1.3573 | 1.5128 | 1.6648 | 0.47513 | 0.54831 | 0.6509 | 0.73388 | 0.81982 | 0.985 | 1.2179 | 1.4934 | 1.7 | 1.847 | 2.1197 | 2.288 | 2.4586 | 2.6238 | 2.7724 | 2.8709 | 3.1976 | 3.5335
South West | Landulph 132 kV | Callington | Primary Substation | 11 | Counterfactual | 1.1462 | 1.1876 | 1.2348 | 1.2866 | 1.3476 | 1.4234 | 1.5094 | 1.6385 | 1.7433 | 1.8553 | 1.969 | 2.0847 | 2.2129 | 2.3404 | 2.4632 | 2.5872 | 3.0376 | 3.2482 | 2.8262 | 2.9147 | 3.0146 | 3.1243 | 3.2533 | 3.4125 | 3.5933 | 3.861 | 4.0801 | 4.3149 | 4.5513 | 4.7901 | 5.0534 | 5.3154 | 5.5675 | 5.8217 | 6.7587 | 7.2116
South West | Landulph 132 kV | Callington | Primary Substation | 11 | Electric Engagement | 1.1958 | 1.2902 | 1.413 | 1.5517 | 1.7062 | 1.8888 | 2.102 | 2.381 | 2.6196 | 2.8248 | 3.0096 | 3.0939 | 3.1755 | 3.2553 | 3.3175 | 3.3738 | 3.6812 | 3.8683 | 2.9364 | 3.1394 | 3.4013 | 3.6967 | 4.0238 | 4.4069 | 4.8521 | 5.4296 | 5.9252 | 6.3543 | 6.7433 | 6.9293 | 7.1105 | 7.2887 | 7.4222 | 7.5432 | 8.2142 | 8.6395
South West | Landulph 132 kV | Callington | Primary Substation | 11 | Holistic Transition | 1.1856 | 1.2586 | 1.3518 | 1.4508 | 1.5665 | 1.7136 | 1.8796 | 2.0993 | 2.2926 | 2.4976 | 2.7027 | 2.8842 | 3.0623 | 3.2272 | 3.3892 | 3.4909 | 3.8253 | 4.1673 | 2.9216 | 3.0862 | 3.2947 | 3.5148 | 3.7705 | 4.0898 | 4.4498 | 4.9201 | 5.335 | 5.7723 | 6.2049 | 6.5816 | 6.9519 | 7.2942 | 7.6325 | 7.8496 | 8.5847 | 9.3858
South West | Landulph 132 kV | Callington | Primary Substation | 11 | Hydrogen Evolution | 1.1623 | 1.216 | 1.2831 | 1.3621 | 1.4547 | 1.5703 | 1.7052 | 1.8888 | 2.0672 | 2.2545 | 2.4402 | 2.6165 | 2.7896 | 2.9485 | 3.0895 | 3.1632 | 3.3869 | 3.6791 | 2.8621 | 2.9782 | 3.1209 | 3.2894 | 3.4863 | 3.73 | 4.0134 | 4.3942 | 4.7665 | 5.1584 | 5.5434 | 5.9084 | 6.2665 | 6.5968 | 6.8852 | 7.038 | 7.5239 | 8.1944
South West | Landulph 132 kV | Eggbuckland | Primary Substation | 11 | Counterfactual | 0.64391 | 0.6914 | 0.74632 | 0.8056 | 0.87247 | 0.94695 | 1.0307 | 1.1636 | 1.2661 | 1.3748 | 1.4862 | 1.6014 | 1.7365 | 1.5324 | 1.6633 | 1.7929 | 2.21 | 2.3178 | 1.567 | 1.6674 | 1.7828 | 1.9072 | 2.0469 | 2.2022 | 2.3762 | 2.6486 | 2.8602 | 3.0844 | 3.3133 | 3.5488 | 3.8244 | 3.2526 | 3.5197 | 3.784 | 4.6438 | 4.8808
South West | Landulph 132 kV | Eggbuckland | Primary Substation | 11 | Electric Engagement | 0.70781 | 0.817 | 0.95485 | 1.1067 | 1.2758 | 1.4578 | 1.6743 | 1.9648 | 2.2005 | 2.3899 | 2.5476 | 2.583 | 2.6215 | 2.3319 | 2.3686 | 2.4029 | 2.5539 | 2.696 | 1.7093 | 1.9409 | 2.231 | 2.549 | 2.9016 | 3.2797 | 3.7266 | 4.3201 | 4.8034 | 5.1935 | 5.5202 | 5.6012 | 5.69 | 4.9592 | 5.0448 | 5.1251 | 5.4846 | 5.8177
South West | Landulph 132 kV | Eggbuckland | Primary Substation | 11 | Holistic Transition | 0.69514 | 0.77396 | 0.86875 | 0.96836 | 1.0783 | 1.2016 | 1.3403 | 1.5334 | 1.6975 | 1.8716 | 2.0539 | 2.2333 | 2.418 | 2.274 | 2.4325 | 2.5188 | 2.7241 | 2.8813 | 1.6914 | 1.8664 | 2.0743 | 2.2916 | 2.5298 | 2.7945 | 3.0889 | 3.4915 | 3.8349 | 4.1977 | 4.5756 | 4.9479 | 5.3325 | 4.901 | 5.2325 | 5.4197 | 5.9002 | 6.2743
South West | Landulph 132 kV | Eggbuckland | Primary Substation | 11 | Hydrogen Evolution | 0.66361 | 0.72462 | 0.80094 | 0.88274 | 0.97575 | 1.0816 | 1.2068 | 1.3863 | 1.5394 | 1.7021 | 1.873 | 2.0389 | 2.207 | 2.031 | 2.1738 | 2.2388 | 2.3625 | 2.4591 | 1.611 | 1.7412 | 1.9024 | 2.075 | 2.2704 | 2.4915 | 2.7514 | 3.1196 | 3.4342 | 3.7676 | 4.1166 | 4.455 | 4.7991 | 4.2887 | 4.5821 | 4.7196 | 5.0042 | 5.2279
South West | Landulph 132 kV | Elim Terrace | Primary Substation | 11 | Counterfactual | 0.19294 | 0.23704 | 0.28716 | 0.34146 | 0.40206 | 0.46929 | 0.54354 | 0.66146 | 0.75169 | 0.84693 | 0.9449 | 1.0484 | 1.1712 | 1.293 | 1.4114 | 1.5284 | 1.917 | 2.0248 | 0.44713 | 0.54085 | 0.64628 | 0.76022 | 0.88688 | 1.027 | 1.1811 | 1.4227 | 1.6086 | 1.8045 | 2.0056 | 2.2173 | 2.4687 | 2.7174 | 2.9594 | 3.1982 | 3.9989 | 4.2337
South West | Landulph 132 kV | Elim Terrace | Primary Substation | 11 | Electric Engagement | 0.24994 | 0.3513 | 0.47488 | 0.61257 | 0.7653 | 0.9308 | 1.1261 | 1.3899 | 1.6035 | 1.7765 | 1.9195 | 1.9541 | 1.992 | 2.0267 | 2.0605 | 2.092 | 2.2254 | 2.3675 | 0.57404 | 0.7898 | 1.0492 | 1.337 | 1.6548 | 1.9977 | 2.4003 | 2.9394 | 3.3774 | 3.7336 | 4.0297 | 4.1084 | 4.1954 | 4.2755 | 4.3535 | 4.4268 | 4.7443 | 5.0728
South West | Landulph 132 kV | Elim Terrace | Primary Substation | 11 | Holistic Transition | 0.23786 | 0.31231 | 0.39711 | 0.48655 | 0.58498 | 0.69554 | 0.82119 | 0.99642 | 1.1454 | 1.3034 | 1.4713 | 1.6439 | 1.8233 | 1.9897 | 2.1422 | 2.2263 | 2.4313 | 2.5859 | 0.55641 | 0.72209 | 0.90717 | 1.1014 | 1.3134 | 1.5498 | 1.8157 | 2.1804 | 2.4919 | 2.8206 | 3.1693 | 3.527 | 3.9004 | 4.2473 | 4.5658 | 4.7474 | 5.223 | 5.5913
South West | Landulph 132 kV | Elim Terrace | Primary Substation | 11 | Hydrogen Evolution | 0.21023 | 0.26736 | 0.33691 | 0.41142 | 0.49542 | 0.59046 | 0.7014 | 0.86199 | 0.99684 | 1.14 | 1.2911 | 1.4397 | 1.5919 | 1.7321 | 1.8603 | 1.9204 | 2.0313 | 2.1192 | 0.48568 | 0.60805 | 0.75504 | 0.91221 | 1.0885 | 1.2869 | 1.517 | 1.846 | 2.1228 | 2.4158 | 2.7242 | 3.0274 | 3.3394 | 3.6266 | 3.8899 | 4.0168 | 4.2701 | 4.4722
South West | Landulph 132 kV | Ernesettle B & S | Primary Substation | 11 | Counterfactual | 0.24425 | 0.24437 | 0.24461 | 0.24491 | 0.24527 | 0.2457 | 0.24625 | 0.2471 | 0.2477 | 0.24856 | 0.24923 | 0.2497 | 0.25023 | 0.25083 | 0.25136 | 0.25195 | 0.25494 | 0.25758 | 0.61063 | 0.6109 | 0.61145 | 0.61211 | 0.61293 | 0.6139 | 0.61519 | 0.6171 | 0.61851 | 0.6205 | 0.62203 | 0.62308 | 0.6242 | 0.62548 | 0.6266 | 0.62784 | 0.63446 | 0.64038
South West | Landulph 132 kV | Ernesettle B & S | Primary Substation | 11 | Electric Engagement | 0.24437 | 0.24461 | 0.24541 | 0.24639 | 0.24736 | 0.24834 | 0.24949 | 0.25099 | 0.25227 | 0.25355 | 0.25483 | 0.25581 | 0.25685 | 0.25795 | 0.259 | 0.25993 | 0.31416 | 0.31728 | 0.61086 | 0.6114 | 0.61332 | 0.61559 | 0.61786 | 0.62013 | 0.62274 | 0.62609 | 0.62902 | 0.63199 | 0.63496 | 0.63727 | 0.63974 | 0.64232 | 0.64478 | 0.64702 | 0.78225 | 0.78991
South West | Landulph 132 kV | Ernesettle B & S | Primary Substation | 11 | Holistic Transition | 0.24431 | 0.24456 | 0.24548 | 0.24647 | 0.24758 | 0.24875 | 0.25024 | 0.25233 | 0.25418 | 0.2559 | 0.25717 | 0.25844 | 0.35986 | 0.36071 | 0.36161 | 0.3624 | 0.36553 | 0.36699 | 0.61078 | 0.61133 | 0.61357 | 0.61592 | 0.61858 | 0.62137 | 0.62493 | 0.62991 | 0.63426 | 0.63833 | 0.64126 | 0.64414 | 0.89743 | 0.89934 | 0.90137 | 0.90316 | 0.91052 | 0.91392
South West | Landulph 132 kV | Ernesettle B & S | Primary Substation | 11 | Hydrogen Evolution | 0.24431 | 0.24449 | 0.24479 | 0.24521 | 0.24569 | 0.24636 | 0.24721 | 0.24834 | 0.24972 | 0.25125 | 0.25245 | 0.25347 | 0.25436 | 0.25527 | 0.25617 | 0.25683 | 0.31007 | 0.31286 | 0.61074 | 0.61113 | 0.61179 | 0.61277 | 0.61386 | 0.61538 | 0.61729 | 0.61978 | 0.6229 | 0.62641 | 0.6291 | 0.63136 | 0.63334 | 0.63537 | 0.63735 | 0.63887 | 0.77171 | 0.77842
South West | Landulph 132 kV | Gunnislake | Primary Substation | 11 | Counterfactual | 0.20192 | 0.23523 | 0.27029 | 0.30951 | 0.35459 | 0.4057 | 0.46431 | 0.55683 | 0.63008 | 0.70791 | 0.78896 | 0.87397 | 0.96971 | 1.0644 | 1.1567 | 1.249 | 1.5693 | 1.7219 | 0.47747 | 0.54856 | 0.62224 | 0.70427 | 0.79814 | 0.90428 | 1.0256 | 1.2149 | 1.3657 | 1.5258 | 1.6922 | 1.8663 | 2.062 | 2.2554 | 2.4438 | 2.6321 | 3.2912 | 3.6121
South West | Landulph 132 kV | Gunnislake | Primary Substation | 11 | Electric Engagement | 0.24117 | 0.31617 | 0.40539 | 0.50537 | 0.61832 | 0.74418 | 0.89454 | 1.0965 | 1.2648 | 1.4063 | 1.5293 | 1.5763 | 1.6179 | 1.6556 | 1.6924 | 1.7409 | 1.886 | 2.0066 | 0.56461 | 0.72603 | 0.91326 | 1.1221 | 1.3571 | 1.6181 | 1.9287 | 2.3423 | 2.6884 | 2.9805 | 3.2357 | 3.3385 | 3.4303 | 3.5143 | 3.5962 | 3.7014 | 4.0338 | 4.3103
South West | Landulph 132 kV | Gunnislake | Primary Substation | 11 | Holistic Transition | 0.23272 | 0.29023 | 0.35218 | 0.41885 | 0.49566 | 0.58727 | 0.69136 | 0.83317 | 0.95776 | 1.0924 | 1.2336 | 1.3699 | 1.5011 | 1.623 | 1.7372 | 1.8214 | 2.0112 | 2.1617 | 0.55208 | 0.68199 | 0.81732 | 0.96199 | 1.1275 | 1.323 | 1.5435 | 1.8391 | 2.1 | 2.3806 | 2.6746 | 2.9587 | 3.2324 | 3.4875 | 3.727 | 3.9062 | 4.3379 | 4.6852
South West | Landulph 132 kV | Gunnislake | Primary Substation | 11 | Hydrogen Evolution | 0.21444 | 0.25737 | 0.30881 | 0.36586 | 0.43275 | 0.51182 | 0.6066 | 0.7408 | 0.86274 | 0.99203 | 1.1263 | 1.2555 | 1.3797 | 1.4919 | 1.5967 | 1.6665 | 1.7897 | 1.8924 | 0.50525 | 0.59823 | 0.70661 | 0.82628 | 0.96618 | 1.1308 | 1.3272 | 1.6024 | 1.8529 | 2.1179 | 2.3926 | 2.6573 | 2.9118 | 3.1422 | 3.3577 | 3.5031 | 3.7769 | 4.0051
South West | Landulph 132 kV | Lanreath | Primary Substation | 11 | Counterfactual | 0.22642 | 0.24156 | 0.26718 | 0.29529 | 0.32933 | 0.38752 | 0.45242 | 0.53674 | 0.61048 | 0.69245 | 0.76802 | 0.83278 | 0.89802 | 0.9654 | 1.0286 | 1.0923 | 1.3792 | 1.5876 | 0.49296 | 0.52542 | 0.58286 | 0.646 | 0.72269 | 0.84986 | 0.99348 | 1.1782 | 1.3413 | 1.5259 | 1.6919 | 1.8314 | 1.9695 | 2.1132 | 2.2466 | 2.3808 | 3.0047 | 3.4719
South West | Landulph 132 kV | Lanreath | Primary Substation | 11 | Electric Engagement | 0.24386 | 0.27848 | 0.35932 | 0.44504 | 0.53623 | 0.66328 | 0.80281 | 0.97474 | 1.1355 | 1.29 | 1.4464 | 1.5554 | 1.6681 | 1.7858 | 1.9099 | 2.0279 | 2.697 | 2.9876 | 0.53165 | 0.6063 | 0.79185 | 0.98742 | 1.1938 | 1.4715 | 1.7744 | 2.1458 | 2.4945 | 2.8324 | 3.1756 | 3.4216 | 3.6761 | 3.9426 | 4.2199 | 4.4855 | 5.9452 | 6.6307
South West | Landulph 132 kV | Lanreath | Primary Substation | 11 | Holistic Transition | 0.24009 | 0.26702 | 0.34671 | 0.42899 | 0.52688 | 0.66006 | 0.82006 | 1.0253 | 1.2108 | 1.3991 | 1.5567 | 1.6969 | 1.835 | 1.9512 | 2.0702 | 2.1623 | 2.7072 | 2.8911 | 0.52609 | 0.58704 | 0.77732 | 0.97298 | 1.2057 | 1.5088 | 1.878 | 2.3508 | 2.777 | 3.2064 | 3.5554 | 3.8651 | 4.1695 | 4.4204 | 4.6747 | 4.8754 | 6.0549 | 6.466
South West | Landulph 132 kV | Lanreath | Primary Substation | 11 | Hydrogen Evolution | 0.23194 | 0.2516 | 0.28461 | 0.32503 | 0.37362 | 0.45608 | 0.54508 | 0.65359 | 0.77986 | 0.92384 | 1.0444 | 1.1546 | 1.2608 | 1.3678 | 1.4752 | 1.5575 | 1.981 | 2.2733 | 0.50522 | 0.54785 | 0.62152 | 0.71261 | 0.82222 | 1.0027 | 1.1981 | 1.4336 | 1.7153 | 2.0396 | 2.3041 | 2.5431 | 2.7716 | 3.0039 | 3.2354 | 3.4171 | 4.3634 | 5.0356
South West | Landulph 132 kV | Lifton | Primary Substation | 11 | Counterfactual | 0.56652 | 0.5926 | 0.61858 | 0.63322 | 0.65104 | 0.6721 | 0.69705 | 0.73458 | 0.76685 | 0.80264 | 0.83577 | 0.86977 | 0.90699 | 0.94408 | 0.98018 | 1.0159 | 1.1481 | 1.2104 | 1.2516 | 1.3067 | 1.3611 | 1.3917 | 1.4292 | 1.474 | 1.5271 | 1.6053 | 1.6736 | 1.7493 | 1.818 | 1.8877 | 1.9637 | 2.0394 | 2.1131 | 2.1858 | 2.4572 | 2.5875
South West | Landulph 132 kV | Lifton | Primary Substation | 11 | Electric Engagement | 0.58138 | 0.62502 | 0.67425 | 0.71817 | 0.77337 | 0.83868 | 0.90878 | 0.99035 | 1.0569 | 1.1156 | 1.167 | 1.1884 | 1.2058 | 1.2206 | 1.3049 | 1.3168 | 1.4792 | 1.5254 | 1.2845 | 1.3783 | 1.4826 | 1.5765 | 1.6967 | 1.8395 | 1.9894 | 2.1581 | 2.2945 | 2.4156 | 2.522 | 2.5682 | 2.6062 | 2.6388 | 2.8193 | 2.846 | 3.1862 | 3.2913
South West | Landulph 132 kV | Lifton | Primary Substation | 11 | Holistic Transition | 0.57778 | 0.61421 | 0.65563 | 0.68808 | 0.72653 | 0.7719 | 0.8206 | 0.88208 | 0.93377 | 1.0245 | 1.0825 | 1.138 | 1.1893 | 1.2358 | 1.332 | 1.3576 | 1.5364 | 1.5908 | 1.2789 | 1.3594 | 1.4504 | 1.5229 | 1.6092 | 1.7099 | 1.8161 | 1.947 | 2.0557 | 2.259 | 2.3791 | 2.4944 | 2.6012 | 2.6983 | 2.8946 | 2.9499 | 3.3264 | 3.4516
South West | Landulph 132 kV | Lifton | Primary Substation | 11 | Hydrogen Evolution | 0.57125 | 0.60329 | 0.63847 | 0.66576 | 0.70225 | 0.74838 | 0.79726 | 0.85759 | 0.90659 | 0.96084 | 1.0172 | 1.0711 | 1.1208 | 1.165 | 1.2498 | 1.2707 | 1.3736 | 1.4109 | 1.262 | 1.3313 | 1.4063 | 1.4656 | 1.5466 | 1.6492 | 1.7555 | 1.8827 | 1.9834 | 2.0945 | 2.2098 | 2.3202 | 2.4218 | 2.5126 | 2.6932 | 2.7372 | 2.953 | 3.0362
South West | Landulph 132 kV | Liskeard | Primary Substation | 11 | Counterfactual | 1.2962 | 1.3875 | 1.5157 | 1.6618 | 1.835 | 2.0603 | 2.3186 | 2.6792 | 2.9842 | 3.3261 | 3.6678 | 3.963 | 3.6418 | 3.9562 | 4.2537 | 4.5526 | 5.7792 | 6.5457 | 3.0757 | 3.2696 | 3.5501 | 3.8687 | 4.2477 | 4.737 | 5.3022 | 6.0789 | 6.7433 | 7.4973 | 8.2432 | 8.8692 | 7.9397 | 8.5997 | 9.2204 | 9.8435 | 12.4719 | 14.1766
South West | Landulph 132 kV | Liskeard | Primary Substation | 11 | Electric Engagement | 1.3999 | 1.5987 | 1.9683 | 2.3764 | 2.8168 | 3.3346 | 3.9189 | 4.7054 | 5.3642 | 5.9678 | 6.5455 | 6.8913 | 6.6081 | 7.0148 | 7.3593 | 7.8287 | 9.4154 | 10.3685 | 3.3057 | 3.7319 | 4.5568 | 5.4636 | 6.4351 | 7.5572 | 8.8133 | 10.5046 | 11.9167 | 13.2228 | 14.4827 | 15.2694 | 14.487 | 15.4045 | 16.1915 | 17.2297 | 20.8268 | 23.0931
South West | Landulph 132 kV | Liskeard | Primary Substation | 11 | Holistic Transition | 1.3773 | 1.529 | 1.8648 | 2.2171 | 2.6327 | 3.1298 | 3.7248 | 4.503 | 5.2361 | 5.9416 | 6.5559 | 7.1235 | 7.0463 | 7.57 | 8.0153 | 8.4694 | 9.8074 | 10.4531 | 3.2718 | 3.6122 | 4.3963 | 5.2144 | 6.1784 | 7.3037 | 8.6608 | 10.4236 | 12.0938 | 13.6795 | 15.0239 | 16.2615 | 15.8914 | 17.0073 | 17.9608 | 18.9327 | 21.943 | 23.4194
South West | Landulph 132 kV | Liskeard | Primary Substation | 11 | Hydrogen Evolution | 1.3301 | 1.4458 | 1.6225 | 1.8389 | 2.094 | 2.4275 | 2.8048 | 3.2921 | 3.8561 | 4.4384 | 4.9555 | 5.4333 | 5.2596 | 5.7266 | 6.1443 | 6.5072 | 7.6488 | 8.5631 | 3.151 | 3.4002 | 3.7853 | 4.2616 | 4.8228 | 5.5479 | 6.3663 | 7.4079 | 8.6552 | 9.939 | 11.0523 | 12.0722 | 11.4662 | 12.4625 | 13.3556 | 14.1404 | 16.7608 | 18.8842
South West | Landulph 132 kV | Longbridge | Primary Substation | 11 | Counterfactual | 2.5696 | 2.6158 | 2.6881 | 2.7811 | 2.8674 | 2.9633 | 3.0677 | 3.2119 | 3.3298 | 3.4421 | 3.5644 | 3.665 | 3.7814 | 3.8942 | 4.0065 | 4.118 | 4.5002 | 4.6262 | 6.3473 | 6.4449 | 6.5961 | 6.7907 | 6.9716 | 7.1723 | 7.3908 | 7.6895 | 7.9359 | 8.1701 | 8.4244 | 8.6308 | 8.8688 | 9.0997 | 9.3293 | 9.5569 | 10.3464 | 10.62
South West | Landulph 132 kV | Longbridge | Primary Substation | 11 | Electric Engagement | 2.6186 | 2.7143 | 2.8599 | 3.0385 | 3.2187 | 3.4125 | 3.6326 | 3.9135 | 4.1506 | 4.3372 | 4.5259 | 4.5964 | 4.6656 | 4.7331 | 4.8016 | 4.8703 | 5.1922 | 5.5124 | 6.4561 | 6.6596 | 6.9672 | 7.3459 | 7.7258 | 8.1338 | 8.5944 | 9.1765 | 9.6705 | 10.0598 | 10.4554 | 10.6076 | 10.7587 | 10.9062 | 11.0553 | 11.2047 | 11.9059 | 12.6079
South West | Landulph 132 kV | Longbridge | Primary Substation | 11 | Holistic Transition | 2.6079 | 2.6801 | 2.7953 | 2.9324 | 3.0676 | 3.2163 | 3.3808 | 3.5918 | 3.7783 | 3.9573 | 4.1698 | 4.3565 | 4.5475 | 4.7224 | 4.8915 | 4.9993 | 5.4088 | 5.6674 | 6.4402 | 6.6002 | 6.8504 | 7.1491 | 7.4429 | 7.7649 | 8.1195 | 8.5682 | 8.9661 | 9.3451 | 9.7905 | 10.1776 | 10.5747 | 10.9377 | 11.2889 | 11.5174 | 12.4254 | 12.9963
South West | Landulph 132 kV | Longbridge | Primary Substation | 11 | Hydrogen Evolution | 2.585 | 2.6427 | 2.7465 | 2.8708 | 2.99 | 3.1251 | 3.2785 | 3.4736 | 3.6504 | 3.8181 | 4.0076 | 4.1659 | 4.3261 | 4.4789 | 4.6178 | 4.7022 | 4.9547 | 5.7929 | 6.3816 | 6.5049 | 6.7232 | 6.9878 | 7.2409 | 7.5274 | 7.8506 | 8.2572 | 8.6279 | 8.9774 | 9.3706 | 9.6944 | 10.0227 | 10.3363 | 10.6217 | 10.7981 | 11.3418 | 13.3761
South West | Landulph 132 kV | Looe | Primary Substation | 11 | Counterfactual | 0.28096 | 0.33147 | 0.3862 | 0.44747 | 0.51854 | 0.61193 | 0.71676 | 0.87016 | 0.99523 | 1.1294 | 1.2643 | 1.4 | 1.5485 | 1.6974 | 1.8407 | 1.9844 | 2.531 | 2.8383 | 0.63759 | 0.74725 | 0.8647 | 0.99568 | 1.1472 | 1.3448 | 1.5669 | 1.8875 | 2.1512 | 2.4356 | 2.7187 | 3.001 | 3.3076 | 3.6156 | 3.9112 | 4.2075 | 5.3523 | 6.0151
South West | Landulph 132 kV | Looe | Primary Substation | 11 | Electric Engagement | 0.33421 | 0.44965 | 0.59724 | 0.75917 | 0.93901 | 1.2571 | 1.5103 | 1.8403 | 2.1252 | 2.3759 | 2.6066 | 2.7265 | 2.8422 | 2.9669 | 3.0811 | 3.214 | 3.7424 | 4.0707 | 0.75562 | 1.0082 | 1.327 | 1.6747 | 2.0586 | 2.7189 | 3.2505 | 3.9376 | 4.5339 | 5.0622 | 5.5516 | 5.8174 | 6.0756 | 6.3527 | 6.6075 | 6.8999 | 8.0789 | 8.8394
South West | Landulph 132 kV | Looe | Primary Substation | 11 | Holistic Transition | 0.32254 | 0.41815 | 0.5345 | 0.65715 | 0.80014 | 0.98272 | 1.1927 | 1.4693 | 1.7158 | 1.9742 | 2.2265 | 2.4702 | 2.7083 | 2.9346 | 3.1401 | 3.3034 | 3.8212 | 4.1376 | 0.73818 | 0.95776 | 1.2211 | 1.4971 | 1.8174 | 2.2173 | 2.6783 | 3.2787 | 3.8153 | 4.374 | 4.9115 | 5.4294 | 5.9358 | 6.4134 | 6.8485 | 7.1988 | 8.3548 | 9.0778
South West | Landulph 132 kV | Looe | Primary Substation | 11 | Hydrogen Evolution | 0.29832 | 0.36464 | 0.4437 | 0.53224 | 0.63667 | 0.77543 | 0.93423 | 1.149 | 1.3566 | 1.5799 | 1.7984 | 2.0085 | 2.2121 | 2.409 | 2.591 | 2.727 | 3.1022 | 3.4055 | 0.67599 | 0.82175 | 0.99114 | 1.1809 | 1.4043 | 1.6982 | 2.0335 | 2.4813 | 2.92 | 3.393 | 3.8503 | 4.2883 | 4.7122 | 5.1238 | 5.5046 | 5.7934 | 6.6325 | 7.3165
South West | Landulph 132 kV | Merrivale | Primary Substation | 11 | Counterfactual | 0.46945 | 0.55177 | 0.73155 | 0.83024 | 0.94089 | 1.0646 | 1.203 | 1.4212 | 1.5902 | 1.7694 | 1.9667 | 2.173 | 2.4 | 2.6238 | 2.8419 | 3.0573 | 3.7813 | 3.9834 | 1.0896 | 1.2639 | 1.6775 | 1.885 | 2.1169 | 2.3754 | 2.6639 | 3.1123 | 3.4622 | 3.8331 | 4.2415 | 4.671 | 5.1362 | 5.5939 | 6.0398 | 6.4799 | 7.9745 | 8.4189
South West | Landulph 132 kV | Merrivale | Primary Substation | 11 | Electric Engagement | 0.57486 | 0.84898 | 1.0787 | 1.3329 | 1.6149 | 1.9213 | 2.2836 | 2.7716 | 3.2041 | 3.5285 | 3.8143 | 3.8843 | 3.9588 | 4.0282 | 4.0957 | 4.1591 | 4.4339 | 4.7092 | 1.3243 | 1.9397 | 2.424 | 2.9578 | 3.5467 | 4.1837 | 4.9326 | 5.9325 | 6.837 | 7.5075 | 8.104 | 8.2648 | 8.437 | 8.5987 | 8.7556 | 8.9042 | 9.5569 | 10.1983
South West | Landulph 132 kV | Merrivale | Primary Substation | 11 | Holistic Transition | 0.64151 | 0.77734 | 0.93657 | 1.1037 | 1.289 | 1.4969 | 1.7374 | 2.0707 | 2.363 | 2.6921 | 3.0222 | 3.3421 | 3.6719 | 3.976 | 4.2538 | 4.4066 | 4.7832 | 5.0619 | 1.5139 | 1.8152 | 2.1651 | 2.5304 | 2.9327 | 3.3801 | 3.8935 | 4.5934 | 5.2125 | 5.9139 | 6.6039 | 7.2693 | 7.9575 | 8.592 | 9.1729 | 9.5036 | 10.38 | 11.0437
South West | Landulph 132 kV | Merrivale | Primary Substation | 11 | Hydrogen Evolution | 0.50234 | 0.69719 | 0.8242 | 0.96076 | 1.1154 | 1.292 | 1.499 | 1.7962 | 2.073 | 2.3591 | 2.6593 | 2.9379 | 3.2208 | 3.4825 | 3.7216 | 3.8342 | 4.0621 | 4.2416 | 1.1629 | 1.6115 | 1.8804 | 2.1692 | 2.4947 | 2.8645 | 3.2953 | 3.9058 | 4.4869 | 5.0824 | 5.7001 | 6.2703 | 6.851 | 7.3888 | 7.8811 | 8.1197 | 8.6438 | 9.0611
South West | Landulph 132 kV | Newport Street | Primary Substation | 11 | Counterfactual | 0.12802 | 0.19267 | 0.27733 | 0.3492 | 0.42376 | 0.52993 | 0.65427 | 0.83795 | 0.95715 | 1.0846 | 1.209 | 1.3198 | 1.452 | 1.5802 | 1.7053 | 1.8296 | 2.6626 | 2.8589 | 0.29566 | 0.43282 | 0.60924 | 0.75915 | 0.91428 | 1.1353 | 1.3938 | 1.7735 | 2.0197 | 2.2825 | 2.5392 | 2.7654 | 3.0352 | 3.2965 | 3.5515 | 3.8049 | 5.4938 | 5.9051
South West | Landulph 132 kV | Newport Street | Primary Substation | 11 | Electric Engagement | 0.17754 | 0.3004 | 0.46292 | 0.61361 | 0.77333 | 0.98214 | 1.2408 | 1.5655 | 1.805 | 2.0107 | 2.2174 | 2.3041 | 2.3921 | 2.4796 | 2.563 | 2.6368 | 2.9761 | 3.3045 | 0.40638 | 0.6715 | 1.0142 | 1.3301 | 1.6632 | 2.1004 | 2.6414 | 3.3139 | 3.8081 | 4.2342 | 4.6623 | 4.8452 | 5.0319 | 5.2173 | 5.3944 | 5.552 | 6.2818 | 6.9818
South West | Landulph 132 kV | Newport Street | Primary Substation | 11 | Holistic Transition | 0.16662 | 0.26865 | 0.3784 | 0.48164 | 0.59208 | 0.75102 | 0.94319 | 1.1871 | 1.3675 | 1.5572 | 1.7897 | 2.0074 | 2.2282 | 2.4399 | 2.6393 | 2.7614 | 3.173 | 3.4867 | 0.3904 | 0.61773 | 0.85794 | 1.0818 | 1.3193 | 1.66 | 2.0705 | 2.5839 | 2.9625 | 3.3592 | 3.8413 | 4.2888 | 4.7445 | 5.1815 | 5.5935 | 5.8507 | 6.7382 | 7.4223
South West | Landulph 132 kV | Newport Street | Primary Substation | 11 | Hydrogen Evolution | 0.14466 | 0.57611 | 0.68936 | 0.78262 | 1.0566 | 1.2041 | 1.3897 | 1.7403 | 1.914 | 2.2133 | 2.4382 | 2.6142 | 2.7963 | 2.9664 | 3.1227 | 3.2163 | 3.4848 | 3.6783 | 0.3325 | 1.2099 | 1.4498 | 1.6468 | 2.2045 | 2.5157 | 2.9069 | 3.6275 | 3.9866 | 4.5965 | 5.0571 | 5.415 | 5.7865 | 6.1337 | 6.453 | 6.6468 | 7.2158 | 7.6288
South West | Landulph 132 kV | Old Laira Road | Primary Substation | 11 | Counterfactual | 0.13567 | 0.18475 | 0.22849 | 0.276 | 0.32929 | 0.38821 | 0.45394 | 0.55819 | 0.63817 | 0.72263 | 0.80961 | 0.90081 | 1.0089 | 1.1158 | 1.2203 | 1.3234 | 1.6597 | 1.7501 | 0.3073 | 0.41107 | 0.50289 | 0.60239 | 0.71351 | 0.836 | 0.97216 | 1.1854 | 1.3499 | 1.5233 | 1.7016 | 1.8881 | 2.1088 | 2.327 | 2.5403 | 2.7504 | 3.4425 | 3.6392
South West | Landulph 132 kV | Old Laira Road | Primary Substation | 11 | Electric Engagement | 0.18762 | 0.28845 | 0.3975 | 0.51849 | 0.65322 | 0.79875 | 0.97083 | 1.203 | 1.3912 | 1.5422 | 1.6674 | 1.6962 | 1.7276 | 1.7565 | 1.7845 | 1.8106 | 1.9198 | 2.0387 | 0.42326 | 0.63794 | 0.86663 | 1.1193 | 1.3993 | 1.7006 | 2.055 | 2.5292 | 2.9146 | 3.2252 | 3.484 | 3.5498 | 3.6221 | 3.6889 | 3.7538 | 3.8144 | 4.0746 | 4.3494
South West | Landulph 132 kV | Old Laira Road | Primary Substation | 11 | Holistic Transition | 0.17712 | 0.25343 | 0.32765 | 0.40536 | 0.49155 | 0.58796 | 0.6981 | 0.85139 | 0.98206 | 1.1203 | 1.2673 | 1.4162 | 1.5703 | 1.7137 | 1.8442 | 1.9151 | 2.0846 | 2.2113 | 0.40822 | 0.57698 | 0.73882 | 0.90736 | 1.0929 | 1.2988 | 1.5318 | 1.8505 | 2.1234 | 2.411 | 2.716 | 3.0244 | 3.3449 | 3.6434 | 3.9158 | 4.0689 | 4.4624 | 4.7652
South West | Landulph 132 kV | Old Laira Road | Primary Substation | 11 | Hydrogen Evolution | 0.15223 | 0.21429 | 0.27545 | 0.34064 | 0.41457 | 0.49845 | 0.59649 | 0.73805 | 0.85708 | 0.98312 | 1.1169 | 1.2482 | 1.3822 | 1.5059 | 1.6186 | 1.6707 | 1.7636 | 1.8341 | 0.34451 | 0.47761 | 0.60668 | 0.74402 | 0.899 | 1.0739 | 1.277 | 1.5667 | 1.8108 | 2.0685 | 2.3412 | 2.609 | 2.8833 | 3.1365 | 3.3675 | 3.4771 | 3.689 | 3.8521
South West | Landulph 132 kV | Pensilva | Primary Substation | 11 | Counterfactual | 0.34768 | 0.37033 | 0.39851 | 0.42907 | 0.46572 | 0.51489 | 0.57029 | 0.65032 | 0.71662 | 0.78809 | 0.85846 | 0.9275 | 1.0028 | 1.0784 | 1.1508 | 1.2239 | 1.5045 | 1.6526 | 0.82349 | 0.87169 | 0.93194 | 0.99726 | 1.0758 | 1.1802 | 1.298 | 1.4659 | 1.6063 | 1.7587 | 1.9067 | 2.0503 | 2.2056 | 2.362 | 2.5111 | 2.6615 | 3.249 | 3.5701
South West | Landulph 132 kV | Pensilva | Primary Substation | 11 | Electric Engagement | 0.37555 | 0.42756 | 0.50693 | 0.59819 | 0.69784 | 0.81976 | 0.95868 | 1.136 | 1.2922 | 1.4322 | 1.5621 | 1.6308 | 1.6979 | 1.7646 | 1.8827 | 1.9473 | 2.2545 | 2.4324 | 0.88541 | 0.99669 | 1.1699 | 1.369 | 1.5846 | 1.8447 | 2.1385 | 2.5096 | 2.838 | 3.1344 | 3.4112 | 3.5641 | 3.7141 | 3.8645 | 4.1165 | 4.2617 | 4.9468 | 5.3635
South West | Landulph 132 kV | Pensilva | Primary Substation | 11 | Holistic Transition | 0.36978 | 0.40907 | 0.47178 | 0.53851 | 0.61653 | 0.71818 | 0.83487 | 0.98703 | 1.1229 | 1.2665 | 1.4039 | 1.532 | 1.6564 | 1.7671 | 1.9255 | 1.9975 | 2.272 | 2.4271 | 0.87703 | 0.96511 | 1.1082 | 1.2594 | 1.4356 | 1.6592 | 1.9169 | 2.2493 | 2.5461 | 2.8573 | 3.1499 | 3.4225 | 3.6872 | 3.9215 | 4.2502 | 4.4062 | 5.0162 | 5.3685
South West | Landulph 132 kV | Pensilva | Primary Substation | 11 | Hydrogen Evolution | 0.35638 | 0.38587 | 0.4255 | 0.47538 | 0.53297 | 0.6098 | 0.69674 | 0.81154 | 0.92717 | 1.0522 | 1.1717 | 1.2836 | 1.392 | 1.4925 | 1.6153 | 1.6746 | 1.8826 | 2.0532 | 0.84292 | 0.9063 | 0.99164 | 1.1002 | 1.2249 | 1.3892 | 1.5741 | 1.8148 | 2.0598 | 2.3258 | 2.5764 | 2.8103 | 3.0361 | 3.2473 | 3.5022 | 3.6303 | 4.0967 | 4.482
South West | Landulph 132 kV | Plymstock South | Primary Substation | 11 | Counterfactual | 0.14262 | 0.1696 | 0.20098 | 0.23452 | 0.27229 | 0.3144 | 0.36197 | 0.43652 | 0.49451 | 0.55622 | 0.61889 | 0.68442 | 0.76102 | 0.83691 | 0.91098 | 0.98439 | 1.2232 | 1.2835 | 0.33314 | 0.39031 | 0.45638 | 0.52689 | 0.606 | 0.694 | 0.7931 | 0.9463 | 1.0663 | 1.194 | 1.3231 | 1.4574 | 1.6141 | 1.7693 | 1.9206 | 2.0705 | 2.5639 | 2.6978
South West | Landulph 132 kV | Plymstock South | Primary Substation | 11 | Electric Engagement | 0.17888 | 0.24189 | 0.32079 | 0.40766 | 0.50427 | 0.61158 | 0.73517 | 0.90109 | 1.0368 | 1.1466 | 1.2385 | 1.2613 | 1.286 | 1.3095 | 1.3325 | 1.3543 | 1.4505 | 1.5361 | 0.41397 | 0.54813 | 0.71477 | 0.89735 | 1.0994 | 1.3225 | 1.5783 | 1.9184 | 2.1977 | 2.425 | 2.6163 | 2.6691 | 2.7265 | 2.7813 | 2.8349 | 2.886 | 3.1141 | 3.3156
South West | Landulph 132 kV | Plymstock South | Primary Substation | 11 | Holistic Transition | 0.17184 | 0.218 | 0.27585 | 0.33345 | 0.39726 | 0.46881 | 0.5512 | 0.66497 | 0.76238 | 0.86533 | 0.972 | 1.078 | 1.1867 | 1.2872 | 1.3791 | 1.4295 | 1.5538 | 1.6473 | 0.40408 | 0.50695 | 0.63373 | 0.75989 | 0.89873 | 1.0529 | 1.2291 | 1.4683 | 1.6739 | 1.8903 | 2.113 | 2.334 | 2.5612 | 2.7711 | 2.9637 | 3.073 | 3.3636 | 3.5859
South West | Landulph 132 kV | Plymstock South | Primary Substation | 11 | Hydrogen Evolution | 0.15386 | 0.18904 | 0.2351 | 0.28167 | 0.33457 | 0.39467 | 0.46551 | 0.56685 | 0.65473 | 0.74839 | 0.84564 | 0.9404 | 1.0362 | 1.1249 | 1.2064 | 1.2437 | 1.3183 | 1.3788 | 0.3583 | 0.4336 | 0.53082 | 0.62937 | 0.74081 | 0.86677 | 1.0142 | 1.2225 | 1.404 | 1.5972 | 1.7966 | 1.9907 | 2.1873 | 2.3699 | 2.5376 | 2.6169 | 2.7893 | 2.9296
South West | Landulph 132 kV | Prince Rock | Primary Substation | 11 | Counterfactual | 0.13506 | 0.16494 | 0.19926 | 0.33366 | 0.38588 | 0.44226 | 0.503 | 0.61254 | 0.69048 | 0.77241 | 0.83084 | 0.89279 | 0.96625 | 1.0378 | 1.107 | 1.1768 | 1.431 | 1.5375 | 0.32113 | 0.38489 | 0.45681 | 0.729 | 0.83849 | 0.9566 | 1.0837 | 1.3115 | 1.4743 | 1.6454 | 1.7658 | 1.8928 | 2.0433 | 2.1896 | 2.3313 | 2.4738 | 2.9992 | 3.2256
South West | Landulph 132 kV | Prince Rock | Primary Substation | 11 | Electric Engagement | 0.16461 | 0.22744 | 0.30483 | 0.48719 | 0.59551 | 0.71464 | 0.84938 | 1.0516 | 1.2057 | 1.3389 | 1.4266 | 1.4592 | 1.4921 | 1.523 | 1.566 | 1.6155 | 1.8431 | 2.0423 | 0.38679 | 0.5219 | 0.68442 | 1.0569 | 1.285 | 1.5353 | 1.8171 | 2.2396 | 2.5611 | 2.841 | 3.0237 | 3.0954 | 3.1688 | 3.2379 | 3.3313 | 3.4375 | 3.9324 | 4.3622
South West | Landulph 132 kV | Prince Rock | Primary Substation | 11 | Holistic Transition | 0.15835 | 0.2089 | 0.26967 | 0.42367 | 0.50464 | 0.5968 | 0.69597 | 0.85361 | 0.97468 | 1.1018 | 1.2032 | 1.3095 | 1.4186 | 1.5208 | 1.6324 | 1.7108 | 1.976 | 2.1643 | 0.37753 | 0.49099 | 0.62242 | 0.94024 | 1.1159 | 1.3145 | 1.5269 | 1.862 | 2.1195 | 2.3887 | 2.6002 | 2.8215 | 3.0496 | 3.2633 | 3.4956 | 3.6615 | 4.2382 | 4.6539
South West | Landulph 132 kV | Prince Rock | Primary Substation | 11 | Hydrogen Evolution | 0.14469 | 0.18262 | 0.23648 | 0.37923 | 0.45189 | 0.53258 | 0.62312 | 0.77226 | 0.89027 | 1.0113 | 1.1044 | 1.195 | 1.288 | 1.3725 | 1.4516 | 1.5042 | 1.6809 | 1.8151 | 0.34241 | 0.42412 | 0.5367 | 0.82721 | 0.98138 | 1.1523 | 1.3431 | 1.6567 | 1.9039 | 2.1568 | 2.3476 | 2.5332 | 2.7244 | 2.8985 | 3.0618 | 3.1718 | 3.55 | 3.8378
South West | Landulph 132 kV | Saltash Dunheved Rd | Primary Substation | 11 | Counterfactual | 0.28623 | 0.34078 | 0.40106 | 0.46755 | 0.54408 | 0.63291 | 0.73162 | 0.88623 | 1.0085 | 1.1386 | 1.2735 | 1.4148 | 1.5734 | 1.7341 | 1.8876 | 2.0403 | 2.5533 | 2.7375 | 0.66933 | 0.78529 | 0.91216 | 1.0516 | 1.2114 | 1.3962 | 1.6011 | 1.9183 | 2.1707 | 2.4393 | 2.7171 | 3.0072 | 3.3318 | 3.6607 | 3.9748 | 4.287 | 5.3462 | 5.7431
South West | Landulph 132 kV | Saltash Dunheved Rd | Primary Substation | 11 | Electric Engagement | 0.35422 | 0.47742 | 0.62919 | 0.79666 | 0.98713 | 1.1982 | 1.447 | 1.7808 | 2.0552 | 2.2795 | 2.4738 | 2.5364 | 2.5975 | 2.6569 | 2.7115 | 2.7645 | 2.9992 | 3.2167 | 0.82043 | 1.0837 | 1.4028 | 1.7532 | 2.1504 | 2.5891 | 3.1041 | 3.7889 | 4.3546 | 4.8194 | 5.2242 | 5.3649 | 5.5029 | 5.6369 | 5.7613 | 5.8819 | 6.4257 | 6.9241
South West | Landulph 132 kV | Saltash Dunheved Rd | Primary Substation | 11 | Holistic Transition | 0.34003 | 0.43189 | 0.53705 | 0.64813 | 0.77822 | 0.93123 | 1.1025 | 1.3356 | 1.5374 | 1.7534 | 1.9767 | 2.2004 | 2.4173 | 2.6239 | 2.8161 | 2.93 | 3.2438 | 3.4988 | 0.79977 | 1.0056 | 1.2358 | 1.4777 | 1.7591 | 2.0871 | 2.452 | 2.9403 | 3.3652 | 3.8179 | 4.2847 | 4.7521 | 5.2059 | 5.6386 | 6.0421 | 6.2887 | 7.0066 | 7.5964
South West | Landulph 132 kV | Saltash Dunheved Rd | Primary Substation | 11 | Hydrogen Evolution | 0.30747 | 0.37673 | 0.46284 | 0.55562 | 0.6658 | 0.79531 | 0.94736 | 1.1624 | 1.3529 | 1.5526 | 1.764 | 1.9675 | 2.1697 | 2.3572 | 2.5283 | 2.6169 | 2.8204 | 2.9963 | 0.71659 | 0.86542 | 1.0471 | 1.2424 | 1.4736 | 1.7441 | 2.0606 | 2.503 | 2.8959 | 3.3074 | 3.7413 | 4.1595 | 4.5748 | 4.9607 | 5.3135 | 5.5009 | 5.9572 | 6.3513
South West | Landulph 132 kV | Saltash Whity Cross | Primary Substation | 11 | Counterfactual | 0.38693 | 0.43142 | 0.49201 | 0.56553 | 0.6493 | 0.75087 | 0.86557 | 1.0095 | 1.1344 | 1.2734 | 1.4049 | 1.5293 | 1.659 | 1.79 | 1.9154 | 2.0413 | 2.5273 | 2.801 | 0.93838 | 1.0327 | 1.1637 | 1.3217 | 1.5024 | 1.7215 | 1.9706 | 2.2798 | 2.5508 | 2.8557 | 3.1394 | 3.4034 | 3.6753 | 3.951 | 4.2138 | 4.4773 | 5.5159 | 6.1217
South West | Landulph 132 kV | Saltash Whity Cross | Primary Substation | 11 | Electric Engagement | 0.42265 | 0.5075 | 0.65645 | 0.82592 | 1.0087 | 1.2184 | 1.4513 | 1.7298 | 1.9786 | 2.2086 | 2.4277 | 2.5695 | 2.7075 | 2.8447 | 2.9782 | 3.131 | 3.6569 | 3.9752 | 1.0173 | 1.2004 | 1.5309 | 1.9046 | 2.306 | 2.7617 | 3.2643 | 3.8589 | 4.3934 | 4.8919 | 5.3706 | 5.6914 | 6.0058 | 6.3203 | 6.6253 | 6.9805 | 8.1878 | 8.9464
South West | Landulph 132 kV | Saltash Whity Cross | Primary Substation | 11 | Holistic Transition | 0.4141 | 0.48187 | 0.61824 | 0.76735 | 0.94011 | 1.1422 | 1.3785 | 1.669 | 1.9286 | 2.1954 | 2.4785 | 2.698 | 2.9099 | 3.0917 | 3.2649 | 3.3958 | 3.8634 | 4.0762 | 1.004 | 1.1557 | 1.47 | 1.8109 | 2.2067 | 2.6624 | 3.1984 | 3.8543 | 4.4401 | 5.0378 | 5.6722 | 6.1508 | 6.6132 | 7.0049 | 7.3779 | 7.6661 | 8.7262 | 9.215
South West | Landulph 132 kV | Saltash Whity Cross | Primary Substation | 11 | Hydrogen Evolution | 0.39876 | 0.45543 | 0.53912 | 0.64362 | 0.76372 | 0.91326 | 1.0801 | 1.2787 | 1.4888 | 1.7212 | 1.9313 | 2.1258 | 2.3111 | 2.4872 | 2.6553 | 2.7992 | 3.2261 | 3.5234 | 0.9644 | 1.0876 | 1.2692 | 1.4969 | 1.7594 | 2.0852 | 2.4476 | 2.8726 | 3.3309 | 3.8412 | 4.2933 | 4.7091 | 5.1038 | 5.4822 | 5.843 | 6.1668 | 7.1465 | 7.8411
South West | Landulph 132 kV | Southway | Primary Substation | 11 | Counterfactual | 3.4256 | 3.4924 | 3.5636 | 3.6419 | 3.7656 | 3.9189 | 4.0972 | 4.3371 | 4.5426 | 4.7588 | 4.98 | 5.2148 | 5.4713 | 5.7221 | 5.9705 | 6.2114 | 6.8555 | 7.0488 | 8.5044 | 8.6462 | 8.7963 | 8.9612 | 9.2207 | 9.542 | 9.9156 | 10.4133 | 10.8429 | 11.2951 | 11.7573 | 12.2489 | 12.7814 | 13.3017 | 13.8167 | 14.3159 | 15.6509 | 16.0703
South West | Landulph 132 kV | Southway | Primary Substation | 11 | Electric Engagement | 3.5058 | 3.6546 | 3.8353 | 4.0382 | 4.3357 | 4.6609 | 5.0259 | 5.493 | 5.9068 | 6.2497 | 6.55 | 6.7009 | 6.8499 | 6.9977 | 7.1443 | 7.277 | 7.6086 | 7.8383 | 8.6828 | 9.0008 | 9.3822 | 9.8097 | 10.4394 | 11.1261 | 11.8925 | 12.8622 | 13.7339 | 14.4551 | 15.0899 | 15.4229 | 15.7539 | 16.0813 | 16.4065 | 16.7033 | 17.4631 | 17.9935
South West | Landulph 132 kV | Southway | Primary Substation | 11 | Holistic Transition | 3.4893 | 3.6014 | 3.73 | 3.865 | 4.0887 | 4.3418 | 4.6112 | 4.9553 | 5.2667 | 5.6037 | 5.9366 | 6.2727 | 6.6134 | 6.9323 | 7.2379 | 7.444 | 6.5981 | 8.1424 | 8.6587 | 8.9095 | 9.1928 | 9.4888 | 9.9761 | 10.5246 | 11.1049 | 11.8344 | 12.4982 | 13.2185 | 13.9216 | 14.6309 | 15.35 | 16.0235 | 16.6701 | 17.1174 | 14.9099 | 18.7284
South West | Landulph 132 kV | Southway | Primary Substation | 11 | Hydrogen Evolution | 3.451 | 3.5376 | 3.639 | 3.7525 | 3.9573 | 4.1815 | 4.4334 | 4.7566 | 5.065 | 5.3801 | 5.7001 | 6.0084 | 6.32 | 6.615 | 6.8923 | 7.0672 | 7.3484 | 7.5501 | 8.5609 | 8.747 | 8.9617 | 9.2023 | 9.6393 | 10.1178 | 10.6515 | 11.3272 | 11.9788 | 12.6429 | 13.3114 | 13.9547 | 14.6047 | 15.2211 | 15.8016 | 16.1773 | 16.806 | 17.269
South West | Landulph 132 kV | St Levan Road | Primary Substation | 11 | Counterfactual | 0.10562 | 0.1581 | 0.2135 | 0.27257 | 0.33842 | 0.41032 | 0.48589 | 0.60628 | 0.69743 | 0.79589 | 0.89414 | 1.0246 | 1.1529 | 1.28 | 1.4013 | 1.5211 | 1.9386 | 2.0645 | 0.23353 | 0.34581 | 0.46369 | 0.58882 | 0.72799 | 0.87776 | 1.0345 | 1.2808 | 1.4686 | 1.6708 | 1.8724 | 2.1417 | 2.404 | 2.6635 | 2.9113 | 3.1559 | 4.0142 | 4.2856
South West | Landulph 132 kV | St Levan Road | Primary Substation | 11 | Electric Engagement | 0.16225 | 0.28112 | 0.4173 | 0.56751 | 0.73255 | 0.90225 | 1.0983 | 1.3628 | 1.5787 | 1.7549 | 1.9068 | 1.9847 | 2.0361 | 2.0844 | 2.1281 | 2.1745 | 2.3677 | 2.5657 | 0.35954 | 0.61838 | 0.90732 | 1.226 | 1.5757 | 1.9283 | 2.332 | 2.8723 | 3.3148 | 3.6773 | 3.9908 | 4.162 | 4.276 | 4.3833 | 4.481 | 4.5839 | 5.021 | 5.4615
South West | Landulph 132 kV | St Levan Road | Primary Substation | 11 | Holistic Transition | 0.15075 | 0.24636 | 0.34162 | 0.44444 | 0.55928 | 0.6772 | 0.80429 | 0.98391 | 1.1354 | 1.2991 | 1.4787 | 1.699 | 1.8946 | 2.08 | 2.2507 | 2.349 | 2.6174 | 2.8223 | 0.3431 | 0.55922 | 0.76949 | 0.99628 | 1.2485 | 1.5007 | 1.7692 | 2.1423 | 2.4586 | 2.7988 | 3.1706 | 3.6295 | 4.0351 | 4.4201 | 4.775 | 4.9849 | 5.5876 | 6.0574
South West | Landulph 132 kV | St Levan Road | Primary Substation | 11 | Hydrogen Evolution | 0.12361 | 0.20238 | 0.28608 | 0.37505 | 0.47912 | 0.57888 | 0.69442 | 0.85961 | 1 | 1.1481 | 1.3071 | 1.4935 | 1.6552 | 1.8078 | 1.9448 | 2.0141 | 2.1797 | 2.3024 | 0.27355 | 0.44746 | 0.62723 | 0.81938 | 1.0433 | 1.2525 | 1.4916 | 1.8297 | 2.1176 | 2.4203 | 2.7443 | 3.1287 | 3.4597 | 3.7721 | 4.0528 | 4.198 | 4.5608 | 4.833
South West | Landulph 132 kV | St Neot | Primary Substation | 11 | Counterfactual | 0.28701 | 0.3084 | 0.41315 | 0.46327 | 0.50386 | 0.5662 | 0.63605 | 0.73182 | 0.81308 | 0.9028 | 0.9881 | 1.0671 | 1.1497 | 1.2341 | 1.3135 | 1.3941 | 1.7413 | 1.9763 | 0.67784 | 0.72328 | 0.93878 | 1.0468 | 1.1357 | 1.2699 | 1.4217 | 1.6271 | 1.8031 | 2.0001 | 2.1836 | 2.3506 | 2.523 | 2.6999 | 2.8654 | 3.0329 | 3.7722 | 4.2864
South West | Landulph 132 kV | St Neot | Primary Substation | 11 | Electric Engagement | 0.31178 | 0.4312 | 0.5237 | 0.64089 | 0.74629 | 0.88647 | 1.0436 | 1.2422 | 1.4236 | 1.5937 | 1.76 | 1.8677 | 1.9788 | 2.0874 | 2.2207 | 2.3272 | 2.8338 | 3.0984 | 0.73266 | 0.9782 | 1.1849 | 1.4439 | 1.6762 | 1.9777 | 2.3135 | 2.7353 | 3.1223 | 3.4881 | 3.8475 | 4.0874 | 4.3353 | 4.5797 | 4.8716 | 5.1106 | 6.233 | 6.855
South West | Landulph 132 kV | St Neot | Primary Substation | 11 | Holistic Transition | 0.30588 | 0.41364 | 0.49664 | 0.60073 | 0.70095 | 0.83702 | 0.99757 | 1.2052 | 1.3927 | 1.5871 | 1.759 | 1.9154 | 2.0716 | 2.2015 | 2.3536 | 2.4495 | 2.8709 | 3.0614 | 0.72352 | 0.94786 | 1.1416 | 1.3804 | 1.6131 | 1.9178 | 2.2812 | 2.749 | 3.1708 | 3.6046 | 3.9782 | 4.3172 | 4.655 | 4.9324 | 5.2526 | 5.4605 | 6.3886 | 6.8164
South West | Landulph 132 kV | St Neot | Primary Substation | 11 | Hydrogen Evolution | 0.29584 | 0.39536 | 0.43991 | 0.51082 | 0.57207 | 0.66475 | 0.7677 | 0.90003 | 1.0462 | 1.2084 | 1.3526 | 1.4847 | 1.6142 | 1.7361 | 1.8672 | 1.9527 | 2.3036 | 2.5753 | 0.69724 | 0.90034 | 0.99735 | 1.1518 | 1.2859 | 1.4852 | 1.7067 | 1.9879 | 2.3051 | 2.6602 | 2.9687 | 3.2494 | 3.5227 | 3.7828 | 4.06 | 4.2462 | 5.0349 | 5.6543
South West | Landulph 132 kV | Stentaway | Primary Substation | 11 | Counterfactual | 0.45142 | 0.5453 | 0.67787 | 0.81183 | 0.96074 | 1.1291 | 1.3149 | 1.5817 | 1.8006 | 2.0264 | 2.2571 | 2.4698 | 2.6939 | 2.9174 | 3.1339 | 3.3463 | 4.0642 | 4.3263 | 1.0505 | 1.2492 | 1.527 | 1.8081 | 2.1209 | 2.4741 | 2.8642 | 3.4179 | 3.8758 | 4.3494 | 4.8301 | 5.2689 | 5.7287 | 6.1875 | 6.631 | 7.0647 | 8.5509 | 9.1265
South West | Landulph 132 kV | Stentaway | Primary Substation | 11 | Electric Engagement | 0.55177 | 0.76182 | 1.0534 | 1.3592 | 1.6947 | 2.0627 | 2.4847 | 3.0293 | 3.4901 | 3.8796 | 4.2229 | 4.3423 | 4.4409 | 4.5371 | 4.6303 | 4.7197 | 5.1312 | 5.4569 | 1.2737 | 1.7274 | 2.3496 | 3.0002 | 3.7111 | 4.4875 | 5.3715 | 6.5009 | 7.4625 | 8.283 | 9.0105 | 9.2807 | 9.5069 | 9.7287 | 9.943 | 10.1496 | 11.1012 | 11.8653
South West | Landulph 132 kV | Stentaway | Primary Substation | 11 | Holistic Transition | 0.53088 | 0.69301 | 0.91959 | 1.1421 | 1.3891 | 1.669 | 1.9856 | 2.3996 | 2.7631 | 3.136 | 3.518 | 3.8637 | 4.1851 | 4.4769 | 4.746 | 4.9029 | 5.3545 | 5.6525 | 1.2434 | 1.6079 | 2.1082 | 2.5982 | 3.1411 | 3.7511 | 4.4387 | 5.3258 | 6.107 | 6.9046 | 7.7147 | 8.4445 | 9.1204 | 9.7317 | 10.2961 | 10.6361 | 11.6719 | 12.3724
South West | Landulph 132 kV | Stentaway | Primary Substation | 11 | Hydrogen Evolution | 0.48275 | 0.61659 | 0.80041 | 0.98596 | 1.1943 | 1.4352 | 1.7068 | 2.0669 | 2.3943 | 2.7421 | 3.096 | 3.411 | 3.698 | 3.9663 | 4.213 | 4.3385 | 4.6552 | 4.9127 | 1.1203 | 1.4133 | 1.8055 | 2.2021 | 2.6469 | 3.1594 | 3.7339 | 4.4847 | 5.1739 | 5.9079 | 6.648 | 7.3012 | 7.8926 | 8.447 | 8.9573 | 9.225 | 9.9486 | 10.5432
South West | Landulph 132 kV | Tavistock | Primary Substation | 11 | Counterfactual | 1.3956 | 1.4899 | 1.6028 | 1.7395 | 1.8927 | 2.0565 | 2.2372 | 2.5044 | 2.715 | 2.9201 | 3.1287 | 3.3454 | 3.5841 | 3.8201 | 4.0515 | 4.2807 | 5.0523 | 5.3367 | 3.4159 | 3.6167 | 3.8534 | 4.1391 | 4.4601 | 4.8027 | 5.1796 | 5.7303 | 6.1674 | 6.5916 | 7.0214 | 7.466 | 7.9545 | 8.437 | 8.91 | 9.3781 | 10.968 | 11.5756
South West | Landulph 132 kV | Tavistock | Primary Substation | 11 | Electric Engagement | 1.4991 | 1.7034 | 1.9835 | 2.3257 | 2.6987 | 3.0944 | 3.5449 | 4.1208 | 4.5971 | 4.9821 | 5.3172 | 5.4504 | 5.5688 | 5.6791 | 5.7899 | 5.891 | 6.3275 | 6.7369 | 3.6465 | 4.0856 | 4.6869 | 5.4236 | 6.2228 | 7.0673 | 8.0189 | 9.2192 | 10.2158 | 11.0254 | 11.7351 | 12.0373 | 12.3092 | 12.5647 | 12.8213 | 13.0578 | 14.0907 | 15.0571
South West | Landulph 132 kV | Tavistock | Primary Substation | 11 | Holistic Transition | 1.4783 | 1.6361 | 1.8326 | 2.0618 | 2.3118 | 2.5932 | 2.905 | 3.3099 | 3.656 | 4.0017 | 4.362 | 4.7116 | 5.0451 | 5.3543 | 5.6447 | 5.8166 | 6.2897 | 6.6908 | 3.6166 | 3.9706 | 4.4044 | 4.9069 | 5.4527 | 6.0636 | 6.7339 | 7.5894 | 8.322 | 9.0481 | 9.8031 | 10.5366 | 11.2371 | 11.8885 | 12.5019 | 12.8777 | 13.9759 | 14.9162
South West | Landulph 132 kV | Tavistock | Primary Substation | 11 | Hydrogen Evolution | 1.4294 | 1.5535 | 1.7168 | 1.9269 | 2.1569 | 2.4091 | 2.6975 | 3.0813 | 3.4105 | 3.7375 | 4.0772 | 4.4063 | 4.719 | 5.0046 | 5.2718 | 5.4077 | 5.7264 | 6.0051 | 3.4917 | 3.7605 | 4.11 | 4.5636 | 5.0578 | 5.5968 | 6.2076 | 7.0086 | 7.6942 | 8.3706 | 9.072 | 9.7514 | 10.3974 | 10.9889 | 11.5433 | 11.8344 | 12.5625 | 13.2002
South West | Landulph 132 kV | Torpoint Antony | Primary Substation | 11 | Counterfactual | 0.63828 | 0.6711 | 0.70839 | 0.74878 | 0.79594 | 0.85761 | 0.92663 | 1.0292 | 1.112 | 1.1999 | 1.2902 | 1.3823 | 1.4842 | 1.5857 | 1.6838 | 1.7824 | 2.1522 | 2.338 | 1.5644 | 1.6347 | 1.7138 | 1.7993 | 1.8988 | 2.028 | 2.1726 | 2.3848 | 2.5574 | 2.7414 | 2.929 | 3.1193 | 3.3288 | 3.5375 | 3.739 | 3.9411 | 4.7094 | 5.1069
South West | Landulph 132 kV | Torpoint Antony | Primary Substation | 11 | Electric Engagement | 0.67572 | 0.7507 | 0.84589 | 0.95131 | 1.07 | 1.2164 | 1.3881 | 1.6127 | 1.807 | 1.9774 | 2.1327 | 2.2091 | 2.2823 | 2.3546 | 2.4261 | 2.4947 | 2.9304 | 3.1233 | 1.6474 | 1.809 | 2.0119 | 2.2353 | 2.4855 | 2.7915 | 3.1488 | 3.6127 | 4.0159 | 4.3711 | 4.6966 | 4.8635 | 5.0243 | 5.1838 | 5.3407 | 5.4919 | 6.4762 | 6.9185
South West | Landulph 132 kV | Torpoint Antony | Primary Substation | 11 | Holistic Transition | 0.66758 | 0.72624 | 0.79742 | 0.87316 | 0.96196 | 1.08 | 1.2135 | 1.3904 | 1.549 | 1.7178 | 1.8883 | 2.2521 | 2.413 | 2.5611 | 2.7017 | 2.7954 | 3.1412 | 3.3462 | 1.6353 | 1.7679 | 1.9264 | 2.0941 | 2.2897 | 2.5442 | 2.8325 | 3.21 | 3.5491 | 3.9081 | 4.267 | 5.1112 | 5.4498 | 5.7608 | 6.0562 | 6.2576 | 7.0195 | 7.4845
South West | Landulph 132 kV | Torpoint Antony | Primary Substation | 11 | Hydrogen Evolution | 0.65002 | 0.69294 | 0.74512 | 0.8038 | 0.87327 | 0.96582 | 1.0729 | 1.2181 | 1.3588 | 1.5081 | 1.6571 | 1.8004 | 1.94 | 2.0695 | 2.1928 | 2.2661 | 2.5932 | 2.7821 | 1.5904 | 1.6833 | 1.7943 | 1.9187 | 2.0658 | 2.26 | 2.484 | 2.7844 | 3.0779 | 3.3899 | 3.6985 | 3.9951 | 4.2836 | 4.5527 | 4.8086 | 4.9646 | 5.712 | 6.1309
South West | Landulph 132 kV | Torpoint Town | Primary Substation | 11 | Counterfactual | 0.11394 | 0.14152 | 0.17213 | 0.20621 | 0.24564 | 0.29005 | 0.34095 | 0.42018 | 0.48266 | 0.54915 | 0.61847 | 0.6917 | 0.77387 | 0.85591 | 0.93538 | 1.0142 | 1.2812 | 1.3814 | 0.26475 | 0.32328 | 0.38769 | 0.4591 | 0.54139 | 0.63382 | 0.73947 | 0.90196 | 1.0309 | 1.168 | 1.3108 | 1.4612 | 1.6296 | 1.7975 | 1.9601 | 2.1214 | 2.6722 | 2.8873
South West | Landulph 132 kV | Torpoint Town | Primary Substation | 11 | Electric Engagement | 0.14909 | 0.21108 | 0.28887 | 0.37457 | 0.47248 | 0.57994 | 0.70816 | 0.88013 | 1.021 | 1.1372 | 1.2362 | 1.2711 | 1.3027 | 1.333 | 1.3621 | 1.389 | 1.5036 | 1.6173 | 0.34296 | 0.47516 | 0.63853 | 0.81767 | 1.0217 | 1.245 | 1.5103 | 1.863 | 2.1531 | 2.3937 | 2.6001 | 2.6778 | 2.7491 | 2.8177 | 2.8836 | 2.945 | 3.2111 | 3.4713
South West | Landulph 132 kV | Torpoint Town | Primary Substation | 11 | Holistic Transition | 0.14184 | 0.18762 | 0.24122 | 0.29805 | 0.36465 | 0.44152 | 0.52971 | 0.64984 | 0.75425 | 0.86415 | 0.97992 | 1.0969 | 1.2118 | 1.32 | 1.4197 | 1.4787 | 1.6388 | 1.7694 | 0.33243 | 0.43469 | 0.55176 | 0.67525 | 0.81899 | 0.98377 | 1.1713 | 1.4228 | 1.6423 | 1.8726 | 2.1145 | 2.3588 | 2.599 | 2.8254 | 3.0345 | 3.1622 | 3.5285 | 3.8318
South West | Landulph 132 kV | Torpoint Town | Primary Substation | 11 | Hydrogen Evolution | 0.12515 | 0.16023 | 0.20504 | 0.2527 | 0.30964 | 0.37568 | 0.45421 | 0.56528 | 0.66173 | 0.76393 | 0.87111 | 0.97693 | 1.0802 | 1.1766 | 1.2649 | 1.3111 | 1.4158 | 1.5038 | 0.28966 | 0.3649 | 0.45939 | 0.55971 | 0.67924 | 0.81737 | 0.98081 | 1.2093 | 1.4084 | 1.6188 | 1.839 | 2.0564 | 2.2687 | 2.467 | 2.6491 | 2.7469 | 2.9812 | 3.1795
South West | Landulph 132 kV | Weston Mill | Primary Substation | 11 | Counterfactual | 0.29628 | 0.35937 | 0.44302 | 0.57807 | 0.70646 | 0.7963 | 0.89669 | 1.0553 | 1.1775 | 1.3067 | 1.4387 | 1.5781 | 1.7422 | 1.9049 | 2.0631 | 2.2196 | 2.7395 | 2.8813 | 0.70262 | 0.83637 | 1.0122 | 1.2949 | 1.5637 | 1.7512 | 1.96 | 2.2856 | 2.538 | 2.8047 | 3.0764 | 3.3619 | 3.6977 | 4.0303 | 4.3535 | 4.6732 | 5.7462 | 6.0574
South West | Landulph 132 kV | Weston Mill | Primary Substation | 11 | Electric Engagement | 0.3721 | 0.51269 | 0.69983 | 0.96152 | 1.2271 | 1.4493 | 1.7124 | 2.0666 | 2.3554 | 2.5892 | 2.7837 | 2.8331 | 2.887 | 2.9371 | 2.9853 | 3.0305 | 3.2297 | 3.4251 | 0.8713 | 1.1705 | 1.5658 | 2.1191 | 2.6787 | 3.1403 | 3.6837 | 4.4087 | 5.0021 | 5.4849 | 5.889 | 6.0022 | 6.1264 | 6.2426 | 6.3543 | 6.4599 | 6.9325 | 7.3873
South West | Landulph 132 kV | Weston Mill | Primary Substation | 11 | Holistic Transition | 0.35635 | 0.46125 | 0.59696 | 0.79528 | 0.99013 | 1.1413 | 1.3145 | 1.5548 | 1.7599 | 1.9771 | 2.2041 | 2.4354 | 2.6746 | 2.8961 | 3.0991 | 3.2113 | 3.4912 | 3.6991 | 0.84856 | 1.0815 | 1.3785 | 1.8094 | 2.2323 | 2.5567 | 2.9255 | 3.4284 | 3.8598 | 4.3143 | 4.7871 | 5.2679 | 5.767 | 6.2292 | 6.6536 | 6.8964 | 7.5464 | 8.0407
South West | Landulph 132 kV | Weston Mill | Primary Substation | 11 | Hydrogen Evolution | 0.3197 | 0.40179 | 0.515 | 0.6916 | 0.86474 | 0.99252 | 1.143 | 1.3588 | 1.5444 | 1.7411 | 1.9462 | 2.1471 | 2.3525 | 2.5417 | 2.715 | 2.796 | 2.9574 | 3.0874 | 0.75488 | 0.93077 | 1.1713 | 1.548 | 1.9168 | 2.1841 | 2.4969 | 2.9399 | 3.3224 | 3.727 | 4.1468 | 4.5577 | 4.9792 | 5.3679 | 5.7244 | 5.8961 | 6.2669 | 6.5668
South West | Landulph 132 kV | Yelverton | Primary Substation | 11 | Counterfactual | 0.29679 | 0.33077 | 0.36896 | 0.41052 | 0.45746 | 0.50932 | 0.56918 | 0.66387 | 0.74119 | 0.82709 | 0.91505 | 1.007 | 1.108 | 1.2082 | 1.3062 | 1.4034 | 1.7273 | 1.8415 | 0.70882 | 0.78078 | 0.86078 | 0.9476 | 1.0453 | 1.1529 | 1.2768 | 1.4703 | 1.6295 | 1.8065 | 1.9874 | 2.1761 | 2.3825 | 2.5873 | 2.7873 | 2.9857 | 3.6529 | 3.8972
South West | Landulph 132 kV | Yelverton | Primary Substation | 11 | Electric Engagement | 0.34033 | 0.41787 | 0.51449 | 0.62197 | 0.74128 | 0.87291 | 1.0303 | 1.2411 | 1.4193 | 1.5708 | 1.7002 | 1.7447 | 1.783 | 1.8185 | 1.8532 | 1.8844 | 2.0208 | 2.1452 | 0.80562 | 0.97075 | 1.1739 | 1.3987 | 1.6472 | 1.9205 | 2.2456 | 2.677 | 3.0439 | 3.3578 | 3.6272 | 3.7263 | 3.8127 | 3.8932 | 3.972 | 4.0435 | 4.3611 | 4.6484
South West | Landulph 132 kV | Yelverton | Primary Substation | 11 | Holistic Transition | 0.33117 | 0.38827 | 0.45367 | 0.52349 | 0.60036 | 0.69206 | 0.79761 | 0.94159 | 1.0708 | 1.2135 | 1.3619 | 1.5067 | 1.645 | 1.7726 | 1.8919 | 1.9599 | 2.1376 | 2.2828 | 0.79224 | 0.9196 | 1.0624 | 1.214 | 1.3796 | 1.5756 | 1.7993 | 2.0993 | 2.3702 | 2.6684 | 2.9779 | 3.28 | 3.5686 | 3.8356 | 4.0858 | 4.233 | 4.6424 | 4.9805
South West | Landulph 132 kV | Yelverton | Primary Substation | 11 | Hydrogen Evolution | 0.31042 | 0.35417 | 0.40827 | 0.46749 | 0.53452 | 0.61351 | 0.70855 | 0.84308 | 0.96577 | 1.1006 | 1.2404 | 1.3756 | 1.5041 | 1.6219 | 1.7311 | 1.7848 | 1.9 | 1.9972 | 0.73914 | 0.83282 | 0.94695 | 1.0715 | 1.2118 | 1.3765 | 1.5734 | 1.8492 | 2.1018 | 2.3792 | 2.6663 | 2.9438 | 3.2075 | 3.4498 | 3.6745 | 3.7882 | 4.0477 | 4.2669
South West | Melksham 132 kV | Batheaston | Primary Substation | 11 | Counterfactual | 0.37339 | 0.45427 | 0.5456 | 0.64346 | 0.75695 | 0.88432 | 1.0252 | 1.2424 | 1.4136 | 1.5849 | 1.76 | 1.9389 | 2.1422 | 2.3445 | 2.5415 | 2.7339 | 3.3434 | 3.4948 | 0.83423 | 1.0054 | 1.197 | 1.402 | 1.6393 | 1.9048 | 2.1977 | 2.6435 | 2.9974 | 3.3502 | 3.71 | 4.0764 | 4.4906 | 4.9028 | 5.3042 | 5.6958 | 6.9483 | 7.2783
South West | Melksham 132 kV | Batheaston | Primary Substation | 11 | Electric Engagement | 0.46953 | 0.64882 | 0.86752 | 1.1192 | 1.4006 | 1.7041 | 2.0396 | 2.4908 | 2.8545 | 3.1504 | 3.4072 | 3.4836 | 3.5495 | 3.6114 | 3.6686 | 3.7236 | 3.9516 | 4.1713 | 1.0481 | 1.4297 | 1.8892 | 2.4175 | 3.0055 | 3.6378 | 4.3302 | 5.2533 | 6.0002 | 6.6108 | 7.1432 | 7.3138 | 7.4627 | 7.6037 | 7.7346 | 7.8607 | 8.3936 | 8.898
South West | Melksham 132 kV | Batheaston | Primary Substation | 11 | Holistic Transition | 0.44982 | 0.58382 | 0.74577 | 0.91883 | 1.1086 | 1.3026 | 1.5241 | 1.8305 | 2.0922 | 2.3664 | 2.6633 | 2.9561 | 3.2374 | 3.4986 | 3.7387 | 3.869 | 4.1805 | 4.3971 | 1.0199 | 1.3177 | 1.6718 | 2.0482 | 2.4593 | 2.8752 | 3.346 | 3.9866 | 4.5361 | 5.1095 | 5.7267 | 6.3348 | 6.9194 | 7.4626 | 7.963 | 8.2435 | 8.9612 | 9.4744
South West | Melksham 132 kV | Batheaston | Primary Substation | 11 | Hydrogen Evolution | 0.40259 | 0.50727 | 0.63477 | 0.77249 | 0.93096 | 1.1099 | 1.3184 | 1.6155 | 1.8579 | 2.1162 | 2.388 | 2.655 | 2.9113 | 3.1456 | 3.3627 | 3.4632 | 3.6355 | 3.7536 | 0.89915 | 1.1231 | 1.3913 | 1.6822 | 2.0154 | 2.3898 | 2.8234 | 3.434 | 3.9325 | 4.4626 | 5.0181 | 5.5632 | 6.0861 | 6.5647 | 7.0086 | 7.219 | 7.6082 | 7.88
South West | Melksham 132 kV | Combe Park | Primary Substation | 6.6 | Counterfactual | 1.9102 | 1.9975 | 2.0722 | 2.1636 | 2.2718 | 2.4077 | 2.5616 | 2.7639 | 2.897 | 3.033 | 3.1772 | 3.322 | 3.4959 | 3.6641 | 3.8264 | 3.9817 | 4.4718 | 4.5919 | 4.4188 | 4.6028 | 4.7596 | 4.9507 | 5.1766 | 5.4606 | 5.7812 | 6.1984 | 6.4725 | 6.7524 | 7.0483 | 7.3445 | 7.7022 | 8.0485 | 8.3818 | 8.6979 | 9.7052 | 9.9669
South West | Melksham 132 kV | Combe Park | Primary Substation | 6.6 | Electric Engagement | 1.9849 | 2.1631 | 2.3392 | 2.5233 | 2.7722 | 3.039 | 3.3471 | 3.7488 | 4.0411 | 4.2973 | 4.5148 | 4.5768 | 4.6313 | 4.6868 | 4.7372 | 4.7834 | 4.9969 | 4.1788 | 4.5849 | 4.9663 | 5.3359 | 5.7215 | 6.244 | 6.8026 | 7.4454 | 8.2739 | 8.8752 | 9.4135 | 9.8688 | 10.0056 | 10.1272 | 10.25 | 10.3627 | 10.4665 | 10.9539 | 8.8584
South West | Melksham 132 kV | Combe Park | Primary Substation | 6.6 | Holistic Transition | 1.9698 | 2.1183 | 2.2388 | 2.3647 | 2.5432 | 2.7404 | 2.9659 | 3.252 | 3.4603 | 3.6798 | 3.9343 | 4.1851 | 3.389 | 3.6059 | 3.8069 | 3.9184 | 4.2057 | 5.4671 | 4.5634 | 4.891 | 5.1543 | 5.4278 | 5.8142 | 6.239 | 6.7196 | 7.321 | 7.7559 | 8.2144 | 8.7476 | 9.2732 | 7.1842 | 7.6347 | 8.0532 | 8.2923 | 8.9453 | 12.0583
South West | Melksham 132 kV | Combe Park | Primary Substation | 6.6 | Hydrogen Evolution | 1.9329 | 2.0564 | 2.1591 | 2.2641 | 2.422 | 2.602 | 2.8058 | 3.0803 | 3.276 | 3.4974 | 3.7272 | 3.9497 | 4.157 | 4.3454 | 4.5216 | 4.6059 | 5.3076 | 5.4321 | 4.4693 | 4.7343 | 4.9503 | 5.1713 | 5.5056 | 5.8852 | 6.3137 | 6.8831 | 7.2843 | 7.7443 | 8.2195 | 8.6768 | 9.0991 | 9.4832 | 9.8427 | 10.0183 | 11.7269 | 12.0042
South West | Melksham 132 kV | Dorchester St - New | Primary Substation | 6.6 | Counterfactual | 0.41572 | 0.60797 | 0.76543 | 1.1345 | 1.4503 | 1.8943 | 2.4186 | 2.7579 | 3.0318 | 3.3086 | 3.5987 | 3.8961 | 4.3501 | 4.8022 | 5.2204 | 5.537 | 6.701 | 7.3313 | 0.9182 | 1.3315 | 1.6645 | 2.4371 | 3.0994 | 4.0318 | 5.1344 | 5.8354 | 6.405 | 6.9798 | 7.5812 | 8.1954 | 9.1842 | 10.1723 | 11.0782 | 11.7285 | 14.1475 | 15.4848
South West | Melksham 132 kV | Dorchester St - New | Primary Substation | 6.6 | Electric Engagement | 0.53044 | 0.91719 | 1.4145 | 1.9468 | 2.5396 | 3.22 | 3.9248 | 4.5706 | 5.1689 | 5.9616 | 6.6173 | 6.8727 | 7.0886 | 7.2845 | 7.4744 | 7.6498 | 8.4661 | 9.1887 | 1.172 | 2.0184 | 3.0808 | 4.2124 | 5.4753 | 6.9283 | 8.4243 | 9.7595 | 11.0251 | 12.8175 | 14.2888 | 14.8513 | 15.3298 | 15.7598 | 16.177 | 16.5651 | 18.4043 | 20.0183
South West | Melksham 132 kV | Dorchester St - New | Primary Substation | 6.6 | Holistic Transition | 0.50623 | 0.85513 | 1.2351 | 1.7537 | 2.2232 | 2.7964 | 3.3941 | 3.8789 | 4.3162 | 4.8357 | 5.5704 | 6.2971 | 6.813 | 7.261 | 7.6866 | 7.9864 | 9.0219 | 9.8432 | 1.1354 | 1.9214 | 2.7514 | 3.8783 | 4.9004 | 6.1471 | 7.4417 | 8.4647 | 9.3926 | 10.5146 | 12.1575 | 13.7803 | 14.8827 | 15.827 | 16.726 | 17.3731 | 19.6819 | 21.5315
South West | Melksham 132 kV | Dorchester St - New | Primary Substation | 6.6 | Hydrogen Evolution | 0.45181 | 0.74043 | 1.1349 | 1.5252 | 1.9604 | 2.5072 | 3.0766 | 3.5427 | 3.9656 | 4.6128 | 5.3012 | 5.8952 | 6.3372 | 6.7303 | 7.1044 | 7.3401 | 8.0702 | 8.6979 | 0.99736 | 1.6291 | 2.4747 | 3.3084 | 4.2401 | 5.4159 | 6.6325 | 7.5977 | 8.4763 | 9.9093 | 11.4355 | 12.7309 | 13.6519 | 14.467 | 15.2434 | 15.743 | 17.3441 | 18.7179
South West | Melksham 132 kV | Entry Hill | Primary Substation | 6.6 | Counterfactual | 0.45797 | 0.56923 | 0.6777 | 0.84148 | 0.99744 | 1.1694 | 1.3247 | 1.5672 | 1.7721 | 1.9906 | 2.2182 | 2.4498 | 2.7099 | 2.9629 | 3.2131 | 3.4539 | 4.2908 | 4.635 | 1.0235 | 1.2589 | 1.4869 | 1.8301 | 2.1564 | 2.5163 | 2.8398 | 3.3392 | 3.7646 | 4.2187 | 4.6904 | 5.1689 | 5.7048 | 6.2262 | 6.7409 | 7.2352 | 8.9735 | 9.7185
South West | Melksham 132 kV | Entry Hill | Primary Substation | 6.6 | Electric Engagement | 0.55979 | 0.79876 | 1.0631 | 1.3672 | 1.7027 | 2.0467 | 2.4132 | 2.953 | 3.4107 | 3.794 | 4.1329 | 4.2692 | 4.3907 | 4.5115 | 4.6286 | 4.7459 | 5.2738 | 5.7768 | 1.2498 | 1.7603 | 2.3182 | 2.9589 | 3.6627 | 4.3809 | 5.1386 | 6.2511 | 7.2005 | 8.0035 | 8.7153 | 9.0157 | 9.2857 | 9.5562 | 9.8183 | 10.0807 | 11.2743 | 12.4016
South West | Melksham 132 kV | Entry Hill | Primary Substation | 6.6 | Holistic Transition | 0.53811 | 0.72911 | 0.91214 | 1.1528 | 1.3881 | 1.6289 | 1.8904 | 2.2775 | 2.63 | 2.999 | 3.39 | 3.7808 | 4.155 | 4.5028 | 4.8253 | 5.0302 | 5.685 | 6.1984 | 1.2183 | 1.6401 | 2.0404 | 2.5641 | 3.0739 | 3.5927 | 4.1486 | 4.9644 | 5.712 | 6.4919 | 7.3147 | 8.1368 | 8.922 | 9.6517 | 10.3298 | 10.7722 | 12.2433 | 13.4126
South West | Melksham 132 kV | Entry Hill | Primary Substation | 6.6 | Hydrogen Evolution | 0.48845 | 0.6478 | 0.81441 | 1.0084 | 1.2131 | 1.425 | 1.6425 | 1.9838 | 2.2953 | 2.6349 | 2.9868 | 3.3272 | 3.6501 | 3.9498 | 4.2303 | 4.3881 | 4.841 | 5.2178 | 1.0913 | 1.4337 | 1.7862 | 2.1984 | 2.6314 | 3.0769 | 3.5289 | 4.2341 | 4.8835 | 5.5925 | 6.3229 | 7.0267 | 7.6927 | 8.311 | 8.8923 | 9.2281 | 10.234 | 11.0756
South West | Melksham 132 kV | Oldfield Park | Primary Substation | 6.6 | Counterfactual | 0.87194 | 0.9865 | 1.1074 | 1.3853 | 1.57 | 1.7469 | 1.8988 | 2.1367 | 2.339 | 2.5591 | 2.7796 | 3.0148 | 3.2692 | 3.5251 | 3.7684 | 4.0135 | 4.8577 | 5.1976 | 1.971 | 2.2138 | 2.4679 | 3.0489 | 3.4358 | 3.8059 | 4.1221 | 4.6122 | 5.032 | 5.489 | 5.9461 | 6.4319 | 6.9565 | 7.4836 | 7.9844 | 8.4876 | 10.2408 | 10.977
South West | Melksham 132 kV | Oldfield Park | Primary Substation | 6.6 | Electric Engagement | 0.97391 | 1.2204 | 1.5903 | 1.9909 | 2.3066 | 2.619 | 2.982 | 3.5175 | 3.9727 | 4.3568 | 4.698 | 4.845 | 4.9782 | 5.1009 | 5.2246 | 5.3424 | 5.8827 | 6.4036 | 2.1979 | 2.7254 | 3.5114 | 4.3606 | 5.0216 | 5.6706 | 6.4213 | 7.5247 | 8.469 | 9.2726 | 9.988 | 10.3124 | 10.6081 | 10.8822 | 11.1574 | 11.4203 | 12.6377 | 13.8
South West | Melksham 132 kV | Oldfield Park | Primary Substation | 6.6 | Holistic Transition | 0.95362 | 1.1528 | 1.3931 | 1.8082 | 1.9968 | 2.2163 | 2.4766 | 2.8677 | 3.2172 | 3.5779 | 3.9722 | 4.3698 | 4.7515 | 5.1086 | 5.4414 | 5.6505 | 6.3301 | 6.8758 | 2.1695 | 2.6097 | 3.1337 | 4.0341 | 4.4428 | 4.9133 | 5.469 | 6.2929 | 7.0334 | 7.7955 | 8.6242 | 9.4596 | 10.2598 | 11.0084 | 11.7075 | 12.1591 | 13.6823 | 14.9199
South West | Melksham 132 kV | Oldfield Park | Primary Substation | 6.6 | Hydrogen Evolution | 0.90242 | 1.0686 | 1.3378 | 1.6527 | 1.8112 | 1.9956 | 2.2099 | 2.5471 | 2.8611 | 3.195 | 3.5419 | 3.8817 | 4.2109 | 4.5121 | 4.7961 | 4.9515 | 5.4037 | 5.7829 | 2.0388 | 2.3965 | 2.9717 | 3.6447 | 3.9781 | 4.3636 | 4.8086 | 5.5057 | 6.1596 | 6.8558 | 7.5753 | 8.2793 | 8.9595 | 9.5831 | 10.1712 | 10.502 | 11.5053 | 12.3502
South West | Melksham 132 kV | Park Street | Primary Substation | 6.6 | Counterfactual | 0.26117 | 0.34418 | 0.44644 | 0.5985 | 0.71637 | 0.8503 | 1.0063 | 1.2282 | 1.4184 | 1.6201 | 1.8326 | 2.0502 | 2.2958 | 2.533 | 2.7675 | 2.9946 | 3.8219 | 4.2146 | 0.56691 | 0.74426 | 0.95844 | 1.2766 | 1.5232 | 1.8019 | 2.1266 | 2.5826 | 2.9765 | 3.3943 | 3.8339 | 4.2831 | 4.7895 | 5.2784 | 5.761 | 6.2275 | 7.9436 | 8.782
South West | Melksham 132 kV | Park Street | Primary Substation | 6.6 | Electric Engagement | 0.34763 | 0.52654 | 0.75756 | 1.0566 | 1.3279 | 1.6095 | 1.9683 | 2.4519 | 2.8687 | 3.2203 | 3.5386 | 3.6912 | 3.8279 | 3.9578 | 4.0889 | 4.208 | 4.7708 | 5.3064 | 0.75862 | 1.1432 | 1.6288 | 2.2583 | 2.8243 | 3.4082 | 4.1536 | 5.1501 | 6.0152 | 6.7518 | 7.419 | 7.7517 | 8.0517 | 8.3372 | 8.6245 | 8.8875 | 10.1443 | 11.3287
South West | Melksham 132 kV | Park Street | Primary Substation | 6.6 | Holistic Transition | 0.32921 | 0.47021 | 0.62978 | 0.87284 | 1.0477 | 1.2475 | 1.5161 | 1.8706 | 2.1929 | 2.5297 | 2.8978 | 3.2721 | 3.635 | 3.9768 | 4.2931 | 4.5105 | 5.2345 | 5.817 | 0.73191 | 1.0487 | 1.3963 | 1.9228 | 2.2996 | 2.7264 | 3.2992 | 4.0438 | 4.7244 | 5.4334 | 6.2068 | 6.9932 | 7.7534 | 8.47 | 9.1349 | 9.6017 | 11.2092 | 12.5188
South West | Melksham 132 kV | Park Street | Primary Substation | 6.6 | Hydrogen Evolution | 0.28749 | 0.39254 | 0.54196 | 0.75154 | 0.90326 | 1.0737 | 1.3048 | 1.6181 | 1.9158 | 2.231 | 2.5631 | 2.8843 | 3.196 | 3.4847 | 3.7542 | 3.9169 | 4.4115 | 4.8276 | 0.62506 | 0.85168 | 1.1666 | 1.6117 | 1.9295 | 2.2847 | 2.7672 | 3.4141 | 4.0323 | 4.6879 | 5.3762 | 6.0415 | 6.6854 | 7.2825 | 7.8404 | 8.1848 | 9.2669 | 10.18
South West | Melksham 132 kV | Twerton | Primary Substation | 6.6 | Counterfactual | 0.27319 | 0.3484 | 0.43805 | 0.83795 | 1.0015 | 1.2069 | 1.365 | 1.5964 | 1.796 | 1.9776 | 2.1648 | 2.3614 | 2.5853 | 2.8062 | 3.0189 | 3.2255 | 3.9486 | 4.2619 | 0.60879 | 0.76817 | 0.95599 | 1.7643 | 2.1064 | 2.5362 | 2.8657 | 3.3429 | 3.758 | 4.1338 | 4.5207 | 4.926 | 5.3896 | 5.8468 | 6.2862 | 6.7099 | 8.2082 | 8.8786
South West | Melksham 132 kV | Twerton | Primary Substation | 6.6 | Electric Engagement | 0.35739 | 0.51789 | 0.72003 | 1.2995 | 1.6753 | 2.0598 | 2.3748 | 2.8204 | 3.2013 | 3.5376 | 3.8166 | 3.9252 | 4.0216 | 4.1121 | 4.2005 | 4.282 | 4.6593 | 5.095 | 0.79566 | 1.1375 | 1.5606 | 2.747 | 3.5427 | 4.3555 | 5.0067 | 5.9236 | 6.7143 | 7.4241 | 8.013 | 8.2536 | 8.469 | 8.6718 | 8.87 | 9.0538 | 9.9202 | 10.8861
South West | Melksham 132 kV | Twerton | Primary Substation | 6.6 | Holistic Transition | 0.33899 | 0.46005 | 0.64388 | 1.1514 | 1.4451 | 1.7024 | 1.9171 | 2.2365 | 2.5203 | 2.8221 | 3.1472 | 3.4747 | 3.7794 | 4.0636 | 4.3289 | 4.4948 | 5.0004 | 5.4855 | 0.76858 | 1.0379 | 1.4363 | 2.484 | 3.1202 | 3.6747 | 4.13 | 4.7995 | 5.3978 | 6.0335 | 6.7211 | 7.4138 | 8.0535 | 8.65 | 9.2082 | 9.5672 | 10.7135 | 11.8043
South West | Melksham 132 kV | Twerton | Primary Substation | 6.6 | Hydrogen Evolution | 0.2993 | 0.39318 | 0.51934 | 0.98073 | 1.2349 | 1.4935 | 1.7115 | 2.0382 | 2.3055 | 2.5997 | 2.9001 | 3.1886 | 3.459 | 3.7073 | 3.9388 | 4.0657 | 4.4016 | 4.6876 | 0.66642 | 0.86718 | 1.1317 | 2.0724 | 2.6147 | 3.1656 | 3.6217 | 4.3009 | 4.8551 | 5.471 | 6.0977 | 6.6969 | 7.2551 | 7.7684 | 8.2474 | 8.5174 | 9.2674 | 9.9062
South West | Sandford 132 kV | Axbridge | Primary Substation | 11 | Counterfactual | 2.296 | 2.3263 | 2.3666 | 2.3949 | 2.4275 | 2.4677 | 2.5135 | 2.5805 | 2.6349 | 2.6955 | 2.7527 | 2.8061 | 2.8643 | 2.9242 | 2.9831 | 3.0418 | 3.257 | 3.3641 | 5.7193 | 5.784 | 5.8703 | 5.9315 | 6.0021 | 6.089 | 6.1885 | 6.3312 | 6.4486 | 6.5807 | 6.7032 | 6.8153 | 6.9361 | 7.0605 | 7.1829 | 7.3046 | 7.763 | 8.0045
South West | Sandford 132 kV | Axbridge | Primary Substation | 11 | Electric Engagement | 2.3193 | 2.3778 | 2.4672 | 2.5444 | 2.6276 | 2.72 | 2.8259 | 2.9617 | 3.0774 | 3.1769 | 3.2674 | 3.3117 | 3.3564 | 3.4033 | 3.4494 | 3.4943 | 3.6653 | 3.7953 | 5.7708 | 5.8976 | 6.0941 | 6.2633 | 6.4442 | 6.6433 | 6.8691 | 7.1551 | 7.4007 | 7.6143 | 7.8104 | 7.9132 | 8.0174 | 8.1267 | 8.2338 | 8.3386 | 8.7294 | 9.0377
South West | Sandford 132 kV | Axbridge | Primary Substation | 11 | Holistic Transition | 2.3141 | 2.3627 | 2.439 | 2.4991 | 2.5676 | 2.6467 | 2.738 | 2.86 | 2.9654 | 3.0733 | 3.1729 | 3.26 | 3.3468 | 3.4236 | 3.4976 | 3.5457 | 3.7579 | 3.8673 | 5.7631 | 5.8725 | 6.046 | 6.1839 | 6.3407 | 6.519 | 6.7248 | 6.9965 | 7.2318 | 7.471 | 7.6863 | 7.8717 | 8.0568 | 8.2186 | 8.3757 | 8.4806 | 8.9742 | 9.2298
South West | Sandford 132 kV | Axbridge | Primary Substation | 11 | Hydrogen Evolution | 2.3034 | 2.3417 | 2.3947 | 2.4341 | 2.4794 | 2.5363 | 2.6016 | 2.6892 | 2.7737 | 2.8683 | 2.9556 | 3.0395 | 3.1201 | 3.1986 | 3.272 | 3.3171 | 4.5605 | 4.6908 | 5.7356 | 5.819 | 5.9338 | 6.0197 | 6.1183 | 6.2413 | 6.3818 | 6.5673 | 6.7501 | 6.9561 | 7.1419 | 7.3191 | 7.4887 | 7.6547 | 7.8102 | 7.9091 | 10.9899 | 11.2957
South West | Sandford 132 kV | Blagdon 33/11kv S/S | Primary Substation | 11 | Counterfactual | 0.11562 | 0.12798 | 0.1461 | 0.16692 | 0.19218 | 0.22775 | 0.26812 | 0.32236 | 0.36935 | 0.42268 | 0.4708 | 0.51244 | 0.5549 | 0.59776 | 0.639 | 0.68029 | 0.86029 | 0.98506 | 0.27303 | 0.29982 | 0.3402 | 0.38652 | 0.44282 | 0.52114 | 0.61094 | 0.72977 | 0.83392 | 0.95386 | 1.0598 | 1.1493 | 1.2389 | 1.3296 | 1.4166 | 1.5036 | 1.8947 | 2.1753
South West | Sandford 132 kV | Blagdon 33/11kv S/S | Primary Substation | 11 | Electric Engagement | 0.128 | 0.15589 | 0.21098 | 0.27222 | 0.33715 | 0.41465 | 0.50011 | 0.60532 | 0.70026 | 0.78942 | 0.87661 | 0.93414 | 0.99121 | 1.0489 | 1.1059 | 1.1621 | 1.4244 | 1.5896 | 0.30038 | 0.36135 | 0.48715 | 0.62574 | 0.77177 | 0.94249 | 1.1293 | 1.3567 | 1.5633 | 1.7592 | 1.9521 | 2.084 | 2.2154 | 2.3486 | 2.4797 | 2.6095 | 3.208 | 3.603
South West | Sandford 132 kV | Blagdon 33/11kv S/S | Primary Substation | 11 | Holistic Transition | 0.12494 | 0.1479 | 0.19845 | 0.2527 | 0.31658 | 0.39367 | 0.48419 | 0.60112 | 0.70513 | 0.81034 | 0.89872 | 0.97871 | 1.0562 | 1.1207 | 1.1826 | 1.2302 | 1.4389 | 1.541 | 0.29565 | 0.34836 | 0.46816 | 0.59577 | 0.74605 | 0.92273 | 1.1314 | 1.3998 | 1.6381 | 1.8774 | 2.0728 | 2.2494 | 2.4204 | 2.5602 | 2.6942 | 2.7996 | 3.2709 | 3.5052
South West | Sandford 132 kV | Blagdon 33/11kv S/S | Primary Substation | 11 | Hydrogen Evolution | 0.11973 | 0.1359 | 0.15986 | 0.19119 | 0.22795 | 0.27908 | 0.33558 | 0.40696 | 0.48534 | 0.57484 | 0.65075 | 0.7198 | 0.78448 | 0.84666 | 0.90621 | 0.95002 | 1.1422 | 1.2992 | 0.28201 | 0.31746 | 0.37062 | 0.44042 | 0.52251 | 0.63521 | 0.75965 | 0.91463 | 1.089 | 1.2897 | 1.4558 | 1.6052 | 1.7443 | 1.879 | 2.008 | 2.1055 | 2.5499 | 2.9171
South West | Sandford 132 kV | Bournville | Primary Substation | 11 | Counterfactual | 2.9322 | 2.9907 | 3.0599 | 3.1389 | 3.2345 | 3.3432 | 3.4658 | 3.6489 | 3.7995 | 3.9602 | 4.1214 | 4.2803 | 4.454 | 4.6247 | 4.1667 | 4.3357 | 4.902 | 5.1257 | 7.279 | 7.4032 | 7.5496 | 7.7166 | 7.9178 | 8.1467 | 8.4048 | 8.7851 | 9.1006 | 9.4381 | 9.7742 | 10.102 | 10.4581 | 10.8076 | 9.5871 | 9.9335 | 11.1131 | 11.602
South West | Sandford 132 kV | Bournville | Primary Substation | 11 | Electric Engagement | 3.0029 | 3.1357 | 3.3118 | 3.5188 | 3.7476 | 3.9987 | 4.291 | 4.6691 | 4.986 | 5.2482 | 5.4767 | 5.5615 | 5.6405 | 5.0916 | 5.1684 | 5.241 | 5.5994 | 5.8783 | 7.4361 | 7.7195 | 8.095 | 8.535 | 9.019 | 9.5475 | 10.1593 | 10.9409 | 11.5992 | 12.1477 | 12.6294 | 12.8212 | 13.0004 | 11.6107 | 11.7852 | 11.951 | 12.7734 | 13.4222
South West | Sandford 132 kV | Bournville | Primary Substation | 11 | Holistic Transition | 2.9877 | 3.0872 | 3.2156 | 3.3629 | 3.5325 | 3.7288 | 3.9418 | 4.2264 | 4.4732 | 4.7297 | 4.9851 | 5.2293 | 5.4661 | 4.9359 | 5.1436 | 5.2703 | 4.0412 | 4.3436 | 7.4135 | 7.6363 | 7.9226 | 8.2486 | 8.6226 | 9.0508 | 9.5116 | 10.1183 | 10.6459 | 11.191 | 11.7276 | 12.242 | 12.741 | 11.329 | 11.7668 | 12.0426 | 8.8832 | 9.5803
South West | Sandford 132 kV | Bournville | Primary Substation | 11 | Hydrogen Evolution | 2.954 | 3.0291 | 3.1234 | 3.2417 | 3.3769 | 3.5352 | 3.719 | 3.9702 | 4.201 | 4.443 | 4.685 | 4.9155 | 5.1375 | 4.711 | 4.9037 | 5.0038 | 5.2897 | 5.5383 | 7.3275 | 7.4888 | 7.689 | 7.9408 | 8.2281 | 8.5636 | 8.9511 | 9.4737 | 9.9563 | 10.4627 | 10.9649 | 11.4421 | 11.9008 | 10.7465 | 11.1458 | 11.3598 | 12.0087 | 12.5717
South West | Sandford 132 kV | Cheddar | Primary Substation | 11 | Counterfactual | 0.17142 | 0.20509 | 0.24262 | 0.28377 | 0.33062 | 0.3864 | 0.46032 | 0.56659 | 0.64981 | 0.73182 | 0.8126 | 0.89185 | 0.98147 | 1.0724 | 1.1648 | 1.2708 | 1.5925 | 1.7351 | 0.40142 | 0.47402 | 0.55427 | 0.64206 | 0.7418 | 0.86023 | 1.0171 | 1.2396 | 1.4154 | 1.5894 | 1.7588 | 1.923 | 2.1074 | 2.2946 | 2.4858 | 2.7114 | 3.3892 | 3.7025
South West | Sandford 132 kV | Cheddar | Primary Substation | 11 | Electric Engagement | 0.20753 | 0.28387 | 0.38233 | 0.48994 | 0.60704 | 0.74694 | 0.90782 | 1.1119 | 1.2846 | 1.4219 | 1.5477 | 1.6386 | 1.6905 | 1.7439 | 1.7971 | 1.848 | 2.0821 | 2.2588 | 0.48142 | 0.64731 | 0.85983 | 1.0908 | 1.3404 | 1.6373 | 1.9762 | 2.4007 | 2.7623 | 3.0514 | 3.32 | 3.5352 | 3.6536 | 3.7757 | 3.897 | 4.0137 | 4.5513 | 4.9666
South West | Sandford 132 kV | Cheddar | Primary Substation | 11 | Holistic Transition | 0.19954 | 0.26126 | 0.33652 | 0.41505 | 0.50297 | 0.61638 | 0.74124 | 0.90319 | 1.045 | 1.183 | 1.3207 | 1.4552 | 1.6136 | 1.7531 | 1.8681 | 1.9431 | 2.1878 | 2.3562 | 0.46947 | 0.61023 | 0.78007 | 0.95642 | 1.1531 | 1.4029 | 1.6768 | 2.0273 | 2.3351 | 2.6323 | 2.9245 | 3.2103 | 3.5566 | 3.8582 | 4.1023 | 4.2661 | 4.8244 | 5.2152
South West | Sandford 132 kV | Cheddar | Primary Substation | 11 | Hydrogen Evolution | 0.18291 | 0.22691 | 0.27975 | 0.33789 | 0.40411 | 0.49404 | 0.59626 | 0.73137 | 0.85716 | 0.9834 | 1.1066 | 1.2453 | 1.3883 | 1.5015 | 1.6081 | 1.6689 | 1.8525 | 2.0096 | 0.42682 | 0.52282 | 0.63587 | 0.76046 | 0.90192 | 1.0936 | 1.3104 | 1.5927 | 1.8587 | 2.1255 | 2.3821 | 2.6779 | 2.9851 | 3.221 | 3.4435 | 3.5743 | 3.9923 | 4.3516
South West | Sandford 132 kV | Chew Stoke | Primary Substation | 11 | Counterfactual | 0.15911 | 0.17465 | 0.19375 | 0.21578 | 0.24175 | 0.27423 | 0.31069 | 0.36574 | 0.41207 | 0.46322 | 0.51346 | 0.56241 | 0.6159 | 0.66935 | 0.72052 | 0.77113 | 0.96532 | 1.0752 | 0.37392 | 0.4068 | 0.44771 | 0.49473 | 0.55011 | 0.61906 | 0.69684 | 0.81248 | 0.9108 | 1.0201 | 1.1262 | 1.2283 | 1.3393 | 1.4505 | 1.5565 | 1.6609 | 2.0695 | 2.308
South West | Sandford 132 kV | Chew Stoke | Primary Substation | 11 | Electric Engagement | 0.17688 | 0.21061 | 0.2628 | 0.32152 | 0.38549 | 0.45953 | 0.54468 | 0.65999 | 0.7611 | 0.85242 | 0.93507 | 0.979 | 1.0204 | 1.0614 | 1.101 | 1.1391 | 1.3153 | 1.4317 | 0.41326 | 0.48528 | 0.59845 | 0.72502 | 0.86209 | 1.0191 | 1.1986 | 1.44 | 1.6533 | 1.8484 | 2.0257 | 2.1239 | 2.2172 | 2.3101 | 2.3997 | 2.4861 | 2.8858 | 3.1577
South West | Sandford 132 kV | Chew Stoke | Primary Substation | 11 | Holistic Transition | 0.17277 | 0.19785 | 0.23845 | 0.28254 | 0.33288 | 0.39422 | 0.46771 | 0.56843 | 0.65823 | 0.75185 | 0.8416 | 0.92538 | 1.0047 | 1.0748 | 1.1413 | 1.1873 | 1.3551 | 1.4568 | 0.40705 | 0.46318 | 0.55524 | 0.65453 | 0.76767 | 0.90288 | 1.0654 | 1.2858 | 1.4827 | 1.6869 | 1.8795 | 2.0592 | 2.229 | 2.3776 | 2.5186 | 2.6186 | 2.9954 | 3.227
South West | Sandford 132 kV | Chew Stoke | Primary Substation | 11 | Hydrogen Evolution | 0.16491 | 0.1843 | 0.21177 | 0.24453 | 0.28254 | 0.33033 | 0.38548 | 0.46292 | 0.54171 | 0.62889 | 0.71114 | 0.78813 | 0.86015 | 0.92779 | 0.99131 | 1.0318 | 1.1694 | 1.2791 | 0.38672 | 0.42825 | 0.4869 | 0.55708 | 0.63842 | 0.74005 | 0.8569 | 1.0191 | 1.187 | 1.3742 | 1.5481 | 1.7099 | 1.8605 | 2.0028 | 2.1363 | 2.2239 | 2.5356 | 2.7861
South West | Sandford 132 kV | Churchill Gate 33/11 | Primary Substation | 11 | Counterfactual | 0.12355 | 0.13281 | 0.14482 | 0.1586 | 0.17557 | 0.19472 | 0.2165 | 0.24833 | 0.27491 | 0.30413 | 0.33183 | 0.35939 | 0.38824 | 0.41723 | 0.44526 | 0.47353 | 0.57856 | 0.62842 | 0.2911 | 0.31074 | 0.33653 | 0.36608 | 0.40241 | 0.44352 | 0.49038 | 0.55776 | 0.61464 | 0.67763 | 0.73656 | 0.79436 | 0.85417 | 0.91439 | 0.97246 | 1.0311 | 1.2538 | 1.3656
South West | Sandford 132 kV | Churchill Gate 33/11 | Primary Substation | 11 | Electric Engagement | 0.13494 | 0.15576 | 0.18772 | 0.22535 | 0.26628 | 0.31093 | 0.36198 | 0.42834 | 0.48474 | 0.53336 | 0.57617 | 0.5964 | 0.61501 | 0.63347 | 0.65142 | 0.66934 | 0.74865 | 0.81872 | 0.31636 | 0.36064 | 0.43029 | 0.51173 | 0.59984 | 0.69542 | 0.80389 | 0.94335 | 1.0628 | 1.1667 | 1.2593 | 1.3062 | 1.3498 | 1.3934 | 1.4357 | 1.4781 | 1.6657 | 1.8312
South West | Sandford 132 kV | Churchill Gate 33/11 | Primary Substation | 11 | Holistic Transition | 0.13238 | 0.14785 | 0.17298 | 0.20146 | 0.23509 | 0.27215 | 0.31558 | 0.37347 | 0.4246 | 0.47702 | 0.52567 | 0.57277 | 0.61847 | 0.65865 | 0.69573 | 0.71953 | 0.79842 | 0.85329 | 0.31254 | 0.34695 | 0.40419 | 0.46851 | 0.54428 | 0.627 | 0.72398 | 0.85172 | 0.96487 | 1.0801 | 1.185 | 1.2861 | 1.3843 | 1.4699 | 1.549 | 1.6016 | 1.7848 | 1.9123
South West | Sandford 132 kV | Churchill Gate 33/11 | Primary Substation | 11 | Hydrogen Evolution | 0.12697 | 0.13885 | 0.15496 | 0.17589 | 0.19973 | 0.22779 | 0.26011 | 0.30367 | 0.34586 | 0.39215 | 0.4353 | 0.47648 | 0.51525 | 0.55169 | 0.58562 | 0.60589 | 0.67286 | 0.73228 | 0.29869 | 0.32412 | 0.35872 | 0.40389 | 0.45535 | 0.51588 | 0.58521 | 0.67724 | 0.76805 | 0.86806 | 0.95959 | 1.0465 | 1.128 | 1.2051 | 1.2769 | 1.3216 | 1.4782 | 1.6171
South West | Sandford 132 kV | Compton Martin 33/11kv S/S | Primary Substation | 11 | Counterfactual | 0.13997 | 0.15305 | 0.17128 | 0.19114 | 0.21471 | 0.24589 | 0.2814 | 0.33332 | 0.37786 | 0.42835 | 0.47562 | 0.51868 | 0.56379 | 0.60882 | 0.65208 | 0.69562 | 0.87438 | 0.98534 | 0.33269 | 0.36073 | 0.40064 | 0.44413 | 0.49583 | 0.56371 | 0.64155 | 0.75343 | 0.85045 | 0.96167 | 1.0638 | 1.1552 | 1.2495 | 1.3438 | 1.4342 | 1.5251 | 1.9081 | 2.1549
South West | Sandford 132 kV | Compton Martin 33/11kv S/S | Primary Substation | 11 | Electric Engagement | 0.15513 | 0.18521 | 0.23764 | 0.29488 | 0.35609 | 0.42791 | 0.50907 | 0.6162 | 0.71189 | 0.79916 | 0.88146 | 0.9313 | 0.97915 | 1.0267 | 1.073 | 1.1186 | 1.3302 | 1.4689 | 0.36631 | 0.43136 | 0.54859 | 0.67565 | 0.81046 | 0.96622 | 1.1408 | 1.369 | 1.5741 | 1.7629 | 1.9423 | 2.0555 | 2.1651 | 2.2745 | 2.3805 | 2.4853 | 2.9685 | 3.2976
South West | Sandford 132 kV | Compton Martin 33/11kv S/S | Primary Substation | 11 | Holistic Transition | 0.15189 | 0.1757 | 0.22068 | 0.26796 | 0.32227 | 0.38819 | 0.46775 | 0.575 | 0.67085 | 0.76918 | 0.85611 | 0.93577 | 1.0124 | 1.0777 | 1.1399 | 1.1849 | 1.3665 | 1.4675 | 0.36149 | 0.41556 | 0.52057 | 0.63012 | 0.75601 | 0.90516 | 1.0857 | 1.3271 | 1.5426 | 1.762 | 1.9512 | 2.1244 | 2.2912 | 2.4313 | 2.5648 | 2.6639 | 3.0744 | 3.3057
South West | Sandford 132 kV | Compton Martin 33/11kv S/S | Primary Substation | 11 | Hydrogen Evolution | 0.1447 | 0.1617 | 0.18589 | 0.21526 | 0.24928 | 0.29483 | 0.34684 | 0.41725 | 0.49314 | 0.57786 | 0.65339 | 0.72347 | 0.78856 | 0.85038 | 0.90862 | 0.94768 | 1.1043 | 1.2334 | 0.34316 | 0.38009 | 0.43297 | 0.49747 | 0.57223 | 0.67125 | 0.78402 | 0.9346 | 1.1004 | 1.2867 | 1.4491 | 1.5986 | 1.7368 | 1.8689 | 1.9934 | 2.0796 | 2.4408 | 2.741
South West | Sandford 132 kV | Congresbury | Primary Substation | 11 | Counterfactual | 1.5877 | 1.6628 | 1.747 | 1.8448 | 1.9635 | 2.1008 | 2.259 | 2.489 | 2.6817 | 2.895 | 3.0975 | 3.2773 | 3.4885 | 3.3704 | 3.5855 | 3.7838 | 4.5119 | 4.8795 | 3.8307 | 3.9898 | 4.1713 | 4.3815 | 4.6366 | 4.9322 | 5.2739 | 5.7623 | 6.1761 | 6.6379 | 7.0699 | 7.4421 | 7.8836 | 7.502 | 7.9556 | 8.3668 | 9.9165 | 10.7409
South West | Sandford 132 kV | Congresbury | Primary Substation | 11 | Electric Engagement | 1.6655 | 1.8234 | 2.054 | 2.3211 | 2.6109 | 2.9246 | 3.2838 | 3.7121 | 4.0783 | 4.4312 | 4.7458 | 4.8534 | 4.9412 | 4.9939 | 5.1339 | 5.2703 | 5.976 | 6.572 | 4.0037 | 4.3411 | 4.8464 | 5.4279 | 6.055 | 6.7296 | 7.496 | 8.3851 | 9.1519 | 9.9142 | 10.5992 | 10.8413 | 11.0381 | 11.1491 | 11.4784 | 11.8013 | 13.4331 | 14.8661
South West | Sandford 132 kV | Congresbury | Primary Substation | 11 | Holistic Transition | 1.6492 | 1.7703 | 1.9556 | 2.1634 | 2.4053 | 2.6762 | 2.9332 | 3.2763 | 3.5951 | 3.8959 | 4.2253 | 4.5843 | 4.8984 | 5.165 | 5.4137 | 5.5778 | 6.4587 | 6.8314 | 3.9799 | 4.2499 | 4.6745 | 5.1464 | 5.6952 | 6.3026 | 6.8645 | 7.605 | 8.3013 | 8.9446 | 9.6534 | 10.4433 | 11.1249 | 11.6957 | 12.2287 | 12.5927 | 14.6448 | 15.5088
South West | Sandford 132 kV | Congresbury | Primary Substation | 11 | Hydrogen Evolution | 1.612 | 1.7076 | 1.8223 | 1.9694 | 2.1395 | 2.3411 | 2.5744 | 2.8854 | 3.1586 | 3.4846 | 3.8135 | 4.1062 | 4.352 | 4.429 | 4.6731 | 4.8192 | 5.374 | 5.919 | 3.8849 | 4.0901 | 4.337 | 4.6553 | 5.0232 | 5.4589 | 5.9605 | 6.6191 | 7.1959 | 7.899 | 8.604 | 9.2232 | 9.7296 | 9.8236 | 10.342 | 10.6648 | 11.9471 | 13.2405
South West | Sandford 132 kV | East Brent | Primary Substation | 11 | Counterfactual | 0.1782 | 0.20884 | 0.25532 | 0.30056 | 0.35488 | 0.43189 | 0.5223 | 0.64098 | 0.74505 | 0.86892 | 0.97345 | 1.0576 | 1.1391 | 1.2248 | 1.3062 | 1.3872 | 1.7723 | 2.0569 | 0.42241 | 0.4888 | 0.59394 | 0.69752 | 0.82244 | 0.99703 | 1.2043 | 1.4723 | 1.7101 | 1.9974 | 2.2344 | 2.4201 | 2.5958 | 2.7813 | 2.9562 | 3.1304 | 3.9901 | 4.6497
South West | Sandford 132 kV | East Brent | Primary Substation | 11 | Electric Engagement | 0.2011 | 0.2638 | 0.40481 | 0.54694 | 0.69434 | 0.86511 | 1.0508 | 1.2758 | 1.4829 | 1.6824 | 1.881 | 2.0213 | 2.1639 | 2.3117 | 2.4557 | 2.6 | 3.2458 | 3.6833 | 0.47324 | 0.61115 | 0.93994 | 1.2704 | 1.6109 | 1.9969 | 2.4128 | 2.9113 | 3.3734 | 3.823 | 4.2743 | 4.6035 | 4.9396 | 5.2886 | 5.6276 | 5.9676 | 7.4746 | 8.5377
South West | Sandford 132 kV | East Brent | Primary Substation | 11 | Holistic Transition | 0.19622 | 0.25123 | 0.39058 | 0.52685 | 0.68687 | 0.87202 | 1.0972 | 1.39 | 1.6476 | 1.9052 | 2.1051 | 2.2859 | 2.4619 | 2.5994 | 2.7292 | 2.8343 | 3.3112 | 3.5249 | 0.46606 | 0.59195 | 0.92637 | 1.2537 | 1.6385 | 2.0733 | 2.6056 | 3.2951 | 3.9009 | 4.5027 | 4.9562 | 5.3651 | 5.7632 | 6.067 | 6.3535 | 6.5909 | 7.6906 | 8.189
South West | Sandford 132 kV | East Brent | Primary Substation | 11 | Hydrogen Evolution | 0.1854 | 0.22544 | 0.2841 | 0.3496 | 0.42719 | 0.53646 | 0.65849 | 0.80768 | 0.98432 | 1.1939 | 1.3588 | 1.5052 | 1.6397 | 1.775 | 1.9033 | 2.0041 | 2.4848 | 2.8889 | 0.43841 | 0.52669 | 0.65927 | 0.80954 | 0.988 | 1.2354 | 1.5116 | 1.8443 | 2.2496 | 2.7342 | 3.1054 | 3.4305 | 3.7271 | 4.028 | 4.313 | 4.5436 | 5.6823 | 6.6477
South West | Sandford 132 kV | Lypstone Farm | Primary Substation | 11 | Counterfactual | 0.75307 | 1.1026 | 1.5387 | 1.6948 | 1.8839 | 2.0944 | 2.3311 | 2.6876 | 2.98 | 3.2902 | 3.6018 | 3.9223 | 4.3016 | 4.6929 | 5.0765 | 5.4216 | 6.5747 | 7.0102 | 1.7129 | 2.4327 | 3.3229 | 3.6519 | 4.0492 | 4.4914 | 4.988 | 5.7261 | 6.3367 | 6.9853 | 7.6334 | 8.2957 | 9.0885 | 9.9117 | 10.719 | 11.4304 | 13.8313 | 14.7874
South West | Sandford 132 kV | Lypstone Farm | Primary Substation | 11 | Electric Engagement | 0.89995 | 1.5916 | 2.49 | 2.8996 | 3.3531 | 3.8447 | 4.4185 | 5.1768 | 5.8156 | 6.3869 | 6.8965 | 7.0974 | 7.2835 | 7.4501 | 7.6069 | 7.7471 | 8.3756 | 8.9438 | 2.0392 | 3.5095 | 5.412 | 6.2788 | 7.2344 | 8.267 | 9.4643 | 11.0318 | 12.3617 | 13.5766 | 14.6742 | 15.1392 | 15.5741 | 15.9622 | 16.3263 | 16.6513 | 18.1184 | 19.4375
South West | Sandford 132 kV | Lypstone Farm | Primary Substation | 11 | Holistic Transition | 0.86922 | 1.4158 | 2.1135 | 2.3989 | 2.729 | 3.1004 | 3.5236 | 4.0902 | 4.5873 | 5.1187 | 5.7113 | 6.304 | 6.821 | 7.2736 | 7.6942 | 7.9485 | 8.6899 | 9.2761 | 1.9946 | 3.1896 | 4.7055 | 5.3332 | 6.0565 | 6.8642 | 7.7798 | 8.9881 | 10.0528 | 11.1905 | 12.4695 | 13.7526 | 14.8528 | 15.8055 | 16.6927 | 17.2472 | 18.9562 | 20.3145
South West | Sandford 132 kV | Lypstone Farm | Primary Substation | 11 | Hydrogen Evolution | 0.79883 | 1.2812 | 1.9023 | 2.1381 | 2.4077 | 2.7163 | 3.0738 | 3.5663 | 4.0132 | 4.5164 | 5.0439 | 5.5676 | 6.044 | 6.4753 | 6.8706 | 7.0731 | 7.6118 | 8.0829 | 1.8146 | 2.8476 | 4.1698 | 4.671 | 5.2429 | 5.8963 | 6.6485 | 7.6709 | 8.607 | 9.673 | 10.7893 | 11.9006 | 12.9009 | 13.8035 | 14.6297 | 15.065 | 16.2966 | 17.3732
South West | Sandford 132 kV | Nailsea | Primary Substation | 11 | Counterfactual | 0.61464 | 0.72306 | 0.83303 | 0.98116 | 1.1299 | 1.2953 | 1.4741 | 1.7436 | 1.9635 | 2.1968 | 2.4341 | 2.6713 | 2.9366 | 3.1988 | 3.4566 | 3.7072 | 4.5384 | 4.8449 | 1.4309 | 1.6601 | 1.8918 | 2.2028 | 2.5149 | 2.8617 | 3.2361 | 3.7933 | 4.2518 | 4.7388 | 5.2314 | 5.721 | 6.2674 | 6.8076 | 7.3376 | 7.8518 | 9.582 | 10.2557
South West | Sandford 132 kV | Nailsea | Primary Substation | 11 | Electric Engagement | 0.72505 | 0.95952 | 1.2514 | 1.5574 | 1.8964 | 2.2652 | 2.6933 | 3.259 | 3.7361 | 4.1358 | 4.4745 | 4.5932 | 4.7043 | 4.8135 | 4.9232 | 5.0271 | 5.5084 | 5.9213 | 1.6764 | 2.1769 | 2.7977 | 3.4449 | 4.1586 | 4.9325 | 5.8249 | 6.9933 | 7.985 | 8.8253 | 9.541 | 9.8121 | 10.0676 | 10.3195 | 10.5712 | 10.8115 | 11.9247 | 12.8816
South West | Sandford 132 kV | Nailsea | Primary Substation | 11 | Holistic Transition | 0.70231 | 0.88406 | 1.0865 | 1.3177 | 1.5622 | 1.8402 | 2.154 | 2.574 | 2.9449 | 3.331 | 3.7238 | 4.0954 | 4.4492 | 4.7747 | 5.0801 | 5.2656 | 5.8137 | 6.2543 | 1.6438 | 2.0468 | 2.4942 | 3.002 | 3.5373 | 4.141 | 4.8195 | 5.7145 | 6.5078 | 7.3303 | 8.161 | 8.9476 | 9.6945 | 10.3799 | 11.0241 | 11.4285 | 12.6877 | 13.7019
South West | Sandford 132 kV | Nailsea | Primary Substation | 11 | Hydrogen Evolution | 0.64781 | 0.79537 | 0.96872 | 1.1426 | 1.3411 | 1.5725 | 1.8383 | 2.2035 | 2.5374 | 2.8982 | 3.2592 | 3.6061 | 3.9354 | 4.2434 | 4.5322 | 4.6809 | 5.0818 | 5.4376 | 1.505 | 1.8219 | 2.1909 | 2.5603 | 2.9811 | 3.4702 | 4.0287 | 4.7862 | 5.4848 | 6.2423 | 6.9941 | 7.7137 | 8.3944 | 9.0327 | 9.6321 | 9.951 | 10.8631 | 11.671
South West | Sandford 132 kV | Weston Central | Primary Substation | 11 | Counterfactual | 0.1752 | 0.24532 | 0.32047 | 0.40716 | 0.5114 | 0.62588 | 0.75612 | 0.95034 | 1.108 | 1.2757 | 1.4447 | 1.6231 | 1.8161 | 2.0112 | 2.2023 | 2.389 | 3.0146 | 3.2453 | 0.38114 | 0.53019 | 0.68798 | 0.86956 | 1.0872 | 1.3258 | 1.5963 | 1.9951 | 2.3214 | 2.6677 | 3.0163 | 3.3834 | 3.779 | 4.1786 | 4.5698 | 4.9523 | 6.2476 | 6.7469
South West | Sandford 132 kV | Weston Central | Primary Substation | 11 | Electric Engagement | 0.25563 | 0.41268 | 0.5965 | 0.8182 | 1.0646 | 1.3294 | 1.6402 | 2.0553 | 2.3953 | 2.675 | 2.9092 | 2.9915 | 3.0646 | 3.1352 | 3.2044 | 3.2733 | 3.5774 | 3.8695 | 0.55974 | 0.89568 | 1.282 | 1.7472 | 2.2626 | 2.8151 | 3.46 | 4.3134 | 5.0158 | 5.5965 | 6.0861 | 6.2711 | 6.437 | 6.5978 | 6.7555 | 6.9123 | 7.6157 | 8.2831
South West | Sandford 132 kV | Weston Central | Primary Substation | 11 | Holistic Transition | 0.23865 | 0.359 | 0.48584 | 0.63588 | 0.80809 | 1.0009 | 1.2199 | 1.51 | 1.7663 | 2.0333 | 2.311 | 2.5826 | 2.846 | 3.0965 | 3.3257 | 3.4646 | 3.8678 | 4.2175 | 0.53501 | 0.80435 | 1.0819 | 1.4083 | 1.7809 | 2.196 | 2.6629 | 3.272 | 3.8126 | 4.3735 | 4.9552 | 5.5241 | 6.0762 | 6.6018 | 7.0844 | 7.3863 | 8.3095 | 9.1141
South West | Sandford 132 kV | Weston Central | Primary Substation | 11 | Hydrogen Evolution | 0.1998 | 0.29072 | 0.3946 | 0.52405 | 0.67119 | 0.83787 | 1.0335 | 1.3009 | 1.5369 | 1.7839 | 2.0404 | 2.2894 | 2.5344 | 2.7606 | 2.9696 | 3.0785 | 3.3515 | 3.5994 | 0.43591 | 0.63116 | 0.85049 | 1.1243 | 1.4347 | 1.7854 | 2.1939 | 2.7461 | 3.235 | 3.7454 | 4.2735 | 4.7865 | 5.2909 | 5.7575 | 6.1891 | 6.4206 | 7.0328 | 7.5864
South West | Sandford 132 kV | Weston Locking Rd | Primary Substation | 11 | Counterfactual | 0.8524 | 1.1411 | 1.4747 | 1.7306 | 1.9714 | 2.2489 | 2.556 | 2.9665 | 3.2731 | 3.5959 | 3.9251 | 4.2632 | 4.7109 | 5.1765 | 5.6363 | 6.0196 | 6.8797 | 7.3376 | 2.018 | 2.6374 | 3.3499 | 3.8855 | 4.3889 | 4.9692 | 5.6106 | 6.4574 | 7.0931 | 7.7622 | 8.4423 | 9.1381 | 10.0899 | 11.087 | 12.0738 | 12.8686 | 14.5081 | 15.4993
South West | Sandford 132 kV | Weston Locking Rd | Primary Substation | 11 | Electric Engagement | 1.0075 | 1.4871 | 2.1206 | 2.5831 | 3.1036 | 3.6699 | 4.3245 | 5.1229 | 5.804 | 6.4914 | 7.1056 | 7.3437 | 7.5485 | 7.7385 | 7.9225 | 8.0794 | 8.3795 | 8.9159 | 2.3624 | 3.3948 | 4.7469 | 5.7221 | 6.8171 | 8.0061 | 9.3724 | 11.0163 | 12.4329 | 13.9236 | 15.2688 | 15.8212 | 16.2969 | 16.7374 | 17.163 | 17.525 | 18.1463 | 19.3839
South West | Sandford 132 kV | Weston Locking Rd | Primary Substation | 11 | Holistic Transition | 0.97486 | 1.382 | 1.8639 | 2.2412 | 2.6263 | 3.0636 | 3.5474 | 4.1261 | 4.6299 | 5.1942 | 5.9038 | 6.6176 | 7.1871 | 7.6702 | 8.1058 | 8.371 | 8.8018 | 9.4148 | 2.3148 | 3.2143 | 4.2662 | 5.0881 | 5.9256 | 6.8707 | 7.9105 | 9.1319 | 10.2 | 11.4058 | 12.963 | 14.541 | 15.7653 | 16.7869 | 17.7039 | 18.28 | 19.1909 | 20.6052
South West | Sandford 132 kV | Weston Locking Rd | Primary Substation | 11 | Hydrogen Evolution | 0.90035 | 1.2562 | 1.7328 | 2.0249 | 2.355 | 2.7307 | 3.1589 | 3.6815 | 4.1522 | 4.7363 | 5.3712 | 5.9998 | 6.5197 | 6.9954 | 7.4384 | 7.6684 | 7.8613 | 8.3238 | 2.1247 | 2.8947 | 3.9164 | 4.5364 | 5.2365 | 6.0314 | 6.9322 | 8.0115 | 8.9891 | 10.2395 | 11.6064 | 12.9639 | 14.0575 | 15.0571 | 15.9888 | 16.4851 | 16.8344 | 17.8761
South West | Sandford 132 kV | Westwick | Primary Substation | 11 | Counterfactual | 0.58225 | 0.6948 | 0.84144 | 0.87303 | 0.9114 | 0.95352 | 1.0014 | 1.0735 | 1.1324 | 1.1949 | 1.2583 | 1.3233 | 1.4183 | 1.5134 | 1.6014 | 1.6704 | 1.9003 | 1.9832 | 1.4267 | 1.6703 | 1.9864 | 2.0527 | 2.1332 | 2.2214 | 2.3215 | 2.4704 | 2.5929 | 2.7232 | 2.8546 | 2.9886 | 3.1941 | 3.4 | 3.5889 | 3.7302 | 4.2079 | 4.3894
South West | Sandford 132 kV | Westwick | Primary Substation | 11 | Electric Engagement | 0.61252 | 0.75459 | 0.9442 | 1.027 | 1.1189 | 1.2177 | 1.3334 | 1.4869 | 1.6302 | 1.8061 | 1.9327 | 1.9639 | 1.9927 | 2.0208 | 2.0483 | 2.0748 | 2.3083 | 2.412 | 1.4939 | 1.8005 | 2.2078 | 2.3826 | 2.5759 | 2.7829 | 3.0237 | 3.3405 | 3.6444 | 4.0411 | 4.3223 | 4.3933 | 4.4596 | 4.5245 | 4.5879 | 4.6494 | 5.2147 | 5.4559
South West | Sandford 132 kV | Westwick | Primary Substation | 11 | Holistic Transition | 0.6061 | 0.73362 | 0.9025 | 0.95965 | 1.0256 | 1.0996 | 1.1833 | 1.2964 | 1.3948 | 1.5092 | 1.658 | 2.035 | 2.1397 | 2.2294 | 2.3131 | 2.3632 | 2.5025 | 2.6127 | 1.4845 | 1.764 | 2.1319 | 2.2573 | 2.4014 | 2.5619 | 2.7424 | 2.9826 | 3.1927 | 3.4403 | 3.7714 | 4.6744 | 4.8978 | 5.0863 | 5.2624 | 5.3716 | 5.6935 | 5.949
South West | Sandford 132 kV | Westwick | Primary Substation | 11 | Hydrogen Evolution | 0.59167 | 0.71046 | 0.86861 | 0.91603 | 0.97072 | 1.0328 | 1.105 | 1.2053 | 1.2963 | 1.4399 | 1.581 | 1.699 | 1.789 | 1.873 | 1.9509 | 1.9915 | 2.2099 | 2.2963 | 1.4476 | 1.7051 | 2.0458 | 2.1463 | 2.262 | 2.393 | 2.5445 | 2.7523 | 2.9421 | 3.2615 | 3.5729 | 3.8273 | 4.0131 | 4.1869 | 4.3483 | 4.4354 | 4.9593 | 5.1569
South West | Sandford 132 kV | Winscombe | Primary Substation | 11 | Counterfactual | 0.60173 | 0.62786 | 0.65835 | 0.69376 | 0.73633 | 0.78512 | 0.83982 | 0.92189 | 0.98925 | 1.0616 | 1.1327 | 1.204 | 1.2815 | 1.3593 | 1.4352 | 1.5109 | 1.7764 | 1.8949 | 1.2988 | 1.3543 | 1.4192 | 1.4942 | 1.5844 | 1.6876 | 1.8033 | 1.9744 | 2.1162 | 2.2692 | 2.418 | 2.5658 | 2.7255 | 2.8857 | 3.0418 | 3.1977 | 3.7531 | 4.0127
South West | Sandford 132 kV | Winscombe | Primary Substation | 11 | Electric Engagement | 0.63313 | 0.69239 | 0.77274 | 0.86675 | 0.96997 | 1.0827 | 1.2137 | 1.385 | 1.5291 | 1.6507 | 1.7578 | 1.8028 | 1.8439 | 1.8839 | 1.9231 | 1.9603 | 2.1275 | 2.2694 | 1.3684 | 1.4954 | 1.6678 | 1.8685 | 2.0878 | 2.3261 | 2.6011 | 2.9565 | 3.2576 | 3.5134 | 3.7405 | 3.8428 | 3.9372 | 4.0293 | 4.1198 | 4.2062 | 4.5953 | 4.9276
South West | Sandford 132 kV | Winscombe | Primary Substation | 11 | Holistic Transition | 0.62622 | 0.67094 | 0.73045 | 0.79827 | 0.87637 | 0.96519 | 1.0665 | 1.2016 | 1.3202 | 1.4437 | 1.5641 | 1.6791 | 1.7904 | 1.8903 | 1.9837 | 2.0423 | 2.2246 | 2.3596 | 1.3581 | 1.4586 | 1.5921 | 1.7429 | 1.9161 | 2.1111 | 2.3325 | 2.6241 | 2.8807 | 3.1461 | 3.4015 | 3.6451 | 3.8812 | 4.0923 | 4.29 | 4.4182 | 4.8375 | 5.1502
South West | Sandford 132 kV | Winscombe | Primary Substation | 11 | Hydrogen Evolution | 0.61156 | 0.64504 | 0.68794 | 0.74104 | 0.80168 | 0.87305 | 0.9559 | 1.0688 | 1.1733 | 1.2866 | 1.3985 | 1.5055 | 1.607 | 1.7012 | 1.789 | 1.8377 | 1.9791 | 2.1007 | 1.3206 | 1.3927 | 1.4841 | 1.5975 | 1.7268 | 1.8785 | 2.0537 | 2.2891 | 2.5095 | 2.7488 | 2.9822 | 3.2049 | 3.4155 | 3.6117 | 3.7948 | 3.8999 | 4.2237 | 4.5032
South West | Seabank 132 kV | Avonmouth | Primary Substation | 11 | Counterfactual | 5.4068 | 5.5262 | 5.6811 | 7.1074 | 7.2876 | 7.4398 | 7.5995 | 7.8227 | 8.0004 | 8.196 | 8.1587 | 8.3618 | 8.9949 | 9.2162 | 9.4315 | 9.6492 | 10.4601 | 10.8672 | 13.0599 | 13.3175 | 13.6493 | 17.1526 | 17.5361 | 17.8597 | 18.1975 | 18.6626 | 19.0362 | 19.4487 | 19.2743 | 19.6952 | 21.1791 | 21.6348 | 22.0779 | 22.5256 | 24.2195 | 25.0984
South West | Seabank 132 kV | Avonmouth | Primary Substation | 11 | Electric Engagement | 5.7171 | 5.9664 | 6.507 | 8.1661 | 8.5322 | 8.8493 | 9.2041 | 9.6704 | 10.0753 | 10.4193 | 10.489 | 10.6356 | 10.7739 | 10.9083 | 11.0377 | 11.1826 | 11.7465 | 12.1908 | 13.8119 | 14.3649 | 15.611 | 19.6253 | 20.4169 | 21.0915 | 21.8355 | 22.803 | 23.6495 | 24.3739 | 24.433 | 24.7608 | 25.0729 | 25.3772 | 25.6701 | 26.006 | 27.3132 | 28.342
South West | Seabank 132 kV | Avonmouth | Primary Substation | 11 | Holistic Transition | 5.7234 | 6.1614 | 6.4783 | 8.0292 | 8.3129 | 8.5772 | 8.8531 | 9.2391 | 9.5747 | 9.9231 | 10.0784 | 10.469 | 10.8079 | 11.1188 | 11.413 | 11.6067 | 12.2325 | 12.6709 | 13.8461 | 14.8971 | 15.6038 | 19.4041 | 20.0409 | 20.6253 | 21.2266 | 22.057 | 22.7817 | 23.5299 | 23.7877 | 24.6319 | 25.3501 | 26.0065 | 26.6286 | 27.0496 | 28.4694 | 29.4781
South West | Seabank 132 kV | Avonmouth | Primary Substation | 11 | Hydrogen Evolution | 5.6603 | 5.8409 | 6.2856 | 7.8066 | 8.0733 | 8.3006 | 8.5312 | 8.846 | 9.147 | 9.4635 | 9.5416 | 9.8449 | 10.1396 | 10.4128 | 10.6709 | 10.849 | 11.3322 | 11.7068 | 13.6852 | 14.0918 | 15.1309 | 18.8496 | 19.4318 | 19.9211 | 20.4076 | 21.0621 | 21.6947 | 22.3611 | 22.426 | 23.057 | 23.6692 | 24.2389 | 24.7778 | 25.1689 | 26.2686 | 27.1219
South West | Seabank 132 kV | Cairns Road | Primary Substation | 11 | Counterfactual | 0.9604 | 1.1774 | 1.4216 | 1.7135 | 2.012 | 2.3399 | 2.702 | 3.2933 | 3.7603 | 4.2612 | 4.7842 | 5.3425 | 5.9995 | 6.675 | 7.3555 | 7.9809 | 10.0793 | 10.8869 | 2.1148 | 2.5771 | 3.0922 | 3.7049 | 4.3295 | 5.0139 | 5.7669 | 6.9819 | 7.9483 | 8.9845 | 10.0647 | 11.214 | 12.5799 | 13.9906 | 15.4188 | 16.7131 | 21.0656 | 22.8059
South West | Seabank 132 kV | Cairns Road | Primary Substation | 11 | Electric Engagement | 1.2224 | 1.7141 | 2.3114 | 2.9799 | 3.7064 | 4.5021 | 5.4572 | 6.7448 | 7.8565 | 8.8329 | 9.6953 | 10.0388 | 10.3596 | 10.663 | 10.9548 | 11.2321 | 12.2118 | 13.2108 | 2.6975 | 3.7512 | 5.0092 | 6.4108 | 7.9261 | 9.5798 | 11.557 | 14.1991 | 16.5001 | 18.5558 | 20.3917 | 21.1713 | 21.906 | 22.6038 | 23.2757 | 23.9172 | 26.1819 | 28.457
South West | Seabank 132 kV | Cairns Road | Primary Substation | 11 | Holistic Transition | 1.1812 | 1.5617 | 1.9964 | 2.435 | 2.9323 | 3.5217 | 4.1853 | 5.147 | 5.9847 | 6.8765 | 7.8912 | 8.9642 | 9.9551 | 10.8589 | 11.6487 | 12.131 | 13.4833 | 14.5645 | 2.6521 | 3.5072 | 4.461 | 5.4193 | 6.4976 | 7.7669 | 9.1811 | 11.2042 | 12.974 | 14.8586 | 17.0254 | 19.3262 | 21.4301 | 23.343 | 25.0019 | 26.0446 | 29.1237 | 31.627
South West | Seabank 132 kV | Cairns Road | Primary Substation | 11 | Hydrogen Evolution | 1.0419 | 1.3287 | 1.6772 | 2.0413 | 2.4562 | 2.9313 | 3.5069 | 4.3304 | 5.0563 | 5.8652 | 6.7434 | 7.6333 | 8.4631 | 9.2378 | 9.9583 | 10.367 | 11.2586 | 12.0263 | 2.296 | 2.9156 | 3.6528 | 4.4218 | 5.2937 | 6.2876 | 7.4874 | 9.1838 | 10.6874 | 12.3772 | 14.2166 | 16.0862 | 17.8162 | 19.4343 | 20.9433 | 21.8281 | 23.8247 | 25.5514
South West | Seabank 132 kV | Chewton Mendip | Primary Substation | 11 | Counterfactual | 0.24871 | 1.8461 | 1.8805 | 1.9214 | 1.9714 | 2.0464 | 2.1316 | 2.2448 | 2.3442 | 2.4584 | 2.5601 | 2.6463 | 2.7321 | 2.8203 | 2.9041 | 2.9886 | 3.3248 | 3.5612 | 0.59727 | 4.5829 | 4.6606 | 4.7526 | 4.8655 | 5.0314 | 5.2219 | 5.4718 | 5.6937 | 5.9523 | 6.1773 | 6.3632 | 6.545 | 6.7326 | 6.9098 | 7.0881 | 7.8076 | 8.3275
South West | Seabank 132 kV | Chewton Mendip | Primary Substation | 11 | Electric Engagement | 0.27173 | 0.3202 | 0.4404 | 0.57428 | 0.713 | 0.88355 | 1.0664 | 1.2933 | 1.5016 | 1.6974 | 1.892 | 2.0304 | 2.1724 | 2.3171 | 2.4554 | 2.6054 | 3.2605 | 3.6401 | 0.64807 | 0.7539 | 1.0312 | 1.3396 | 1.6567 | 2.036 | 2.439 | 2.9339 | 3.3913 | 3.8244 | 4.257 | 4.5734 | 4.8996 | 5.232 | 5.5475 | 5.8885 | 7.3718 | 8.2797
South West | Seabank 132 kV | Chewton Mendip | Primary Substation | 11 | Holistic Transition | 0.26614 | 0.30549 | 0.42071 | 0.5389 | 0.67598 | 0.84542 | 1.0442 | 1.304 | 1.5332 | 1.7625 | 1.9526 | 2.1246 | 2.2932 | 2.4338 | 2.569 | 2.689 | 3.1961 | 3.4159 | 0.63938 | 0.72974 | 1.005 | 1.2863 | 1.6127 | 2.0028 | 2.4638 | 3.064 | 3.5922 | 4.117 | 4.5397 | 4.921 | 5.2947 | 5.5995 | 5.8921 | 6.1544 | 7.2884 | 7.7899
South West | Seabank 132 kV | Chewton Mendip | Primary Substation | 11 | Hydrogen Evolution | 0.2564 | 0.2842 | 0.33295 | 0.39758 | 0.47223 | 0.58149 | 0.69953 | 0.84819 | 1.0159 | 1.2067 | 1.3647 | 1.5094 | 1.6455 | 1.7815 | 1.9118 | 2.0193 | 2.4765 | 2.831 | 0.61414 | 0.67509 | 0.78352 | 0.93008 | 1.0992 | 1.3414 | 1.6031 | 1.9277 | 2.3031 | 2.7343 | 3.0821 | 3.3969 | 3.6905 | 3.9862 | 4.2689 | 4.5068 | 5.5575 | 6.386
South West | Seabank 132 kV | Clevedon | Primary Substation | 11 | Counterfactual | 0.70254 | 0.79808 | 0.90749 | 1.0356 | 1.1899 | 1.3629 | 1.5571 | 1.8503 | 2.0903 | 2.3452 | 2.602 | 2.8621 | 3.1515 | 3.4402 | 3.7195 | 3.9951 | 4.9169 | 5.2905 | 1.6383 | 1.8408 | 2.0717 | 2.3413 | 2.6653 | 3.0281 | 3.4352 | 4.0417 | 4.5421 | 5.0744 | 5.6078 | 6.1449 | 6.7417 | 7.3372 | 7.9122 | 8.4775 | 10.3971 | 11.2119
South West | Seabank 132 kV | Clevedon | Primary Substation | 11 | Electric Engagement | 0.81875 | 1.0324 | 1.3119 | 1.6437 | 2.011 | 2.4087 | 2.8722 | 3.4844 | 3.9985 | 4.4346 | 4.8072 | 4.9453 | 5.0728 | 5.1984 | 5.3206 | 5.4369 | 5.9656 | 6.4171 | 1.8963 | 2.352 | 2.9451 | 3.6469 | 4.4207 | 5.2556 | 6.2227 | 7.4879 | 8.5581 | 9.4776 | 10.2667 | 10.58 | 10.8717 | 11.1601 | 11.4403 | 11.7089 | 12.9381 | 13.9874
South West | Seabank 132 kV | Clevedon | Primary Substation | 11 | Holistic Transition | 0.79383 | 0.95235 | 1.1526 | 1.3842 | 1.6517 | 1.9549 | 2.2981 | 2.7576 | 3.1593 | 3.5787 | 4.0061 | 4.4139 | 4.8001 | 5.1554 | 5.4873 | 5.6916 | 6.3049 | 6.7786 | 1.8598 | 2.2141 | 2.6574 | 3.1669 | 3.7527 | 4.4113 | 5.1535 | 6.1332 | 6.9933 | 7.8878 | 8.7937 | 9.6584 | 10.4745 | 11.2233 | 11.924 | 12.3696 | 13.7789 | 14.8738
South West | Seabank 132 kV | Clevedon | Primary Substation | 11 | Hydrogen Evolution | 0.73847 | 0.85925 | 1.013 | 1.2053 | 1.4251 | 1.6779 | 1.9714 | 2.375 | 2.7444 | 3.1441 | 3.545 | 3.9262 | 4.2867 | 4.6231 | 4.9361 | 5.1041 | 5.5536 | 5.941 | 1.7183 | 1.9772 | 2.3028 | 2.7109 | 3.1763 | 3.7106 | 4.3273 | 5.1643 | 5.9371 | 6.7776 | 7.6137 | 8.4054 | 9.1511 | 9.8492 | 10.4994 | 10.8596 | 11.8835 | 12.7658
South West | Seabank 132 kV | Dinder | Primary Substation | 11 | Counterfactual | 0.40956 | 0.42327 | 0.44543 | 0.46989 | 0.49911 | 0.54341 | 0.59397 | 0.66054 | 0.7184 | 0.78507 | 0.8446 | 0.90217 | 0.95185 | 1.003 | 1.0521 | 1.1012 | 1.3335 | 1.5009 | 0.99094 | 1.0209 | 1.0711 | 1.1266 | 1.1931 | 1.2918 | 1.4058 | 1.5538 | 1.6838 | 1.8361 | 1.9692 | 2.0972 | 2.2032 | 2.3126 | 2.417 | 2.5213 | 3.0295 | 3.4083
South West | Seabank 132 kV | Dinder | Primary Substation | 11 | Electric Engagement | 0.42407 | 0.45572 | 0.52675 | 0.60278 | 0.68223 | 0.78205 | 0.89187 | 1.0253 | 1.1698 | 1.2898 | 1.4091 | 1.492 | 1.5754 | 1.6701 | 1.7544 | 1.8735 | 2.2646 | 2.497 | 1.0232 | 1.0928 | 1.2573 | 1.432 | 1.6133 | 1.8347 | 2.0763 | 2.3667 | 2.6892 | 2.9536 | 3.2182 | 3.4078 | 3.599 | 3.8142 | 4.0075 | 4.2708 | 5.1578 | 5.7149
South West | Seabank 132 kV | Dinder | Primary Substation | 11 | Holistic Transition | 0.42111 | 0.44789 | 0.51577 | 0.58608 | 0.66812 | 0.77098 | 0.89282 | 1.0504 | 1.1954 | 1.3554 | 1.4741 | 1.5828 | 1.6883 | 1.7841 | 1.8667 | 1.9669 | 2.2653 | 2.3956 | 1.0189 | 1.0807 | 1.2434 | 1.4109 | 1.6065 | 1.8438 | 2.1268 | 2.4918 | 2.8272 | 3.1969 | 3.4604 | 3.701 | 3.9347 | 4.1411 | 4.32 | 4.5343 | 5.2048 | 5.5038
South West | Seabank 132 kV | Dinder | Primary Substation | 11 | Hydrogen Evolution | 0.41418 | 0.43224 | 0.46069 | 0.49635 | 0.53839 | 0.60222 | 0.67264 | 0.75923 | 0.87145 | 0.99548 | 1.0915 | 1.1792 | 1.2605 | 1.3456 | 1.4229 | 1.4995 | 1.7703 | 1.9887 | 1.0012 | 1.0411 | 1.1053 | 1.1862 | 1.2819 | 1.4237 | 1.5802 | 1.77 | 2.0259 | 2.3089 | 2.5207 | 2.7118 | 2.8879 | 3.0726 | 3.2412 | 3.4084 | 4.0359 | 4.5489
South West | Seabank 132 kV | Easton-In-Gordano | Primary Substation | 11 | Counterfactual | 0.20073 | 0.22447 | 0.25267 | 0.28672 | 0.32764 | 0.37671 | 0.43157 | 0.51252 | 0.57925 | 0.65113 | 0.72178 | 0.7916 | 0.86675 | 0.94228 | 1.0154 | 1.1023 | 1.4366 | 1.6273 | 0.4658 | 0.5158 | 0.57579 | 0.64794 | 0.73458 | 0.83826 | 0.9544 | 1.1234 | 1.2641 | 1.4164 | 1.5645 | 1.7095 | 1.8643 | 2.0201 | 2.1705 | 2.3486 | 3.0417 | 3.4463
South West | Seabank 132 kV | Easton-In-Gordano | Primary Substation | 11 | Electric Engagement | 0.22971 | 0.28163 | 0.35881 | 0.44862 | 0.547 | 0.65691 | 1.1024 | 1.2682 | 1.4082 | 1.5266 | 1.6327 | 1.6819 | 1.7366 | 1.7888 | 1.8379 | 1.8838 | 2.0807 | 2.2244 | 0.52996 | 0.64017 | 0.80609 | 0.99817 | 1.2076 | 1.44 | 2.5031 | 2.8483 | 3.1414 | 3.3915 | 3.6175 | 3.7288 | 3.851 | 3.9686 | 4.0795 | 4.1841 | 4.6345 | 4.971
South West | Seabank 132 kV | Easton-In-Gordano | Primary Substation | 11 | Holistic Transition | 0.22303 | 0.26039 | 0.31775 | 0.38274 | 0.45817 | 0.54615 | 0.64793 | 0.78329 | 0.90215 | 1.0246 | 1.1416 | 1.2514 | 1.3578 | 1.4541 | 1.5439 | 1.6028 | 1.7991 | 1.9241 | 0.51985 | 0.60291 | 0.73177 | 0.87668 | 1.0445 | 1.2376 | 1.4613 | 1.7553 | 2.0142 | 2.2794 | 2.5287 | 2.7623 | 2.9886 | 3.1921 | 3.382 | 3.5103 | 3.9552 | 4.2428
South West | Seabank 132 kV | Easton-In-Gordano | Primary Substation | 11 | Hydrogen Evolution | 0.21 | 0.23946 | 0.28056 | 0.33166 | 0.39012 | 0.46136 | 0.86161 | 0.97218 | 1.0764 | 1.1885 | 1.3098 | 1.445 | 1.5745 | 1.6968 | 1.8093 | 1.8829 | 2.0944 | 2.2235 | 0.48625 | 0.54908 | 0.63645 | 0.74557 | 0.8703 | 1.0217 | 1.991 | 2.2218 | 2.4426 | 2.681 | 2.934 | 3.2131 | 3.4801 | 3.733 | 3.966 | 4.1212 | 4.5877 | 4.8841
South West | Seabank 132 kV | Evercreech | Primary Substation | 11 | Counterfactual | 0.78275 | 0.81155 | 0.86198 | 0.91902 | 0.99428 | 1.1056 | 1.2355 | 1.4003 | 1.5568 | 1.7409 | 1.8829 | 1.9896 | 2.0926 | 2.2001 | 2.3105 | 2.4804 | 3.0279 | 3.4335 | 1.9397 | 2.0039 | 2.1209 | 2.253 | 2.4291 | 2.6845 | 2.9859 | 3.3636 | 3.7276 | 4.1609 | 4.4862 | 4.7233 | 4.9467 | 5.1809 | 5.4229 | 5.813 | 7.047 | 7.9816
South West | Seabank 132 kV | Evercreech | Primary Substation | 11 | Electric Engagement | 0.80792 | 0.86993 | 1.0507 | 1.274 | 1.5191 | 1.8118 | 2.1199 | 2.4654 | 2.7544 | 3.0285 | 3.3153 | 3.6652 | 3.9034 | 4.1208 | 4.3242 | 4.5354 | 5.4903 | 6.1072 | 1.9956 | 2.1338 | 2.5619 | 3.0922 | 3.6736 | 4.3531 | 5.0629 | 5.8478 | 6.4997 | 7.1205 | 7.7753 | 8.6157 | 9.1777 | 9.688 | 10.1622 | 10.6563 | 12.867 | 14.3642
South West | Seabank 132 kV | Evercreech | Primary Substation | 11 | Holistic Transition | 0.80244 | 0.85718 | 1.0524 | 1.2641 | 1.5157 | 1.814 | 2.1607 | 2.5879 | 2.9397 | 3.278 | 3.543 | 3.783 | 4.1206 | 4.3745 | 4.5506 | 4.6983 | 5.3976 | 5.7101 | 1.9874 | 2.1153 | 2.5903 | 3.1046 | 3.7162 | 4.4239 | 5.2505 | 6.2648 | 7.0946 | 7.8848 | 8.4867 | 9.03 | 9.8194 | 10.4018 | 10.7907 | 11.1231 | 12.7226 | 13.4511
South West | Seabank 132 kV | Evercreech | Primary Substation | 11 | Hydrogen Evolution | 0.79084 | 0.82625 | 0.88952 | 0.99839 | 1.1378 | 1.3336 | 1.545 | 1.7953 | 2.0337 | 2.3063 | 2.5191 | 2.7719 | 3.0568 | 3.2305 | 3.3982 | 3.5349 | 4.1977 | 4.7375 | 1.9577 | 2.037 | 2.1819 | 2.4385 | 2.7691 | 3.2247 | 3.7164 | 4.2921 | 4.8407 | 5.4715 | 5.9511 | 6.5311 | 7.1927 | 7.5797 | 7.9523 | 8.2638 | 9.8216 | 11.1058
South West | Seabank 132 kV | Foxhills | Primary Substation | 11 | Counterfactual | 0.18837 | 0.23529 | 0.2904 | 0.35368 | 0.43104 | 0.53337 | 0.69813 | 0.85688 | 0.96349 | 1.0825 | 1.1992 | 1.3141 | 1.4423 | 1.5696 | 1.6915 | 1.8102 | 2.2415 | 2.4493 | 0.42476 | 0.5244 | 0.64209 | 0.77665 | 0.941 | 1.1582 | 1.5082 | 1.8423 | 2.0684 | 2.3224 | 2.5686 | 2.8082 | 3.0753 | 3.3406 | 3.5938 | 3.8389 | 4.7475 | 5.2055
South West | Seabank 132 kV | Foxhills | Primary Substation | 11 | Electric Engagement | 0.23753 | 0.35094 | 0.50394 | 0.69472 | 0.89323 | 1.1072 | 1.3005 | 1.5698 | 1.8032 | 2.0128 | 2.1953 | 2.2795 | 2.3596 | 2.439 | 2.5162 | 2.5901 | 2.9284 | 3.1875 | 0.53402 | 0.77794 | 1.1091 | 1.52 | 1.9465 | 2.4042 | 2.8117 | 3.3747 | 3.8678 | 4.3186 | 4.7125 | 4.9044 | 5.0883 | 5.2712 | 5.4487 | 5.6197 | 6.404 | 7.0125
South West | Seabank 132 kV | Foxhills | Primary Substation | 11 | Holistic Transition | 0.22768 | 0.31993 | 0.46293 | 0.61496 | 0.75381 | 0.93476 | 1.0954 | 1.3222 | 1.5222 | 1.7307 | 1.9344 | 2.1298 | 2.312 | 2.4755 | 2.6287 | 2.7294 | 3.0727 | 3.2987 | 0.51964 | 0.7252 | 1.0445 | 1.3823 | 1.6926 | 2.0924 | 2.4479 | 2.9435 | 3.382 | 3.8374 | 4.2769 | 4.6978 | 5.0881 | 5.4354 | 5.7612 | 5.9819 | 6.7665 | 7.2878
South West | Seabank 132 kV | Foxhills | Primary Substation | 11 | Hydrogen Evolution | 0.20367 | 0.276 | 0.37663 | 0.49463 | 0.62308 | 0.79114 | 0.91054 | 1.087 | 1.2624 | 1.4597 | 1.6479 | 1.8238 | 1.988 | 2.1418 | 2.2861 | 2.3719 | 2.6512 | 2.879 | 0.45883 | 0.6152 | 0.83132 | 1.085 | 1.3615 | 1.7241 | 1.9773 | 2.3472 | 2.7209 | 3.1462 | 3.5459 | 3.9169 | 4.2605 | 4.5836 | 4.8868 | 5.0735 | 5.714 | 6.2398
South West | Seabank 132 kV | Gas Lane | Primary Substation | 11 | Counterfactual | 0.73729 | 0.79764 | 0.8687 | 0.95063 | 1.0491 | 1.1608 | 1.2868 | 1.4756 | 1.6305 | 1.7946 | 1.9597 | 2.1266 | 2.3085 | 2.4903 | 2.6672 | 2.8438 | 3.4334 | 3.6646 | 1.7419 | 1.8697 | 2.0197 | 2.1922 | 2.399 | 2.6336 | 2.8978 | 3.2886 | 3.6119 | 3.9552 | 4.2984 | 4.6433 | 5.0169 | 5.3907 | 5.7537 | 6.116 | 7.3447 | 7.8518
South West | Seabank 132 kV | Gas Lane | Primary Substation | 11 | Electric Engagement | 0.81265 | 0.94966 | 1.1296 | 1.3428 | 1.5787 | 1.8364 | 2.1367 | 2.5327 | 2.8639 | 3.1371 | 3.3748 | 3.4646 | 3.5482 | 3.6312 | 3.7123 | 3.7911 | 4.1526 | 4.4452 | 1.9094 | 2.2011 | 2.5835 | 3.035 | 3.5324 | 4.0735 | 4.7004 | 5.5191 | 6.2077 | 6.7798 | 7.2815 | 7.4855 | 7.6769 | 7.8675 | 8.0534 | 8.2347 | 9.0689 | 9.7495
South West | Seabank 132 kV | Gas Lane | Primary Substation | 11 | Holistic Transition | 0.79677 | 0.89769 | 1.0266 | 1.1759 | 1.3476 | 1.544 | 1.7672 | 2.0656 | 2.3271 | 2.5985 | 2.8691 | 3.1271 | 3.3767 | 3.6074 | 3.8226 | 3.9549 | 4.3577 | 4.6598 | 1.8863 | 2.1113 | 2.3974 | 2.7262 | 3.103 | 3.5299 | 4.0134 | 4.6508 | 5.2115 | 5.7905 | 6.3619 | 6.9067 | 7.4338 | 7.9197 | 8.374 | 8.6624 | 9.5851 | 10.2831
South West | Seabank 132 kV | Gas Lane | Primary Substation | 11 | Hydrogen Evolution | 0.76039 | 0.83795 | 0.93563 | 1.0577 | 1.1972 | 1.3597 | 1.5482 | 1.8063 | 2.0419 | 2.2911 | 2.5416 | 2.7828 | 3.0143 | 3.2314 | 3.4333 | 3.5415 | 3.8367 | 4.09 | 1.7934 | 1.9594 | 2.1665 | 2.426 | 2.7217 | 3.0655 | 3.4618 | 3.9975 | 4.4912 | 5.0136 | 5.5338 | 6.0337 | 6.5127 | 6.9633 | 7.3828 | 7.6151 | 8.2871 | 8.8642
South West | Seabank 132 kV | High Littleton | Primary Substation | 11 | Counterfactual | 0.26011 | 0.29261 | 0.33877 | 0.39097 | 0.45149 | 0.53253 | 0.62455 | 0.76518 | 0.88714 | 1.0227 | 1.1468 | 1.2618 | 1.3802 | 1.5003 | 1.6141 | 1.7283 | 2.1862 | 2.461 | 0.58078 | 0.64956 | 0.75045 | 0.86429 | 0.99658 | 1.1725 | 1.3736 | 1.6757 | 1.9404 | 2.2378 | 2.5057 | 2.7493 | 2.9969 | 3.2487 | 3.4863 | 3.7244 | 4.7062 | 5.32
South West | Seabank 132 kV | High Littleton | Primary Substation | 11 | Electric Engagement | 0.30015 | 0.37212 | 0.50763 | 0.65417 | 0.81046 | 0.99386 | 1.2189 | 1.4989 | 1.7472 | 1.9717 | 2.184 | 2.3105 | 2.4353 | 2.5623 | 2.694 | 2.8164 | 3.3757 | 3.7362 | 0.66972 | 0.82315 | 1.1249 | 1.4491 | 1.7924 | 2.189 | 2.6728 | 3.269 | 3.8015 | 4.2879 | 4.7515 | 5.0403 | 5.3266 | 5.619 | 5.9186 | 6.2001 | 7.4766 | 8.3317
South West | Seabank 132 kV | High Littleton | Primary Substation | 11 | Holistic Transition | 0.2918 | 0.34504 | 0.46007 | 0.5798 | 0.71666 | 0.89966 | 1.104 | 1.3834 | 1.6334 | 1.8878 | 2.111 | 2.317 | 2.5161 | 2.6875 | 2.8567 | 2.9753 | 3.4481 | 3.6956 | 0.6576 | 0.77662 | 1.0439 | 1.3207 | 1.6373 | 2.0495 | 2.5136 | 3.1431 | 3.7063 | 4.2759 | 4.7635 | 5.2121 | 5.6455 | 6.0133 | 6.3746 | 6.6352 | 7.7025 | 8.2682
South West | Seabank 132 kV | High Littleton | Primary Substation | 11 | Hydrogen Evolution | 0.27264 | 0.31339 | 0.37718 | 0.45193 | 0.5382 | 0.65384 | 0.79159 | 0.98014 | 1.1802 | 1.3987 | 1.593 | 1.7739 | 1.9446 | 2.1094 | 2.269 | 2.3759 | 2.7937 | 3.1304 | 0.60861 | 0.69594 | 0.83464 | 0.99827 | 1.1872 | 1.4381 | 1.7364 | 2.1394 | 2.5772 | 3.0587 | 3.4771 | 3.8636 | 4.2264 | 4.5793 | 4.9202 | 5.1563 | 6.1185 | 6.9022
South West | Seabank 132 kV | Keynsham East | Primary Substation | 11 | Counterfactual | 0.50257 | 0.56161 | 0.6254 | 0.69415 | 0.77129 | 0.85934 | 0.94151 | 1.0678 | 1.1672 | 1.2754 | 1.3835 | 1.4933 | 1.6651 | 1.8509 | 2.0334 | 2.1624 | 2.6002 | 2.8058 | 1.0761 | 1.2013 | 1.3368 | 1.4818 | 1.6445 | 1.8301 | 2.0035 | 2.2659 | 2.4741 | 2.7017 | 2.9269 | 3.1533 | 3.5278 | 3.9378 | 4.3412 | 4.6105 | 5.5245 | 5.9632
South West | Seabank 132 kV | Keynsham East | Primary Substation | 11 | Electric Engagement | 0.55517 | 0.66929 | 0.81123 | 0.97126 | 1.1469 | 1.3178 | 1.5147 | 1.7766 | 2.0052 | 2.2901 | 2.5476 | 2.6597 | 2.7622 | 2.8479 | 2.9264 | 2.9986 | 3.2204 | 3.3954 | 1.1928 | 1.4382 | 1.7417 | 2.0822 | 2.4547 | 2.8133 | 3.2247 | 3.7667 | 4.248 | 4.8872 | 5.4693 | 5.7289 | 5.9698 | 6.1703 | 6.3529 | 6.5231 | 7.0473 | 7.4611
South West | Seabank 132 kV | Keynsham East | Primary Substation | 11 | Holistic Transition | 0.54334 | 0.63516 | 0.74437 | 0.86256 | 0.99601 | 1.1266 | 1.2744 | 1.4768 | 1.6495 | 1.8563 | 2.1506 | 2.4586 | 2.6716 | 2.846 | 2.9925 | 3.0847 | 3.3503 | 3.4923 | 1.1743 | 1.3792 | 1.6214 | 1.8822 | 2.176 | 2.4603 | 2.7818 | 3.2157 | 3.5878 | 4.0396 | 4.7061 | 5.4069 | 5.8725 | 6.2462 | 6.554 | 6.7532 | 7.36 | 7.6971
South West | Seabank 132 kV | Keynsham East | Primary Substation | 11 | Hydrogen Evolution | 0.52099 | 0.5918 | 0.68789 | 0.78549 | 0.89602 | 1.0251 | 1.1527 | 1.3328 | 1.5001 | 1.7433 | 2.0062 | 2.2586 | 2.4563 | 2.627 | 2.783 | 2.881 | 3.0823 | 3.2124 | 1.1167 | 1.2696 | 1.474 | 1.6812 | 1.9156 | 2.1888 | 2.4561 | 2.8285 | 3.178 | 3.714 | 4.2969 | 4.8559 | 5.2803 | 5.6439 | 5.9752 | 6.1904 | 6.6473 | 6.951
South West | Seabank 132 kV | Kingsweston | Primary Substation | 11 | Counterfactual | 4.5568 | 4.5758 | 4.6018 | 4.6338 | 4.6756 | 4.7271 | 4.7875 | 4.8579 | 4.8823 | 4.9109 | 4.9327 | 4.9492 | 4.9661 | 4.979 | 5.2075 | 5.2237 | 5.3032 | 5.375 | 10.2919 | 10.3382 | 10.4022 | 10.4805 | 10.5828 | 10.7086 | 10.8563 | 11.0274 | 11.084 | 11.1506 | 11.1997 | 11.2354 | 11.2713 | 11.2978 | 11.7562 | 11.79 | 11.9602 | 12.1135
South West | Seabank 132 kV | Kingsweston | Primary Substation | 11 | Electric Engagement | 4.8416 | 4.9019 | 4.9974 | 5.2237 | 5.373 | 5.5536 | 5.7285 | 5.897 | 5.927 | 5.956 | 5.9863 | 6.0098 | 6.0327 | 4.3337 | 4.7892 | 4.811 | 5.4544 | 5.9628 | 10.872 | 11.0213 | 11.2568 | 11.8184 | 12.1872 | 12.6311 | 13.0606 | 13.4716 | 13.5373 | 13.6009 | 13.6674 | 13.719 | 13.7687 | 9.5137 | 10.4298 | 10.4781 | 11.7971 | 12.8384
South West | Seabank 132 kV | Kingsweston | Primary Substation | 11 | Holistic Transition | 4.5854 | 4.6496 | 4.7589 | 4.8866 | 5.0403 | 5.2255 | 5.3958 | 5.5721 | 5.6062 | 5.6378 | 5.663 | 5.6887 | 4.0003 | 4.0233 | 4.3959 | 4.4197 | 6.3524 | 6.8572 | 10.3628 | 10.5226 | 10.7933 | 11.1099 | 11.4906 | 11.9459 | 12.3651 | 12.7964 | 12.874 | 12.9442 | 12.998 | 13.0535 | 8.8241 | 8.8738 | 9.6233 | 9.6753 | 14.2142 | 15.2399
South West | Seabank 132 kV | Kingsweston | Primary Substation | 11 | Hydrogen Evolution | 4.5782 | 4.6345 | 4.7195 | 4.8353 | 4.9762 | 5.1469 | 5.315 | 5.4846 | 5.522 | 5.5576 | 5.5865 | 5.6109 | 5.6349 | 3.9278 | 4.1658 | 6.7807 | 7.1273 | 7.4169 | 10.3451 | 10.4848 | 10.6947 | 10.9804 | 11.328 | 11.7489 | 12.1624 | 12.5768 | 12.6574 | 12.7349 | 12.7972 | 12.8496 | 12.9006 | 8.626 | 9.1052 | 15.637 | 16.3539 | 16.9518
South West | Seabank 132 kV | Midsomer Norton | Primary Substation | 11 | Counterfactual | 2.3033 | 2.3927 | 2.4872 | 2.6117 | 2.7284 | 2.8775 | 3.0401 | 3.2887 | 3.4901 | 3.7075 | 3.9259 | 4.1414 | 4.3964 | 4.6496 | 4.8901 | 5.112 | 5.8882 | 6.228 | 5.6757 | 5.8661 | 6.0664 | 6.3292 | 6.5758 | 6.8901 | 7.2329 | 7.7501 | 8.1727 | 8.6302 | 9.0869 | 9.5335 | 10.0693 | 10.6018 | 11.1054 | 11.5616 | 13.185 | 13.9269
South West | Seabank 132 kV | Midsomer Norton | Primary Substation | 11 | Electric Engagement | 2.3948 | 2.5885 | 2.8475 | 3.0956 | 3.368 | 3.6915 | 4.0664 | 4.5832 | 5.0431 | 5.4751 | 5.8276 | 5.9582 | 6.0824 | 6.2036 | 6.3219 | 6.434 | 6.9372 | 7.3332 | 5.8792 | 6.2956 | 6.8499 | 7.3772 | 7.9528 | 8.6345 | 9.4203 | 10.4958 | 11.4652 | 12.4028 | 13.168 | 13.4633 | 13.7459 | 14.0229 | 14.2927 | 14.5501 | 15.7069 | 16.625
South West | Seabank 132 kV | Midsomer Norton | Primary Substation | 11 | Holistic Transition | 2.3763 | 2.5302 | 2.7162 | 2.9116 | 3.1067 | 3.3605 | 3.6684 | 4.0907 | 4.4438 | 4.8079 | 5.2035 | 5.5776 | 5.9047 | 6.1987 | 6.4783 | 6.6557 | 7.2736 | 7.7054 | 5.8525 | 6.1975 | 6.6113 | 7.0441 | 7.4751 | 8.029 | 8.6996 | 9.6081 | 10.3698 | 11.155 | 12.0117 | 12.8195 | 13.5139 | 14.1336 | 14.7246 | 15.1109 | 16.5276 | 17.5209
South West | Seabank 132 kV | Midsomer Norton | Primary Substation | 11 | Hydrogen Evolution | 2.3322 | 2.4519 | 2.6087 | 2.7457 | 2.9015 | 3.1079 | 3.3466 | 3.6907 | 4.0284 | 4.4118 | 4.7875 | 5.1218 | 5.4206 | 5.697 | 5.9577 | 6.103 | 7.4852 | 7.8565 | 5.7403 | 5.9989 | 6.3338 | 6.625 | 6.955 | 7.3929 | 7.8963 | 8.6146 | 9.3267 | 10.1527 | 10.9566 | 11.6635 | 12.2842 | 12.8605 | 13.4048 | 13.718 | 17.0749 | 17.918
South West | Seabank 132 kV | Newbury | Primary Substation | 11 | Counterfactual | 0.25872 | 0.29094 | 0.34333 | 0.40709 | 0.49331 | 0.60567 | 0.7331 | 0.89077 | 1.0291 | 1.1896 | 1.421 | 1.5588 | 1.699 | 1.8431 | 1.9816 | 2.0969 | 2.6224 | 2.9912 | 0.62762 | 0.69768 | 0.81615 | 0.95949 | 1.1532 | 1.404 | 1.6914 | 2.0429 | 2.3552 | 2.7228 | 3.2645 | 3.572 | 3.8794 | 4.1968 | 4.5002 | 4.7451 | 5.901 | 6.7428
South West | Seabank 132 kV | Newbury | Primary Substation | 11 | Electric Engagement | 0.29303 | 0.36749 | 0.53684 | 0.74697 | 0.97239 | 1.2124 | 1.4709 | 1.7893 | 2.201 | 2.5183 | 2.8216 | 3.0383 | 3.2592 | 3.4871 | 3.698 | 3.8853 | 4.7483 | 5.2813 | 0.70396 | 0.86703 | 1.2583 | 1.74 | 2.2547 | 2.7923 | 3.3654 | 4.0645 | 5.0095 | 5.7281 | 6.4166 | 6.925 | 7.4442 | 7.9806 | 8.4729 | 8.9073 | 10.8886 | 12.1727
South West | Seabank 132 kV | Newbury | Primary Substation | 11 | Holistic Transition | 0.28629 | 0.34857 | 0.52549 | 0.72139 | 0.93159 | 1.1774 | 1.4665 | 1.8386 | 2.3503 | 2.7711 | 3.0775 | 3.3619 | 3.6383 | 3.834 | 4.0218 | 4.1703 | 4.8337 | 5.1353 | 0.69443 | 0.8376 | 1.2587 | 1.7214 | 2.2217 | 2.7921 | 3.4679 | 4.3335 | 5.5542 | 6.5419 | 7.2374 | 7.8819 | 8.5078 | 8.9348 | 9.3435 | 9.6741 | 11.1794 | 11.8733
South West | Seabank 132 kV | Newbury | Primary Substation | 11 | Hydrogen Evolution | 0.26923 | 0.31164 | 0.38067 | 0.49243 | 0.62471 | 0.79112 | 0.96153 | 1.1681 | 1.5418 | 1.86 | 2.1185 | 2.3547 | 2.5779 | 2.7997 | 3.0016 | 3.1363 | 3.7512 | 4.2557 | 0.6511 | 0.74442 | 0.89946 | 1.1528 | 1.4543 | 1.8282 | 2.2107 | 2.6663 | 3.5433 | 4.2785 | 4.8627 | 5.3919 | 5.8892 | 6.3873 | 6.8366 | 7.1404 | 8.5767 | 9.7664
South West | Seabank 132 kV | Paulton | Primary Substation | 11 | Counterfactual | 0.10755 | 0.13053 | 0.16042 | 0.21052 | 0.25008 | 0.29316 | 0.36481 | 0.46456 | 0.52605 | 0.59401 | 0.66164 | 0.72918 | 0.80272 | 0.87627 | 0.94695 | 1.0173 | 1.2674 | 1.3797 | 0.24032 | 0.28905 | 0.35259 | 0.4582 | 0.54192 | 0.63302 | 0.78461 | 0.99361 | 1.1231 | 1.2668 | 1.4086 | 1.5489 | 1.7008 | 1.8529 | 1.9987 | 2.1435 | 2.6679 | 2.9143
South West | Seabank 132 kV | Paulton | Primary Substation | 11 | Electric Engagement | 0.13645 | 0.18799 | 0.27435 | 0.36929 | 0.45969 | 0.55514 | 0.69999 | 0.89134 | 1.0271 | 1.1432 | 1.2444 | 1.289 | 1.3309 | 1.372 | 1.4116 | 1.4504 | 1.6274 | 1.77 | 0.30459 | 0.41446 | 0.59996 | 0.80288 | 0.99473 | 1.1958 | 1.5025 | 1.9046 | 2.1892 | 2.4351 | 2.6509 | 2.7522 | 2.8481 | 2.9424 | 3.0334 | 3.1227 | 3.5323 | 3.8644
South West | Seabank 132 kV | Paulton | Primary Substation | 11 | Holistic Transition | 0.13066 | 0.16887 | 0.23101 | 0.31365 | 0.37707 | 0.45087 | 0.57271 | 0.73316 | 0.84641 | 0.96395 | 1.0783 | 1.1889 | 1.2957 | 1.3925 | 1.483 | 1.5411 | 1.7304 | 1.8639 | 0.29634 | 0.38174 | 0.52038 | 0.70282 | 0.8437 | 1.0055 | 1.2726 | 1.6207 | 1.8665 | 2.1203 | 2.3641 | 2.5996 | 2.8265 | 3.0313 | 3.2232 | 3.35 | 3.7823 | 4.0898
South West | Seabank 132 kV | Paulton | Primary Substation | 11 | Hydrogen Evolution | 0.11655 | 0.14566 | 0.19809 | 0.25922 | 0.30829 | 0.36655 | 0.46685 | 0.60177 | 0.70182 | 0.80956 | 0.91429 | 1.0143 | 1.11 | 1.1991 | 1.2822 | 1.3302 | 1.4773 | 1.6013 | 0.26037 | 0.32281 | 0.43498 | 0.56583 | 0.67018 | 0.7936 | 1.0079 | 1.2931 | 1.5047 | 1.7336 | 1.9533 | 2.1623 | 2.3616 | 2.5481 | 2.722 | 2.8258 | 3.1619 | 3.4458
South West | Seabank 132 kV | Peasedown | Primary Substation | 11 | Counterfactual | 0.14258 | 0.17072 | 0.20795 | 0.26462 | 0.32243 | 0.39035 | 0.45941 | 0.55828 | 0.64292 | 0.73974 | 0.83009 | 0.9149 | 1.0029 | 1.0914 | 1.1758 | 1.26 | 1.5909 | 1.7707 | 0.32304 | 0.38256 | 0.46358 | 0.58538 | 0.71049 | 0.85753 | 1.0085 | 1.221 | 1.405 | 1.6176 | 1.8125 | 1.9922 | 2.1761 | 2.3617 | 2.5376 | 2.7132 | 3.4228 | 3.8291
South West | Seabank 132 kV | Peasedown | Primary Substation | 11 | Electric Engagement | 0.17418 | 0.23754 | 0.34969 | 0.48236 | 0.61504 | 0.74784 | 0.89899 | 1.1053 | 1.2863 | 1.4475 | 1.597 | 1.6793 | 1.76 | 1.8417 | 1.9205 | 1.9985 | 2.3462 | 2.6002 | 0.39326 | 0.5285 | 0.7771 | 1.0689 | 1.3595 | 1.6471 | 1.9715 | 2.4103 | 2.7983 | 3.1479 | 3.475 | 3.6656 | 3.8534 | 4.0442 | 4.2279 | 4.4102 | 5.2181 | 5.8233
South West | Seabank 132 kV | Peasedown | Primary Substation | 11 | Holistic Transition | 0.1675 | 0.21576 | 0.31549 | 0.43457 | 0.53624 | 0.65359 | 0.79953 | 1.0013 | 1.181 | 1.3638 | 1.5239 | 1.675 | 1.8209 | 1.9455 | 2.0619 | 2.1427 | 2.4431 | 2.6154 | 0.3835 | 0.49073 | 0.7199 | 0.99031 | 1.225 | 1.4911 | 1.823 | 2.2773 | 2.6821 | 3.0915 | 3.4412 | 3.7699 | 4.0872 | 4.3544 | 4.6041 | 4.7827 | 5.472 | 5.87
South West | Seabank 132 kV | Peasedown | Primary Substation | 11 | Hydrogen Evolution | 0.15236 | 0.19125 | 0.24952 | 0.32769 | 0.4025 | 0.48773 | 0.58095 | 0.71386 | 0.85393 | 1.0109 | 1.1516 | 1.2832 | 1.4069 | 1.5258 | 1.6365 | 1.7083 | 1.98 | 2.2069 | 0.3448 | 0.42835 | 0.55499 | 0.72554 | 0.88931 | 1.075 | 1.2771 | 1.561 | 1.8677 | 2.2137 | 2.5169 | 2.7979 | 3.0607 | 3.3151 | 3.5521 | 3.7115 | 4.3455 | 4.8789
South West | Seabank 132 kV | Portishead Ashlands | Primary Substation | 11 | Counterfactual | 0.17235 | 0.20282 | 0.2384 | 0.27523 | 0.32223 | 0.37385 | 0.42826 | 0.51441 | 0.5853 | 0.65955 | 0.73485 | 0.8127 | 0.90197 | 0.99101 | 1.0775 | 1.1605 | 1.4275 | 1.5149 | 0.37945 | 0.44341 | 0.51774 | 0.59483 | 0.69272 | 0.8001 | 0.91324 | 1.0901 | 1.2366 | 1.3901 | 1.5452 | 1.7052 | 1.8897 | 2.0738 | 2.2522 | 2.422 | 2.974 | 3.1648
South West | Seabank 132 kV | Portishead Ashlands | Primary Substation | 11 | Electric Engagement | 0.20906 | 0.27556 | 0.35528 | 0.45073 | 0.56003 | 0.67404 | 0.80872 | 0.99055 | 1.1415 | 1.273 | 1.3832 | 1.4134 | 1.4442 | 1.4744 | 1.5011 | 1.53 | 1.6551 | 1.7745 | 0.46107 | 0.60163 | 0.76928 | 0.96968 | 1.198 | 1.4359 | 1.7152 | 2.0888 | 2.4017 | 2.6798 | 2.9123 | 2.9815 | 3.0515 | 3.1204 | 3.182 | 3.248 | 3.5369 | 3.8099
South West | Seabank 132 kV | Portishead Ashlands | Primary Substation | 11 | Holistic Transition | 0.20156 | 0.25014 | 0.30753 | 0.37149 | 0.44825 | 0.53315 | 0.62922 | 0.75791 | 0.87062 | 0.98958 | 1.1183 | 1.2432 | 1.361 | 1.4679 | 1.5667 | 1.6247 | 1.7878 | 1.9269 | 0.4503 | 0.55728 | 0.68245 | 0.82174 | 0.98757 | 1.17 | 1.375 | 1.6455 | 1.8835 | 2.1343 | 2.4069 | 2.6713 | 2.9179 | 3.1419 | 3.3493 | 3.4748 | 3.8479 | 4.1672
South West | Seabank 132 kV | Portishead Ashlands | Primary Substation | 11 | Hydrogen Evolution | 0.18335 | 0.22183 | 0.26849 | 0.32284 | 0.38784 | 0.46131 | 0.54609 | 0.66262 | 0.76544 | 0.88149 | 1.0005 | 1.1137 | 1.2188 | 1.3202 | 1.4114 | 1.4574 | 1.5671 | 1.6672 | 0.40402 | 0.48568 | 0.58391 | 0.69893 | 0.83584 | 0.9902 | 1.1672 | 1.4077 | 1.6209 | 1.8645 | 2.1129 | 2.3476 | 2.5638 | 2.7724 | 2.9605 | 3.0582 | 3.3052 | 3.5294
South West | Seabank 132 kV | Shepton Mallet | Primary Substation | 11 | Counterfactual | 0.30752 | 0.36489 | 0.44885 | 0.54495 | 0.65321 | 0.79926 | 0.96694 | 1.1918 | 1.382 | 1.5863 | 1.7746 | 1.9552 | 2.1521 | 2.3528 | 2.5283 | 2.7045 | 3.3679 | 3.72 | 0.7389 | 0.86178 | 1.042 | 1.2476 | 1.4795 | 1.7903 | 2.1486 | 2.6234 | 3.0287 | 3.4675 | 3.8667 | 4.2446 | 4.6533 | 5.0706 | 5.4334 | 5.7972 | 7.1975 | 7.9708
South West | Seabank 132 kV | Shepton Mallet | Primary Substation | 11 | Electric Engagement | 0.37392 | 0.5042 | 0.71474 | 1.1372 | 1.3903 | 1.7015 | 2.0607 | 2.5073 | 2.8997 | 3.2497 | 3.5627 | 3.7383 | 3.9159 | 4.0993 | 4.2567 | 4.4111 | 5.1506 | 5.5764 | 0.88629 | 1.1674 | 1.6271 | 2.6061 | 3.1526 | 3.8168 | 4.5794 | 5.5179 | 6.3473 | 7.0927 | 7.7631 | 8.1555 | 8.5539 | 8.966 | 9.3195 | 9.6673 | 11.3225 | 12.3222
South West | Seabank 132 kV | Shepton Mallet | Primary Substation | 11 | Holistic Transition | 0.35988 | 0.46174 | 0.63342 | 0.81734 | 1.0239 | 1.2935 | 1.6025 | 1.9941 | 2.3433 | 2.7056 | 3.0396 | 3.3568 | 3.6699 | 3.9556 | 4.2047 | 4.3786 | 5.0409 | 5.4005 | 0.86572 | 1.0966 | 1.4868 | 1.9023 | 2.3687 | 2.9643 | 3.649 | 4.509 | 5.2768 | 6.0682 | 6.784 | 7.4637 | 8.135 | 8.7426 | 9.271 | 9.6486 | 11.1256 | 11.9464
South West | Seabank 132 kV | Shepton Mallet | Primary Substation | 11 | Hydrogen Evolution | 0.32821 | 0.40199 | 0.5166 | 0.65079 | 0.80292 | 1.0106 | 1.2489 | 1.5499 | 1.8501 | 2.1737 | 2.4645 | 2.7445 | 3.018 | 3.2836 | 3.5134 | 3.6585 | 4.1736 | 4.5834 | 0.78491 | 0.94491 | 1.1919 | 1.4817 | 1.8102 | 2.2555 | 2.7655 | 3.4009 | 4.044 | 4.7404 | 5.3551 | 5.9447 | 6.5189 | 7.0799 | 7.5634 | 7.8775 | 9.0408 | 9.9754
South West | Seabank 132 kV | Stoke Bishop | Primary Substation | 11 | Counterfactual | 0.29672 | 0.34599 | 0.40179 | 0.46841 | 0.53444 | 0.60863 | 0.6941 | 0.82789 | 0.93332 | 1.0475 | 1.1689 | 1.2942 | 1.4324 | 1.5733 | 1.7084 | 1.8418 | 2.3124 | 2.4936 | 0.66419 | 0.76875 | 0.88682 | 1.0273 | 1.1662 | 1.3219 | 1.5006 | 1.777 | 1.9966 | 2.2346 | 2.4865 | 2.7455 | 3.0299 | 3.3192 | 3.5971 | 3.8712 | 4.8485 | 5.2438
South West | Seabank 132 kV | Stoke Bishop | Primary Substation | 11 | Electric Engagement | 0.35604 | 0.46544 | 0.60292 | 0.75371 | 0.92036 | 1.104 | 1.3234 | 1.6173 | 1.871 | 2.0844 | 2.2644 | 2.3339 | 2.401 | 2.4616 | 2.5225 | 2.578 | 2.8211 | 3.0678 | 0.7962 | 1.0288 | 1.3198 | 1.6373 | 1.9865 | 2.3697 | 2.8255 | 3.4301 | 3.9563 | 4.4009 | 4.7792 | 4.9359 | 5.088 | 5.2268 | 5.3652 | 5.4929 | 6.0562 | 6.62
South West | Seabank 132 kV | Stoke Bishop | Primary Substation | 11 | Holistic Transition | 0.34691 | 0.43036 | 0.52908 | 0.63192 | 0.74834 | 0.88644 | 1.0445 | 1.2692 | 1.4642 | 1.6702 | 1.8803 | 2.0995 | 2.3159 | 2.5136 | 2.6975 | 2.8097 | 3.1301 | 3.3793 | 0.78653 | 0.97226 | 1.1905 | 1.4167 | 1.6711 | 1.9706 | 2.3096 | 2.7856 | 3.2007 | 3.6365 | 4.0786 | 4.5385 | 4.9929 | 5.4078 | 5.7946 | 6.0376 | 6.7686 | 7.3474
South West | Seabank 132 kV | Stoke Bishop | Primary Substation | 11 | Hydrogen Evolution | 0.31446 | 0.37745 | 0.45473 | 0.53564 | 0.62731 | 0.73444 | 0.86655 | 1.0507 | 1.2139 | 1.391 | 1.5726 | 1.7562 | 1.9307 | 2.0968 | 2.2469 | 2.3301 | 2.5417 | 2.7224 | 0.70358 | 0.83822 | 1.0024 | 1.174 | 1.3677 | 1.5931 | 1.8697 | 2.2507 | 2.5909 | 2.9594 | 3.3356 | 3.7149 | 4.0759 | 4.4196 | 4.7309 | 4.9084 | 5.387 | 5.7982
South West | Seabank 132 kV | Weston-In-Gordano | Primary Substation | 11 | Counterfactual | 0.19953 | 0.22481 | 0.25719 | 0.29392 | 0.33852 | 0.39076 | 0.4492 | 0.53505 | 0.60646 | 0.68299 | 0.75809 | 0.83279 | 0.91306 | 0.9936 | 1.0718 | 1.1496 | 1.4173 | 1.5247 | 0.45657 | 0.50987 | 0.57873 | 0.65671 | 0.7513 | 0.86195 | 0.98591 | 1.1654 | 1.3161 | 1.4785 | 1.6363 | 1.7917 | 1.9574 | 2.1239 | 2.2851 | 2.4456 | 3.0081 | 3.2487
South West | Seabank 132 kV | Weston-In-Gordano | Primary Substation | 11 | Electric Engagement | 0.23306 | 0.29117 | 0.37458 | 0.47328 | 0.58205 | 0.70185 | 0.84052 | 1.0221 | 1.1757 | 1.3047 | 1.4181 | 1.4642 | 1.5086 | 1.5533 | 1.5972 | 1.6412 | 1.8399 | 1.9976 | 0.53111 | 0.65411 | 0.83343 | 1.0446 | 1.2762 | 1.5298 | 1.8212 | 2.1992 | 2.5208 | 2.7935 | 3.0352 | 3.1415 | 3.2443 | 3.3482 | 3.4498 | 3.5518 | 4.0102 | 4.3793
South West | Seabank 132 kV | Weston-In-Gordano | Primary Substation | 11 | Holistic Transition | 0.22603 | 0.26769 | 0.32953 | 0.40065 | 0.48376 | 0.57833 | 0.68818 | 0.83427 | 0.96277 | 1.0948 | 1.2226 | 1.3451 | 1.4639 | 1.5721 | 1.6723 | 1.7345 | 1.9367 | 2.0758 | 0.52096 | 0.61313 | 0.75214 | 0.91074 | 1.0955 | 1.3036 | 1.5451 | 1.8622 | 2.1421 | 2.428 | 2.7004 | 2.9611 | 3.2136 | 3.4424 | 3.6544 | 3.7907 | 4.2537 | 4.576
South West | Seabank 132 kV | Weston-In-Gordano | Primary Substation | 11 | Hydrogen Evolution | 0.2095 | 0.24202 | 0.28479 | 0.33898 | 0.40143 | 0.47637 | 0.56158 | 0.67691 | 0.78466 | 0.90093 | 1.0143 | 1.1233 | 1.2276 | 1.3268 | 1.4188 | 1.4702 | 1.626 | 1.7585 | 0.47884 | 0.54809 | 0.63946 | 0.75565 | 0.88942 | 1.0494 | 1.2304 | 1.4718 | 1.7008 | 1.9486 | 2.1866 | 2.4143 | 2.6319 | 2.8395 | 3.0323 | 3.1441 | 3.5028 | 3.8094
South West | Taunton 132 kV | Alcombe | Primary Substation | 11 | Counterfactual | 2.5983 | 2.6693 | 2.7575 | 2.8672 | 2.9926 | 3.1183 | 3.2723 | 3.5569 | 3.7987 | 4.0235 | 4.2491 | 4.4852 | 4.707 | 4.9034 | 5.0982 | 5.2917 | 5.9423 | 6.194 | 6.4659 | 6.6178 | 6.8039 | 7.0343 | 7.2973 | 7.5606 | 7.8831 | 8.4751 | 8.9819 | 9.4528 | 9.9251 | 10.4279 | 10.8854 | 11.2875 | 11.6865 | 12.0827 | 13.4319 | 13.9778
South West | Taunton 132 kV | Alcombe | Primary Substation | 11 | Electric Engagement | 2.6817 | 2.8427 | 3.0558 | 3.3042 | 3.5827 | 3.8793 | 4.224 | 4.7509 | 5.2772 | 5.6314 | 5.9381 | 6.0602 | 6.1703 | 6.2534 | 6.3361 | 6.4126 | 6.7642 | 7.0551 | 6.6508 | 6.9975 | 7.4497 | 7.9751 | 8.5624 | 9.1852 | 9.9046 | 11.0033 | 12.1389 | 12.8837 | 13.5325 | 13.806 | 14.0544 | 14.2438 | 14.4321 | 14.6076 | 15.4225 | 16.0996
South West | Taunton 132 kV | Alcombe | Primary Substation | 11 | Holistic Transition | 2.6631 | 2.7873 | 2.9432 | 3.1221 | 3.3239 | 3.5494 | 3.7976 | 4.2038 | 4.5771 | 4.9814 | 5.3283 | 5.646 | 5.95 | 6.2075 | 6.4479 | 6.5927 | 7.0097 | 7.3329 | 6.6228 | 6.9036 | 7.2478 | 7.6402 | 8.0814 | 8.5705 | 9.105 | 9.9727 | 10.7786 | 11.6633 | 12.3973 | 13.0682 | 13.7101 | 14.2513 | 14.7581 | 15.0732 | 16.0316 | 16.7829
South West | Taunton 132 kV | Alcombe | Primary Substation | 11 | Hydrogen Evolution | 2.6246 | 2.7159 | 2.841 | 2.9912 | 3.1645 | 3.3568 | 3.5775 | 3.9554 | 4.3462 | 4.702 | 5.0258 | 5.3205 | 5.6 | 5.8382 | 6.0603 | 6.1767 | 7.6199 | 7.8654 | 6.5243 | 6.722 | 6.9876 | 7.3066 | 7.6745 | 8.081 | 8.5447 | 9.3383 | 10.1827 | 10.9418 | 11.6172 | 12.2288 | 12.8081 | 13.2997 | 13.7593 | 14.007 | 17.5463 | 18.1033
South West | Taunton 132 kV | Bowhays Cross | Primary Substation | 11 | Counterfactual | 0.48703 | 0.56073 | 0.65939 | 0.77605 | 0.9245 | 1.0904 | 1.3506 | 1.6592 | 1.9371 | 2.2338 | 2.4927 | 2.788 | 3.0036 | 3.2008 | 3.3943 | 3.587 | 4.3406 | 4.7685 | 1.1943 | 1.3526 | 1.568 | 1.8213 | 2.1436 | 2.5049 | 3.0696 | 3.7347 | 4.3388 | 4.9908 | 5.5563 | 6.2189 | 6.6744 | 7.0886 | 7.494 | 7.8977 | 9.5197 | 10.4852
South West | Taunton 132 kV | Bowhays Cross | Primary Substation | 11 | Electric Engagement | 0.55109 | 0.70163 | 0.97031 | 1.2835 | 1.6519 | 2.0765 | 2.511 | 3.0472 | 3.7417 | 4.1928 | 4.5808 | 4.8092 | 5.0316 | 5.2366 | 5.4333 | 5.629 | 6.4624 | 7.0487 | 1.3361 | 1.664 | 2.2673 | 2.9647 | 3.7797 | 4.7115 | 5.6573 | 6.8116 | 8.3901 | 9.3764 | 10.2311 | 10.757 | 11.273 | 11.7513 | 12.2085 | 12.6659 | 14.611 | 16.0226
South West | Taunton 132 kV | Bowhays Cross | Primary Substation | 11 | Holistic Transition | 0.53625 | 0.66087 | 0.91049 | 1.1797 | 1.5115 | 1.9025 | 2.3191 | 2.8533 | 3.369 | 4.037 | 4.441 | 4.8037 | 5.1507 | 5.4321 | 5.699 | 5.8917 | 6.5929 | 6.9646 | 1.3134 | 1.5967 | 2.1755 | 2.7952 | 3.5573 | 4.4425 | 5.3892 | 6.5958 | 7.7705 | 9.3131 | 10.1993 | 10.993 | 11.7525 | 12.3597 | 12.9361 | 13.3641 | 14.9789 | 15.8476
South West | Taunton 132 kV | Bowhays Cross | Primary Substation | 11 | Hydrogen Evolution | 0.50769 | 0.60077 | 0.73611 | 0.9069 | 1.1368 | 1.4417 | 1.7557 | 2.1481 | 2.6734 | 3.1994 | 3.5626 | 3.8817 | 4.1763 | 4.4448 | 4.7001 | 4.8731 | 5.5165 | 6.021 | 1.24 | 1.4436 | 1.7394 | 2.114 | 2.619 | 3.2881 | 3.975 | 4.8226 | 6.0189 | 7.205 | 7.9918 | 8.6768 | 9.3059 | 9.882 | 10.4305 | 10.8144 | 12.3173 | 13.5124
South West | Taunton 132 kV | Culmhead | Primary Substation | 11 | Counterfactual | 0.17079 | 0.18661 | 0.20727 | 0.23022 | 0.25808 | 0.29737 | 0.34255 | 0.40291 | 0.4551 | 0.51431 | 0.5671 | 0.61129 | 0.65633 | 0.702 | 0.74772 | 0.79324 | 0.99499 | 1.1325 | 0.414 | 0.44915 | 0.4956 | 0.54719 | 0.61003 | 0.69724 | 0.79837 | 0.93138 | 1.0478 | 1.1817 | 1.2985 | 1.3935 | 1.4885 | 1.5849 | 1.6814 | 1.7774 | 2.2152 | 2.5244
South West | Taunton 132 kV | Culmhead | Primary Substation | 11 | Electric Engagement | 0.18505 | 0.22234 | 0.28627 | 0.35825 | 0.43334 | 0.52401 | 0.62391 | 0.74256 | 0.84993 | 0.9516 | 1.0509 | 1.1153 | 1.1788 | 1.2421 | 1.306 | 1.3708 | 1.6688 | 1.8515 | 0.44568 | 0.52924 | 0.67589 | 0.84027 | 1.0104 | 1.2111 | 1.4301 | 1.6859 | 1.9185 | 2.1406 | 2.359 | 2.5055 | 2.6509 | 2.7958 | 2.942 | 3.0897 | 3.7658 | 4.2035
South West | Taunton 132 kV | Culmhead | Primary Substation | 11 | Holistic Transition | 0.18198 | 0.21574 | 0.2767 | 0.34068 | 0.41426 | 0.50408 | 0.60477 | 0.73421 | 0.8484 | 0.96474 | 1.0639 | 1.1554 | 1.2444 | 1.3178 | 1.389 | 1.4461 | 1.6837 | 1.8044 | 0.44117 | 0.52041 | 0.66573 | 0.81721 | 0.9915 | 1.1981 | 1.4301 | 1.7266 | 1.987 | 2.25 | 2.4676 | 2.6683 | 2.8639 | 3.0224 | 3.1765 | 3.3023 | 3.8383 | 4.117
South West | Taunton 132 kV | Culmhead | Primary Substation | 11 | Hydrogen Evolution | 0.17528 | 0.19661 | 0.22409 | 0.2608 | 0.30246 | 0.36116 | 0.42607 | 0.50621 | 0.59057 | 0.68857 | 0.77201 | 0.84884 | 0.91992 | 0.98738 | 1.0527 | 1.1006 | 1.3083 | 1.4777 | 0.42401 | 0.47202 | 0.53355 | 0.6167 | 0.71101 | 0.8413 | 0.98495 | 1.1595 | 1.3468 | 1.5658 | 1.7475 | 1.9131 | 2.0654 | 2.2106 | 2.3513 | 2.4572 | 2.9371 | 3.3336
South West | Taunton 132 kV | Exebridge | Primary Substation | 11 | Counterfactual | 0.18784 | 0.21436 | 0.26986 | 0.3338 | 0.41224 | 0.53777 | 0.68338 | 0.8654 | 1.0297 | 1.2259 | 1.389 | 1.5135 | 1.6286 | 1.7511 | 1.8664 | 1.9824 | 2.6051 | 3.1301 | 0.44943 | 0.50818 | 0.63841 | 0.78809 | 0.9724 | 1.2585 | 1.5952 | 2.0121 | 2.3922 | 2.8535 | 3.2282 | 3.5067 | 3.7577 | 4.0267 | 4.2775 | 4.5294 | 5.9274 | 7.1332
South West | Taunton 132 kV | Exebridge | Primary Substation | 11 | Electric Engagement | 0.21136 | 0.27179 | 0.47519 | 0.68897 | 0.90726 | 1.1814 | 1.4735 | 1.8172 | 2.1455 | 2.477 | 2.8198 | 3.0862 | 3.3562 | 3.6364 | 3.9117 | 4.1896 | 5.4622 | 6.2323 | 0.50144 | 0.63672 | 1.1217 | 1.6284 | 2.1431 | 2.7673 | 3.4278 | 4.1986 | 4.9379 | 5.689 | 6.4683 | 7.0858 | 7.7138 | 8.3669 | 9.0058 | 9.6512 | 12.5672 | 14.4314
South West | Taunton 132 kV | Exebridge | Primary Substation | 11 | Holistic Transition | 0.20589 | 0.26055 | 0.47171 | 0.6876 | 0.94294 | 1.2554 | 1.6352 | 2.1231 | 2.5571 | 2.9917 | 3.3208 | 3.6143 | 3.8983 | 4.1178 | 4.3289 | 4.5138 | 5.4317 | 5.7881 | 0.49303 | 0.6213 | 1.1362 | 1.6608 | 2.2819 | 3.0168 | 3.9185 | 5.0764 | 6.1023 | 7.1226 | 7.8729 | 8.5402 | 9.1856 | 9.6715 | 10.1372 | 10.5511 | 12.6272 | 13.4476
South West | Taunton 132 kV | Exebridge | Primary Substation | 11 | Hydrogen Evolution | 0.19585 | 0.23066 | 0.3022 | 0.39706 | 0.51114 | 0.69064 | 0.88556 | 1.1149 | 1.4041 | 1.7503 | 2.0139 | 2.244 | 2.4538 | 2.6677 | 2.8751 | 3.055 | 3.963 | 4.6924 | 0.46709 | 0.54538 | 0.71119 | 0.93266 | 1.1997 | 1.6077 | 2.0523 | 2.5695 | 3.2389 | 4.0465 | 4.6459 | 5.1619 | 5.628 | 6.1077 | 6.5712 | 6.9808 | 9.1046 | 10.8363
South West | Taunton 132 kV | Holford | Primary Substation | 11 | Counterfactual | 0.045642 | 0.053914 | 0.068778 | 0.086408 | 0.10779 | 0.14123 | 0.17995 | 0.22913 | 0.27306 | 0.32508 | 0.36883 | 0.40245 | 0.4345 | 0.46758 | 0.49939 | 0.53121 | 0.69448 | 0.82799 | 0.11087 | 0.12924 | 0.16398 | 0.20491 | 0.25479 | 0.33066 | 0.41981 | 0.53171 | 0.63272 | 0.75434 | 0.85424 | 0.92895 | 0.9984 | 1.0704 | 1.1391 | 1.2078 | 1.5726 | 1.8787
South West | Taunton 132 kV | Holford | Primary Substation | 11 | Electric Engagement | 0.053001 | 0.071849 | 0.12628 | 0.18357 | 0.24231 | 0.31545 | 0.39368 | 0.48598 | 0.57285 | 0.65943 | 0.74784 | 0.81521 | 0.88329 | 0.95316 | 1.0221 | 1.0915 | 1.4089 | 1.6034 | 0.12713 | 0.16949 | 0.29842 | 0.43328 | 0.57076 | 0.7365 | 0.91245 | 1.1179 | 1.3123 | 1.5075 | 1.7076 | 1.8635 | 2.0215 | 2.184 | 2.3438 | 2.5046 | 3.2317 | 3.7021
South West | Taunton 132 kV | Holford | Primary Substation | 11 | Holistic Transition | 0.051106 | 0.068049 | 0.1236 | 0.1805 | 0.24743 | 0.32904 | 0.42643 | 0.55179 | 0.66287 | 0.77393 | 0.85931 | 0.93597 | 1.0107 | 1.069 | 1.1249 | 1.1727 | 1.4031 | 1.4938 | 0.1241 | 0.16403 | 0.299 | 0.43676 | 0.59903 | 0.79056 | 1.021 | 1.3172 | 1.5786 | 1.8383 | 2.0319 | 2.2054 | 2.3745 | 2.5031 | 2.6261 | 2.7329 | 3.2543 | 3.4643
South West | Taunton 132 kV | Holford | Primary Substation | 11 | Hydrogen Evolution | 0.048146 | 0.058821 | 0.078866 | 0.10448 | 0.1353 | 0.183 | 0.23487 | 0.29685 | 0.3714 | 0.46066 | 0.52998 | 0.59158 | 0.64729 | 0.7042 | 0.75889 | 0.80535 | 1.0321 | 1.2129 | 0.11635 | 0.14044 | 0.18655 | 0.24602 | 0.31771 | 0.42572 | 0.54345 | 0.68245 | 0.85422 | 1.0614 | 1.2181 | 1.3553 | 1.4784 | 1.6049 | 1.7263 | 1.8315 | 2.3614 | 2.7913
South West | Taunton 132 kV | Luckwell Bridge | Primary Substation | 11 | Counterfactual | 0.086256 | 0.11348 | 0.15094 | 0.19524 | 0.24848 | 0.33419 | 0.43178 | 0.55414 | 0.66376 | 0.79214 | 0.90139 | 0.98353 | 1.061 | 1.1395 | 1.2175 | 1.2961 | 1.6999 | 2.0397 | 0.20876 | 0.27132 | 0.35941 | 0.46275 | 0.58733 | 0.78143 | 1.0056 | 1.2838 | 1.5356 | 1.8354 | 2.0846 | 2.2665 | 2.4338 | 2.6031 | 2.7716 | 2.941 | 3.8389 | 4.6103
South West | Taunton 132 kV | Luckwell Bridge | Primary Substation | 11 | Electric Engagement | 0.10245 | 0.16544 | 0.30054 | 0.4423 | 0.58723 | 0.77252 | 0.97029 | 1.1943 | 1.4063 | 1.6186 | 1.8372 | 2.0051 | 2.172 | 2.3398 | 2.5098 | 2.6793 | 3.4813 | 3.9555 | 0.24442 | 0.39118 | 0.71209 | 1.0468 | 1.3872 | 1.8068 | 2.2516 | 2.7485 | 3.2209 | 3.6966 | 4.188 | 4.5722 | 4.9551 | 5.3399 | 5.7292 | 6.1172 | 7.9335 | 9.0758
South West | Taunton 132 kV | Luckwell Bridge | Primary Substation | 11 | Holistic Transition | 0.098165 | 0.16313 | 0.30339 | 0.44679 | 0.61387 | 0.82108 | 1.0541 | 1.3501 | 1.6118 | 1.8733 | 2.0764 | 2.2618 | 2.4429 | 2.5864 | 2.7284 | 2.8528 | 3.4571 | 3.7148 | 0.23752 | 0.39453 | 0.73586 | 1.0836 | 1.4891 | 1.9745 | 2.5232 | 3.2193 | 3.8315 | 4.439 | 4.896 | 5.3132 | 5.7207 | 6.0354 | 6.3472 | 6.6236 | 7.9796 | 8.5761
South West | Taunton 132 kV | Luckwell Bridge | Primary Substation | 11 | Hydrogen Evolution | 0.091741 | 0.12808 | 0.17957 | 0.24484 | 0.322 | 0.44441 | 0.57606 | 0.73193 | 0.91146 | 1.124 | 1.2916 | 1.4417 | 1.5781 | 1.7111 | 1.8429 | 1.9548 | 2.5129 | 2.9517 | 0.22077 | 0.30569 | 0.42471 | 0.5767 | 0.75661 | 1.033 | 1.3314 | 1.6806 | 2.0917 | 2.5823 | 2.9591 | 3.2915 | 3.5908 | 3.8835 | 4.1737 | 4.4239 | 5.7144 | 6.7491
South West | Taunton 132 kV | Lydeard St Lawrence Primary | Primary Substation | 11 | Counterfactual | 0.4732 | 0.50136 | 0.54721 | 0.59922 | 0.66257 | 0.75921 | 0.87215 | 1.0158 | 1.1447 | 1.2982 | 1.4264 | 1.5255 | 1.6185 | 1.7161 | 1.8091 | 1.9024 | 2.389 | 2.7851 | 1.1672 | 1.2292 | 1.336 | 1.457 | 1.6049 | 1.8252 | 2.086 | 2.4139 | 2.711 | 3.0706 | 3.3641 | 3.5847 | 3.7867 | 3.9998 | 4.2013 | 4.4031 | 5.4921 | 6.4021
South West | Taunton 132 kV | Lydeard St Lawrence Primary | Primary Substation | 11 | Electric Engagement | 0.49501 | 0.55559 | 0.71707 | 0.88746 | 1.0625 | 1.2767 | 1.5072 | 1.7798 | 2.038 | 2.2957 | 2.5586 | 2.7571 | 2.9845 | 3.19 | 3.3921 | 3.6452 | 4.5655 | 5.143 | 1.2155 | 1.351 | 1.7339 | 2.1354 | 2.5453 | 3.032 | 3.5514 | 4.1598 | 4.7385 | 5.32 | 5.9164 | 6.3769 | 6.9111 | 7.3909 | 7.8611 | 8.4595 | 10.5791 | 11.9788
South West | Taunton 132 kV | Lydeard St Lawrence Primary | Primary Substation | 11 | Holistic Transition | 0.49027 | 0.54565 | 0.71149 | 0.88206 | 1.0827 | 1.3239 | 1.6147 | 2.0426 | 2.3754 | 2.7089 | 3.0662 | 3.296 | 3.5183 | 3.6893 | 3.8532 | 3.9931 | 4.6612 | 4.9354 | 1.2084 | 1.3377 | 1.7408 | 2.1538 | 2.64 | 3.2072 | 3.8961 | 4.9155 | 5.6995 | 6.4799 | 7.3145 | 7.835 | 8.3388 | 8.7169 | 9.0786 | 9.3925 | 10.9133 | 11.5482
South West | Taunton 132 kV | Lydeard St Lawrence Primary | Primary Substation | 11 | Hydrogen Evolution | 0.4802 | 0.51708 | 0.57589 | 0.65287 | 0.74447 | 0.88386 | 1.0371 | 1.22 | 1.4439 | 1.7121 | 1.9194 | 2.1019 | 2.2942 | 2.4602 | 2.6198 | 2.804 | 3.465 | 4.003 | 1.1826 | 1.2653 | 1.4009 | 1.5797 | 1.7931 | 2.1095 | 2.4582 | 2.8689 | 3.3853 | 4.0082 | 4.4768 | 4.884 | 5.3176 | 5.688 | 6.0438 | 6.4749 | 8.0279 | 9.3088
South West | Taunton 132 kV | Periton | Primary Substation | 11 | Counterfactual | 0.051295 | 0.076515 | 0.099372 | 0.12527 | 0.15563 | 0.19851 | 0.24702 | 0.32081 | 0.38505 | 0.45278 | 0.51458 | 0.56343 | 0.61395 | 0.66543 | 0.71651 | 0.7675 | 0.98476 | 1.1275 | 0.12319 | 0.17841 | 0.22964 | 0.28751 | 0.3555 | 0.45019 | 0.55832 | 0.71956 | 0.86148 | 1.0136 | 1.1495 | 1.2542 | 1.3605 | 1.4689 | 1.5764 | 1.6837 | 2.1546 | 2.4763
South West | Taunton 132 kV | Periton | Primary Substation | 11 | Electric Engagement | 0.067351 | 0.11774 | 0.1887 | 0.26447 | 0.34405 | 0.43977 | 0.54565 | 0.68334 | 0.8075 | 0.91877 | 1.0267 | 1.0929 | 1.1581 | 1.2242 | 1.2909 | 1.3571 | 1.6677 | 1.8636 | 0.15879 | 0.27129 | 0.43333 | 0.60518 | 0.78435 | 0.99524 | 1.2265 | 1.5232 | 1.7925 | 2.036 | 2.2738 | 2.425 | 2.5749 | 2.7265 | 2.8794 | 3.031 | 3.7374 | 4.2065
South West | Taunton 132 kV | Periton | Primary Substation | 11 | Holistic Transition | 0.063661 | 0.11025 | 0.17546 | 0.24246 | 0.31958 | 0.413 | 0.518 | 0.66429 | 0.7938 | 0.91977 | 1.0279 | 1.125 | 1.2205 | 1.3015 | 1.3795 | 1.4389 | 1.6919 | 1.8187 | 0.15318 | 0.26126 | 0.41594 | 0.57425 | 0.75644 | 0.97109 | 1.2128 | 1.5465 | 1.8413 | 2.1262 | 2.3639 | 2.5771 | 2.7869 | 2.9616 | 3.1302 | 3.2616 | 3.8328 | 4.1274
South West | Taunton 132 kV | Periton | Primary Substation | 11 | Hydrogen Evolution | 0.056507 | 0.089243 | 0.1209 | 0.15824 | 0.20161 | 0.26299 | 0.33085 | 0.42664 | 0.52571 | 0.63303 | 0.72626 | 0.80865 | 0.88568 | 0.96017 | 1.0323 | 1.0841 | 1.3062 | 1.4848 | 0.13474 | 0.20784 | 0.27823 | 0.36193 | 0.45918 | 0.59453 | 0.74406 | 0.95216 | 1.1719 | 1.4117 | 1.6149 | 1.7923 | 1.9571 | 2.1169 | 2.2721 | 2.3865 | 2.8986 | 3.3169
South West | Taunton 132 kV | Priorswood | Primary Substation | 11 | Counterfactual | 0.31143 | 0.3746 | 0.45175 | 0.54133 | 0.62371 | 0.73537 | 0.95008 | 1.1774 | 1.3566 | 1.5438 | 1.7173 | 1.8936 | 2.0664 | 2.2396 | 2.4108 | 2.5812 | 3.1992 | 3.4371 | 0.73295 | 0.86698 | 1.031 | 1.2209 | 1.3963 | 1.6337 | 2.0896 | 2.5689 | 2.9508 | 3.3515 | 3.718 | 4.086 | 4.4427 | 4.8006 | 5.1544 | 5.5064 | 6.8055 | 7.3298
South West | Taunton 132 kV | Priorswood | Primary Substation | 11 | Electric Engagement | 0.37553 | 0.51537 | 0.71696 | 0.92955 | 1.1912 | 1.4806 | 1.8339 | 2.2356 | 2.5465 | 2.8303 | 3.0841 | 3.2212 | 3.3292 | 3.4417 | 3.5531 | 3.6606 | 4.157 | 4.4741 | 0.87515 | 1.1749 | 1.6094 | 2.0668 | 2.6299 | 3.2521 | 4.0108 | 4.8565 | 5.5088 | 6.1107 | 6.652 | 6.9603 | 7.206 | 7.4618 | 7.7148 | 7.9599 | 9.0913 | 9.8306
South West | Taunton 132 kV | Priorswood | Primary Substation | 11 | Holistic Transition | 0.36131 | 0.47173 | 0.61846 | 0.82375 | 1.0091 | 1.2467 | 1.5329 | 1.862 | 2.1236 | 2.4094 | 2.689 | 2.9757 | 3.2334 | 3.4696 | 3.6928 | 3.8413 | 4.3497 | 4.6312 | 0.85385 | 1.1001 | 1.4296 | 1.8855 | 2.3008 | 2.8288 | 3.4622 | 4.1812 | 4.7516 | 5.3703 | 5.9667 | 6.578 | 7.1259 | 7.626 | 8.0995 | 8.4234 | 9.5731 | 10.2228
South West | Taunton 132 kV | Priorswood | Primary Substation | 11 | Hydrogen Evolution | 0.33185 | 0.41965 | 0.54201 | 0.69377 | 0.84173 | 1.0388 | 1.2867 | 1.5753 | 1.8061 | 2.0709 | 2.325 | 2.584 | 2.8063 | 3.025 | 3.2311 | 3.3569 | 3.7632 | 4.0287 | 0.77821 | 0.96722 | 1.2293 | 1.556 | 1.8762 | 2.3042 | 2.8424 | 3.4575 | 3.9474 | 4.5121 | 5.0463 | 5.5901 | 6.0538 | 6.5118 | 6.9444 | 7.2162 | 8.136 | 8.7457
South West | Taunton 132 kV | Staplegrove | Primary Substation | 11 | Counterfactual | 0.77149 | 0.85295 | 0.95669 | 1.0967 | 1.2592 | 1.437 | 1.7905 | 2.1498 | 2.4949 | 2.812 | 3.1019 | 3.324 | 3.5726 | 3.828 | 4.0776 | 4.3297 | 5.1455 | 5.4717 | 1.8158 | 1.9884 | 2.2086 | 2.5046 | 2.8497 | 3.2279 | 3.9777 | 4.7333 | 5.4659 | 6.1414 | 6.7532 | 7.2144 | 7.7275 | 8.2549 | 8.7703 | 9.2905 | 11.0002 | 11.7215
South West | Taunton 132 kV | Staplegrove | Primary Substation | 11 | Electric Engagement | 0.86797 | 1.0485 | 1.3266 | 1.664 | 2.1665 | 2.6208 | 3.1215 | 3.7487 | 4.3306 | 4.79 | 5.1628 | 5.3126 | 5.4618 | 5.6166 | 5.8481 | 5.9915 | 6.5626 | 7.0224 | 2.03 | 2.4151 | 3.0126 | 3.7411 | 4.8267 | 5.802 | 6.8682 | 8.1857 | 9.4186 | 10.3952 | 11.1908 | 11.5305 | 11.8711 | 12.2248 | 12.7702 | 13.0997 | 14.4219 | 15.4915
South West | Taunton 132 kV | Staplegrove | Primary Substation | 11 | Holistic Transition | 0.84717 | 0.9825 | 1.1874 | 1.5384 | 1.8734 | 2.2472 | 2.6572 | 3.1758 | 3.6811 | 4.2974 | 4.7164 | 5.0927 | 5.4637 | 5.8067 | 6.1295 | 6.3404 | 6.9394 | 7.3551 | 1.9993 | 2.3015 | 2.7627 | 3.5395 | 4.2842 | 5.1105 | 6.0131 | 7.1421 | 8.2434 | 9.6306 | 10.5236 | 11.3227 | 12.1113 | 12.8376 | 13.5224 | 13.9829 | 15.3542 | 16.3115
South West | Taunton 132 kV | Staplegrove | Primary Substation | 11 | Hydrogen Evolution | 0.80193 | 0.9056 | 1.0676 | 1.3529 | 1.6435 | 1.9693 | 2.3252 | 2.7774 | 3.2411 | 3.6763 | 4.059 | 4.3934 | 4.7225 | 5.0399 | 5.4173 | 5.5925 | 6.0585 | 6.4281 | 1.8834 | 2.1055 | 2.4515 | 3.0694 | 3.7006 | 4.4069 | 5.1724 | 6.1309 | 7.1235 | 8.0523 | 8.8562 | 9.554 | 10.2395 | 10.9042 | 11.7273 | 12.1065 | 13.1725 | 14.024
South West | Taunton 132 kV | Taunton Local | Primary Substation | 11 | Counterfactual | 0.29374 | 0.3951 | 0.50024 | 0.60907 | 0.74456 | 0.89807 | 1.1833 | 1.539 | 1.8503 | 2.1666 | 2.4414 | 2.715 | 2.9761 | 3.2221 | 3.4662 | 3.7084 | 4.5041 | 4.802 | 0.65153 | 0.8666 | 1.0866 | 1.3139 | 1.5966 | 1.9167 | 2.5133 | 3.2506 | 3.9007 | 4.5614 | 5.1315 | 5.6973 | 6.2321 | 6.7344 | 7.2331 | 7.7279 | 9.369 | 10.008
South West | Taunton 132 kV | Taunton Local | Primary Substation | 11 | Electric Engagement | 0.39694 | 0.61048 | 0.85914 | 1.1644 | 1.5961 | 1.9797 | 2.4223 | 3.0448 | 3.5919 | 4.0528 | 4.424 | 4.5944 | 4.7021 | 4.8082 | 4.9096 | 5.0062 | 5.4419 | 5.8504 | 0.8803 | 1.3377 | 1.8596 | 2.502 | 3.4172 | 4.2236 | 5.1467 | 6.4383 | 7.5801 | 8.5485 | 9.3266 | 9.702 | 9.9407 | 10.1763 | 10.4025 | 10.6182 | 11.6011 | 12.5156
South West | Taunton 132 kV | Taunton Local | Primary Substation | 11 | Holistic Transition | 0.3741 | 0.53984 | 0.74332 | 0.97319 | 1.2594 | 1.5313 | 1.8436 | 2.3064 | 2.7343 | 3.1735 | 3.5997 | 4.0151 | 4.3649 | 4.6935 | 4.9992 | 5.1891 | 5.7396 | 6.1941 | 0.84613 | 1.2167 | 1.6605 | 2.1613 | 2.7825 | 3.3693 | 4.0374 | 5.0172 | 5.927 | 6.8581 | 7.7531 | 8.6267 | 9.357 | 10.0439 | 10.6845 | 11.093 | 12.3316 | 13.3636
South West | Taunton 132 kV | Taunton Local | Primary Substation | 11 | Hydrogen Evolution | 0.32668 | 0.45576 | 0.60651 | 0.81174 | 1.0784 | 1.344 | 1.6466 | 2.106 | 2.5234 | 2.9533 | 3.3458 | 3.7302 | 4.0466 | 4.3481 | 4.6249 | 4.7787 | 5.152 | 5.4748 | 0.72449 | 1.002 | 1.3188 | 1.7547 | 2.3237 | 2.887 | 3.5244 | 4.4852 | 5.361 | 6.2613 | 7.0741 | 7.8703 | 8.519 | 9.1381 | 9.7077 | 10.0308 | 10.8515 | 11.5622
South West | Taunton 132 kV | Trull | Primary Substation | 11 | Counterfactual | 1.2728 | 1.4283 | 1.5883 | 1.7661 | 1.9749 | 2.1861 | 2.4319 | 2.8018 | 3.1512 | 3.521 | 3.8678 | 4.2168 | 4.5778 | 4.8849 | 5.1898 | 5.4898 | 6.3069 | 6.5988 | 2.8582 | 3.1845 | 3.5218 | 3.8954 | 4.3334 | 4.7771 | 5.2916 | 6.0604 | 6.7897 | 7.5632 | 8.2848 | 9.0071 | 9.7503 | 10.3775 | 11.0001 | 11.6126 | 13.3151 | 13.9614
South West | Taunton 132 kV | Trull | Primary Substation | 11 | Electric Engagement | 1.3852 | 1.664 | 2.0023 | 2.376 | 2.7941 | 3.2262 | 3.727 | 4.4041 | 5.0187 | 5.5553 | 6.0216 | 6.2792 | 6.5167 | 6.6909 | 6.8637 | 7.0575 | 7.5684 | 8.0121 | 3.1089 | 3.7036 | 4.4294 | 5.2269 | 6.1146 | 7.0277 | 8.0767 | 9.4864 | 10.7709 | 11.8989 | 12.8824 | 13.4475 | 13.9704 | 14.3539 | 14.734 | 15.167 | 16.3445 | 17.369
South West | Taunton 132 kV | Trull | Primary Substation | 11 | Holistic Transition | 1.3622 | 1.5892 | 1.8557 | 2.1427 | 2.4638 | 2.8065 | 3.1921 | 3.7276 | 4.2376 | 4.7653 | 5.3304 | 5.8414 | 6.3304 | 6.725 | 7.0932 | 7.3383 | 7.9033 | 8.3233 | 3.0754 | 3.5746 | 4.1656 | 4.7973 | 5.5017 | 6.2486 | 7.0824 | 8.2298 | 9.3217 | 10.4468 | 11.6575 | 12.7363 | 13.7678 | 14.5916 | 15.3617 | 15.8851 | 17.1773 | 18.1469
South West | Taunton 132 kV | Trull | Primary Substation | 11 | Hydrogen Evolution | 1.3095 | 1.5024 | 1.7221 | 1.9651 | 2.2405 | 2.5338 | 2.8703 | 3.3482 | 3.8279 | 4.3281 | 4.8071 | 5.2805 | 5.7282 | 6.0924 | 6.4351 | 6.665 | 7.0764 | 7.4238 | 2.9407 | 3.3541 | 3.8254 | 4.346 | 4.9343 | 5.5589 | 6.2688 | 7.2701 | 8.28 | 9.3335 | 10.3319 | 11.318 | 12.2484 | 12.9992 | 13.7065 | 14.1994 | 15.1351 | 15.9296
South West | Taunton 132 kV | Wellington Primary | Primary Substation | 11 | Counterfactual | 0.09563 | 0.11503 | 0.14259 | 0.17396 | 0.21114 | 0.25807 | 0.31312 | 0.40959 | 0.51558 | 0.63325 | 0.76484 | 0.84856 | 0.90989 | 0.97254 | 1.0333 | 1.0944 | 1.3569 | 1.5242 | 0.22845 | 0.27041 | 0.33185 | 0.40165 | 0.48463 | 0.5891 | 0.71252 | 0.92317 | 1.1553 | 1.4158 | 1.7024 | 1.8823 | 2.0116 | 2.1441 | 2.2721 | 2.4008 | 2.9717 | 3.3517
South West | Taunton 132 kV | Wellington Primary | Primary Substation | 11 | Electric Engagement | 0.11642 | 0.15994 | 0.24516 | 0.33783 | 0.43547 | 0.54411 | 0.66532 | 0.84161 | 1.0252 | 1.1988 | 1.3916 | 1.4936 | 1.5661 | 1.6398 | 1.7118 | 1.782 | 2.0916 | 2.3203 | 0.27457 | 0.36951 | 0.56335 | 0.77281 | 0.9919 | 1.2323 | 1.498 | 1.88 | 2.2812 | 2.6637 | 3.091 | 3.3252 | 3.4953 | 3.669 | 3.8384 | 4.0042 | 4.7341 | 5.2871
South West | Taunton 132 kV | Wellington Primary | Primary Substation | 11 | Holistic Transition | 0.11189 | 0.14739 | 0.22567 | 0.30667 | 0.40039 | 0.50745 | 0.63402 | 0.8262 | 1.022 | 1.22 | 1.4188 | 1.564 | 1.6769 | 1.7698 | 1.8582 | 1.9222 | 2.1751 | 2.3099 | 0.26773 | 0.3491 | 0.53412 | 0.7247 | 0.94523 | 1.1925 | 1.486 | 1.9256 | 2.3709 | 2.819 | 3.2584 | 3.5791 | 3.8288 | 4.0308 | 4.223 | 4.3662 | 4.9532 | 5.2678
South West | Taunton 132 kV | Wellington Primary | Primary Substation | 11 | Hydrogen Evolution | 0.10257 | 0.12762 | 0.16549 | 0.21227 | 0.26674 | 0.33607 | 0.41556 | 0.54305 | 0.70492 | 0.88309 | 1.0669 | 1.1954 | 1.2877 | 1.3773 | 1.4623 | 1.5209 | 1.7637 | 1.9687 | 0.24382 | 0.2987 | 0.38237 | 0.48673 | 0.6083 | 0.76207 | 0.93774 | 1.2152 | 1.5742 | 1.9718 | 2.3747 | 2.6538 | 2.8524 | 3.0468 | 3.2313 | 3.3633 | 3.9376 | 4.4255
South West | Taunton 132 kV | Wellington Town | Primary Substation | 11 | Counterfactual | 0.70163 | 0.79124 | 0.91559 | 1.0467 | 1.2007 | 1.3847 | 1.593 | 1.8833 | 2.135 | 2.3788 | 2.2014 | 2.403 | 2.6266 | 2.8533 | 3.0754 | 3.2991 | 4.1114 | 4.5098 | 1.7101 | 1.9015 | 2.1674 | 2.4474 | 2.7787 | 3.1748 | 3.6248 | 4.243 | 4.7872 | 5.3193 | 4.7961 | 5.2166 | 5.6786 | 6.1478 | 6.607 | 7.0692 | 8.7881 | 9.6729
South West | Taunton 132 kV | Wellington Town | Primary Substation | 11 | Electric Engagement | 0.78974 | 0.97766 | 1.2726 | 1.6117 | 1.9857 | 2.4068 | 2.8849 | 3.4718 | 3.9425 | 4.3082 | 4.2389 | 4.3896 | 4.5412 | 4.699 | 4.8542 | 5.0012 | 5.6767 | 6.1791 | 1.9054 | 2.311 | 2.9537 | 3.6978 | 4.5166 | 5.4344 | 6.4702 | 7.7217 | 8.7206 | 9.501 | 9.2159 | 9.5631 | 9.9144 | 10.2806 | 10.6398 | 10.9829 | 12.5618 | 13.757
South West | Taunton 132 kV | Wellington Town | Primary Substation | 11 | Holistic Transition | 0.77035 | 0.92042 | 1.1765 | 1.4431 | 1.747 | 2.1104 | 2.5178 | 3.0312 | 3.4564 | 3.8442 | 3.8128 | 4.1606 | 4.5018 | 4.8084 | 5.1006 | 5.2924 | 5.945 | 6.3644 | 1.8763 | 2.215 | 2.7976 | 3.4039 | 4.0958 | 4.9148 | 5.8338 | 6.976 | 7.9182 | 8.769 | 8.5631 | 9.3101 | 10.0434 | 10.6969 | 11.3202 | 11.7426 | 13.2453 | 14.2172
South West | Taunton 132 kV | Wellington Town | Primary Substation | 11 | Hydrogen Evolution | 0.72943 | 0.84254 | 1.0128 | 1.2208 | 1.4609 | 1.7525 | 2.0836 | 2.5123 | 2.889 | 3.2464 | 3.1826 | 3.4964 | 3.8009 | 4.0915 | 4.3683 | 4.5295 | 5.0628 | 5.5108 | 1.7718 | 2.017 | 2.3835 | 2.8403 | 3.369 | 4.0109 | 4.7363 | 5.6628 | 6.4724 | 7.2407 | 6.9521 | 7.6109 | 8.2486 | 8.8607 | 9.4445 | 9.7972 | 11.0352 | 12.0779
South West | Taunton 132 kV | Wiveliscombe | Primary Substation | 11 | Counterfactual | 0.89676 | 0.92988 | 0.99437 | 1.0823 | 1.1723 | 1.2997 | 1.4673 | 1.6725 | 1.8509 | 2.0599 | 2.2316 | 2.3621 | 2.4876 | 2.6191 | 2.7442 | 2.8698 | 3.4918 | 3.9825 | 2.2234 | 2.2962 | 2.4436 | 2.6416 | 2.8481 | 3.1351 | 3.5144 | 3.9752 | 4.3805 | 4.8628 | 5.2509 | 5.5389 | 5.8093 | 6.0939 | 6.3627 | 6.6325 | 8.0151 | 9.137
South West | Taunton 132 kV | Wiveliscombe | Primary Substation | 11 | Electric Engagement | 0.92785 | 1.0031 | 1.2116 | 1.4547 | 1.6985 | 1.9791 | 2.301 | 2.6797 | 3.0313 | 3.381 | 3.7269 | 3.9765 | 4.231 | 4.4951 | 4.7952 | 5.0574 | 6.2715 | 6.983 | 2.2924 | 2.4592 | 2.9484 | 3.5127 | 4.0768 | 4.7084 | 5.4265 | 6.2634 | 7.044 | 7.8261 | 8.6036 | 9.1786 | 9.7666 | 10.3777 | 11.0771 | 11.6816 | 14.4449 | 16.1598
South West | Taunton 132 kV | Wiveliscombe | Primary Substation | 11 | Holistic Transition | 0.9211 | 0.9869 | 1.198 | 1.4342 | 1.7011 | 2.0065 | 2.3918 | 2.8805 | 3.3121 | 3.8267 | 4.1628 | 4.4579 | 4.7457 | 4.9743 | 5.1938 | 5.3807 | 6.2741 | 6.6355 | 2.2824 | 2.4354 | 2.9445 | 3.5074 | 4.1466 | 4.8588 | 5.762 | 6.9069 | 7.9146 | 9.1226 | 9.8796 | 10.5433 | 11.1901 | 11.6914 | 12.1716 | 12.5871 | 14.598 | 15.4273
South West | Taunton 132 kV | Wiveliscombe | Primary Substation | 11 | Hydrogen Evolution | 0.90659 | 0.94991 | 1.0324 | 1.1595 | 1.2985 | 1.4813 | 1.6993 | 1.9555 | 2.2529 | 2.6043 | 2.8742 | 3.1086 | 3.3251 | 3.5445 | 3.7958 | 3.9712 | 4.8169 | 5.4963 | 2.2453 | 2.3417 | 2.5295 | 2.8195 | 3.1389 | 3.5505 | 4.0414 | 4.6117 | 5.291 | 6.0997 | 6.7056 | 7.2247 | 7.7002 | 8.1858 | 8.7525 | 9.1482 | 11.1158 | 12.7192