## Introduction
Data Dictionary
Column Heading | Description
Associated GSP | Name of the upstream Grid Supply Point (GSP) which supplies the substation. Note that some GSPs which run in parallel are reported as groups.
Substation | Name of the substation for which the generation and demand headroom figures have been calculated.
Supply Level | Identifier for whether the substation is a Primary or a Bulk Supply Point. The definition is supplied in the 'NDP 2026 Introduction & Methodology Report'.
Voltage Level (kV) | Voltage of the lower voltage side of the transformation at the substation.
Scenario | Identifier for one of the four Distribution Future Energy Scenarios (DFES) the headroom figures refer to. Holistic Transition was chosen as the best view scenario for the NDP 2026.
Units | The units used to define the headroom available at each substation under each scenario and all of the years reported on (see below).
2024 | Defines the year snapshot for the headroom calculation, where the year refers to the end of the fiscal year.
2025
2026
2027
2028
2029
2030
2031
2032
2033
2034
2035
2036
2037
2038
2039
2040
2045
2050
West Midlands
Network Headroom Report 2026
May 2026
v1.0
How to use this workbook
The 'Demand Headroom' and 'Generation Headroom' sheets contain data as described by the data dictionary below. Cells highlighted in red indicate zero headroom, which is defined as the point at which adding demand or generation at a given substation would cause a thermal overload to occur on an related asset in the network. The impact of some high-certainty medium-term reinforcement schemes on the network has been included from the year 2030. This may be observed as a step change increase in the available headroom from the year 2030.
The 'Fault Level Contribution' sheet contains the total make and break contribution (kA) from the demand and generation expected to connect at each primary substation for each year and scenario under the DFES forecasts. The existing maximum prospective fault levels under normal system running conditions and the make and break switchgear ratings at bussing points can be taken from the LTDS Table 4.
In the context of the NHR, zero headroom does not necessarily mean a prospective customer would not be able to connect. This data should not be used to make connections decisions as it is intended to provide a view of the capacity of the network against the DFES scenarios rather than a view of the contractually available capacity. Prospective customers should follow the regular connections application process to gain an accurate assessment of the headroom available for their connection.
Summary
This Network Headroom Report (NHR) workbook provides a view of the capacity to connect additional demand and generation to NGED's West Midlands network, in line with the load growth forecasted across the four Distribution Future Energy Scenarios (DFES) out to 2050. The DFES 2024 publication was used as the basis for this NHR to align with the forecasts used for the Network Development Reports.
The NHR forms one part of the wider Network Development Plan (NDP), and it is recommended to view this report alongside the NDP Introduction & Methodology Report and the Network Development Reports which are presented as an interactive map on the Network Opportunity and Development Map (NODM).

## Demand Headroom
Associated GSP | Substation | Supply Level | Voltage Level (kV) | Scenario | Units | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050
Bishops Wood 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.6 | 3.6 | 3.5 | 3.3 | 3.1 | 2.8 | 2.3 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.6 | 3.6 | 3.3 | 2.7 | 2.3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.6 | 3.6 | 3.5 | 3.2 | 2.9 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.6 | 3.6 | 3.4 | 3 | 2.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | BODENHAM 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6 | 5.9 | 5.9 | 5.8 | 5.7 | 4.6 | 5.6 | 5.5 | 5.4 | 5.3 | 5.1 | 4.9 | 4.7 | 4.4 | 4.2 | 4 | 3.8 | 2.3 | 0
Bishops Wood 132kV | BODENHAM 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6 | 5.9 | 5.8 | 4.4 | 2.3 | 0 | 5.2 | 5 | 4.7 | 4.3 | 4 | 3.7 | 3.3 | 2.9 | 2.6 | 0 | 0 | 0 | 0
Bishops Wood 132kV | BODENHAM 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6 | 5.9 | 5.8 | 5.8 | 4.9 | 3 | 5.6 | 5.4 | 5.1 | 4.8 | 4.5 | 4.1 | 3.6 | 3.3 | 2.9 | 2.6 | 0 | 0 | 0
Bishops Wood 132kV | BODENHAM 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6 | 5.9 | 5.8 | 5.5 | 3.4 | 1.4 | 5.4 | 5.2 | 5 | 4.7 | 4.4 | 4 | 3.5 | 3.1 | 2.8 | 2.4 | 0 | 0 | 0
Bishops Wood 132kV | BROMYARD 66/11kV | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 3.6 | 3.3 | 3 | 2.7 | 2.5 | 2.1 | 1.5 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | BROMYARD 66/11kV | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 3.5 | 3.1 | 2.6 | 2.2 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | BROMYARD 66/11kV | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 3.6 | 3.3 | 2.9 | 2.7 | 2 | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | BROMYARD 66/11kV | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 3.5 | 3.2 | 2.8 | 2.4 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | CLEOBURY MORTIMER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.8 | 5.6 | 5.6 | 5.5 | 5.5 | 5.3 | 4.9 | 4.7 | 4.4 | 4.1 | 3.8 | 3.4 | 2.9 | 2.3 | 1.8 | 1.3 | 0.8 | 0 | 0
Bishops Wood 132kV | CLEOBURY MORTIMER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.8 | 5.6 | 5.5 | 5.4 | 5.2 | 4.8 | 4.3 | 3.8 | 3.1 | 2.4 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | CLEOBURY MORTIMER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.8 | 5.6 | 5.6 | 5.5 | 5.4 | 5.3 | 4.8 | 4.5 | 3.9 | 3.3 | 2.7 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | CLEOBURY MORTIMER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.8 | 5.6 | 5.6 | 5.5 | 5.3 | 5 | 4.6 | 4.2 | 3.5 | 2.9 | 2.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | CRAVEN ARMS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.5 | 3.4 | 3.2 | 3 | 2.8 | 2.7 | 2.3 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | CRAVEN ARMS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.5 | 3.3 | 3 | 2.6 | 2.3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | CRAVEN ARMS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.5 | 3.4 | 3.1 | 2.9 | 2.8 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | CRAVEN ARMS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.5 | 3.3 | 3.1 | 2.8 | 2.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.4 | 12.2 | 12.1 | 11.9 | 11.7 | 11.3 | 6.1 | 5.6 | 4.8 | 4.4 | 3.9 | 3.1 | 2.3 | 1.5 | 0.7 | 0 | 0 | 0 | 0
Bishops Wood 132kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.4 | 12 | 11.6 | 11.1 | 10.4 | 9.8 | 4.4 | 3.1 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.4 | 12 | 11.8 | 11.3 | 10.7 | 10.3 | 4.6 | 3.7 | 2.8 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.4 | 12 | 11.8 | 11.5 | 10.9 | 10.4 | 5 | 3.9 | 2.8 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | DYMOCK 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | DYMOCK 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | DYMOCK 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | DYMOCK 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | HEREFORD 132kV S STN | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 19 | 15.3 | 14.2 | 12.9 | 11.5 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | HEREFORD 132kV S STN | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 19 | 14.5 | 12.4 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | HEREFORD 132kV S STN | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 19 | 15 | 13.8 | 11.7 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | HEREFORD 132kV S STN | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 19 | 14.7 | 13.2 | 11 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KENSWICK 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.9 | 7.7 | 7.7 | 7.5 | 7.4 | 7.3 | 7.1 | 6.9 | 6.7 | 6.5 | 6.3 | 6 | 5.8 | 5.5 | 5.2 | 4.9 | 4.6 | 0 | 0
Bishops Wood 132kV | KENSWICK 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.9 | 7.7 | 7.6 | 7.4 | 7.1 | 6.9 | 6.7 | 6.3 | 5.9 | 5.5 | 5 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KENSWICK 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.9 | 7.7 | 7.7 | 7.6 | 7.4 | 7.3 | 7.1 | 6.7 | 6.3 | 5.8 | 5.3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KENSWICK 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.9 | 7.7 | 7.6 | 7.5 | 7.3 | 7.2 | 7 | 6.7 | 6.3 | 5.8 | 5.3 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Kidderminster 132/33/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 34.4 | 33.5 | 32.9 | 31.8 | 30.9 | 29.8 | 27.2 | 25.7 | 22.9 | 21 | 19 | 16.8 | 14 | 11.1 | 8.3 | 5.9 | 3.3 | 0 | 0
Bishops Wood 132kV | Kidderminster 132/33/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 34.4 | 32.6 | 30.4 | 28.3 | 26.4 | 23.9 | 20.2 | 15.1 | 9.9 | 5.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Kidderminster 132/33/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 34.4 | 32.8 | 31.1 | 30 | 28.5 | 26.8 | 22.9 | 19.5 | 15.7 | 12.5 | 9.2 | 5.4 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Kidderminster 132/33/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 34.4 | 32.7 | 31.1 | 29.5 | 27.7 | 25.8 | 22.3 | 18.7 | 14.8 | 11.7 | 8.2 | 4.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KINGTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.8 | 4 | 1.5 | 0 | 0 | 0 | 4.4 | 4.2 | 3.9 | 3.7 | 3.4 | 3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KINGTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.8 | 2.3 | 0 | 0 | 0 | 0 | 3.7 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KINGTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.8 | 3.3 | 0.6 | 0 | 0 | 0 | 4 | 3.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KINGTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.8 | 2.8 | 0 | 0 | 0 | 0 | 3.8 | 3.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KNIGHTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.5 | 4.2 | 1.6 | 0 | 0 | 0 | 6.9 | 6.7 | 6.5 | 6.3 | 6.1 | 5.9 | 5.5 | 5.1 | 4.7 | 4.4 | 4 | 0 | 0
Bishops Wood 132kV | KNIGHTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.5 | 2.4 | 0 | 0 | 0 | 0 | 6.3 | 5.9 | 5.5 | 5.1 | 4.7 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KNIGHTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.5 | 3.4 | 0.7 | 0 | 0 | 0 | 6.6 | 6.2 | 5.7 | 5.4 | 4.8 | 4.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KNIGHTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.5 | 2.9 | 0 | 0 | 0 | 0 | 6.3 | 5.9 | 5.4 | 5 | 4.2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEDBURY 66/11kV | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEDBURY 66/11kV | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEDBURY 66/11kV | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEDBURY 66/11kV | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.1 | 3.8 | 3.6 | 3.3 | 3.1 | 2.8 | 2.3 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.1 | 3.7 | 3.3 | 2.7 | 2.3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.1 | 3.8 | 3.5 | 3.2 | 2.9 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 3.8 | 3.4 | 3 | 2.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEOMINSTER 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.5 | 8.1 | 3.6 | 0 | 0 | 0 | 6.8 | 6 | 5.1 | 4.5 | 3.8 | 2.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEOMINSTER 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.5 | 5.3 | 0 | 0 | 0 | 0 | 4 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEOMINSTER 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.5 | 7.6 | 1.5 | 0 | 0 | 0 | 5.4 | 3.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEOMINSTER 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.5 | 6.4 | 0 | 0 | 0 | 0 | 4.7 | 3.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LOWER CHADNOR 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LOWER CHADNOR 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LOWER CHADNOR 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LOWER CHADNOR 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Ludlow 132/66/33/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 3.4 | 3.2 | 2.8 | 2.5 | 2.1 | 1.8 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Ludlow 132/66/33/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 3.4 | 3 | 2.4 | 1.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Ludlow 132/66/33/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 3.4 | 3.1 | 2.6 | 2.3 | 1.9 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Ludlow 132/66/33/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 3.4 | 3 | 2.5 | 2 | 1.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LUDLOW 132kV S STN | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 11.1 | 10.7 | 10.5 | 10.2 | 9.7 | 9.1 | 6.9 | 6.1 | 5.2 | 4.5 | 3.8 | 2.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LUDLOW 132kV S STN | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 11.1 | 10.5 | 9.8 | 8.9 | 1 | 0 | 4 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LUDLOW 132kV S STN | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 11.1 | 10.6 | 10.2 | 9.8 | 9.1 | 0 | 5.5 | 3.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LUDLOW 132kV S STN | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 11.1 | 10.5 | 10.1 | 9.5 | 8.5 | 0 | 4.7 | 3.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | MADLEY 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | MADLEY 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | MADLEY 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | MADLEY 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Malvern 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 12.3 | 11.9 | 11.5 | 11.1 | 10.5 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Malvern 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 12.3 | 11.3 | 10.2 | 9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Malvern 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 12.3 | 11.5 | 10.6 | 9.9 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Malvern 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 12.3 | 11.4 | 10.6 | 9.6 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | NEWENT 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | NEWENT 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | NEWENT 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | NEWENT 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PETERCHURCH 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PETERCHURCH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PETERCHURCH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PETERCHURCH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PONTRILAS 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PONTRILAS 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PONTRILAS 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PONTRILAS 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PRESTEIGNE 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.8 | 4.2 | 1.6 | 0 | 0 | 0 | 7.1 | 6.2 | 5.3 | 4.7 | 4 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PRESTEIGNE 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.8 | 2.4 | 0 | 0 | 0 | 0 | 4.2 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PRESTEIGNE 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.8 | 3.4 | 0.7 | 0 | 0 | 0 | 5.7 | 3.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PRESTEIGNE 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.8 | 2.9 | 0 | 0 | 0 | 0 | 4.8 | 3.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 21.1 | 18.6 | 17.9 | 17.6 | 17.2 | 16.8 | 10.6 | 10.2 | 9.6 | 9.1 | 8.6 | 7.9 | 7.2 | 6.5 | 5.9 | 5.4 | 4.7 | 0.8 | 0
Bishops Wood 132kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 21.1 | 18.3 | 17.3 | 16.6 | 16 | 15.3 | 8.8 | 7.5 | 6.2 | 4.7 | 3.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 21.1 | 18.4 | 17.5 | 17 | 16.6 | 16.1 | 9.7 | 8.9 | 7.8 | 6.8 | 5.7 | 4.2 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 21.1 | 18.3 | 17.5 | 16.9 | 16.3 | 15.7 | 9.2 | 8.3 | 7.3 | 6.3 | 5.3 | 4 | 3 | 2 | 1.1 | 0 | 0 | 0 | 0
Bishops Wood 132kV | ROSS ON WYE 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | ROSS ON WYE 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | ROSS ON WYE 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | ROSS ON WYE 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | ST WEONARDS 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | ST WEONARDS 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | ST WEONARDS 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | ST WEONARDS 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | STOCKTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.3 | 6.1 | 6 | 5.8 | 5.6 | 5.4 | 5.1 | 4.8 | 4.4 | 4.1 | 3.8 | 3.3 | 2.8 | 2.3 | 1.8 | 1.3 | 0.8 | 0 | 0
Bishops Wood 132kV | STOCKTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.3 | 6 | 5.7 | 5.4 | 5.1 | 4.7 | 4.3 | 3.7 | 3.1 | 2.4 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | STOCKTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.3 | 6.1 | 5.9 | 5.8 | 5.6 | 5.4 | 5 | 4.6 | 3.9 | 3.3 | 2.6 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | STOCKTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.3 | 6 | 5.9 | 5.7 | 5.3 | 4.9 | 4.6 | 4.2 | 3.5 | 2.9 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | STOURPORT 132 66 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 5.9 | 5.7 | 5.6 | 5.4 | 5.2 | 5.1 | 23.2 | 23.3 | 23.3 | 23.3 | 23.3 | 26.9 | 27 | 27.1 | 27.2 | 27.3 | 27.4 | 0 | 0
Bishops Wood 132kV | STOURPORT 132 66 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 5.9 | 5.7 | 5.4 | 5.1 | 4.9 | 4.7 | 27 | 27 | 27.1 | 27.2 | 27.3 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | STOURPORT 132 66 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 5.9 | 5.7 | 5.5 | 5.3 | 5.2 | 5.2 | 27 | 27 | 27 | 27.1 | 27.1 | 27.3 | 13 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | STOURPORT 132 66 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.7 | 5.5 | 5.3 | 5.1 | 5 | 27 | 27 | 27 | 27.1 | 27.2 | 27.4 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | STOURPORT 132 66 33kV S STN | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 47.3 | 44.4 | 43.6 | 43.1 | 42.5 | 41.8 | 39.2 | 38.9 | 38.5 | 37.6 | 36.8 | 35.6 | 34.2 | 32.9 | 31.7 | 30.6 | 29.2 | 21.3 | 15.8
Bishops Wood 132kV | STOURPORT 132 66 33kV S STN | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 47.3 | 43.9 | 42.4 | 41.1 | 40.1 | 38.6 | 36.8 | 34.5 | 31.9 | 29.4 | 27.2 | 24.5 | 21.6 | 19.1 | 16.8 | 14.5 | 12.4 | 0 | 0
Bishops Wood 132kV | STOURPORT 132 66 33kV S STN | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 47.3 | 44 | 42.8 | 42.1 | 41.3 | 40.2 | 38.6 | 37 | 35 | 33.2 | 31.2 | 28.6 | 25.8 | 23.3 | 20.9 | 18.2 | 15.8 | 0 | 0
Bishops Wood 132kV | STOURPORT 132 66 33kV S STN | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 47.3 | 44 | 42.7 | 41.8 | 40.6 | 39.4 | 37.8 | 36.2 | 34.2 | 32.4 | 30.3 | 27.8 | 25.8 | 23.8 | 22.2 | 20.4 | 18.8 | 0.8 | 0
Bishops Wood 132kV | Stourport 132/66/33/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 2.5 | 2 | 1.7 | 1.4 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Stourport 132/66/33/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 2.5 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Stourport 132/66/33/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 2.5 | 1.7 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Stourport 132/66/33/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 2.5 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | TENBURY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 7 | 7 | 6.9 | 6.7 | 6.6 | 6.6 | 6.3 | 5.9 | 5.6 | 5.3 | 4.9 | 4.3 | 3.8 | 3.3 | 2.8 | 2.3 | 0 | 0
Bishops Wood 132kV | TENBURY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 6.9 | 6.8 | 6.5 | 6.2 | 5.9 | 5.6 | 4.9 | 4.2 | 3.4 | 2.7 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | TENBURY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 7 | 6.9 | 6.8 | 6.6 | 6.3 | 6.1 | 5.6 | 5 | 4.4 | 3.7 | 2.8 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | TENBURY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 7 | 6.9 | 6.7 | 6.4 | 6.1 | 5.8 | 5.3 | 4.6 | 3.9 | 3.2 | 2.4 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Timberdine 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 17.5 | 3.3 | 3 | 2.7 | 2.3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Timberdine 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 17.5 | 2.8 | 2.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Timberdine 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 17.5 | 3 | 2.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Timberdine 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 17.5 | 2.9 | 2.4 | 1.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Upton Warren 132/66/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 8.5 | 5.3 | 5 | 4.7 | 4.2 | 3.9 | 3.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Upton Warren 132/66/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 8.5 | 5.1 | 4.6 | 3.8 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Upton Warren 132/66/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 8.5 | 5.2 | 4.8 | 4.3 | 3.9 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Upton Warren 132/66/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 8.5 | 5.2 | 4.7 | 4.1 | 3.5 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | UPTON WARREN 132kV S STN | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 53.2 | 37.6 | 34.3 | 29.4 | 23.7 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | UPTON WARREN 132kV S STN | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 53.2 | 34.2 | 24.7 | 12.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | UPTON WARREN 132kV S STN | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 53.2 | 35.3 | 29.5 | 21.1 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | UPTON WARREN 132kV S STN | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 53.2 | 34.8 | 28.1 | 19.2 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Warndon 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 34.4 | 33.9 | 33.5 | 32.9 | 30 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Warndon 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 34.4 | 33.1 | 30.3 | 20.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Warndon 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 34.4 | 33.3 | 32.5 | 27 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Warndon 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 34.4 | 33.2 | 32.4 | 25.8 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | WOOFFERTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8 | 7.9 | 4.7 | 0 | 0 | 0 | 6.7 | 5.9 | 5.1 | 4.5 | 3.8 | 2.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | WOOFFERTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8 | 7 | 0 | 0 | 0 | 0 | 4 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | WOOFFERTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8 | 7.9 | 1.9 | 0 | 0 | 0 | 5.4 | 3.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | WOOFFERTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8 | 7.8 | 0 | 0 | 0 | 0 | 4.6 | 3.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Worcester 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 16.3 | 12.9 | 12.7 | 12.3 | 11.9 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Worcester 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 16.3 | 12.5 | 11.7 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Worcester 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 16.3 | 12.6 | 12.1 | 11.4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Worcester 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 16.3 | 12.5 | 12 | 11.3 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | WRIBBENHALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.4 | 4 | 4 | 3.9 | 3.8 | 3.7 | 7.5 | 7.2 | 6.8 | 6.6 | 6.3 | 5.8 | 5 | 4.2 | 3.3 | 2.6 | 1.7 | 0 | 0
Bishops Wood 132kV | WRIBBENHALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.4 | 3.8 | 3.3 | 2.9 | 2.5 | 2 | 5.9 | 5.1 | 4.1 | 3 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | WRIBBENHALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.4 | 3.9 | 3.6 | 3.5 | 3.4 | 3 | 7 | 6.5 | 5.8 | 5 | 4.2 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | WRIBBENHALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.4 | 3.8 | 3.5 | 3.2 | 2.9 | 2.5 | 6.5 | 5.9 | 5.1 | 4.4 | 3.4 | 2.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.5 | 7.3 | 7.2 | 7.1 | 7 | 6.7 | 10.4 | 10.1 | 9.8 | 9.6 | 9.4 | 9.1 | 8.7 | 8.3 | 7.9 | 7.5 | 7 | 4.9 | 3.4
Bushbury 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.5 | 7.2 | 7 | 6.7 | 6.4 | 5.8 | 9.4 | 8.8 | 8.2 | 7.6 | 7.2 | 6.7 | 6.1 | 5.4 | 4.9 | 4.5 | 4.1 | 2.7 | 1.6
Bushbury 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.5 | 7.2 | 7 | 6.7 | 6.4 | 5.8 | 9.5 | 9.1 | 8.6 | 8.1 | 7.7 | 7 | 6.3 | 5.7 | 5.2 | 4.6 | 4.1 | 2.4 | 1.4
Bushbury 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.5 | 7.2 | 7 | 6.8 | 6.5 | 5.9 | 9.6 | 9.1 | 8.5 | 8.1 | 7.6 | 7.1 | 6.5 | 5.9 | 5.3 | 4.8 | 4.4 | 3 | 2.3
Bushbury 132kV | Bushbury B-C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | Bushbury B-C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | Bushbury B-C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | Bushbury B-C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | BUSHBURY C 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | BUSHBURY C 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | BUSHBURY C 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | BUSHBURY C 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | FOUR ASHES 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | FOUR ASHES 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | FOUR ASHES 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | FOUR ASHES 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | I54 Busines Park 33/11kv | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.5 | 20.5 | 20.6 | 20.8 | 20.9 | 20.3 | 19.4 | 19.1 | 19 | 19.2 | 19.1 | 19 | 18.8 | 18.7 | 18.6 | 18.3 | 17.9 | 16.9 | 16.3
Bushbury 132kV | I54 Busines Park 33/11kv | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.5 | 20.4 | 20.5 | 20.6 | 20.2 | 19.1 | 18.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.7 | 17.1 | 16.6 | 16.1 | 15.9 | 15.6 | 14.4 | 13.9
Bushbury 132kV | I54 Busines Park 33/11kv | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.5 | 20.5 | 20.5 | 19.9 | 19.5 | 18.8 | 18.5 | 18.5 | 18.6 | 18.6 | 18.6 | 17.7 | 17.1 | 16.7 | 16.4 | 16.1 | 15.8 | 14.6 | 14
Bushbury 132kV | I54 Busines Park 33/11kv | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.5 | 20.5 | 20.6 | 20.7 | 20.4 | 19.4 | 18.9 | 18.5 | 18.5 | 18.6 | 18.6 | 18.2 | 18 | 17.6 | 17.2 | 17 | 16.8 | 16.3 | 16.2
Bushbury 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 45.9 | 41.7 | 40.7 | 39.4 | 37.8 | 35.4 | 32.1 | 31.2 | 29.9 | 29.1 | 27.9 | 26.4 | 24.7 | 22.9 | 21.3 | 17.4 | 12.3 | 1.7 | 0
Bushbury 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 45.9 | 41 | 39.4 | 37.2 | 34.7 | 31.8 | 29 | 25.2 | 21.6 | 18.7 | 16.2 | 13.5 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 45.9 | 41.2 | 39.8 | 37.5 | 35.9 | 33.1 | 30.9 | 28.4 | 26.3 | 24.6 | 21.9 | 12.3 | 5.9 | 3.3 | 1 | 0 | 0 | 0 | 0
Bushbury 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 45.9 | 41.1 | 39.6 | 37.8 | 35.3 | 32.5 | 30.3 | 27.1 | 24.1 | 22 | 19.7 | 17.1 | 13.8 | 6.6 | 0.7 | 0 | 0 | 0 | 0
Bushbury 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 43.6 | 43.1 | 42.6 | 42 | 41.2 | 40.3 | 38.2 | 37.8 | 37.1 | 36.4 | 35.3 | 33.8 | 31.8 | 29.6 | 27.3 | 25.3 | 23.2 | 10.5 | 1.6
Bushbury 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 43.6 | 42.3 | 40.9 | 39.3 | 37.7 | 35.9 | 34.5 | 31.2 | 27.7 | 24.2 | 21.2 | 18.2 | 14.5 | 11.3 | 8.5 | 5.9 | 3.5 | 0 | 0
Bushbury 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 43.6 | 42.4 | 41.4 | 40.2 | 39 | 37.7 | 36.9 | 34.8 | 32 | 29.5 | 26.6 | 23.5 | 20.1 | 16.8 | 13.4 | 10.2 | 7.2 | 0 | 0
Bushbury 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 43.6 | 42.4 | 41.4 | 40.2 | 38.8 | 37.4 | 36.3 | 34.1 | 31.5 | 29.1 | 26.3 | 23.2 | 20.1 | 17.2 | 14.4 | 11.8 | 9.1 | 0 | 0
Bushbury 132kV | Wednesfield 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 30.4 | 29.6 | 28.5 | 24.3 | 22.9 | 21.8 | 17.2 | 15.8 | 13.5 | 12 | 10.2 | 7.8 | 4.7 | 1.4 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | Wednesfield 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 30.4 | 28.4 | 25.9 | 10.5 | 8.1 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | Wednesfield 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 30.4 | 28.6 | 26.6 | 11.9 | 10 | 7.8 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | Wednesfield 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 30.4 | 28.5 | 26.8 | 21.7 | 19.6 | 17.5 | 12.1 | 8.6 | 4.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 30.3 | 14.5 | 14.2 | 13.8 | 13.3 | 12.5 | 5.7 | 5 | 2.8 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 30.3 | 13.7 | 12.6 | 11.2 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 30.3 | 13.8 | 13.1 | 11.8 | 10.1 | 6.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 30.3 | 13.7 | 13.1 | 12.1 | 10.8 | 6.7 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | BUSTLEHOLM 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 10.2 | 9.9 | 9.6 | 9.2 | 8.7 | 8.2 | 7.3 | 6.4 | 5 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | BUSTLEHOLM 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 10.2 | 9.3 | 8.2 | 6.7 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | BUSTLEHOLM 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 10.2 | 9.4 | 8.7 | 7.7 | 6.8 | 5.8 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | BUSTLEHOLM 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 10.2 | 9.4 | 8.7 | 7.7 | 6.7 | 5.8 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Kingstanding 132/11kVDummy | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 26.3 | 25.7 | 25.2 | 24.7 | 24 | 23.3 | 22.5 | 21.4 | 19.6 | 18.3 | 16.9 | 15 | 12.2 | 9.3 | 6.4 | 3.8 | 1.1 | 0 | 0
Bustleholm 132kV | Kingstanding 132/11kVDummy | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 26.3 | 24.6 | 23 | 21.1 | 19.2 | 17.2 | 15 | 10.7 | 5.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Kingstanding 132/11kVDummy | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 26.3 | 24.9 | 23.8 | 22.7 | 21.6 | 20.3 | 19.1 | 16.3 | 12.7 | 9.5 | 6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Kingstanding 132/11kVDummy | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 26.3 | 24.8 | 23.8 | 22.5 | 21.2 | 19.8 | 18.1 | 15.4 | 11.8 | 8.6 | 5.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Ladywood 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 40.8 | 40 | 39 | 37.7 | 33.4 | 31.6 | 28.7 | 26.4 | 15.2 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Ladywood 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 40.8 | 39.7 | 38.6 | 28.5 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Ladywood 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 40.8 | 39.8 | 39 | 36.6 | 22.5 | 13.8 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Ladywood 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 40.8 | 39.7 | 38.7 | 36.1 | 22.8 | 11.3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Perry Barr 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Perry Barr 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Perry Barr 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Perry Barr 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Rushall 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 9.4 | 9 | 8.7 | 8.1 | 7.5 | 6.6 | 4.7 | 3.9 | 2.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Rushall 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 9.4 | 8.3 | 7.2 | 5.6 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Rushall 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 9.4 | 8.4 | 7.7 | 6.2 | 4.7 | 3.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Rushall 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 9.4 | 8.4 | 7.6 | 6.4 | 5 | 3.6 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Smethwick 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 6.1 | 5.8 | 5.5 | 5.2 | 4.8 | 4.4 | 3.9 | 3.1 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Smethwick 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 6.1 | 5.4 | 4.4 | 3.2 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Smethwick 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 6.1 | 5.5 | 4.6 | 4 | 3 | 2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Smethwick 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 6.1 | 5.4 | 4.5 | 3.6 | 2.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Winson Green 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 16 | 13.2 | 12.9 | 12.4 | 11.8 | 11.2 | 10 | 9.1 | 7.9 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Winson Green 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 16 | 12.8 | 11.9 | 10.5 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Winson Green 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 16 | 12.9 | 12.2 | 11.1 | 10.1 | 9.2 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bustleholm 132kV | Winson Green 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 16 | 12.8 | 12.2 | 11.3 | 10.3 | 9.3 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | BEARSTONE | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | BEARSTONE | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | BEARSTONE | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | BEARSTONE | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Boothen 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 5.7 | 5.4 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Boothen 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 5.7 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Boothen 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 5.7 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Boothen 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 5.7 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | BOOTHEN 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 62 | 61.9 | 61.8 | 60.9 | 8.9 | 0 | 60.3 | 60 | 55.2 | 49 | 40.8 | 29.1 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | BOOTHEN 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 62 | 61.7 | 60.7 | 15.9 | 0 | 0 | 38.3 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | BOOTHEN 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 62 | 61.7 | 60.8 | 29.5 | 0 | 0 | 49.3 | 31 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | BOOTHEN 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 62 | 61.7 | 60.8 | 32.9 | 0 | 0 | 51.8 | 34.7 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Burslem 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 33.3 | 31.4 | 30.1 | 28.6 | 4.1 | 0 | 21.2 | 19.3 | 16.2 | 14.5 | 11.4 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Burslem 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 33.3 | 30.6 | 28 | 7.2 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Burslem 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 33.3 | 30.8 | 29 | 13.4 | 0 | 0 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Burslem 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 33.3 | 30.7 | 28.9 | 15 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | CAULDON | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.3 | 7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.9 | 6.9 | 6.4 | 5.8 | 5.1 | 4 | 3.3 | 2.5 | 1.9 | 1.4 | 0.8 | 0 | 0
Cellarhead 132kV | CAULDON | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.3 | 6.9 | 6.5 | 6.3 | 6.1 | 6 | 6 | 4.9 | 3.4 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | CAULDON | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.3 | 7 | 6.7 | 6.7 | 6.6 | 6.5 | 6 | 4.8 | 3.5 | 2.7 | 2.2 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | CAULDON | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.3 | 6.9 | 6.6 | 6.5 | 6.3 | 6.2 | 6.2 | 5.4 | 4.1 | 2.8 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | CHEADLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.3 | 9.1 | 8.8 | 8.5 | 8.3 | 8 | 7.8 | 6.9 | 5.8 | 5 | 4.4 | 3.5 | 2.2 | 0.8 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | CHEADLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.3 | 8.9 | 8.4 | 7.7 | 7.2 | 6.1 | 4.8 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | CHEADLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.3 | 9 | 8.6 | 8.1 | 7.8 | 6.5 | 5.6 | 3.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | CHEADLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.3 | 9 | 8.5 | 7.9 | 7.6 | 6.7 | 5.5 | 3.8 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | CHEDDLETON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.6 | 3.9 | 3.4 | 2.8 | 2.1 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | CHEDDLETON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.6 | 3.3 | 2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | CHEDDLETON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.6 | 3.5 | 2.6 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | CHEDDLETON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.6 | 3.4 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | CONGLETON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | CONGLETON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | CONGLETON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | CONGLETON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | COTES HEATH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.1 | 8 | 8 | 8 | 8 | 8 | 8.2 | 8.2 | 8.1 | 8.1 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7.1 | 6.8 | 0 | 0
Cellarhead 132kV | COTES HEATH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.1 | 8 | 8 | 7.9 | 7.8 | 7.7 | 7.8 | 7.6 | 7.3 | 7.1 | 6.9 | 6.5 | 5.1 | 2.2 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | COTES HEATH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.1 | 8 | 8 | 8 | 7.9 | 7.9 | 8 | 7.8 | 7.6 | 7.3 | 7.1 | 6.8 | 6.4 | 3.6 | 0.9 | 0 | 0 | 0 | 0
Cellarhead 132kV | COTES HEATH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.1 | 8 | 8 | 8 | 7.9 | 7.8 | 7.9 | 7.8 | 7.5 | 7.3 | 7 | 6.6 | 6.2 | 2.9 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | ECCLESHALL PRIMARY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | ECCLESHALL PRIMARY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | ECCLESHALL PRIMARY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | ECCLESHALL PRIMARY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | ENDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.7 | 4 | 3.4 | 2.9 | 2.2 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | ENDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.7 | 3.4 | 2.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | ENDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.7 | 3.6 | 2.6 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | ENDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.7 | 3.5 | 2.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | FORSBROOK 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 66.2 | 65.4 | 64.4 | 63.7 | 62.9 | 62.3 | 61.7 | 60.3 | 58.8 | 57.2 | 48.8 | 34.8 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | FORSBROOK 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 66.2 | 64.9 | 63.4 | 61.8 | 60.6 | 16.6 | 45.8 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | FORSBROOK 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 66.2 | 65.1 | 63.9 | 62.9 | 62 | 42.7 | 58.1 | 37.1 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | FORSBROOK 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 66.2 | 65 | 63.8 | 62.5 | 61.4 | 45.9 | 58.2 | 41.4 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | FROGHALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 6.8 | 6.8 | 6.8 | 6.7 | 6.7 | 6.8 | 6.8 | 6.5 | 5.9 | 5.1 | 4.1 | 3.4 | 2.6 | 1.9 | 1.4 | 0.8 | 0 | 0
Cellarhead 132kV | FROGHALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 4.9 | 3.4 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | FROGHALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 6.8 | 6.8 | 6.7 | 6.7 | 6.5 | 6.1 | 4.9 | 3.6 | 2.7 | 2.3 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | FROGHALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.8 | 6.7 | 6.6 | 6.4 | 6.2 | 6.3 | 5.5 | 4.2 | 2.8 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | GNOSALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | GNOSALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | GNOSALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | GNOSALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | GOLDENHILL BANK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.1 | 7.8 | 7.4 | 7.1 | 6.8 | 6.3 | 5.7 | 5 | 4 | 3.4 | 2.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | GOLDENHILL BANK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.1 | 7.3 | 6.4 | 5.5 | 4.6 | 3.4 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | GOLDENHILL BANK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.1 | 7.4 | 6.8 | 6.1 | 5.4 | 4.7 | 3.9 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | GOLDENHILL BANK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.1 | 7.4 | 6.7 | 6.1 | 5.3 | 4.5 | 3.4 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HIGH OFFLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HIGH OFFLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HIGH OFFLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HIGH OFFLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HILL CHORLTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HILL CHORLTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HILL CHORLTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HILL CHORLTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HINSTOCK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HINSTOCK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HINSTOCK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HINSTOCK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HOOKGATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HOOKGATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HOOKGATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HOOKGATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | KINGSLEY HOLT 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 6.4 | 6 | 5.9 | 5.8 | 5.7 | 5.7 | 5.6 | 5.4 | 5.3 | 5.1 | 4 | 3.3 | 2.6 | 1.9 | 1.4 | 0.8 | 0 | 0
Cellarhead 132kV | KINGSLEY HOLT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 6.3 | 5.9 | 5.7 | 5.4 | 5.3 | 5 | 4.7 | 3.4 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | KINGSLEY HOLT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 6.4 | 6 | 5.9 | 5.7 | 5.6 | 5.5 | 4.8 | 3.5 | 2.7 | 2.2 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | KINGSLEY HOLT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 6.4 | 5.9 | 5.8 | 5.6 | 5.4 | 5.2 | 4.9 | 4.1 | 2.8 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | KNYPERSLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.2 | 10.6 | 10.2 | 9.8 | 9.5 | 9 | 8.8 | 7.8 | 6.8 | 6 | 5.3 | 4.1 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | KNYPERSLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.2 | 10.2 | 9.2 | 8.2 | 7.3 | 6.2 | 4.9 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | KNYPERSLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.2 | 10.3 | 9.6 | 9.1 | 8.4 | 7.4 | 6.7 | 4.7 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | KNYPERSLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.2 | 10.3 | 9.6 | 8.9 | 8.1 | 7.2 | 6 | 4.3 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | LEEK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | LEEK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | LEEK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | LEEK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Longton 132/33/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 32.9 | 32.3 | 31.9 | 31.4 | 8.2 | 0 | 27 | 25.7 | 23.9 | 22.6 | 21 | 18.9 | 16 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Longton 132/33/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 32.9 | 31.4 | 30 | 14.7 | 0 | 0 | 19.7 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Longton 132/33/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 32.9 | 31.6 | 30.7 | 27.4 | 0 | 0 | 23.5 | 21 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Longton 132/33/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 32.9 | 31.5 | 30.6 | 29.3 | 0 | 0 | 22.6 | 19.9 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | MARKET DRAYTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | MARKET DRAYTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | MARKET DRAYTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | MARKET DRAYTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Meaford C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 11.3 | 7.3 | 7.2 | 7.1 | 7 | 0 | 5.3 | 4.5 | 4 | 3.7 | 3.3 | 2.9 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Meaford C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 11.3 | 7.2 | 6.9 | 6.6 | 0 | 0 | 3.6 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Meaford C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 11.3 | 7.2 | 7.1 | 6.5 | 0 | 0 | 4.2 | 3.4 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Meaford C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 7.2 | 7 | 6.8 | 0 | 0 | 4.2 | 3.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | MEAFORD C 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 45.4 | 37 | 35.7 | 34.6 | 7.5 | 0 | 29.6 | 25.4 | 21.6 | 19.9 | 17.8 | 15.1 | 11 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | MEAFORD C 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 45.4 | 36.2 | 33.9 | 13.4 | 0 | 0 | 20.2 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | MEAFORD C 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 45.4 | 36.5 | 34.9 | 24.9 | 0 | 0 | 23.9 | 18.1 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | MEAFORD C 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 45.4 | 36.4 | 34.6 | 27.8 | 0 | 0 | 22.9 | 17.4 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Newcastle 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 23.3 | 22.9 | 21.8 | 21.2 | 4.2 | 0 | 13.4 | 11.5 | 8.9 | 7.1 | 6 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Newcastle 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 23.3 | 22.5 | 20.9 | 7.4 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Newcastle 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 23.3 | 22.6 | 21.3 | 13.8 | 0 | 0 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Newcastle 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 23.3 | 22.6 | 21.2 | 15.4 | 0 | 0 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | NEWCASTLE 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 16 | 15.8 | 15.4 | 15.3 | 4.1 | 0 | 15.4 | 14.9 | 14.1 | 13.6 | 11.5 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | NEWCASTLE 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 16 | 15.5 | 14.8 | 7.4 | 0 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | NEWCASTLE 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 16 | 15.6 | 15 | 13.7 | 0 | 0 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | NEWCASTLE 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 16 | 15.5 | 14.9 | 14.5 | 0 | 0 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | SCOT HAY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.3 | 1.2 | 1 | 0.9 | 0.8 | 0.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | SCOT HAY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.3 | 1.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | SCOT HAY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.3 | 1.1 | 0.8 | 0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | SCOT HAY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.3 | 1.1 | 0.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | SIMPLEX 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.4 | 2.8 | 2.2 | 1.5 | 0.8 | 0 | 7.9 | 6.7 | 5.6 | 4.8 | 4.2 | 3.4 | 2.2 | 0.7 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | SIMPLEX 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.4 | 2.6 | 1.6 | 0.6 | 0 | 0 | 4.6 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | SIMPLEX 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.4 | 2.6 | 1.8 | 1 | 0 | 0 | 5.4 | 3.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | SIMPLEX 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.4 | 2.6 | 1.8 | 0.9 | 0 | 0 | 5.3 | 3.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Stagefields 132/33/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 22.8 | 20.5 | 20 | 19.5 | 8.9 | 0 | 12.9 | 10.9 | 7.9 | 6.8 | 5.1 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Stagefields 132/33/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 22.8 | 19.4 | 17.9 | 15.8 | 0 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Stagefields 132/33/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 22.8 | 19.6 | 18.8 | 16.4 | 0 | 0 | 6.6 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Stagefields 132/33/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 22.8 | 19.5 | 18.5 | 17.1 | 0 | 0 | 7.1 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | TALKE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.2 | 7.8 | 7.5 | 7.2 | 6.8 | 6.4 | 5.8 | 5.1 | 4.1 | 3.4 | 2.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | TALKE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.2 | 7.4 | 6.5 | 5.6 | 4.6 | 3.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | TALKE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.2 | 7.5 | 6.8 | 6.2 | 5.5 | 4.8 | 3.9 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | TALKE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.2 | 7.5 | 6.8 | 6.2 | 5.4 | 4.5 | 3.4 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | TEAN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.7 | 9.4 | 9.1 | 8.8 | 8.5 | 8.2 | 8 | 6.8 | 5.8 | 4.9 | 4.3 | 3.5 | 2.2 | 0.8 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | TEAN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.7 | 9.2 | 8.6 | 7.9 | 7.2 | 6 | 4.7 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | TEAN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.7 | 9.3 | 8.9 | 8.4 | 8.1 | 6.5 | 5.5 | 3.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | TEAN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.7 | 9.3 | 8.8 | 8.2 | 7.8 | 6.6 | 5.4 | 3.8 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | WHITFIELD 132 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 74.2 | 52.5 | 39.2 | 27.1 | 3.7 | 0 | 38.7 | 32.3 | 22.7 | 17.8 | 13.9 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | WHITFIELD 132 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 74.2 | 46.8 | 25.6 | 6.6 | 0 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | WHITFIELD 132 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 74.2 | 48.2 | 29.8 | 12.3 | 0 | 0 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | WHITFIELD 132 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 74.2 | 47.7 | 28.9 | 13.7 | 0 | 0 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Whitfield 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 11.6 | 11.5 | 11.4 | 11.2 | 3.7 | 0 | 10.7 | 10.3 | 9.8 | 9.5 | 9.1 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Whitfield 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 11.6 | 11.2 | 10.9 | 6.6 | 0 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Whitfield 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 11.6 | 11.3 | 11 | 10.6 | 0 | 0 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Whitfield 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 11.6 | 11.3 | 11 | 10.7 | 0 | 0 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.9 | 3.4 | 3.2 | 2.8 | 2.2 | 1.7 | 1.2 | 0.9 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.9 | 3.3 | 3 | 2.4 | 1.7 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.9 | 3.4 | 3.1 | 2.7 | 2.2 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.9 | 3.3 | 3.1 | 2.5 | 1.9 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.3 | 4.1 | 3.9 | 3.6 | 3.4 | 3.2 | 3.1 | 2.9 | 2.3 | 2.1 | 1.7 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.3 | 4.1 | 3.7 | 3.3 | 2.9 | 2.6 | 2.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.3 | 4.1 | 3.9 | 3.6 | 3.3 | 3 | 2.2 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.3 | 4.1 | 3.8 | 3.4 | 3.1 | 2.8 | 2.5 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.2 | 10.9 | 10.2 | 9.3 | 8.4 | 7.4 | 6.6 | 5.8 | 4.5 | 3.8 | 2.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.2 | 10.6 | 9.5 | 8.1 | 6.7 | 5.1 | 3.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.2 | 10.7 | 9.9 | 8.9 | 7.8 | 6.6 | 4.7 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.2 | 10.6 | 9.8 | 8.6 | 7.3 | 5.9 | 4.5 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BEVINGTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.9 | 2.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BEVINGTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.9 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BEVINGTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.9 | 2.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BEVINGTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.9 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.9 | 3.7 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.9 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.9 | 3.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.9 | 3.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BROADWAY 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.7 | 8.3 | 6.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BROADWAY 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.7 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BROADWAY 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.7 | 8.1 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BROADWAY 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.7 | 8 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BROTHERIDGE GRN 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.5 | 2.7 | 2.1 | 1.2 | 0 | 0 | 4.7 | 4.5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BROTHERIDGE GRN 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.5 | 2.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BROTHERIDGE GRN 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.5 | 2.3 | 1.4 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BROTHERIDGE GRN 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.5 | 2.3 | 1.3 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.5 | 2.6 | 2.1 | 1.1 | 0 | 0 | 10.5 | 8.6 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.5 | 2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.5 | 2.2 | 1.3 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.5 | 2.2 | 1.2 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.3 | 4.2 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.3 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.3 | 4.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.3 | 4.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | EVESHAM 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.1 | 6.6 | 6.4 | 6 | 5.3 | 4.4 | 2.8 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | EVESHAM 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.1 | 6.1 | 5.3 | 4.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | EVESHAM 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.1 | 6.3 | 5.8 | 4.9 | 3.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | EVESHAM 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.1 | 6.2 | 5.7 | 4.9 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | Feckenham 66/11kVDUMMY | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.6 | 10 | 3.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | Feckenham 66/11kVDUMMY | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.6 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | Feckenham 66/11kVDUMMY | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.6 | 9 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | Feckenham 66/11kVDUMMY | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.6 | 8.6 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | GREAT ALNE 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12 | 11.8 | 6 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | GREAT ALNE 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | GREAT ALNE 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12 | 11.7 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | GREAT ALNE 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12 | 11.7 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | IPSLEY 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 25.1 | 20.7 | 18.6 | 17.2 | 17 | 16.7 | 13.3 | 12.9 | 12.6 | 12.5 | 12.3 | 11.7 | 11.1 | 10.4 | 9.7 | 9 | 8.4 | 3.6 | 0
Feckenham 66kV | IPSLEY 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 25.1 | 20.2 | 17.6 | 15.6 | 14.8 | 13.9 | 10.2 | 8.5 | 7 | 5.6 | 4.3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | IPSLEY 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 25.1 | 20.3 | 17.8 | 16 | 15.5 | 13.3 | 10.5 | 9.6 | 8.5 | 7.6 | 6.6 | 4.6 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | IPSLEY 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 25.1 | 20.3 | 17.8 | 15.9 | 15.2 | 14.4 | 12 | 9.9 | 8.5 | 7.5 | 6.4 | 4.8 | 3.4 | 1.9 | 0.6 | 0 | 0 | 0 | 0
Feckenham 66kV | LEDBURY 66/11kV | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.9 | 2.7 | 2.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | LEDBURY 66/11kV | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.9 | 2.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | LEDBURY 66/11kV | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.9 | 2.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | LEDBURY 66/11kV | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.9 | 2.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | LONG MARSTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.2 | 4.3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | LONG MARSTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.2 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | LONG MARSTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.2 | 3.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | LONG MARSTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.2 | 3.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | MORETON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.2 | 7.8 | 3.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | MORETON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.2 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | MORETON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.2 | 7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | MORETON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.2 | 6.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | PERSHORE 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.3 | 2.7 | 2.1 | 1.2 | 0 | 0 | 7.8 | 7.7 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | PERSHORE 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.3 | 2.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | PERSHORE 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.3 | 2.3 | 1.4 | 0 | 0 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | PERSHORE 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.3 | 2.3 | 1.3 | 0 | 0 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.4 | 0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | REDDITCH SOUTH 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.1 | 10.7 | 10.2 | 9.4 | 8.1 | 6.6 | 4 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | REDDITCH SOUTH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.1 | 10 | 8.8 | 7 | 5 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | REDDITCH SOUTH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.1 | 10.2 | 9.3 | 8.1 | 6.6 | 4.9 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | REDDITCH SOUTH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.1 | 10.2 | 9.3 | 7.9 | 6.1 | 4.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.2 | 5.7 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.2 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.2 | 5.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.2 | 4.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STOW 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.8 | 7.7 | 3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STOW 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.8 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STOW 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.8 | 6.9 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STOW 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.8 | 6.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STRATFORD 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.6 | 5.2 | 3.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STRATFORD 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.6 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STRATFORD 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.6 | 5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STRATFORD 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.6 | 4.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STRENSHAM 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.5 | 2.8 | 2.2 | 1.2 | 0 | 0 | 5 | 4.9 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STRENSHAM 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.5 | 2.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STRENSHAM 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.5 | 2.4 | 1.4 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STRENSHAM 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.5 | 2.3 | 1.3 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | TEWKESBURY 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.9 | 2.7 | 2.1 | 1.2 | 0 | 0 | 8.6 | 8.5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | TEWKESBURY 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.9 | 2.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | TEWKESBURY 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.9 | 2.3 | 1.4 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | TEWKESBURY 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.9 | 2.3 | 1.3 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | ALVESTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | ALVESTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | ALVESTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | ALVESTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | BERKELEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8 | 5.1 | 0 | 0 | 0 | 0 | 5.2 | 5.1 | 5.1 | 5 | 4.8 | 4.3 | 3.8 | 3.1 | 2.5 | 0.6 | 0 | 0 | 0
Iron Acton 132kV | BERKELEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8 | 4.7 | 0 | 0 | 0 | 0 | 4.3 | 4 | 3.5 | 3 | 2.6 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | BERKELEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8 | 4.8 | 0 | 0 | 0 | 0 | 4.6 | 4.1 | 3.6 | 3.1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | BERKELEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8 | 4.9 | 0 | 0 | 0 | 0 | 4.4 | 4.1 | 3.6 | 3.1 | 2.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | CAMP 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 6.4 | 6.4 | 6.3 | 6.2 | 6.1 | 6.2 | 6 | 5.7 | 5.5 | 5.3 | 4.9 | 4.5 | 4 | 3.5 | 3 | 2.5 | 0 | 0
Iron Acton 132kV | CAMP 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 6.3 | 6.2 | 5.9 | 5.7 | 5.3 | 5.3 | 4.7 | 4 | 3.3 | 2.8 | 2.3 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | CAMP 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 6.4 | 6.3 | 6.2 | 6.1 | 5.9 | 6 | 5.6 | 5.1 | 4.6 | 4.1 | 3.5 | 2.8 | 2.2 | 1.5 | 0.9 | 0 | 0 | 0
Iron Acton 132kV | CAMP 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 6.4 | 6.3 | 6.1 | 5.9 | 5.6 | 5.7 | 5.2 | 4.7 | 4.2 | 3.7 | 3 | 2.4 | 1.7 | 1.1 | 0 | 0 | 0 | 0
Iron Acton 132kV | CHERINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.2 | 4.2 | 3.9 | 3.9 | 3.8 | 3.7 | 3.8 | 3.7 | 3.5 | 3.4 | 3.2 | 3 | 2.7 | 2.5 | 2.2 | 2 | 1.7 | 0 | 0
Iron Acton 132kV | CHERINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.2 | 4.1 | 3.8 | 3.7 | 3.6 | 3.5 | 3.5 | 3.2 | 2.9 | 2.6 | 2.3 | 2 | 1.6 | 1.3 | 1 | 0.6 | 0 | 0 | 0
Iron Acton 132kV | CHERINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.2 | 4.2 | 3.9 | 3.9 | 3.8 | 3.7 | 3.6 | 3.4 | 3.1 | 2.8 | 2.5 | 2.2 | 1.8 | 1.4 | 1.1 | 0.7 | 0 | 0 | 0
Iron Acton 132kV | CHERINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.2 | 4.1 | 3.9 | 3.8 | 3.7 | 3.5 | 3.5 | 3.3 | 3 | 2.8 | 2.4 | 2 | 1.6 | 1.2 | 0.8 | 0 | 0 | 0 | 0
Iron Acton 132kV | Chipping Sodbury 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 12.4 | 12 | 9.3 | 8.1 | 6.7 | 5 | 6.8 | 6 | 5 | 4.4 | 3.6 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | Chipping Sodbury 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 12.4 | 11.1 | 6.6 | 3.5 | 0.7 | 0 | 3.9 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | Chipping Sodbury 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 12.4 | 11.5 | 8 | 6.1 | 4.3 | 2.1 | 5.5 | 4.1 | 2.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | Chipping Sodbury 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 12.4 | 11.4 | 7.7 | 5.4 | 2.8 | 0 | 4.9 | 3.5 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | CHIPPING SODBURY 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 23.5 | 16.9 | 9.4 | 8.2 | 6.8 | 5.1 | 22.6 | 20.4 | 17 | 14.6 | 11.9 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | CHIPPING SODBURY 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 23.5 | 11.2 | 6.7 | 3.6 | 0.7 | 0 | 11.6 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | CHIPPING SODBURY 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 23.5 | 11.6 | 8.1 | 6.1 | 4.4 | 2.2 | 18.4 | 13.5 | 6.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | CHIPPING SODBURY 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 23.5 | 11.5 | 7.7 | 5.4 | 2.8 | 0 | 15.2 | 10.1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | COWHORN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.7 | 6.4 | 5.5 | 5.3 | 5 | 4.7 | 4.2 | 3.7 | 3.1 | 1.9 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | COWHORN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.7 | 6.1 | 4.7 | 3.8 | 2.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | COWHORN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.7 | 6.2 | 5.1 | 4.7 | 4.3 | 3.8 | 3.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | COWHORN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.7 | 6.2 | 5 | 4.5 | 3.7 | 2.2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | DUDBRIDGE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.1 | 4.8 | 4.4 | 3.9 | 3.2 | 2.5 | 3.1 | 2.3 | 1.3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | DUDBRIDGE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.1 | 4.3 | 3.4 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | DUDBRIDGE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.1 | 4.5 | 3.9 | 3.3 | 2.5 | 0.9 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | DUDBRIDGE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.1 | 4.4 | 3.8 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | DURSLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 7 | 0 | 0 | 0 | 0 | 4.5 | 4.1 | 3.5 | 3.1 | 2.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | DURSLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 6.5 | 0 | 0 | 0 | 0 | 2.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | DURSLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 6.7 | 0 | 0 | 0 | 0 | 2.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | DURSLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 6.7 | 0 | 0 | 0 | 0 | 2.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | HAMMERLEY DOWN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | HAMMERLEY DOWN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | HAMMERLEY DOWN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | HAMMERLEY DOWN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | NAISHCOMBE HILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.7 | 2.4 | 2.1 | 2 | 1.8 | 1.6 | 1.9 | 1.5 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | NAISHCOMBE HILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.7 | 2.2 | 1.6 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | NAISHCOMBE HILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.7 | 2.3 | 1.9 | 1.7 | 1.5 | 1.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | NAISHCOMBE HILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.7 | 2.3 | 1.8 | 1.6 | 1.2 | 0.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | NETHERHILLS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.9 | 0 | 0 | 0 | 0 | 0 | 13.6 | 13.3 | 12.9 | 12.3 | 11.8 | 11.1 | 10.3 | 9.7 | 8.7 | 5.4 | 0 | 0 | 0
Iron Acton 132kV | NETHERHILLS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.9 | 0 | 0 | 0 | 0 | 0 | 12.1 | 11.3 | 10.3 | 9 | 7.4 | 5.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | NETHERHILLS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.9 | 0 | 0 | 0 | 0 | 0 | 12.6 | 11.8 | 10.9 | 10.1 | 8 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | NETHERHILLS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.9 | 0 | 0 | 0 | 0 | 0 | 12.3 | 11.5 | 10.7 | 9.9 | 8.1 | 6 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | OXBRIDGE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 6.5 | 6.2 | 6 | 5.8 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | OXBRIDGE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | OXBRIDGE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 6.1 | 5.7 | 5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | OXBRIDGE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 5.4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | Ryeford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 7.2 | 7 | 6.9 | 6.8 | 6.4 | 5.6 | 5.2 | 5 | 4.7 | 4.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | Ryeford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 7.2 | 6.9 | 6.7 | 6.4 | 5.6 | 2.7 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | Ryeford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 7.2 | 7 | 6.8 | 6 | 5.6 | 5.1 | 4.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | Ryeford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 6.9 | 6.8 | 6.5 | 5.7 | 3.5 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | RYEFORD 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 27.7 | 20.4 | 16 | 15 | 13.7 | 10.3 | 9.3 | 8.2 | 6.3 | 4.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | RYEFORD 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 27.7 | 19.6 | 14.2 | 11.7 | 8.2 | 2.8 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | RYEFORD 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 27.7 | 19.9 | 15 | 10.8 | 8.3 | 5.1 | 5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | RYEFORD 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 27.7 | 19.9 | 14.7 | 12.5 | 9.1 | 3.5 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BAYSTON HILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.4 | 2 | 1.6 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BAYSTON HILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.4 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BAYSTON HILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.4 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BAYSTON HILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.4 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BERRINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BERRINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BERRINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BERRINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.4 | 7.1 | 6.4 | 5.4 | 4.4 | 3.2 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.4 | 6.8 | 4.7 | 2.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.4 | 6.9 | 5.2 | 3.3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.4 | 6.9 | 5.2 | 3.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BROSELEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BROSELEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BROSELEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BROSELEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | DONNINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9 | 8.9 | 9 | 9 | 9 | 9 | 8.7 | 8.7 | 8.1 | 7.8 | 7.4 | 6.6 | 5.4 | 4.2 | 2.9 | 1.8 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | DONNINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9 | 8.8 | 8.7 | 8.6 | 8.2 | 7.7 | 7.2 | 5.7 | 4 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | DONNINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9 | 8.8 | 8.8 | 8.8 | 8.8 | 8.6 | 7.6 | 6.1 | 4.3 | 2.9 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | DONNINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9 | 8.8 | 8.8 | 8.8 | 8.6 | 8.3 | 7.7 | 6.4 | 4.9 | 3.7 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | DOTHILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.2 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | DOTHILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | DOTHILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | DOTHILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | EASTHOPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.3 | 6.3 | 6.3 | 6.2 | 6.2 | 6.1 | 6 | 5.9 | 5.8 | 5.6 | 5.5 | 5.4 | 5.2 | 4.9 | 4.8 | 4.6 | 4.4 | 3.2 | 2
Ironbr. & Shrewsb. 132kV | EASTHOPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.3 | 6.3 | 6.2 | 6.1 | 6.1 | 5.9 | 5.8 | 5.5 | 5.3 | 5 | 4.7 | 4.4 | 4 | 3.7 | 3.4 | 3.1 | 2.8 | 1.8 | 1.3
Ironbr. & Shrewsb. 132kV | EASTHOPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.3 | 6.3 | 6.3 | 6.2 | 6.2 | 6.1 | 5.9 | 5.6 | 5.3 | 5.1 | 4.8 | 4.4 | 4.1 | 3.8 | 3.5 | 3.1 | 2.9 | 1.5 | 0.5
Ironbr. & Shrewsb. 132kV | EASTHOPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.3 | 6.3 | 6.2 | 6.2 | 6 | 5.9 | 5.7 | 5.5 | 5.1 | 4.8 | 4.3 | 3.9 | 3.5 | 3.1 | 2.8 | 2.4 | 2.2 | 0.7 | 0
Ironbr. & Shrewsb. 132kV | HALESFIELD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | HALESFIELD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | HALESFIELD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | HALESFIELD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | HARLESCOTT 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.4 | 13.4 | 13.1 | 13 | 12.9 | 12.8 | 12.6 | 12.3 | 7.9 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | HARLESCOTT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.4 | 13.3 | 12.9 | 12.7 | 12.4 | 11.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | HARLESCOTT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.4 | 13.3 | 12.9 | 12.8 | 12.7 | 12.6 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | HARLESCOTT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.4 | 13.3 | 12.9 | 12.8 | 12.5 | 12.3 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | HORTONWOOD 132 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 16.9 | 13.3 | 13.2 | 13.1 | 12.9 | 11.4 | 9.4 | 8.6 | 7.8 | 7.6 | 7.2 | 6.4 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | HORTONWOOD 132 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 16.9 | 13 | 12.6 | 12.1 | 10.8 | 7.9 | 6.4 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | HORTONWOOD 132 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 16.9 | 13 | 12.7 | 10.7 | 9.1 | 7.4 | 5.7 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | HORTONWOOD 132 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 16.9 | 13 | 12.7 | 12.3 | 11.2 | 8.5 | 6.9 | 5.5 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | IRONBRIDGE 132 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 22.7 | 22 | 21.5 | 21 | 20.3 | 19.3 | 17.4 | 16.8 | 15.6 | 14.7 | 13.9 | 12.1 | 9.8 | 7.3 | 4.9 | 2.9 | 0.7 | 0 | 0
Ironbr. & Shrewsb. 132kV | IRONBRIDGE 132 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 22.7 | 21.2 | 19.8 | 18 | 16.3 | 14.3 | 12.4 | 8.7 | 4.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | IRONBRIDGE 132 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 22.7 | 21.4 | 20.5 | 19 | 18 | 17.1 | 15.4 | 13.1 | 9.8 | 7.2 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | IRONBRIDGE 132 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 22.7 | 21.3 | 20.4 | 19.2 | 17.5 | 16 | 14.2 | 12 | 8.9 | 6.2 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | Ketley 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 19.9 | 17.3 | 16.1 | 13.4 | 12.1 | 9.8 | 6.5 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | Ketley 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 19.9 | 15.8 | 11.6 | 8.2 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | Ketley 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 19.9 | 16.1 | 12.5 | 8.6 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | Ketley 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 19.9 | 16.1 | 12.7 | 10.1 | 7.1 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | KETLEY 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 21.3 | 17.5 | 16.2 | 13.6 | 12.2 | 9.9 | 6.6 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | KETLEY 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 21.3 | 15.9 | 11.7 | 8.3 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | KETLEY 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 21.3 | 16.3 | 12.6 | 8.6 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | KETLEY 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 21.3 | 16.3 | 12.8 | 10.2 | 7.2 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | LEATON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.9 | 3.9 | 3.9 | 3.9 | 3.8 | 3.6 | 3.5 | 3.1 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | LEATON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.9 | 3.9 | 3.8 | 3.6 | 3.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | LEATON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.9 | 3.9 | 3.8 | 3.7 | 3.5 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | LEATON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.9 | 3.9 | 3.9 | 3.7 | 3.5 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.4 | 5.4 | 5.3 | 5.3 | 5.2 | 5.1 | 5.1 | 4.9 | 4.7 | 4.6 | 4.4 | 4.3 | 4 | 3.8 | 3.6 | 3.4 | 3.1 | 1.6 | 0
Ironbr. & Shrewsb. 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.4 | 5.3 | 5.2 | 5.1 | 4.9 | 4.7 | 4.5 | 4.2 | 3.9 | 3.5 | 3.2 | 2.9 | 2.4 | 2.1 | 1.7 | 1.4 | 1.1 | 0 | 0
Ironbr. & Shrewsb. 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.4 | 5.3 | 5.3 | 5.2 | 5.1 | 5 | 4.8 | 4.5 | 4.2 | 3.8 | 3.5 | 3 | 2.6 | 2.2 | 1.8 | 1.4 | 1 | 0 | 0
Ironbr. & Shrewsb. 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.4 | 5.3 | 5.3 | 5.2 | 5 | 4.9 | 4.7 | 4.4 | 4.1 | 3.8 | 3.3 | 2.9 | 2.5 | 2 | 1.7 | 1.3 | 1 | 0 | 0
Ironbr. & Shrewsb. 132kV | MADELEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.4 | 2.2 | 1.7 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | MADELEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.4 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | MADELEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.4 | 1.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | MADELEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.4 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | MALEHURST 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.3 | 2 | 1.6 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | MALEHURST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.3 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | MALEHURST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.3 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | MALEHURST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.3 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | NEWPORT 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.3 | 1.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | NEWPORT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | NEWPORT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | NEWPORT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | PRIESTWESTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.1 | 1.1 | 1.1 | 1 | 1 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | PRIESTWESTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.1 | 1 | 1 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | PRIESTWESTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.1 | 1.1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | PRIESTWESTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.1 | 1.1 | 1 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | ROUSHILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 22.5 | 11.6 | 11.5 | 11.4 | 11.3 | 11.1 | 10.9 | 10.7 | 9.7 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | ROUSHILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 22.5 | 11.4 | 11.1 | 10.7 | 10.3 | 9.9 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | ROUSHILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 22.5 | 11.4 | 11.3 | 11.1 | 10.9 | 10.8 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | ROUSHILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 22.5 | 11.4 | 11.3 | 11.1 | 10.8 | 10.5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | ROWTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.3 | 2 | 1.6 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | ROWTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.3 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | ROWTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.3 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | ROWTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.3 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | SHIFNAL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.8 | 1.4 | 1.1 | 0.7 | 0.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | SHIFNAL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.8 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | SHIFNAL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.8 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | SHIFNAL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.8 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | Shrewsbury 132/33kVDUMMY | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 43.6 | 35.2 | 33.1 | 31 | 28.8 | 26.3 | 23.5 | 19.7 | 12 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | Shrewsbury 132/33kVDUMMY | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 43.6 | 33.7 | 29.6 | 25.1 | 21.2 | 16.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | Shrewsbury 132/33kVDUMMY | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 43.6 | 34.1 | 30.8 | 27.2 | 24.1 | 19.7 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | Shrewsbury 132/33kVDUMMY | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 43.6 | 34 | 30.8 | 27.1 | 23.4 | 19.2 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | SNEDSHILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7 | 6.5 | 6.3 | 5.3 | 5 | 4.1 | 3.2 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | SNEDSHILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7 | 6.2 | 5 | 4.4 | 3.5 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | SNEDSHILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7 | 6.3 | 5.1 | 3.9 | 2.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | SNEDSHILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7 | 6.3 | 5.1 | 4.6 | 3.8 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | SPRING GARDENS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.8 | 9.4 | 8.6 | 7.6 | 6.7 | 5.6 | 3.8 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | SPRING GARDENS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.8 | 8.8 | 7.2 | 5.2 | 3.7 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | SPRING GARDENS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.8 | 9 | 7.8 | 6.3 | 5.1 | 3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | SPRING GARDENS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.8 | 8.9 | 7.7 | 6.1 | 4.6 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | STAR ALUMINIUM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | STAR ALUMINIUM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | STAR ALUMINIUM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | STAR ALUMINIUM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | WEIR HILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.8 | 5.3 | 4.5 | 3.8 | 3.1 | 2.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | WEIR HILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.8 | 4.8 | 3.3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | WEIR HILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.8 | 4.9 | 3.6 | 2.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | WEIR HILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.8 | 4.8 | 3.7 | 2.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | WORFIELD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | WORFIELD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | WORFIELD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | WORFIELD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | BARTLEY GREEN 132 11kV SUBSTN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 11.8 | 1.7 | 1.4 | 1 | 0 | 0 | 6.6 | 6.1 | 5.2 | 4.5 | 3.9 | 3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | BARTLEY GREEN 132 11kV SUBSTN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 11.8 | 1 | 0 | 0 | 0 | 0 | 3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | BARTLEY GREEN 132 11kV SUBSTN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 11.8 | 1.2 | 0 | 0 | 0 | 0 | 5 | 3.8 | 2.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | BARTLEY GREEN 132 11kV SUBSTN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 11.8 | 1.1 | 0 | 0 | 0 | 0 | 4.3 | 3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Bournville 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 4.7 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Bournville 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 4.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Bournville 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 4.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Bournville 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 4.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Chad Valley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 30 | 29.3 | 28.6 | 27.4 | 25.1 | 23.9 | 21.6 | 20.3 | 18.3 | 16.6 | 14.5 | 12 | 8.9 | 5.9 | 2.9 | 0 | 0 | 0 | 0
Kitwell 132kV | Chad Valley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 30 | 28.3 | 26.4 | 22.3 | 18.7 | 16 | 11.8 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Chad Valley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 30 | 28.6 | 27.2 | 24.2 | 21 | 19.2 | 15.6 | 11.6 | 6.9 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Chad Valley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 30 | 28.5 | 27.1 | 24.7 | 21.9 | 19.9 | 16.3 | 12.9 | 8.6 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Halesowen 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 17.2 | 16.9 | 13.8 | 13.5 | 13.1 | 12.6 | 11.5 | 10.8 | 9.8 | 9 | 8.4 | 7.5 | 6.4 | 5.2 | 4 | 2.9 | 1.7 | 0 | 0
Kitwell 132kV | Halesowen 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 17.2 | 13.6 | 12.7 | 11.5 | 10.7 | 9.4 | 7.8 | 5.8 | 3.6 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Halesowen 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 17.2 | 13.8 | 12.9 | 12.1 | 11.3 | 10.3 | 8.9 | 7.4 | 5.7 | 4.1 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Halesowen 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 17.2 | 13.7 | 13 | 12.2 | 11.3 | 10.2 | 8.9 | 7.5 | 5.9 | 4.6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Hall Green 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 16.2 | 12.2 | 10.7 | 9.8 | 8.6 | 7.6 | 9.6 | 6.6 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Hall Green 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 16.2 | 10.6 | 7.5 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Hall Green 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 16.2 | 11.1 | 8.8 | 7.1 | 5.3 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Hall Green 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 16.2 | 10.9 | 8.5 | 6.4 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Highters Heath 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 46.3 | 45.9 | 45.5 | 45.1 | 42.8 | 33.3 | 9.5 | 6.6 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Highters Heath 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 46.3 | 45.2 | 43.9 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Highters Heath 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 46.3 | 45.4 | 44.6 | 39.9 | 13.9 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Highters Heath 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 46.3 | 45.3 | 44.6 | 40.6 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Longbridge 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 13.1 | 12.8 | 12.5 | 12.1 | 10.6 | 10 | 8.2 | 7.7 | 7 | 6.5 | 5.9 | 4.7 | 3 | 1.2 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Longbridge 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 13.1 | 12.4 | 11.4 | 10.1 | 8 | 6.5 | 4.9 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Longbridge 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 13.1 | 12.5 | 11.9 | 11.1 | 9.4 | 8.6 | 7.1 | 6 | 4.1 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Longbridge 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 13.1 | 12.5 | 11.8 | 10.8 | 8.9 | 7.9 | 6.4 | 5 | 2.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Rednal 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 13.9 | 13.5 | 13.4 | 13.2 | 12.6 | 12.2 | 11 | 11 | 10.8 | 9.6 | 9.1 | 8.1 | 6.8 | 5.4 | 4 | 2.5 | 0.8 | 0 | 0
Kitwell 132kV | Rednal 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 13.9 | 13.2 | 12.6 | 11.8 | 10.8 | 9.7 | 9.2 | 7.4 | 5.4 | 2.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Rednal 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 13.9 | 13.3 | 12.9 | 12.5 | 11.6 | 11.1 | 10.8 | 9.4 | 7.9 | 5.6 | 4.1 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Rednal 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 13.9 | 13.2 | 12.8 | 12.3 | 11.5 | 10.6 | 10.1 | 8.8 | 7.1 | 4.8 | 3.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Selly Oak 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 14.4 | 10.4 | 9.7 | 8.5 | 5.5 | 4.7 | 2.5 | 2.2 | 1.9 | 1.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Selly Oak 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 14.4 | 9.7 | 8.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Selly Oak 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 14.4 | 9.8 | 8.8 | 5.8 | 2.4 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Selly Oak 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 14.4 | 9.8 | 8.7 | 7.1 | 3 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 15.9 | 12.2 | 10.6 | 9.8 | 8.6 | 7.6 | 9.5 | 6.6 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 15.9 | 10.6 | 7.5 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 15.9 | 11.1 | 8.8 | 7.1 | 5.3 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitwell 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 15.9 | 10.9 | 8.5 | 6.4 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.7 | 6.6 | 6.5 | 6.3 | 6.1 | 5.8 | 5.2 | 4.7 | 4.1 | 3.6 | 2.6 | 1.9 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.7 | 6.4 | 5.8 | 5.2 | 4.6 | 3.9 | 2.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.7 | 6.4 | 6 | 5.4 | 4.9 | 3.4 | 2.4 | 1.7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.7 | 6.4 | 6.2 | 5.8 | 5.4 | 5 | 4.8 | 3.2 | 1.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 21 | 20.9 | 20.4 | 20 | 19.6 | 19.4 | 19.8 | 20 | 20.1 | 19.9 | 19.6 | 17.9 | 17.8 | 17.9 | 17.8 | 17.8 | 17.9 | 18.3 | 18.4
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 21 | 20.8 | 20.2 | 19.7 | 19.4 | 19.1 | 19.6 | 19.4 | 19.1 | 17.9 | 16.9 | 16.6 | 16.3 | 16.2 | 15.9 | 15.8 | 15.6 | 14.9 | 14.6
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 21 | 20.8 | 20.2 | 19.8 | 19.4 | 19.3 | 19.6 | 19.4 | 19.1 | 17 | 17.3 | 17.3 | 17.2 | 17.1 | 17 | 16.9 | 16.8 | 15.9 | 15.4
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 21 | 20.8 | 20.2 | 19.7 | 19.4 | 19.1 | 19.5 | 19.6 | 19.4 | 19.1 | 17.2 | 16.9 | 16.9 | 17 | 17 | 17 | 17.1 | 17.1 | 16.9
Lea Marston 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 36.3 | 36 | 35.8 | 35.5 | 35 | 34.5 | 33.4 | 32.7 | 31.6 | 30.6 | 29.7 | 28.5 | 26.9 | 21.1 | 15 | 8.4 | 1.7 | 0 | 0
Lea Marston 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 36.3 | 35.3 | 34.4 | 33.3 | 24.9 | 30.8 | 28.9 | 22.8 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 36.3 | 35.5 | 34.9 | 34.4 | 27.2 | 32.8 | 31.5 | 29.9 | 27.7 | 20 | 12.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 36.3 | 35.5 | 34.9 | 34.1 | 29.3 | 32.3 | 30.6 | 28.9 | 25 | 17.4 | 10.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.7 | 29.2 | 27.6 | 25.2 | 23.5 | 22.6 | 20.7 | 19.8 | 18.2 | 14.8 | 9 | 7.2 | 5.4 | 3.4 | 1.3 | 0 | 0 | 0 | 0
Lea Marston 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.7 | 27.9 | 23.8 | 20.7 | 17.9 | 15.5 | 12.1 | 7.4 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.7 | 28.2 | 24.3 | 21.4 | 18.7 | 17 | 13.9 | 11.1 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.7 | 28.1 | 24.2 | 22.1 | 19.5 | 17.5 | 14.6 | 12 | 8.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | CHELMSLEY WOOD | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 16.7 | 16.4 | 14.8 | 14.5 | 14.1 | 13.7 | 12.5 | 12.3 | 11.9 | 11.6 | 11 | 10 | 8.7 | 7.3 | 5.8 | 3.3 | 0.9 | 0 | 0
Lea Marston 132kV | CHELMSLEY WOOD | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 16.7 | 16 | 13.8 | 12.5 | 11.6 | 10.5 | 9.9 | 7.6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | CHELMSLEY WOOD | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 16.7 | 16.1 | 14.1 | 13.4 | 12.8 | 12.1 | 11.4 | 9.6 | 7.5 | 5.5 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | CHELMSLEY WOOD | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 16.7 | 16 | 14.1 | 13.4 | 12.8 | 12.1 | 11.5 | 9.9 | 8 | 6.2 | 4.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Copt Heath 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 39.6 | 37.5 | 37 | 33.8 | 32.9 | 32 | 41.5 | 41.3 | 40.8 | 40.6 | 40.2 | 39.5 | 38.2 | 37 | 35.9 | 34.9 | 34 | 28.7 | 25.1
Lea Marston 132kV | Copt Heath 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 39.5 | 36.2 | 31.9 | 29.7 | 27.7 | 25.3 | 39.6 | 38.6 | 37.2 | 35.8 | 34.8 | 33.5 | 31.8 | 30.3 | 29.3 | 28.4 | 27.4 | 20.6 | 0
Lea Marston 132kV | Copt Heath 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 39.5 | 36.4 | 32.4 | 30.7 | 29 | 26.8 | 40.4 | 39.5 | 38.3 | 37.5 | 36.6 | 35.4 | 33.9 | 32.6 | 31.4 | 30.1 | 28.8 | 24.6 | 0
Lea Marston 132kV | Copt Heath 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 39.5 | 36.3 | 32.5 | 30.9 | 29.2 | 27.3 | 40.2 | 39.4 | 38.1 | 37.2 | 36.3 | 34.9 | 33.4 | 32.4 | 31.3 | 30.3 | 29.2 | 25.5 | 23.4
Lea Marston 132kV | Elmdon 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 17.8 | 17.7 | 17.4 | 15.8 | 14.7 | 13.6 | 16.9 | 16.3 | 16.1 | 16 | 15.8 | 15.3 | 15 | 14.6 | 14.2 | 11.1 | 5.1 | 0 | 0
Lea Marston 132kV | Elmdon 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 17.7 | 15.9 | 12.9 | 10.4 | 8 | 5.3 | 15.1 | 14.3 | 13.5 | 12.7 | 11.9 | 10.9 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Elmdon 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 17.7 | 16.1 | 13.1 | 10.8 | 8.4 | 5.2 | 14.5 | 14 | 13.5 | 13 | 12 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Elmdon 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 17.7 | 16.1 | 13.5 | 11.5 | 9.3 | 6.7 | 15.1 | 14.6 | 14.1 | 13.7 | 13.2 | 12.5 | 10.9 | 5.4 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Hams Hall South 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 19.5 | 19.3 | 18.8 | 18.1 | 6.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Hams Hall South 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 19.5 | 19 | 18.3 | 17.4 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Hams Hall South 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 19.5 | 19 | 18.4 | 17.4 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Hams Hall South 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 19.5 | 19 | 18.4 | 17.6 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Kitts Green 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 38.4 | 38 | 37.7 | 37.3 | 35.6 | 36.2 | 35.5 | 34.8 | 33.5 | 32.6 | 31.8 | 30.6 | 27.1 | 21.1 | 14.9 | 8.4 | 1.7 | 0 | 0
Lea Marston 132kV | Kitts Green 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 38.4 | 37.2 | 36.1 | 34.7 | 24.9 | 31.9 | 30.5 | 22.8 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Kitts Green 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 38.4 | 37.4 | 36.8 | 35.9 | 27.2 | 34.3 | 33.4 | 31.8 | 27.6 | 20 | 12.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Kitts Green 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 38.4 | 37.4 | 36.7 | 35.7 | 29.3 | 33.8 | 32.6 | 30.8 | 25 | 17.4 | 10.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 28.4 | 27.9 | 27.6 | 27.5 | 27.4 | 27.3 | 27.3 | 27.1 | 26.9 | 26.7 | 26.5 | 26.2 | 25.7 | 25.3 | 24.8 | 24.3 | 23.7 | 12.8 | 6.5
Lea Marston 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 28.4 | 27.7 | 27.4 | 27.1 | 26.8 | 26.6 | 26.3 | 25.7 | 25 | 24.3 | 23.8 | 23 | 22.1 | 20.2 | 9.8 | 3.6 | 0 | 0 | 0
Lea Marston 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 28.4 | 27.8 | 27.5 | 27.3 | 27.1 | 26.8 | 26.7 | 26.2 | 25.7 | 25.3 | 24.7 | 23.9 | 21 | 15.4 | 9.3 | 3.3 | 0 | 0 | 0
Lea Marston 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 28.4 | 27.8 | 27.4 | 27.2 | 27 | 26.8 | 26.5 | 26.1 | 25.6 | 25.1 | 24.6 | 23.9 | 23.2 | 22.6 | 20.6 | 13.4 | 5.1 | 0 | 0
Lea Marston 132kV | Solihull 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 19.4 | 18.2 | 17.5 | 15.9 | 14.8 | 13.6 | 36.2 | 35.5 | 34.3 | 33.5 | 32.7 | 31.1 | 29.3 | 27.5 | 25.4 | 23.5 | 21.7 | 12.5 | 6.5
Lea Marston 132kV | Solihull 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 19.1 | 16 | 13 | 10.5 | 8.1 | 5.3 | 31.5 | 28.7 | 25.4 | 22.2 | 19.2 | 15 | 10.7 | 7 | 3.7 | 0.6 | 0 | 0 | 0
Lea Marston 132kV | Solihull 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 19.1 | 16.3 | 13.2 | 10.8 | 8.5 | 5.2 | 32.2 | 30.1 | 27.7 | 25.3 | 22.8 | 19.4 | 15.7 | 12.2 | 8.6 | 4.7 | 0 | 0 | 0
Lea Marston 132kV | Solihull 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 19.1 | 16.2 | 13.6 | 11.5 | 9.3 | 6.7 | 32.7 | 30.9 | 28.5 | 26.5 | 24.3 | 21.2 | 18.6 | 16.3 | 14 | 12.2 | 10.2 | 0 | 0
Lea Marston 132kV | Sutton Coldfield 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 36.3 | 32.2 | 31.8 | 31.3 | 30.5 | 29.8 | 28.4 | 27.6 | 26.2 | 25.1 | 24 | 22.3 | 20 | 17.7 | 15.4 | 13.3 | 11.2 | 0 | 0
Lea Marston 132kV | Sutton Coldfield 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 36.3 | 31.3 | 30 | 28.4 | 26.8 | 25 | 22.6 | 19 | 15.1 | 11.1 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Sutton Coldfield 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 36.3 | 31.5 | 30.5 | 29.5 | 28.2 | 27.1 | 25.2 | 22.8 | 19.8 | 17.1 | 14.2 | 11.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Sutton Coldfield 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 36.3 | 31.5 | 30.5 | 29.3 | 28 | 26.6 | 24.4 | 22.1 | 19.1 | 16.4 | 13.5 | 10 | 7.1 | 4.4 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 35.4 | 32.4 | 30.1 | 19.5 | 17.5 | 14.8 | 3.2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 35.4 | 31.3 | 18.3 | 14.1 | 9.4 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 35.4 | 31.7 | 19.2 | 15 | 11.2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 35.4 | 31.6 | 19.7 | 17 | 13.4 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.6 | 10.1 | 8.5 | 7.5 | 6.5 | 5.2 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.6 | 9.6 | 6.9 | 4.6 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.6 | 9.7 | 7.3 | 5.2 | 3.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.6 | 9.7 | 7.7 | 6.2 | 4.6 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 11.3 | 11 | 10.8 | 10.4 | 10.1 | 9.6 | 8.9 | 8.4 | 7.4 | 6.7 | 5.8 | 4.6 | 3.4 | 2.1 | 0.9 | 0 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 11.3 | 10.4 | 9.6 | 8.2 | 7 | 5.7 | 4.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 11.3 | 10.6 | 10.1 | 9.1 | 8.4 | 7.6 | 6.4 | 5 | 3.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 10.5 | 10.1 | 9.3 | 8.5 | 7.7 | 6.6 | 5.2 | 3.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 24.5 | 24.4 | 24.2 | 24 | 23.8 | 23.5 | 22 | 20.6 | 18.7 | 17.3 | 15.2 | 12.7 | 10.5 | 8.5 | 6.4 | 4.6 | 2.7 | 0 | 0
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 24.5 | 24.1 | 23.5 | 22.4 | 19.9 | 17.1 | 13.5 | 9.6 | 5.9 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 24.5 | 24.2 | 23.7 | 23.1 | 21.3 | 18.2 | 15.2 | 12.7 | 9.8 | 6.6 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 24.5 | 24.2 | 23.9 | 23.5 | 22.5 | 20.6 | 18.9 | 15.3 | 11.9 | 8.9 | 5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.5 | 9.3 | 9.3 | 9.3 | 9.3 | 9.2 | 9 | 8.8 | 8.6 | 8.4 | 8.2 | 7.9 | 7.5 | 7 | 6.6 | 6.2 | 5.8 | 3.9 | 2.3
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.5 | 9.2 | 9.1 | 8.9 | 8.7 | 8.5 | 8.1 | 7.6 | 7 | 6.3 | 5.9 | 5.4 | 4.9 | 4.4 | 3.9 | 3.4 | 2.8 | 0 | 0
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.5 | 9.3 | 9.2 | 9.1 | 9 | 8.9 | 8.6 | 8.3 | 7.8 | 7.3 | 6.8 | 6.2 | 5.4 | 4.7 | 4 | 3.3 | 2.7 | 0 | 0
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.5 | 9.3 | 9.2 | 9 | 8.8 | 8.7 | 8.3 | 7.9 | 7.5 | 7 | 6.5 | 5.9 | 5.3 | 4.7 | 4.1 | 3.6 | 3.3 | 1.7 | 0.8
Nechells 132kV | Bordesley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 51.5 | 51.1 | 49.2 | 46.6 | 43 | 40.2 | 35.5 | 33.1 | 30.6 | 27.8 | 24.5 | 23.3 | 21.9 | 20.5 | 18.9 | 17 | 14.2 | 7.4 | 5.6
Nechells 132kV | Bordesley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 51.5 | 50.9 | 48.8 | 44.4 | 40.7 | 37.2 | 31.6 | 26.9 | 21.6 | 14.9 | 8.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Bordesley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 51.5 | 50.9 | 49 | 45.8 | 42.3 | 39.8 | 33.8 | 29 | 23.7 | 16.5 | 12 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Bordesley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 51.5 | 50.9 | 48.8 | 45.7 | 42 | 38.8 | 33.3 | 29.8 | 26 | 21.6 | 17.4 | 14.9 | 12.5 | 10.1 | 7.8 | 5 | 3.2 | 0 | 0
Nechells 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 36.3 | 36 | 35.8 | 35.5 | 35 | 34.5 | 33.4 | 32.7 | 31.6 | 30.6 | 29.7 | 28.5 | 26.9 | 25.2 | 23.6 | 20.7 | 17.4 | 0 | 0
Nechells 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 36.3 | 35.3 | 34.4 | 33.3 | 32.2 | 30.8 | 28.9 | 26.2 | 18.7 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 36.3 | 35.5 | 34.9 | 34.4 | 33.5 | 32.8 | 31.5 | 29.9 | 27.8 | 19.1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 36.3 | 35.5 | 34.9 | 34.1 | 33.2 | 32.3 | 30.6 | 28.9 | 26.7 | 23.3 | 17.1 | 8.3 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.7 | 29.2 | 27.6 | 25.2 | 23.5 | 22.6 | 20.7 | 19.8 | 18.2 | 14.8 | 9 | 7.2 | 5.4 | 3.4 | 1.3 | 0 | 0 | 0 | 0
Nechells 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.7 | 27.9 | 23.8 | 20.7 | 17.9 | 15.5 | 12.1 | 7.4 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.7 | 28.2 | 24.3 | 21.4 | 18.7 | 17 | 13.9 | 11.1 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.7 | 28.1 | 24.2 | 22.1 | 19.5 | 17.5 | 14.6 | 12 | 8.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Cheapside 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 39.7 | 33.6 | 32.3 | 30.1 | 27.4 | 25.9 | 23.7 | 23.6 | 23.4 | 21.5 | 20.7 | 18.3 | 16.1 | 14.3 | 12.8 | 11.8 | 11 | 0 | 0
Nechells 132kV | Cheapside 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 39.7 | 33.3 | 31.8 | 27 | 24.4 | 22.5 | 19.6 | 17.9 | 15.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Cheapside 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 39.7 | 33.4 | 32.2 | 28 | 25.5 | 24.4 | 20.6 | 18.3 | 16.2 | 12.3 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Cheapside 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 39.7 | 33.3 | 31.8 | 29.2 | 26.5 | 24.7 | 21 | 19.3 | 16.8 | 12.9 | 10.5 | 7 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Chester Street 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 19.3 | 19 | 18.8 | 18.5 | 17.5 | 16.9 | 16.4 | 16.1 | 15.6 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Chester Street 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 19.3 | 18.7 | 18.2 | 17.6 | 16.5 | 15.5 | 14.7 | 13.5 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Chester Street 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 19.3 | 18.8 | 18.4 | 17.9 | 16.7 | 16.1 | 15.3 | 14.3 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Chester Street 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 19.3 | 18.7 | 18.2 | 17.7 | 16.5 | 15.5 | 14.6 | 13.7 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | ERDINGTON 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.6 | 29.1 | 27.5 | 25.1 | 23.4 | 22.6 | 20.6 | 19.7 | 18.1 | 14.7 | 9 | 7.2 | 5.3 | 3.4 | 1.3 | 0 | 0 | 0 | 0
Nechells 132kV | ERDINGTON 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.6 | 27.8 | 23.7 | 20.6 | 17.8 | 15.4 | 12 | 7.3 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | ERDINGTON 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.6 | 28.1 | 24.3 | 21.4 | 18.6 | 16.9 | 13.8 | 11.1 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | ERDINGTON 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.6 | 28 | 24.1 | 22 | 19.5 | 17.5 | 14.5 | 11.9 | 8.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Hockley 132/11kv | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 25.3 | 14.9 | 12.7 | 10.2 | 6.3 | 4.2 | 32.2 | 29.2 | 26 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Hockley 132/11kv | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 25.3 | 14.1 | 11.5 | 8.5 | 4.4 | 1.6 | 26.6 | 19.7 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Hockley 132/11kv | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 25.3 | 14.2 | 11.9 | 9.4 | 5.2 | 3.2 | 29.1 | 23.7 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Hockley 132/11kv | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 25.3 | 14.1 | 11.3 | 8.1 | 3.5 | 0.5 | 24 | 18.9 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Nechells West 132/25/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 44.7 | 44.3 | 44 | 43.6 | 42.5 | 41.9 | 41.6 | 41.2 | 40.5 | 39.9 | 39.3 | 38.3 | 37.2 | 36.1 | 35.1 | 34.2 | 33.1 | 27.2 | 22.8
Nechells 132kV | Nechells West 132/25/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 44.7 | 43.8 | 43 | 42 | 40.5 | 39.2 | 38.4 | 36.4 | 34.2 | 32 | 30.1 | 27.8 | 25.2 | 22.9 | 20.7 | 18.5 | 16.5 | 9.6 | 6.4
Nechells 132kV | Nechells West 132/25/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 44.7 | 43.9 | 43.4 | 42.8 | 41.2 | 40.5 | 39.8 | 38.5 | 36.9 | 35.3 | 33.9 | 32.1 | 29.7 | 27.4 | 25.3 | 23.1 | 21 | 12.5 | 7.8
Nechells 132kV | Nechells West 132/25/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 44.7 | 43.8 | 43.1 | 42.3 | 40.8 | 39.4 | 38.6 | 37.3 | 35.6 | 34 | 32.4 | 30.3 | 28.6 | 26.8 | 25.3 | 23.8 | 22.4 | 17.4 | 14.9
Nechells 132kV | Sparkbrook 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 25.9 | 25.4 | 24.8 | 23.5 | 22.1 | 21.2 | 18.6 | 17.7 | 16.2 | 14.4 | 13 | 11.3 | 9.5 | 7.6 | 5.7 | 3.9 | 2 | 0 | 0
Nechells 132kV | Sparkbrook 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 25.9 | 24.4 | 23 | 18.2 | 15.4 | 12.8 | 8.3 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Sparkbrook 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 25.9 | 24.7 | 23.7 | 19.8 | 17.6 | 15.8 | 12 | 9.2 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Sparkbrook 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 25.9 | 24.5 | 23.4 | 20.9 | 18.8 | 17 | 13.5 | 11.1 | 8.1 | 4.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Summer Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 21.2 | 20.9 | 20.6 | 20.3 | 19.2 | 18.4 | 17.5 | 17 | 16.3 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Summer Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 21.2 | 20.7 | 20.3 | 19.9 | 18.8 | 17.7 | 17 | 15.9 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Summer Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 21.2 | 20.7 | 20.4 | 20 | 18.7 | 18.1 | 17.4 | 16.8 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Summer Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 21.2 | 20.7 | 20.3 | 19.8 | 18.7 | 17.5 | 16.6 | 15.8 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ocker Hill 132kV | Black Lake 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 13.3 | 11.8 | 11.6 | 11.3 | 11 | 10.7 | 9.7 | 9.5 | 9.2 | 8.7 | 8.3 | 7.8 | 7.2 | 6.6 | 5.7 | 5 | 4.4 | 0.8 | 0
Ocker Hill 132kV | Black Lake 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 13.3 | 11.4 | 10.7 | 9.8 | 9.2 | 8.6 | 8.1 | 6.9 | 5.6 | 4.2 | 3.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ocker Hill 132kV | Black Lake 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 13.3 | 11.5 | 10.9 | 10.4 | 9.9 | 9.4 | 9.1 | 8.5 | 7.5 | 6.7 | 5.4 | 3.9 | 2.4 | 0.8 | 0 | 0 | 0 | 0 | 0
Ocker Hill 132kV | Black Lake 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 13.3 | 11.5 | 10.8 | 10.1 | 9.5 | 9 | 8.6 | 7.9 | 6.9 | 6.1 | 5.2 | 4.1 | 2.8 | 1.8 | 0.9 | 0 | 0 | 0 | 0
Ocker Hill 132kV | Ocker Hill B 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ocker Hill 132kV | Ocker Hill B 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ocker Hill 132kV | Ocker Hill B 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ocker Hill 132kV | Ocker Hill B 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ocker Hill 132kV | OCKER HILL B 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3
Ocker Hill 132kV | OCKER HILL B 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 29.8 | 25.5
Ocker Hill 132kV | OCKER HILL B 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 28.6
Ocker Hill 132kV | OCKER HILL B 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 30.3
Oldbury 132kV | Birchfield Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 5.7 | 4.6 | 4.3 | 3.9 | 3.5 | 3 | 2.7 | 1.9 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Oldbury 132kV | Birchfield Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 5.7 | 4 | 3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Oldbury 132kV | Birchfield Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 5.7 | 4.2 | 3.4 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Oldbury 132kV | Birchfield Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 5.7 | 4.1 | 3.3 | 2.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Oldbury 132kV | Oldbury B 11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 12.5 | 12.3 | 12.2 | 12 | 11.8 | 11.6 | 11.2 | 10.8 | 10.2 | 9.8 | 9.4 | 8.9 | 8.3 | 7.7 | 7.2 | 6.7 | 6.1 | 2.7 | 0
Oldbury 132kV | Oldbury B 11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 12.5 | 12 | 11.5 | 10.8 | 10.3 | 9.7 | 8.9 | 7.7 | 6.6 | 5.4 | 4.4 | 2.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Oldbury 132kV | Oldbury B 11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 12.5 | 12.1 | 11.6 | 11.1 | 10.7 | 10.2 | 9.5 | 8.8 | 7.7 | 6.8 | 5.8 | 4.4 | 2.7 | 1.1 | 0 | 0 | 0 | 0 | 0
Oldbury 132kV | Oldbury B 11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 12.5 | 12 | 11.6 | 11.1 | 10.5 | 9.9 | 9.3 | 8.5 | 7.7 | 6.9 | 5.9 | 4.7 | 3.7 | 2.7 | 1.8 | 0.9 | 0 | 0 | 0
Oldbury 132kV | Tividale 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 41.8 | 41.5 | 41.5 | 41.4 | 41.2 | 40.8 | 40 | 39.5 | 38.7 | 38.2 | 37.8 | 37.2 | 36.6 | 35.9 | 35.2 | 34.7 | 34 | 25.8 | 10.2
Oldbury 132kV | Tividale 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 41.8 | 41.1 | 40.2 | 39.1 | 38.6 | 37.7 | 36.8 | 35.4 | 34.1 | 32.7 | 31.3 | 29.4 | 19.7 | 10.9 | 2.8 | 0 | 0 | 0 | 0
Oldbury 132kV | Tividale 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 41.8 | 41.2 | 40.5 | 39.9 | 39.2 | 38.8 | 38 | 37.3 | 36.4 | 35.6 | 34.7 | 32.9 | 30.9 | 24 | 15.1 | 6.4 | 0 | 0 | 0
Oldbury 132kV | Tividale 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 41.8 | 41.2 | 40.4 | 39.5 | 39 | 38.2 | 37.4 | 36.6 | 35.7 | 34.8 | 33.8 | 32.5 | 31.4 | 30.3 | 27.4 | 22.5 | 17.6 | 1.8 | 0
Penn 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.1 | 6.9 | 6.8 | 6.6 | 6.4 | 6 | 3.3 | 3 | 2.6 | 2.3 | 2 | 1.6 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0
Penn 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.1 | 6.8 | 6.4 | 6.1 | 5.6 | 4.8 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.1 | 6.8 | 6.5 | 6 | 5.6 | 4.8 | 2.1 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.1 | 6.8 | 6.5 | 6.1 | 5.7 | 4.9 | 2.2 | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Coseley 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 13.5 | 13.1 | 12.7 | 12.1 | 11.5 | 10.8 | 8.8 | 8.4 | 7.9 | 7.3 | 6.4 | 5.3 | 3.7 | 2.1 | 0.5 | 0 | 0 | 0 | 0
Penn 132kV | Coseley 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 13.5 | 12.5 | 11.2 | 9.8 | 8.8 | 7.6 | 6.1 | 3.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Coseley 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 13.5 | 12.7 | 11.6 | 10.6 | 9.9 | 9.2 | 8 | 6 | 3.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Coseley 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 13.5 | 12.6 | 11.6 | 10.5 | 9.7 | 8.8 | 7.5 | 5.7 | 3.5 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Dudley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 10.6 | 10.2 | 9.7 | 9.2 | 8.5 | 7.8 | 6 | 4.9 | 3.3 | 2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Dudley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 10.6 | 9.4 | 7.9 | 6.3 | 4.8 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Dudley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 10.6 | 9.6 | 8.3 | 7.2 | 5.8 | 4.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Dudley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 10.6 | 9.6 | 8.5 | 7.3 | 5.9 | 4.2 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Hinksford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 5.7 | 5.1 | 4.8 | 4.4 | 3.9 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Hinksford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 5.7 | 4.4 | 3.2 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Hinksford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 5.7 | 4.5 | 3.6 | 2.6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Hinksford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 5.7 | 4.5 | 3.7 | 2.4 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | HINKSFORD 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 25.9 | 25.9 | 25.9 | 25.9 | 25.9 | 25.9 | 24.7 | 24.8 | 24.8 | 24.8 | 24.8 | 25.8 | 25.8 | 25.9 | 26 | 26.1 | 26.3 | 22.4 | 12.9
Penn 132kV | HINKSFORD 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 25.9 | 25.9 | 25.9 | 25.9 | 25.9 | 26 | 25.8 | 25.9 | 26 | 26.2 | 26.3 | 26.5 | 24.8 | 20.9 | 17.1 | 13.6 | 10.2 | 0 | 0
Penn 132kV | HINKSFORD 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 25.9 | 25.9 | 25.9 | 25.9 | 25.9 | 25.9 | 24.8 | 25.8 | 25.9 | 25.9 | 26 | 26.2 | 26.4 | 25.4 | 21.2 | 16.8 | 12.7 | 0 | 0
Penn 132kV | HINKSFORD 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 25.9 | 25.9 | 25.9 | 25.9 | 25.9 | 26 | 25.8 | 25.8 | 25.9 | 26 | 26.1 | 26.2 | 26.4 | 26.6 | 25.6 | 22.8 | 20.1 | 10.8 | 7.1
Penn 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.7 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.3 | 2.3 | 2.2 | 2.2 | 2.2 | 2 | 1.9 | 1.7 | 1.5 | 1.4 | 1.3 | 0 | 0
Penn 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.7 | 2.6 | 2.5 | 2.5 | 2.4 | 2.4 | 1.9 | 1.8 | 1.6 | 1.4 | 1.2 | 1 | 0.8 | 0.5 | 0 | 0 | 0 | 0 | 0
Penn 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.7 | 2.6 | 2.6 | 2.6 | 2.5 | 2.4 | 2.1 | 2 | 1.8 | 1.7 | 1.6 | 1.4 | 1.1 | 0.9 | 0.7 | 0 | 0 | 0 | 0
Penn 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.7 | 2.6 | 2.5 | 2.5 | 2.5 | 2.4 | 2 | 1.9 | 1.7 | 1.6 | 1.5 | 1.3 | 1.1 | 0.9 | 0.7 | 0.5 | 0 | 0 | 0
Penn 132kV | Lye 11kV DUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 3.8 | 3.4 | 3.2 | 2.9 | 2.6 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Lye 11kV DUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 3.8 | 3 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Lye 11kV DUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 3.8 | 3.1 | 2.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Lye 11kV DUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 3.8 | 3.1 | 2.6 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | PATTINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.9 | 15.6 | 15.4 | 15.3 | 15 | 14.5 | 14.2 | 13.7 | 13.2 | 12.8 | 12.5 | 11.9 | 11.1 | 10.3 | 9.6 | 8.8 | 7.9 | 3.9 | 0.8
Penn 132kV | PATTINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.9 | 15.4 | 15 | 14.6 | 14 | 13.1 | 12.5 | 11.4 | 10.3 | 9.2 | 8.4 | 7.5 | 6.3 | 5.3 | 4.4 | 3.6 | 2.9 | 0 | 0
Penn 132kV | PATTINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.9 | 15.4 | 15.1 | 14.6 | 14.1 | 13.2 | 12.7 | 11.9 | 11 | 10.2 | 9.4 | 8.1 | 6.9 | 5.9 | 4.9 | 3.9 | 3 | 0 | 0
Penn 132kV | PATTINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.9 | 15.4 | 15.1 | 14.7 | 14.2 | 13.2 | 12.7 | 11.8 | 10.8 | 9.9 | 9 | 7.9 | 6.8 | 5.6 | 4.6 | 3.6 | 2.8 | 0 | 0
Penn 132kV | Wolverhampton West 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 2.7 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Wolverhampton West 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Wolverhampton West 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Wolverhampton West 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | WOLVERHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 53.7 | 52.9 | 52.4 | 51.8 | 50.8 | 49.6 | 46.9 | 45.2 | 42.7 | 41 | 39 | 36.4 | 32.8 | 29.2 | 25.7 | 22.4 | 19 | 0 | 0
Penn 132kV | WOLVERHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 53.7 | 51.8 | 50 | 47.5 | 45.3 | 42.4 | 38 | 32.3 | 26.1 | 20.2 | 15.5 | 9.7 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | WOLVERHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 53.7 | 52.1 | 50.8 | 48.9 | 47.3 | 44.7 | 41.3 | 37.4 | 32.8 | 28.9 | 24.8 | 18.9 | 12.3 | 6.1 | 0 | 0 | 0 | 0 | 0
Penn 132kV | WOLVERHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 53.7 | 52 | 50.7 | 49 | 47.1 | 44.6 | 40.7 | 36.7 | 31.9 | 28 | 23.6 | 18.5 | 13.8 | 9 | 4.7 | 0.6 | 0 | 0 | 0
Penn 132kV | Woodside 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 16 | 15.6 | 15.6 | 15.5 | 15.3 | 14.7 | 13.1 | 12.6 | 11.6 | 10.7 | 9.7 | 8.4 | 7 | 5.6 | 4.1 | 2.7 | 1.4 | 0 | 0
Penn 132kV | Woodside 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 16 | 15 | 14.2 | 13.4 | 12.6 | 11.1 | 8.8 | 6.5 | 3.4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Woodside 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 16 | 15.1 | 14.6 | 13.9 | 13.3 | 12.2 | 10.1 | 8.5 | 6.2 | 4.3 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penn 132kV | Woodside 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 16 | 15.1 | 14.6 | 13.9 | 13 | 11.5 | 9.6 | 8.1 | 5.9 | 3.8 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ALDERTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4 | 3.9 | 3.9 | 3.8 | 3.7 | 3.7 | 3.7 | 3.6 | 2.9 | 2.7 | 2.4 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ALDERTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 3 | 2.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ALDERTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4 | 3.8 | 3.8 | 3.7 | 3.6 | 3.5 | 2.5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ALDERTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4 | 3.8 | 3.7 | 3.6 | 3.5 | 3.3 | 3.2 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BILSON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BILSON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BILSON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BILSON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BISHOPS CLEEVE 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 4.7 | 4.1 | 3.6 | 2.8 | 2 | 3.3 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BISHOPS CLEEVE 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 4.6 | 3.5 | 2.4 | 1.6 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BISHOPS CLEEVE 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 4.6 | 3.7 | 3.1 | 2.2 | 1.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BISHOPS CLEEVE 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 4.6 | 3.6 | 2.7 | 1.6 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BIXHEAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.9 | 8.5 | 8.4 | 8.2 | 7.9 | 7.5 | 3.3 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BIXHEAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.9 | 8.3 | 7.8 | 7.2 | 6.5 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BIXHEAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.9 | 8.4 | 8.1 | 7.8 | 7.4 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BIXHEAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.9 | 8.3 | 8.1 | 7.6 | 7 | 6.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BROCKWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.5 | 4.2 | 4 | 3.9 | 3.7 | 3.3 | 2.4 | 2.1 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BROCKWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.5 | 4 | 3.6 | 3.1 | 2.6 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BROCKWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.5 | 4.1 | 3.8 | 3.2 | 2.7 | 2.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BROCKWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.5 | 4 | 3.7 | 3.4 | 3 | 2.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | CASTLE MEADS 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 18.5 | 17.5 | 15.8 | 8.8 | 6.9 | 3.5 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | CASTLE MEADS 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 18.5 | 16.4 | 7.9 | 4.5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | CASTLE MEADS 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 18.5 | 16.7 | 8.8 | 4.8 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | CASTLE MEADS 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 18.5 | 16.5 | 8.6 | 5.8 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Cheltenham 132/66/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 12.7 | 11.5 | 11.4 | 11.2 | 11 | 10.5 | 8.6 | 7.8 | 6.3 | 5.8 | 4.7 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Cheltenham 132/66/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 12.7 | 11.2 | 10.6 | 9.9 | 9.2 | 7.8 | 5.5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Cheltenham 132/66/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 12.7 | 11.3 | 10.9 | 10.1 | 9.3 | 8.4 | 5.4 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Cheltenham 132/66/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 12.7 | 11.3 | 10.9 | 10.3 | 9.6 | 8.5 | 6.2 | 4.2 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | CHELTENHAM 66kV S STN | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 43.6 | 41.5 | 40.9 | 40.4 | 39.6 | 38.8 | 36.2 | 35.2 | 34 | 33 | 31.7 | 30 | 28.3 | 26.7 | 24.7 | 23.6 | 22.5 | 15.3 | 7.6
Port Ham 132kV | CHELTENHAM 66kV S STN | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 43.6 | 41.4 | 40.3 | 39.2 | 38.4 | 37.2 | 35.2 | 33.1 | 30.4 | 27.8 | 24.8 | 21.9 | 19.5 | 17.5 | 15.3 | 12.4 | 9.8 | 0 | 0
Port Ham 132kV | CHELTENHAM 66kV S STN | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 43.6 | 41.4 | 40.5 | 39.9 | 39 | 38 | 35.9 | 33.5 | 31.1 | 29 | 26.5 | 24.1 | 21.7 | 19.5 | 17.4 | 15.7 | 14 | 0 | 0
Port Ham 132kV | CHELTENHAM 66kV S STN | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 43.6 | 41.4 | 40.4 | 39.4 | 38.4 | 37.2 | 34.9 | 33.5 | 31.1 | 29.5 | 26.5 | 23.4 | 21 | 19 | 17.2 | 15.7 | 14.2 | 5.5 | 1.6
Port Ham 132kV | COMMERCIAL RD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.1 | 4.8 | 4.4 | 4 | 3.5 | 3 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | COMMERCIAL RD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.1 | 4.2 | 3.4 | 2.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | COMMERCIAL RD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.1 | 4.4 | 3.7 | 2.8 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | COMMERCIAL RD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.1 | 4.3 | 3.7 | 2.9 | 2.1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Eastern Avenue 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 17.8 | 17.7 | 17.5 | 17.5 | 17.4 | 17.2 | 17.1 | 16.9 | 16.4 | 16.3 | 14.9 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Eastern Avenue 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 17.8 | 17.5 | 17.2 | 16.9 | 16.7 | 15.9 | 16 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Eastern Avenue 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 17.8 | 17.6 | 17.3 | 17.2 | 17 | 16.8 | 16.3 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Eastern Avenue 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 17.8 | 17.6 | 17.3 | 17.1 | 16.9 | 16.6 | 16.3 | 12.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ELTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.3 | 2.2 | 2.2 | 2.1 | 2 | 1.9 | 1.8 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ELTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.3 | 2.1 | 2 | 1.9 | 1.7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ELTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.3 | 2.2 | 2.1 | 2.1 | 2 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ELTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.3 | 2.2 | 2.1 | 2 | 1.8 | 1.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | HEREFORD 132kV S STN | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 55.3 | 48.5 | 47.3 | 45.9 | 45.1 | 43.2 | 38.8 | 35.9 | 33.1 | 30.9 | 28.7 | 25.5 | 21.5 | 17.4 | 13.5 | 10.1 | 6.5 | 0 | 0
Port Ham 132kV | HEREFORD 132kV S STN | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 55.3 | 47.2 | 44.5 | 41.2 | 38.6 | 34.4 | 27.4 | 21.7 | 15 | 8.5 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | HEREFORD 132kV S STN | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 55.3 | 47.6 | 45.6 | 42.7 | 41 | 36.5 | 32.6 | 28.4 | 22.8 | 18.1 | 12.9 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | HEREFORD 132kV S STN | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 55.3 | 47.5 | 45.5 | 43 | 40.5 | 37.4 | 30.3 | 26.4 | 21.2 | 16.4 | 11.2 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Hereford Central 66/11kv | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.3 | 16.1 | 15.9 | 15.7 | 15.4 | 15 | 14.5 | 14.2 | 13.7 | 13.2 | 12.8 | 12.1 | 11.3 | 10.6 | 9.2 | 6.3 | 3.1 | 0 | 0
Port Ham 132kV | Hereford Central 66/11kv | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.3 | 15.7 | 15.1 | 14.3 | 13.6 | 12.7 | 11.8 | 10.5 | 8.8 | 5.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Hereford Central 66/11kv | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.3 | 15.7 | 15.3 | 14.8 | 14.4 | 13.8 | 13.3 | 12.5 | 11.2 | 10.2 | 8.8 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Hereford Central 66/11kv | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.3 | 15.7 | 15.3 | 14.8 | 14.1 | 13.4 | 12.6 | 11.8 | 10.7 | 9.4 | 7.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | HEREFORD NORTH 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.5 | 6.3 | 5.8 | 5.3 | 5.1 | 4.6 | 2.9 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | HEREFORD NORTH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.5 | 6 | 5.1 | 4.2 | 3.4 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | HEREFORD NORTH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.5 | 6.1 | 5.4 | 4.3 | 3.8 | 1.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | HEREFORD NORTH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.5 | 6.1 | 5.4 | 4.6 | 4 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | HEREFORD SOUTH 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13 | 12.6 | 11.9 | 11.3 | 10.8 | 9.9 | 7.2 | 5.6 | 4.1 | 3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | HEREFORD SOUTH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13 | 12 | 10.6 | 9 | 7.6 | 5.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | HEREFORD SOUTH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13 | 12.2 | 11.2 | 9.8 | 8.9 | 6.5 | 4.1 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | HEREFORD SOUTH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13 | 12.1 | 11.1 | 9.9 | 8.6 | 6.9 | 2.8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Lydney 33/11kVDUMMY | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.7 | 3.6 | 3.5 | 3.3 | 3.1 | 2.8 | 2.6 | 2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Lydney 33/11kVDUMMY | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.7 | 3.5 | 3.2 | 2.9 | 2.5 | 2.1 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Lydney 33/11kVDUMMY | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.7 | 3.6 | 3.4 | 3.1 | 2.9 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Lydney 33/11kVDUMMY | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.7 | 3.5 | 3.3 | 3 | 2.7 | 2.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | LYDNEY 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 34.5 | 33.5 | 33.3 | 32.9 | 32 | 31.1 | 17.3 | 15.9 | 11 | 9.1 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | LYDNEY 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 34.5 | 32.9 | 31.8 | 30.2 | 28.4 | 26.2 | 11.3 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | LYDNEY 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 34.5 | 33.2 | 32.7 | 32 | 30.9 | 29.3 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | LYDNEY 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 34.5 | 33.1 | 32.4 | 31.3 | 29.7 | 28 | 13.6 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Marle Hill 132/66/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 4.1 | 3.9 | 3.9 | 3.9 | 3.8 | 3.8 | 3.5 | 3.4 | 3.1 | 2.9 | 2.7 | 2.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Marle Hill 132/66/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 4.1 | 3.7 | 3.5 | 3.1 | 2.9 | 2.5 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Marle Hill 132/66/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 4.1 | 3.8 | 3.7 | 3.5 | 3.3 | 3.1 | 2.5 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Marle Hill 132/66/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 4.1 | 3.7 | 3.6 | 3.4 | 3.2 | 2.9 | 2.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | MEAD LA 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 6.8 | 6.8 | 6.9 | 6.9 | 7 | 7.1 | 7.1 | 7 | 7 | 6.7 | 6 | 5.2 | 4.4 | 3.6 | 3 | 2.4 | 1.2 | 0
Port Ham 132kV | MEAD LA 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 6.7 | 6.8 | 6.8 | 6.9 | 6.9 | 6.9 | 6.7 | 6.1 | 5.8 | 4.7 | 3.6 | 2.9 | 2 | 1.2 | 1 | 0.8 | 0 | 0
Port Ham 132kV | MEAD LA 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 6.8 | 6.8 | 6.9 | 6.9 | 7 | 6.8 | 6.1 | 5 | 4.7 | 3.9 | 3.2 | 2.5 | 1.9 | 1.6 | 1.3 | 1.1 | 0 | 0
Port Ham 132kV | MEAD LA 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.7 | 6.8 | 6.9 | 6.9 | 6.9 | 7 | 6.8 | 6.2 | 6 | 5.1 | 4 | 3.1 | 2.2 | 0.9 | 0.6 | 0 | 0 | 0
Port Ham 132kV | MITCHELDEAN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.5 | 5.3 | 5.1 | 4.6 | 4.1 | 3.7 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | MITCHELDEAN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.2 | 4.6 | 3.8 | 2.9 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | MITCHELDEAN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.4 | 5.1 | 4.7 | 4.1 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | MITCHELDEAN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.3 | 4.9 | 4.3 | 3.5 | 2.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Montpellier 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 36.8 | 36.2 | 35.8 | 34.1 | 33.6 | 33 | 31.4 | 30.5 | 28.7 | 27.8 | 26.6 | 25 | 22.7 | 20.2 | 17.8 | 15.6 | 13.3 | 0 | 0
Port Ham 132kV | Montpellier 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 36.8 | 35.4 | 32.7 | 31.2 | 29.8 | 28.2 | 25.7 | 22 | 18 | 14.4 | 11.3 | 8.2 | 4.2 | 0.8 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Montpellier 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 36.8 | 35.6 | 33.5 | 32.7 | 31.9 | 30.9 | 28.6 | 26.2 | 23.3 | 20.9 | 18.4 | 15.3 | 11.5 | 7.8 | 4 | 0 | 0 | 0 | 0
Port Ham 132kV | Montpellier 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 36.8 | 35.5 | 33.3 | 32.3 | 31.3 | 30.1 | 28.1 | 25.6 | 22.6 | 20.4 | 17.6 | 14.3 | 11.1 | 7.9 | 4.8 | 1.9 | 0 | 0 | 0
Port Ham 132kV | PRINCESS ROYAL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.8 | 1.7 | 1.6 | 1.5 | 1.4 | 1.2 | 0.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | PRINCESS ROYAL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.8 | 1.6 | 1.4 | 1.2 | 0.9 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | PRINCESS ROYAL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.8 | 1.6 | 1.6 | 1.4 | 1.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | PRINCESS ROYAL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.8 | 1.6 | 1.5 | 1.3 | 1.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ROTOL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.8 | 16.3 | 14.7 | 14 | 13.4 | 10.9 | 8 | 7.1 | 4.9 | 4.3 | 3.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ROTOL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.8 | 15.9 | 13.8 | 12.5 | 10.5 | 7 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ROTOL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.8 | 16 | 14.2 | 11.2 | 9.6 | 8.4 | 4.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ROTOL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.8 | 16 | 14.1 | 13 | 11.1 | 8 | 5.8 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | STOWFIELD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.5 | 5.3 | 5 | 4.6 | 4.1 | 3.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | STOWFIELD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.2 | 4.6 | 3.8 | 2.9 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | STOWFIELD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.3 | 5.1 | 4.6 | 4.1 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | STOWFIELD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.3 | 4.9 | 4.3 | 3.5 | 2.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Tewkesbury Grid 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 18 | 15.3 | 14.8 | 14.4 | 14.1 | 13 | 11.6 | 11.2 | 10.6 | 10.2 | 9.7 | 9.1 | 8.3 | 7.4 | 6.6 | 5.9 | 5.1 | 0.5 | 0
Port Ham 132kV | Tewkesbury Grid 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 18 | 15.1 | 14.4 | 13.7 | 12.8 | 11.1 | 10.1 | 8.7 | 7.3 | 5.8 | 4.6 | 3.6 | 2.5 | 1.4 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Tewkesbury Grid 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 18 | 15.2 | 14.6 | 13.3 | 12.4 | 11.6 | 10.2 | 8.9 | 7.5 | 6.3 | 5.4 | 4.3 | 2.9 | 1.7 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Tewkesbury Grid 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 18 | 15.1 | 14.5 | 13.9 | 13 | 11.4 | 10.4 | 9.6 | 8.6 | 7.8 | 6.7 | 5.5 | 4.3 | 3.2 | 2.1 | 1.1 | 0 | 0 | 0
Port Ham 132kV | TUFFLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 6.3 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | TUFFLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | TUFFLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | TUFFLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 33.5 | 27.1 | 24.2 | 23 | 21.2 | 18.6 | 15.6 | 13.3 | 8.4 | 5.9 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 33.5 | 23.3 | 19.8 | 15.7 | 11.3 | 6.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 33.5 | 23.8 | 21.2 | 17.3 | 14.5 | 10.7 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 33.5 | 23.7 | 21.4 | 18.4 | 14.7 | 10.5 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | Cannock 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 19.5 | 15.8 | 13.2 | 12.4 | 11.1 | 9.3 | 4.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | Cannock 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 19.5 | 12.8 | 10.5 | 7.8 | 4.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | Cannock 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 19.5 | 13.1 | 11.4 | 8.9 | 7 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | Cannock 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 19.5 | 13 | 11.5 | 9.5 | 7 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | Lichfield 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 23 | 11.1 | 10.6 | 9.9 | 9.2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | Lichfield 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 23 | 10.4 | 8.7 | 6.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | Lichfield 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 23 | 10.6 | 9.4 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | Lichfield 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 23 | 10.5 | 9.6 | 8.4 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | RUGELEY TOWN 132 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 12.7 | 12.2 | 11.9 | 11.5 | 10.9 | 9.5 | 6 | 5.5 | 4.8 | 4.2 | 2.9 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | RUGELEY TOWN 132 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 12.7 | 11.7 | 10.7 | 9.3 | 7 | 4.7 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | RUGELEY TOWN 132 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 12.7 | 11.8 | 11.1 | 9.2 | 7.4 | 5.7 | 4.7 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | RUGELEY TOWN 132 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 12.7 | 11.9 | 11.3 | 10.4 | 8.8 | 7 | 5 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 46.1 | 41.9 | 40.9 | 39.5 | 37.9 | 35.6 | 32.3 | 31.4 | 30.1 | 29.2 | 28.1 | 26.5 | 24.8 | 23.1 | 21.5 | 17.5 | 12.4 | 1.8 | 0
Rugeley 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 46.1 | 41.2 | 39.5 | 37.4 | 34.8 | 31.9 | 29.1 | 25.4 | 21.8 | 18.8 | 16.3 | 13.7 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 46.1 | 41.3 | 40 | 37.7 | 36 | 33.2 | 31 | 28.5 | 26.4 | 24.7 | 22.1 | 12.4 | 6 | 3.4 | 1.1 | 0 | 0 | 0 | 0
Rugeley 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 46.1 | 41.3 | 39.8 | 37.9 | 35.5 | 32.7 | 30.5 | 27.2 | 24.3 | 22.1 | 19.8 | 17.3 | 14 | 6.7 | 0.8 | 0 | 0 | 0 | 0
Rugeley 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 43.6 | 43.1 | 42.6 | 42 | 41.2 | 40.3 | 38.6 | 38.1 | 37.2 | 36.4 | 35.2 | 33.8 | 31.8 | 29.5 | 27.3 | 25.3 | 23.1 | 10.5 | 1.5
Rugeley 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 43.6 | 42.3 | 40.9 | 39.3 | 37.7 | 35.9 | 34.5 | 31.2 | 27.7 | 24.1 | 21.2 | 18.2 | 14.5 | 11.3 | 8.4 | 5.8 | 3.4 | 0 | 0
Rugeley 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 43.6 | 42.5 | 41.4 | 40.2 | 39 | 37.7 | 36.9 | 34.8 | 32 | 29.4 | 26.6 | 23.5 | 20.1 | 16.7 | 13.4 | 10.2 | 7.2 | 0 | 0
Rugeley 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 43.6 | 42.4 | 41.4 | 40.2 | 38.8 | 37.4 | 36.2 | 34.1 | 31.5 | 29.1 | 26.3 | 23.2 | 20.1 | 17.2 | 14.3 | 11.7 | 9.1 | 0 | 0
Willenhall 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 30.3 | 14.5 | 14.2 | 13.8 | 13.3 | 12.5 | 5.7 | 5 | 2.8 | 2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willenhall 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 30.3 | 13.7 | 12.6 | 11.2 | 7.2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willenhall 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 30.3 | 13.8 | 13.1 | 11.8 | 10.1 | 6.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willenhall 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 30.3 | 13.7 | 13.1 | 12.1 | 10.8 | 6.7 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willenhall 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 33.5 | 28.3 | 28 | 27.7 | 27.3 | 26.7 | 25 | 24.3 | 22.6 | 21.9 | 20.8 | 19 | 16.8 | 14.7 | 12.7 | 11 | 9.2 | 0 | 0
Willenhall 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 33.5 | 27.6 | 26.5 | 25.3 | 24 | 22.5 | 20.1 | 16.5 | 12.6 | 9.5 | 6.6 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willenhall 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 33.5 | 27.8 | 27 | 25.8 | 25 | 24.1 | 20.8 | 18.2 | 15.2 | 13.3 | 11 | 7.6 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0
Willenhall 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 33.5 | 27.7 | 27.1 | 26.2 | 25.2 | 24.1 | 21.8 | 19.2 | 16.2 | 14.3 | 11.7 | 8.5 | 5.9 | 3.2 | 0.8 | 0 | 0 | 0 | 0
Willenhall 132kV | Willenhall 132/25/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 12.6 | 12.4 | 12 | 11.9 | 11.7 | 11.4 | 10.7 | 10.2 | 9.4 | 8.9 | 8.3 | 7.3 | 6.1 | 4.9 | 3.8 | 2.9 | 2 | 0 | 0
Willenhall 132kV | Willenhall 132/25/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 12.6 | 11.9 | 11 | 10.4 | 9.8 | 9.1 | 7.8 | 5.9 | 3.7 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willenhall 132kV | Willenhall 132/25/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 12.6 | 12 | 11.3 | 10.9 | 10.4 | 9.9 | 8.3 | 6.7 | 4.7 | 3.2 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willenhall 132kV | Willenhall 132/25/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 12.6 | 12 | 11.4 | 11 | 10.4 | 9.9 | 8.8 | 7.4 | 5.6 | 4.1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willenhall 132kV | Wolverhampton 132/33/11kV DUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 12.4 | 12.4 | 12.3 | 12.2 | 11.9 | 11.8 | 11.9 | 11.9 | 11.8 | 11.8 | 11.7 | 11.5 | 11.4 | 11.3 | 11.1 | 10.9 | 10.7 | 8.1 | 2.6
Willenhall 132kV | Wolverhampton 132/33/11kV DUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 12.4 | 12.3 | 12.2 | 12 | 11.2 | 10.9 | 10.9 | 10.6 | 10.3 | 10 | 8.2 | 5.5 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0
Willenhall 132kV | Wolverhampton 132/33/11kV DUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 12.4 | 12.3 | 12.2 | 12.1 | 11.3 | 11.2 | 11.2 | 11 | 10.8 | 10.6 | 10.3 | 9.3 | 6.3 | 4.2 | 2 | 0 | 0 | 0 | 0
Willenhall 132kV | Wolverhampton 132/33/11kV DUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 12.4 | 12.3 | 12.2 | 12.1 | 11.7 | 11.5 | 11.5 | 11.3 | 11.1 | 10.8 | 10.6 | 10.2 | 9.8 | 7.1 | 4.7 | 2.9 | 1.5 | 0 | 0
Willenhall 132kV | WOLVERHAMPTON 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 64.9 | 64.2 | 63.5 | 62.5 | 61.2 | 59.6 | 64.3 | 64.3 | 64.3 | 64.2 | 63.9 | 63.5 | 62.8 | 62 | 61.1 | 60.2 | 59.3 | 55.7 | 53.6
Willenhall 132kV | WOLVERHAMPTON 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 64.9 | 63.9 | 62.7 | 60.7 | 58.2 | 56.1 | 63.1 | 61.6 | 59.9 | 59 | 58.2 | 57.3 | 56 | 54.6 | 53.7 | 53 | 52.4 | 47.7 | 38.1
Willenhall 132kV | WOLVERHAMPTON 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 64.9 | 63.9 | 63 | 61 | 58.9 | 56.7 | 63.6 | 62.3 | 60.9 | 60.2 | 59.4 | 58.2 | 57.1 | 56.2 | 55.5 | 54.7 | 54 | 51.4 | 41.8
Willenhall 132kV | WOLVERHAMPTON 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 64.9 | 63.9 | 62.9 | 61.4 | 59.5 | 57.2 | 63.9 | 62.9 | 61.5 | 60.7 | 59.9 | 58.9 | 57.8 | 56.6 | 55.7 | 55 | 54.4 | 52.3 | 51.5

## Generation Headroom
Associated GSP | Substation | Supply Level | Voltage Level (kV) | Scenario | Units | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050
Bishops Wood 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.3 | 5.3 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5 | 5 | 5 | 4.9
Bishops Wood 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.3 | 5.3 | 5.2 | 5.2 | 5.1 | 5.1 | 5.1 | 5 | 5 | 5 | 4.9 | 4.9 | 4.9 | 4.8 | 4.7 | 4.7 | 4.7 | 3.6 | 2.5
Bishops Wood 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.3 | 5.2 | 5.2 | 5.1 | 5.1 | 5 | 5 | 4.9 | 4.9 | 4.9 | 4.8 | 4.8 | 4.7 | 4 | 3.8 | 3.6 | 3.3 | 2.8 | 1.5
Bishops Wood 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.3 | 5.3 | 5.2 | 5.2 | 5.2 | 5.2 | 5.1 | 5.1 | 5.1 | 5.1 | 5 | 5 | 5 | 5 | 4.9 | 4.9 | 4.9 | 4.7 | 4.5
Bishops Wood 132kV | BODENHAM 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.4 | 3.4 | 3.3 | 3.3 | 3.2 | 3.2 | 3.2 | 3.1 | 3.1 | 3 | 2.9 | 2.9 | 2.9 | 2.8 | 2.8 | 2.8 | 2.8 | 2.7 | 2.5
Bishops Wood 132kV | BODENHAM 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.4 | 3.3 | 3.3 | 3.1 | 3 | 2.9 | 2.8 | 2.7 | 2.6 | 2.5 | 2.4 | 2.2 | 2.1 | 2 | 1.9 | 1.8 | 1.7 | 0.6 | 0
Bishops Wood 132kV | BODENHAM 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.4 | 3.3 | 3.2 | 3.1 | 3 | 2.9 | 2.8 | 2.7 | 2.6 | 2.5 | 2.3 | 2.2 | 0.7 | 0.7 | 0.6 | 0.5 | 0 | 0 | 0
Bishops Wood 132kV | BODENHAM 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.4 | 3.4 | 3.3 | 3.2 | 3.2 | 3.1 | 3.1 | 3 | 3 | 2.9 | 2.8 | 2.8 | 2.7 | 2.7 | 2.6 | 2.6 | 2.6 | 1.6 | 1.2
Bishops Wood 132kV | BROMYARD 66/11kV | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.5 | 11.5 | 11.4 | 11.3 | 11.1 | 10.9 | 9.9 | 9.7 | 9.5 | 9.2 | 8.7 | 8.3 | 8 | 7.9 | 7.7 | 7.6 | 7.3 | 6.1 | 4.6
Bishops Wood 132kV | BROMYARD 66/11kV | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.5 | 11.4 | 11.2 | 10.7 | 10.1 | 9.5 | 8.4 | 7.7 | 7 | 6.2 | 5.3 | 4.3 | 3.4 | 2.4 | 1.9 | 1.3 | 0.7 | 0 | 0
Bishops Wood 132kV | BROMYARD 66/11kV | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.5 | 11.4 | 11.1 | 10.8 | 10.3 | 9.7 | 9.1 | 8.4 | 7.7 | 6.9 | 6.1 | 5.1 | 4.3 | 3.7 | 3.2 | 2.8 | 2.3 | 0 | 0
Bishops Wood 132kV | BROMYARD 66/11kV | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.5 | 11.5 | 11.3 | 11.1 | 10.8 | 10.5 | 9.4 | 9.1 | 8.6 | 8 | 7.3 | 6.7 | 6.3 | 5.8 | 5.5 | 5.2 | 5 | 2.7 | 0
Bishops Wood 132kV | CLEOBURY MORTIMER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.5 | 9.5 | 9.5 | 9.4 | 9.4 | 9.3 | 9.2 | 9.1 | 8.9 | 8.7 | 8.5 | 8 | 7.7 | 7.5 | 7.3 | 7.1 | 6.9 | 5.3 | 3.4
Bishops Wood 132kV | CLEOBURY MORTIMER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.5 | 9.5 | 9.4 | 9.2 | 9 | 8.7 | 8.4 | 7.8 | 6.9 | 5.9 | 4.9 | 3.8 | 2.8 | 1.8 | 1 | 0 | 0 | 0 | 0
Bishops Wood 132kV | CLEOBURY MORTIMER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.5 | 9.5 | 9.4 | 9.3 | 9.1 | 8.9 | 8.7 | 8.4 | 7.8 | 6.9 | 6.1 | 5.2 | 4.3 | 2.4 | 1.8 | 1.2 | 0.6 | 0 | 0
Bishops Wood 132kV | CLEOBURY MORTIMER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.5 | 9.5 | 9.5 | 9.4 | 9.3 | 9.2 | 9 | 8.8 | 8.6 | 8.2 | 7.4 | 6.9 | 6.4 | 5.9 | 5.6 | 5.2 | 4.9 | 1.4 | 0
Bishops Wood 132kV | CRAVEN ARMS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 7.2 | 7.1 | 7 | 7 | 6.9 | 6.9 | 6.7 | 6.6 | 6.5 | 6.5 | 6.5 | 6.4 | 6.4 | 6.3 | 6.2 | 6.2 | 6 | 5.8
Bishops Wood 132kV | CRAVEN ARMS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 7.1 | 6.9 | 6.8 | 6.7 | 6.6 | 5.6 | 5.5 | 5.4 | 5.2 | 5.1 | 5 | 4.4 | 4.3 | 4.2 | 4 | 3.9 | 3.3 | 2.4
Bishops Wood 132kV | CRAVEN ARMS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 7.1 | 6.8 | 6.6 | 6.5 | 6 | 5.6 | 5.4 | 5.2 | 5 | 4.2 | 4 | 3.8 | 3.7 | 3.6 | 3.5 | 3.3 | 2.8 | 1.5
Bishops Wood 132kV | CRAVEN ARMS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 7.1 | 7 | 6.9 | 6.8 | 6.7 | 5.8 | 5.7 | 5.6 | 5.5 | 5.4 | 5.3 | 4.8 | 4.8 | 4.8 | 4.7 | 4.6 | 4.2 | 3.8
Bishops Wood 132kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 25.5 | 23.7 | 23.5 | 23.4 | 23.3 | 23.1 | 22.8 | 22.5 | 22.2 | 21.9 | 21.6 | 21.3 | 21.1 | 20.9 | 20.8 | 20.7 | 20.6 | 20.2 | 19.4
Bishops Wood 132kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 25.5 | 23.6 | 23.3 | 23 | 22.6 | 21.7 | 21.1 | 20.4 | 19.8 | 19.4 | 18.9 | 18.4 | 18 | 17.5 | 16.8 | 15.5 | 14.2 | 7.7 | 0
Bishops Wood 132kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 25.5 | 23.5 | 23.2 | 22.9 | 22.5 | 22.1 | 21.2 | 20.5 | 19.9 | 19.5 | 19.1 | 18.7 | 18.3 | 18 | 17.8 | 17.5 | 17.3 | 12.3 | 8.6
Bishops Wood 132kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 25.5 | 23.6 | 23.5 | 23.3 | 23 | 22.1 | 21.6 | 20.9 | 20.3 | 20 | 19.4 | 19 | 18.7 | 18.5 | 18.3 | 18.2 | 18.1 | 15.1 | 9.6
Bishops Wood 132kV | DYMOCK 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.5 | 9.5 | 9.4 | 9.4 | 9.3 | 9.3 | 9.3 | 9.2 | 9.1 | 9.1 | 9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.8 | 8.8 | 8.6 | 4.9
Bishops Wood 132kV | DYMOCK 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.5 | 9.4 | 9.3 | 9.2 | 8.9 | 7 | 8.7 | 8.5 | 8.3 | 8.1 | 6.7 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | DYMOCK 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.5 | 9.4 | 9.3 | 9.2 | 9 | 6.7 | 8.7 | 8.6 | 8.4 | 8.3 | 7.9 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | DYMOCK 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.5 | 9.5 | 9.4 | 9.4 | 9.3 | 9.2 | 9.2 | 9.1 | 9 | 8.9 | 8.9 | 8.8 | 8.5 | 7.6 | 6.4 | 5.5 | 4.3 | 0 | 0
Bishops Wood 132kV | HEREFORD 132kV S STN | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 16.2 | 15.6 | 14.9 | 14 | 13.1 | 12 | 18 | 16.3 | 14.6 | 12.9 | 10.8 | 9.4 | 8.5 | 7.8 | 7.2 | 6.2 | 5 | 0 | 0
Bishops Wood 132kV | HEREFORD 132kV S STN | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 16.2 | 15.1 | 13.5 | 10.9 | 7.9 | 4.8 | 8.8 | 5.4 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | HEREFORD 132kV S STN | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 16.2 | 14.7 | 12.5 | 10.6 | 8.1 | 4.5 | 10.4 | 7 | 3.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | HEREFORD 132kV S STN | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 16.2 | 15.5 | 14.4 | 13.2 | 11.6 | 9.6 | 13 | 10.2 | 7.8 | 5.9 | 3.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KENSWICK 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.7 | 8.7 | 8.6 | 8.5 | 8.3 | 8.1 | 7.5 | 7.3 | 7 | 6.5 | 5.9 | 5.5 | 5.2 | 5.1 | 4.9 | 4.7 | 4.6 | 3.8 | 2.3
Bishops Wood 132kV | KENSWICK 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.7 | 8.6 | 8.5 | 8 | 7.5 | 7 | 6.4 | 5.7 | 5 | 4.4 | 3.6 | 2.8 | 2 | 1.2 | 0.8 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KENSWICK 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.7 | 8.6 | 8.4 | 8.3 | 8 | 7.7 | 7.2 | 6.5 | 5.8 | 5.1 | 4.5 | 3.8 | 3.3 | 2.8 | 2.4 | 2.1 | 1.7 | 0 | 0
Bishops Wood 132kV | KENSWICK 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.7 | 8.6 | 8.6 | 8.4 | 8.2 | 7.9 | 7.3 | 6.8 | 6.2 | 5.7 | 5 | 4.5 | 4.1 | 3.8 | 3.5 | 3.3 | 3.1 | 1.4 | 0
Bishops Wood 132kV | Kidderminster 132/33/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 72.3 | 71.9 | 71.5 | 71.3 | 71 | 70.7 | 69.6 | 69.5 | 69.4 | 69.1 | 68.7 | 68.5 | 68.3 | 68.2 | 68.1 | 67.9 | 67.7 | 66.3 | 64.3
Bishops Wood 132kV | Kidderminster 132/33/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 72.3 | 71.5 | 70.9 | 69.7 | 69 | 68 | 68.7 | 67.9 | 66.6 | 65.7 | 64.5 | 63.3 | 62.4 | 61.4 | 60.5 | 59.6 | 58.7 | 53.1 | 49.3
Bishops Wood 132kV | Kidderminster 132/33/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 72.3 | 71.2 | 69.7 | 69.3 | 68.3 | 67.2 | 68 | 66.3 | 64.7 | 63.6 | 62.5 | 61.5 | 60.6 | 59.6 | 58.8 | 58 | 57.2 | 52.3 | 48
Bishops Wood 132kV | Kidderminster 132/33/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 72.3 | 71.7 | 71.3 | 70.8 | 69.7 | 69.2 | 69.2 | 68.6 | 68.1 | 67.4 | 66.4 | 65.7 | 65.2 | 64.7 | 64.3 | 63.9 | 63.5 | 60.1 | 56.4
Bishops Wood 132kV | KINGTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KINGTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KINGTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KINGTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.6 | 7.6 | 7.5 | 7.5 | 7.4 | 7.2 | 8.9 | 8.7 | 8.5 | 8.2 | 7.9 | 7.8 | 7.6 | 7.6 | 7.5 | 7.4 | 7.3 | 6.8 | 6.1
Bishops Wood 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.6 | 7.6 | 7.5 | 7.1 | 6.8 | 6.4 | 8.2 | 7.8 | 7.5 | 7.2 | 6.8 | 6.5 | 6.1 | 5.8 | 5.6 | 5.4 | 5.2 | 4 | 2.7
Bishops Wood 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.6 | 7.5 | 7.4 | 7.2 | 7 | 6.6 | 8.4 | 8.1 | 7.8 | 7.5 | 7.3 | 7 | 6.7 | 6.4 | 6.2 | 6.1 | 5.9 | 5.2 | 4.7
Bishops Wood 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.6 | 7.6 | 7.5 | 7.4 | 7.2 | 6.9 | 8.6 | 8.3 | 8.1 | 7.8 | 7.5 | 7.3 | 7.2 | 7 | 6.9 | 6.9 | 6.8 | 5.8 | 4.7
Bishops Wood 132kV | KNIGHTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KNIGHTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KNIGHTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | KNIGHTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEDBURY 66/11kV | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.6 | 13.2 | 12.8 | 12.4 | 11.8 | 11.2 | 15 | 14.5 | 13.8 | 13.2 | 12.4 | 11.8 | 11.3 | 11.1 | 10.8 | 10.7 | 10.7 | 9 | 4.9
Bishops Wood 132kV | LEDBURY 66/11kV | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.6 | 12.9 | 12.1 | 10.5 | 8.8 | 6.9 | 12.3 | 10.7 | 9.4 | 8.4 | 6.7 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEDBURY 66/11kV | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.6 | 12.7 | 11.6 | 10.5 | 9.1 | 6.6 | 12.3 | 10.9 | 9.6 | 8.7 | 7.9 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEDBURY 66/11kV | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.6 | 13.1 | 12.6 | 11.8 | 10.9 | 9.6 | 13.9 | 12.6 | 11.5 | 10.8 | 9.8 | 9 | 8.5 | 7.6 | 6.4 | 5.4 | 4.3 | 0 | 0
Bishops Wood 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.9 | 9.9 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.4 | 9.3 | 9.2 | 9.1 | 9 | 8.9 | 8.9 | 8.9 | 8.7 | 8.7 | 8.4 | 8
Bishops Wood 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.9 | 9.8 | 9.8 | 9.7 | 9.5 | 9.2 | 8.1 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 6.4 | 6.2 | 5.9 | 5.7 | 5.5 | 3.6 | 2.5
Bishops Wood 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.9 | 9.8 | 9.7 | 9.4 | 9.1 | 8.5 | 7.9 | 7.5 | 7.3 | 7 | 6 | 5.7 | 5.5 | 4 | 3.8 | 3.6 | 3.4 | 2.8 | 1.5
Bishops Wood 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.9 | 9.9 | 9.8 | 9.8 | 9.7 | 9.6 | 8.5 | 8.3 | 8.1 | 8 | 7.8 | 7.7 | 7.2 | 7.1 | 7 | 6.9 | 6.8 | 5.4 | 4.5
Bishops Wood 132kV | LEOMINSTER 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12 | 11.7 | 11 | 10.4 | 9.7 | 9 | 17.2 | 16.5 | 15.6 | 14.8 | 13.8 | 13.2 | 12.8 | 12.5 | 12.2 | 11.9 | 11.5 | 2.9 | 0
Bishops Wood 132kV | LEOMINSTER 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12 | 11.3 | 9.8 | 8.1 | 6.1 | 4.1 | 13.1 | 11.7 | 10.4 | 8.8 | 7.3 | 5.7 | 4 | 2.2 | 1 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEOMINSTER 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12 | 11 | 9 | 7.5 | 5.6 | 3.4 | 13 | 11.6 | 10.1 | 8.7 | 7 | 5.3 | 4 | 2.6 | 1.6 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LEOMINSTER 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12 | 11.6 | 10.6 | 9.8 | 8.7 | 7.5 | 15.8 | 15 | 14.1 | 13.2 | 12.2 | 11.4 | 10.6 | 9.8 | 9.3 | 8.8 | 8.3 | 0 | 0
Bishops Wood 132kV | LOWER CHADNOR 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.3 | 9.3 | 9.3 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 8.2 | 4.8
Bishops Wood 132kV | LOWER CHADNOR 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.2 | 9.2 | 9.2 | 8.1 | 6.6 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LOWER CHADNOR 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.1 | 9 | 9 | 8.9 | 7.6 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LOWER CHADNOR 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9.3 | 9.3 | 9.2 | 9.2 | 9.2 | 9.2 | 8.4 | 7.4 | 6.3 | 5.3 | 4.3 | 0 | 0
Bishops Wood 132kV | Ludlow 132/66/33/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 9.7 | 9.7 | 9.6 | 9.5 | 9.4 | 9.2 | 8 | 7.9 | 7.8 | 7.7 | 7.6 | 7.5 | 7.5 | 7.5 | 7.4 | 7.4 | 7.3 | 0 | 0
Bishops Wood 132kV | Ludlow 132/66/33/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 9.7 | 9.6 | 9.3 | 8.8 | 8.4 | 8 | 7.2 | 6.7 | 6.4 | 6 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Ludlow 132/66/33/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 9.7 | 9.5 | 9.1 | 8.7 | 8.3 | 7.8 | 7.4 | 6.9 | 6.4 | 6.1 | 5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | Ludlow 132/66/33/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 9.7 | 9.7 | 9.4 | 9.2 | 9 | 8.7 | 7.6 | 7.5 | 7.4 | 7.2 | 6.9 | 6.7 | 6.2 | 6.1 | 6 | 5.9 | 5.7 | 0 | 0
Bishops Wood 132kV | LUDLOW 132kV S STN | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 12.3 | 12 | 11.3 | 10.7 | 10.1 | 9.4 | 16.4 | 15.5 | 14.6 | 13.7 | 12.6 | 11.9 | 11.4 | 11.1 | 10.8 | 10.4 | 10 | 0 | 0
Bishops Wood 132kV | LUDLOW 132kV S STN | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 12.3 | 11.6 | 10.2 | 8.6 | 6.7 | 4.8 | 11.9 | 10.4 | 8.8 | 7.2 | 5.5 | 3.7 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LUDLOW 132kV S STN | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 12.3 | 11.3 | 9.4 | 8 | 6.2 | 4.1 | 11.8 | 10.2 | 8.6 | 7 | 5.1 | 3.3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | LUDLOW 132kV S STN | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 12.3 | 11.9 | 10.9 | 10.2 | 9.2 | 8 | 14.9 | 13.9 | 13 | 12 | 10.8 | 9.9 | 9 | 8.1 | 7.6 | 7.1 | 6.5 | 0 | 0
Bishops Wood 132kV | MADLEY 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.5 | 1.2 | 0.7 | 0 | 0 | 0 | 9.9 | 9.9 | 9.8 | 9.8 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 8.4 | 4.7
Bishops Wood 132kV | MADLEY 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.5 | 1 | 0 | 0 | 0 | 0 | 9.6 | 9.6 | 9.5 | 8.3 | 6.5 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | MADLEY 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.5 | 0.8 | 0 | 0 | 0 | 0 | 9.6 | 9.5 | 9.5 | 9.1 | 7.8 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | MADLEY 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.5 | 1.2 | 0 | 0 | 0 | 0 | 9.7 | 9.7 | 9.6 | 9.6 | 9.5 | 9.4 | 8.7 | 7.4 | 6.3 | 5.3 | 4.2 | 0 | 0
Bishops Wood 132kV | Malvern 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.5 | 29.4 | 29.1 | 28.8 | 28.6 | 28.3 | 28.7 | 28.6 | 28.4 | 28.2 | 27.9 | 27.7 | 27.6 | 27.5 | 27.4 | 27.4 | 27.3 | 25.9 | 24.6
Bishops Wood 132kV | Malvern 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.5 | 29.1 | 28.7 | 28.2 | 27.6 | 26.6 | 27.9 | 27.4 | 26.2 | 25.6 | 24.8 | 24.1 | 23.5 | 22.9 | 22.3 | 21.7 | 21.1 | 18 | 0
Bishops Wood 132kV | Malvern 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.5 | 29 | 28.2 | 27.7 | 26.6 | 25.9 | 27.3 | 25.7 | 24.8 | 24 | 23.3 | 22.6 | 22 | 21.4 | 20.8 | 20.3 | 19.7 | 10.8 | 0
Bishops Wood 132kV | Malvern 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.5 | 29.3 | 28.9 | 28.5 | 28.1 | 27.6 | 28.2 | 27.7 | 27.4 | 26.4 | 26 | 25.6 | 25.3 | 25 | 24.7 | 24.5 | 24.2 | 22 | 19.5
Bishops Wood 132kV | NEWENT 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.5 | 10.5 | 10.4 | 10.2 | 10 | 9.8 | 8.2 | 8 | 7.8 | 7.7 | 6.9 | 6.3 | 5.8 | 5.5 | 5.2 | 5 | 4.9 | 3.2 | 1.4
Bishops Wood 132kV | NEWENT 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.5 | 10.4 | 10.2 | 9.6 | 8.9 | 7 | 7.5 | 6 | 4.7 | 3.9 | 2.7 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | NEWENT 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.5 | 10.3 | 10.1 | 9.9 | 9.3 | 6.7 | 7.6 | 6.2 | 5 | 4.2 | 3.4 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | NEWENT 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.5 | 10.4 | 10.3 | 10.1 | 9.8 | 9.4 | 8 | 7.5 | 6.4 | 5.7 | 4.7 | 3.9 | 3.3 | 2.9 | 2.6 | 2.3 | 2 | 0 | 0
Bishops Wood 132kV | PETERCHURCH 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 1.9 | 1.5 | 0.8 | 0 | 0 | 0 | 9 | 9 | 9 | 9 | 8.9 | 8.9 | 9 | 9 | 9 | 9 | 9 | 9 | 4.7
Bishops Wood 132kV | PETERCHURCH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 8.8 | 8.7 | 8.7 | 8.6 | 6.5 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PETERCHURCH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 1.9 | 1 | 0 | 0 | 0 | 0 | 8.6 | 8.6 | 8.5 | 8.5 | 8.4 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PETERCHURCH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 1.9 | 1.5 | 0.5 | 0 | 0 | 0 | 9 | 9 | 9 | 8.9 | 8.9 | 8.9 | 8.9 | 7.4 | 6.3 | 5.3 | 4.2 | 0 | 0
Bishops Wood 132kV | PONTRILAS 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.2 | 2.6 | 1.4 | 0 | 0 | 0 | 8.9 | 8.5 | 8.1 | 7.7 | 7.1 | 6.7 | 6.5 | 6.4 | 6.2 | 6.1 | 5.9 | 4.7 | 3.4
Bishops Wood 132kV | PONTRILAS 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.2 | 2.1 | 0 | 0 | 0 | 0 | 7.6 | 6.9 | 6.3 | 5.7 | 5 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PONTRILAS 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.2 | 1.6 | 0 | 0 | 0 | 0 | 8.4 | 7.8 | 7.2 | 6.6 | 6.1 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PONTRILAS 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.2 | 2.5 | 0.9 | 0 | 0 | 0 | 8.5 | 8 | 7.5 | 7.1 | 6.5 | 6.1 | 5.7 | 5.4 | 5.2 | 5 | 4.2 | 0 | 0
Bishops Wood 132kV | PRESTEIGNE 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PRESTEIGNE 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PRESTEIGNE 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | PRESTEIGNE 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.8 | 7.7 | 7.7 | 7.6 | 7.5 | 7.3 | 8.8 | 8.7 | 8.6 | 8.5 | 8.3 | 8.2 | 8.2 | 8.1 | 8.1 | 8.1 | 8 | 12.6 | 12.4
Bishops Wood 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.8 | 7.7 | 7.6 | 7.3 | 6.9 | 6.5 | 8.4 | 8.2 | 8 | 7.8 | 7.7 | 7.5 | 12.3 | 12.1 | 12 | 11.9 | 11.8 | 10.8 | 6.9
Bishops Wood 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.8 | 7.7 | 7.5 | 7.4 | 7.1 | 6.7 | 8.4 | 8.2 | 8 | 7.8 | 7.6 | 7.5 | 12.3 | 12.2 | 12.1 | 12 | 11.9 | 6.2 | 4.5
Bishops Wood 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.8 | 7.7 | 7.7 | 7.5 | 7.3 | 7 | 8.6 | 8.4 | 8.3 | 8.1 | 8 | 7.9 | 12.6 | 12.6 | 12.5 | 12.5 | 12.5 | 7 | 6.4
Bishops Wood 132kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.9 | 13.8 | 13.7 | 13.5 | 13.3 | 13.1 | 12.8 | 12.5 | 12.3 | 12 | 11.7 | 11.5 | 11.3 | 11.3 | 11.2 | 11.2 | 11.1 | 10.6 | 9.9
Bishops Wood 132kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.9 | 13.7 | 13.2 | 12.9 | 12.5 | 12.1 | 11.6 | 11.1 | 10.7 | 10.2 | 9.8 | 9.3 | 8.9 | 8.4 | 23.3 | 21.6 | 19.9 | 10 | 20.1
Bishops Wood 132kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.9 | 13.6 | 13 | 12.7 | 12.3 | 11.9 | 11.3 | 10.8 | 10.3 | 9.8 | 9.4 | 8.9 | 8.5 | 23.7 | 23.6 | 23.2 | 21.6 | 14.5 | 4.7
Bishops Wood 132kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.9 | 13.8 | 13.4 | 13.2 | 12.9 | 12.6 | 12.1 | 11.7 | 11.4 | 2.8 | 2.4 | 2.1 | 1.9 | 1.8 | 1.7 | 1.6 | 1.5 | 0 | 0
Bishops Wood 132kV | ROSS ON WYE 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 6.6 | 6.5 | 6.4 | 6.3 | 6.2 | 3.9 | 3.6 | 3.5 | 3.3 | 3.1 | 3.1 | 3.1 | 3.1 | 2.9 | 2.5 | 1.7 | 1.2 | 0.6
Bishops Wood 132kV | ROSS ON WYE 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 6.5 | 6.3 | 6.2 | 6 | 5.7 | 1.6 | 1.5 | 1.4 | 1.1 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | ROSS ON WYE 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 6.4 | 6.1 | 6 | 5.7 | 4.7 | 2.4 | 2.2 | 1.9 | 1.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | ROSS ON WYE 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.6 | 6.4 | 6.3 | 6.2 | 6 | 2 | 1.9 | 1.8 | 1.6 | 1.5 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | ST WEONARDS 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 6.7 | 6.6 | 6.5 | 6.4 | 6.3 | 4 | 3.6 | 3.5 | 3.3 | 3.2 | 3.1 | 3.1 | 3.1 | 3 | 2.5 | 1.8 | 1.2 | 0.6
Bishops Wood 132kV | ST WEONARDS 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 5.7 | 1.6 | 1.5 | 1.4 | 1.1 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | ST WEONARDS 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 6.5 | 6.2 | 6 | 5.7 | 4.8 | 2.4 | 2.2 | 2 | 1.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | ST WEONARDS 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.6 | 6.5 | 6.4 | 6.2 | 6 | 2 | 1.9 | 1.8 | 1.6 | 1.5 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Bishops Wood 132kV | STOCKTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.9 | 10.9 | 10.8 | 10.7 | 10.6 | 10.4 | 10.3 | 9.8 | 9.5 | 9.1 | 8.5 | 8 | 7.7 | 7.5 | 7.3 | 7.1 | 6.9 | 5.3 | 3.4
Bishops Wood 132kV | STOCKTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.9 | 10.8 | 10.7 | 10.4 | 9.8 | 9.4 | 8.7 | 7.8 | 6.9 | 5.9 | 4.9 | 3.8 | 2.8 | 1.8 | 1 | 0 | 0 | 0 | 0
Bishops Wood 132kV | STOCKTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.9 | 10.8 | 10.6 | 10.6 | 10.3 | 9.8 | 9.5 | 8.7 | 7.8 | 6.9 | 6.1 | 5.2 | 4.3 | 2.4 | 1.8 | 1.2 | 0.6 | 0 | 0
Bishops Wood 132kV | STOCKTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.9 | 10.9 | 10.8 | 10.6 | 10.4 | 10.3 | 9.7 | 9.3 | 8.8 | 8.2 | 7.4 | 6.9 | 6.4 | 5.9 | 5.5 | 5.2 | 4.8 | 1.4 | 0
Bishops Wood 132kV | STOURPORT 132 66 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 16.7 | 16.7 | 16.6 | 16.5 | 16.5 | 16.4 | 20.1 | 20.1 | 20.1 | 20.1 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 17.4 | 17.8
Bishops Wood 132kV | STOURPORT 132 66 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 16.7 | 16.6 | 16.5 | 16.3 | 16.2 | 16.1 | 24.4 | 24.4 | 24.4 | 24.5 | 24.5 | 24.6 | 17.8 | 18 | 18.1 | 18.2 | 18.3 | 18.9 | 19.4
Bishops Wood 132kV | STOURPORT 132 66 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 16.7 | 16.6 | 16.4 | 16.3 | 16.2 | 16.2 | 24.4 | 24.4 | 24.4 | 24.5 | 24.5 | 24.6 | 17.8 | 18 | 18 | 18.1 | 18.2 | 25.5 | 25.8
Bishops Wood 132kV | STOURPORT 132 66 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 16.7 | 16.7 | 16.6 | 16.5 | 16.4 | 16.4 | 20.1 | 23.7 | 24.4 | 24.4 | 24.4 | 24.5 | 17.4 | 17.5 | 17.5 | 17.6 | 17.6 | 24.9 | 25.3
Bishops Wood 132kV | STOURPORT 132 66 33kV S STN | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 28.4 | 28.3 | 25.6 | 25.5 | 25.3 | 25.2 | 25.3 | 25.1 | 24.8 | 24.5 | 23.1 | 23 | 22.9 | 22.8 | 22.7 | 22.7 | 22.6 | 22 | 20.5
Bishops Wood 132kV | STOURPORT 132 66 33kV S STN | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 28.4 | 28.2 | 24.3 | 23.9 | 23.5 | 23 | 22.7 | 22.3 | 21.9 | 21.2 | 20.3 | 19.4 | 18.7 | 17.9 | 19.5 | 19.2 | 18.9 | 17 | 20.3
Bishops Wood 132kV | STOURPORT 132 66 33kV S STN | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 28.4 | 28.2 | 26.7 | 26.5 | 26.1 | 25.6 | 25.3 | 24.8 | 24.2 | 23.4 | 22.6 | 21.8 | 21 | 22.7 | 22.4 | 22.1 | 21.8 | 22.2 | 22
Bishops Wood 132kV | STOURPORT 132 66 33kV S STN | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 28.4 | 28.3 | 24.4 | 24.2 | 24 | 23.7 | 23.6 | 23.2 | 23 | 15 | 14.3 | 13.8 | 13.4 | 13.2 | 13 | 12.8 | 12.5 | 10.3 | 22.2
Bishops Wood 132kV | Stourport 132/66/33/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 17.6 | 17.4 | 13.6 | 13.5 | 13.3 | 13.1 | 13.7 | 13.4 | 13 | 12.6 | 10.8 | 10.5 | 10.4 | 10.3 | 10.2 | 10.1 | 10 | 9.2 | 8
Bishops Wood 132kV | Stourport 132/66/33/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 17.6 | 17.3 | 11.8 | 11.3 | 10.8 | 10.2 | 10.2 | 9.5 | 9 | 8.5 | 7.9 | 7.3 | 6.8 | 6.2 | 5.8 | 5.3 | 4.9 | 2.3 | 0
Bishops Wood 132kV | Stourport 132/66/33/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 17.6 | 17.2 | 15.2 | 14.9 | 14.3 | 13.7 | 13.7 | 13 | 12.5 | 12.1 | 11.6 | 11.1 | 10.6 | 10.1 | 9.7 | 9.4 | 9 | 6.6 | 0
Bishops Wood 132kV | Stourport 132/66/33/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 17.6 | 17.4 | 12 | 11.7 | 11.5 | 11 | 11.3 | 10.9 | 10.5 | 10.2 | 9.8 | 9.5 | 9.3 | 8.8 | 8.2 | 7.4 | 6.6 | 0 | 5.1
Bishops Wood 132kV | TENBURY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.7 | 11.7 | 11.6 | 11.5 | 11.4 | 11.3 | 11 | 10.5 | 10 | 9.5 | 8.8 | 8.4 | 8.1 | 7.9 | 7.7 | 7.5 | 7.3 | 5.9 | 4.2
Bishops Wood 132kV | TENBURY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.7 | 11.7 | 11.5 | 11.2 | 10.5 | 9.9 | 9.2 | 8.3 | 7.5 | 6.7 | 5.8 | 4.8 | 4 | 3.1 | 2.6 | 2 | 1.4 | 0 | 0
Bishops Wood 132kV | TENBURY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.7 | 11.6 | 11.5 | 11.3 | 10.9 | 10.4 | 9.8 | 9 | 8.1 | 7.3 | 6.6 | 5.9 | 5.1 | 3.3 | 2.9 | 2.4 | 1.9 | 0 | 0
Bishops Wood 132kV | TENBURY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.7 | 11.7 | 11.6 | 11.5 | 11.3 | 10.9 | 10.3 | 9.7 | 9 | 8.4 | 7.6 | 7.1 | 6.7 | 6.3 | 6 | 5.7 | 5.4 | 2.4 | 0
Bishops Wood 132kV | Timberdine 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 28.5 | 28.3 | 28.1 | 27.9 | 27.7 | 27.5 | 27.9 | 27.7 | 27.5 | 27.4 | 26.6 | 26.3 | 26.1 | 25.8 | 25.6 | 25.3 | 25.1 | 23.7 | 22.4
Bishops Wood 132kV | Timberdine 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 28.5 | 28.1 | 27.8 | 27.4 | 26.5 | 25.7 | 26.6 | 25.7 | 24.6 | 23.7 | 22.6 | 21.5 | 20.6 | 19.5 | 19 | 18.5 | 18 | 14.9 | 0
Bishops Wood 132kV | Timberdine 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 28.5 | 27.9 | 27.6 | 26.7 | 26.1 | 25.4 | 26.2 | 25.1 | 23.9 | 22.8 | 21.8 | 20.8 | 19.8 | 19.2 | 18.8 | 18.4 | 18 | 10.8 | 0
Bishops Wood 132kV | Timberdine 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 28.5 | 28.2 | 28 | 27.8 | 27.4 | 26.6 | 27.5 | 27.3 | 26.3 | 25.6 | 24.7 | 24.1 | 23.6 | 23 | 22.6 | 22.1 | 21.6 | 18.8 | 16.5
Bishops Wood 132kV | Upton Warren 132/66/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 18.7 | 18.4 | 18.2 | 18 | 17.8 | 17.6 | 17.2 | 17 | 15.4 | 15 | 14.5 | 14.1 | 13.9 | 13.7 | 13.6 | 13.2 | 13 | 11.6 | 10
Bishops Wood 132kV | Upton Warren 132/66/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 18.7 | 18.3 | 17.9 | 17.3 | 17 | 15.2 | 14.6 | 13.8 | 13 | 12.2 | 11.4 | 10.6 | 8 | 5.8 | 8.1 | 7.5 | 7 | 0 | 0
Bishops Wood 132kV | Upton Warren 132/66/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 18.7 | 18.2 | 17.7 | 17.3 | 17 | 15.3 | 14.8 | 13.9 | 13.1 | 12.3 | 10.9 | 10.2 | 9 | 8.7 | 8.2 | 7.7 | 7.2 | 1.6 | 0
Bishops Wood 132kV | Upton Warren 132/66/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 18.7 | 18.4 | 18.1 | 17.7 | 17.4 | 17.1 | 15.4 | 14.9 | 14.3 | 12.4 | 10.4 | 9.1 | 7.1 | 6.2 | 5.6 | 4.8 | 4 | 0 | 3.9
Bishops Wood 132kV | UPTON WARREN 132kV S STN | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 31.3 | 30.4 | 27.2 | 26.9 | 26.6 | 26.1 | 28.5 | 28 | 27.3 | 26.6 | 24.5 | 24.1 | 23.8 | 23.4 | 23 | 21.9 | 21.5 | 17.7 | 13.1
Bishops Wood 132kV | UPTON WARREN 132kV S STN | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 31.3 | 29.9 | 25 | 24.1 | 22.5 | 20.4 | 23.9 | 22.8 | 20.7 | 18.4 | 15.9 | 13.6 | 10.5 | 8.3 | 23 | 21.4 | 19.7 | 9.9 | 0
Bishops Wood 132kV | UPTON WARREN 132kV S STN | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 31.3 | 29.7 | 27.1 | 25.7 | 23.9 | 22.1 | 27.1 | 24.4 | 21.8 | 19.5 | 15.9 | 13.8 | 11.5 | 25.8 | 24.4 | 22.9 | 21.3 | 11 | 0
Bishops Wood 132kV | UPTON WARREN 132kV S STN | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 31.3 | 30.2 | 25.4 | 24.9 | 24.3 | 23.4 | 25.6 | 24.7 | 24 | 14.9 | 12.9 | 11.6 | 9.6 | 8.7 | 8.1 | 7.3 | 6.5 | 0 | 11.1
Bishops Wood 132kV | Warndon 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 72.1 | 71.5 | 71.3 | 71 | 70.8 | 70.6 | 71.4 | 71.3 | 71.2 | 71.1 | 70.9 | 70.7 | 70.6 | 70.5 | 69.8 | 69.8 | 69.8 | 69.5 | 68.6
Bishops Wood 132kV | Warndon 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 72.1 | 71.2 | 70.8 | 70.4 | 69.7 | 69.3 | 70.8 | 70.5 | 69.2 | 68.9 | 67.3 | 66.1 | 65.7 | 65.3 | 64.8 | 64.3 | 63.8 | 42.1 | 0
Bishops Wood 132kV | Warndon 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 72.1 | 71 | 70.4 | 69.6 | 69.1 | 68.3 | 69.8 | 68.1 | 66 | 65.5 | 64.5 | 64 | 63.6 | 63.2 | 62.8 | 62.4 | 61.9 | 23 | 0
Bishops Wood 132kV | Warndon 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 72.1 | 71.4 | 71.1 | 70.8 | 70.5 | 69.8 | 71.2 | 70.7 | 69.8 | 69.6 | 68.3 | 67.3 | 66.9 | 66.7 | 66.6 | 66.5 | 66.3 | 64.7 | 62.7
Bishops Wood 132kV | WOOFFERTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.7 | 8.6 | 8.6 | 8.6 | 8.5 | 8.5 | 8.1 | 8.1 | 8.1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2.9 | 0
Bishops Wood 132kV | WOOFFERTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.7 | 8.6 | 8.5 | 7.9 | 6 | 4 | 7.9 | 7.8 | 7.7 | 7.5 | 7.1 | 5.6 | 3.9 | 2.2 | 1 | 0 | 0 | 0 | 0
Bishops Wood 132kV | WOOFFERTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.7 | 8.6 | 8.5 | 7.3 | 5.5 | 3.3 | 7.9 | 7.8 | 7.7 | 7.6 | 6.8 | 5.2 | 3.9 | 2.6 | 1.6 | 0 | 0 | 0 | 0
Bishops Wood 132kV | WOOFFERTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.7 | 8.6 | 8.6 | 8.5 | 8.5 | 7.3 | 8.1 | 8.1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7.9 | 7.9 | 0 | 0
Bishops Wood 132kV | Worcester 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 28.8 | 28.7 | 28.5 | 28.3 | 28.1 | 27.9 | 28.3 | 28.1 | 28 | 27.9 | 27.8 | 27.7 | 27.6 | 27.6 | 27.5 | 27.5 | 27.5 | 26.8 | 26.1
Bishops Wood 132kV | Worcester 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 28.8 | 28.5 | 28.1 | 27.8 | 27.4 | 27.2 | 27.8 | 27.6 | 27.3 | 26.8 | 26.4 | 26 | 25.7 | 25.3 | 25 | 24.6 | 21.6 | 0.6 | 0
Bishops Wood 132kV | Worcester 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 28.8 | 28.4 | 27.8 | 27.5 | 27.2 | 26.4 | 27.4 | 26.8 | 26.3 | 25.8 | 25.4 | 25 | 24.3 | 23.5 | 23.2 | 22.9 | 22.1 | 0 | 0
Bishops Wood 132kV | Worcester 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 28.8 | 28.6 | 28.3 | 28.1 | 27.9 | 27.5 | 28 | 27.8 | 27.7 | 27.5 | 27.2 | 26.8 | 26.8 | 26.6 | 26.5 | 26.4 | 26.3 | 24.7 | 9.5
Bishops Wood 132kV | WRIBBENHALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.4 | 15.4 | 15.3 | 15.3 | 15.3 | 15.3 | 16.9 | 16.8 | 16.6 | 16 | 15.5 | 15.2 | 14.9 | 14.8 | 14.6 | 14.5 | 14.3 | 13.1 | 11.5
Bishops Wood 132kV | WRIBBENHALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.4 | 15.3 | 15.2 | 15.2 | 15.2 | 15.3 | 15.8 | 15.2 | 14.6 | 13.9 | 13.2 | 12.4 | 11.7 | 10.9 | 10.4 | 9.9 | 9.4 | 6.2 | 3.1
Bishops Wood 132kV | WRIBBENHALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.4 | 15.3 | 15.2 | 15.2 | 15.2 | 15.4 | 16.4 | 15.6 | 15 | 14.3 | 13.7 | 13 | 12.3 | 11.7 | 11.3 | 10.8 | 10.4 | 6.4 | 4.4
Bishops Wood 132kV | WRIBBENHALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.4 | 15.3 | 15.3 | 15.2 | 15.3 | 15.4 | 16.7 | 16.5 | 15.9 | 15.4 | 14.8 | 14.4 | 14 | 13.7 | 13.5 | 13.2 | 13 | 10.7 | 7.7
Bushbury 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.4 | 16 | 15.8 | 15.7 | 15.7 | 15.6 | 21.8 | 21.7 | 21.5 | 21.3 | 21 | 20.9 | 20.7 | 20.6 | 20.6 | 20.5 | 20.5 | 20 | 19.3
Bushbury 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.4 | 15.8 | 15.6 | 15.3 | 15.1 | 14.9 | 20.8 | 20.5 | 20.1 | 19.8 | 19.4 | 19 | 18.7 | 18.4 | 18.2 | 18 | 17.8 | 16.1 | 14.6
Bushbury 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.4 | 15.8 | 15.5 | 15.5 | 15.4 | 15.1 | 21.1 | 20.7 | 20.4 | 20.1 | 19.8 | 19.6 | 18.8 | 18.5 | 18.3 | 18.1 | 17.9 | 16.6 | 15.8
Bushbury 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.4 | 15.8 | 15.6 | 15.4 | 15.3 | 15.2 | 21.2 | 21 | 20.7 | 20.4 | 20.2 | 20 | 19.8 | 19.7 | 19.7 | 19.6 | 19.5 | 18.2 | 17
Bushbury 132kV | Bushbury B-C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 28.7 | 28.5 | 28.3 | 28.2 | 28 | 27.8 | 25.9 | 25.7 | 25.6 | 25.4 | 25.1 | 24.9 | 24.7 | 24.7 | 24.6 | 24.6 | 24.5 | 23.8 | 22.7
Bushbury 132kV | Bushbury B-C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 28.7 | 28.3 | 27.9 | 27.6 | 27.2 | 25.8 | 24.7 | 24.1 | 22.8 | 21.5 | 20.1 | 18.9 | 18.2 | 17.4 | 16.8 | 16.1 | 15.4 | 12.7 | 10.1
Bushbury 132kV | Bushbury B-C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 28.7 | 28.2 | 27.6 | 27.2 | 26.3 | 24.9 | 24.4 | 22.8 | 21.3 | 19.9 | 18.3 | 17.4 | 15.7 | 15.1 | 14.6 | 14.1 | 13.7 | 11.2 | 9
Bushbury 132kV | Bushbury B-C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 28.7 | 28.5 | 28.1 | 27.9 | 27.6 | 26.3 | 24.8 | 24.3 | 23.2 | 22 | 20.7 | 19.7 | 19.3 | 18.8 | 18.4 | 18.1 | 17.8 | 15.8 | 13.8
Bushbury 132kV | BUSHBURY C 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 14.5 | 14.4 | 13.9 | 13.3 | 12.4 | 11.3 | 61.1 | 60.6 | 59.9 | 59.7 | 59.3 | 59 | 58.8 | 58.6 | 58.4 | 58.3 | 58.2 | 52.1 | 53.2
Bushbury 132kV | BUSHBURY C 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 14.5 | 13.9 | 12.4 | 10 | 6.8 | 3 | 54.9 | 48.7 | 25.9 | 25.8 | 25.6 | 25.3 | 25 | 24.5 | 24.3 | 24.1 | 25.3 | 21.5 | 19.2
Bushbury 132kV | BUSHBURY C 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 14.5 | 13.9 | 12.2 | 10 | 7 | 3 | 55.3 | 48.8 | 26 | 25.9 | 25.7 | 25.5 | 25.2 | 24.9 | 24.8 | 24.7 | 25.7 | 22.5 | 21.6
Bushbury 132kV | BUSHBURY C 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 14.5 | 14 | 12.5 | 10.4 | 7.5 | 3.8 | 55.6 | 48.8 | 26 | 26 | 25.9 | 25.8 | 25.6 | 25.5 | 25.5 | 25.4 | 26.1 | 24.9 | 23.6
Bushbury 132kV | FOUR ASHES 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | FOUR ASHES 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | FOUR ASHES 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | FOUR ASHES 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bushbury 132kV | I54 Busines Park 33/11kv | Primary Substation | 11 | Counterfactual | Headroom (MW) | 24.4 | 24.4 | 24.3 | 24.3 | 24.2 | 24.1 | 24.3 | 24.2 | 24 | 24 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.8 | 23.7 | 23.6 | 23.5
Bushbury 132kV | I54 Busines Park 33/11kv | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 24.4 | 24.4 | 24.3 | 24.3 | 24.1 | 23.4 | 22.9 | 22.5 | 22.3 | 22.2 | 22.1 | 22.1 | 21.8 | 21.5 | 21.3 | 20.4 | 20.4 | 20.2 | 19.9
Bushbury 132kV | I54 Busines Park 33/11kv | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 24.4 | 24.4 | 24.3 | 24.1 | 23.8 | 23.2 | 23 | 22.8 | 22.7 | 22.6 | 20.8 | 20.4 | 20.1 | 20.1 | 20 | 20 | 20 | 19.7 | 19.5
Bushbury 132kV | I54 Busines Park 33/11kv | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 24.4 | 24.4 | 24.3 | 24.3 | 24.1 | 23.4 | 23.1 | 22.5 | 22.3 | 22.3 | 22.2 | 22.1 | 22.1 | 21.8 | 21.5 | 20.6 | 20.6 | 20.5 | 20.3
Bushbury 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 56.6 | 56.4 | 56.1 | 55.6 | 55.1 | 54.6 | 53.6 | 53.2 | 52.7 | 52.3 | 51.7 | 51.3 | 50.9 | 50.4 | 50 | 48.6 | 46.4 | 43.5 | 40.9
Bushbury 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 56.6 | 56.2 | 55.5 | 54.3 | 52.6 | 50.6 | 51 | 48.7 | 46.8 | 45.3 | 43.7 | 42.1 | 37.8 | 33 | 32.1 | 31 | 29.8 | 23.5 | 18
Bushbury 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 56.6 | 56.1 | 55.1 | 53.7 | 52.5 | 50.6 | 51 | 48.6 | 46.9 | 45.3 | 42.7 | 36.4 | 34.9 | 33.4 | 32.3 | 31.3 | 30.2 | 24.2 | 20.9
Bushbury 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 56.6 | 56.4 | 55.7 | 54.9 | 53.6 | 51.9 | 51.9 | 50.7 | 49.1 | 47.8 | 46.4 | 45.5 | 43.2 | 38.6 | 37.2 | 36.7 | 36.1 | 31.5 | 26.9
Bushbury 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 53.1 | 53 | 52.8 | 52.6 | 52.3 | 52 | 50 | 49.8 | 49.5 | 49.3 | 48.9 | 48.6 | 48.3 | 48.2 | 48 | 47.8 | 49.9 | 49.2 | 47.3
Bushbury 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 53.1 | 52.7 | 52.3 | 51.6 | 50.8 | 49.9 | 48.9 | 48.1 | 47.3 | 46.4 | 45.4 | 44.4 | 43.3 | 42.2 | 41.4 | 40.6 | 43 | 38.2 | 33
Bushbury 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 53.1 | 52.5 | 51.9 | 51.3 | 50.6 | 49.7 | 48.8 | 47.7 | 46.6 | 45.5 | 44.4 | 43.4 | 42.4 | 41.4 | 40.7 | 39.9 | 42.5 | 37.8 | 34.2
Bushbury 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 53.1 | 52.9 | 52.6 | 52.3 | 51.8 | 51.2 | 49.5 | 49.2 | 48.9 | 48.3 | 47.5 | 47 | 46.4 | 46 | 45.7 | 45.4 | 48.5 | 45 | 40.7
Bushbury 132kV | Wednesfield 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 56.3 | 55.4 | 55 | 54.6 | 54.2 | 53.9 | 54 | 53.8 | 53.6 | 53.4 | 53.2 | 53 | 52.9 | 52.8 | 52.8 | 52.6 | 52.5 | 51.2 | 49.6
Bushbury 132kV | Wednesfield 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 56.3 | 54.9 | 54.1 | 53.4 | 52.8 | 52.2 | 53 | 52.6 | 52.2 | 51.7 | 50.8 | 50.1 | 48.9 | 48 | 47.2 | 46.2 | 45.2 | 40.2 | 35.3
Bushbury 132kV | Wednesfield 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 56.3 | 54.6 | 53.5 | 52.6 | 51.6 | 50.6 | 52 | 50.6 | 49.4 | 48.3 | 46.7 | 45.9 | 45.1 | 44.3 | 43.5 | 42.7 | 41.8 | 34.9 | 30.6
Bushbury 132kV | Wednesfield 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 56.3 | 55.2 | 54.6 | 54.1 | 53.5 | 52.9 | 53.4 | 52.9 | 52.6 | 52.2 | 51.8 | 51.3 | 50.4 | 49.9 | 49.5 | 49.1 | 48.6 | 45.2 | 41.1
Bustleholm 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 58 | 58 | 57.8 | 57.7 | 57.6 | 57.4 | 57.2 | 57.1 | 57.1 | 56.9 | 56.8 | 56.6 | 56.4 | 56.2 | 56.1 | 56.1 | 56 | 55.6 | 54.8
Bustleholm 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 58 | 58 | 57.8 | 57.7 | 57.6 | 56.9 | 56.8 | 56.2 | 55 | 54.7 | 52.2 | 51 | 50.5 | 50 | 49.5 | 49 | 48.4 | 45.7 | 43.1
Bustleholm 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 58 | 58 | 57.8 | 57.6 | 56.8 | 56 | 56 | 53.1 | 51.3 | 50.3 | 49.2 | 48.7 | 48.2 | 47.7 | 47.2 | 46.7 | 46.2 | 43.2 | 40.1
Bustleholm 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 58 | 58 | 57.8 | 57.7 | 57.6 | 57.4 | 57.2 | 56.5 | 56 | 55.4 | 53.2 | 52.4 | 51.8 | 51.6 | 51.4 | 51.2 | 50.9 | 49.1 | 47.1
Bustleholm 132kV | BUSTLEHOLM 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 27.8 | 27.7 | 27.6 | 27.6 | 27.5 | 26.4 | 25.9 | 25.8 | 25.8 | 25.8 | 25.7 | 25.7 | 25.7 | 25.7 | 25.6 | 25.6 | 25.6 | 25.4 | 24.7
Bustleholm 132kV | BUSTLEHOLM 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 27.8 | 27.5 | 26.4 | 26.2 | 26.1 | 25.8 | 25.7 | 25.5 | 25.4 | 25.3 | 25.1 | 24.8 | 24.5 | 24.1 | 23.6 | 23.1 | 22.6 | 20.1 | 17.4
Bustleholm 132kV | BUSTLEHOLM 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 27.8 | 27.5 | 26.2 | 25.9 | 25.5 | 25 | 25.3 | 24.8 | 24.4 | 23.9 | 23.4 | 23 | 22.6 | 22.1 | 21.7 | 21.3 | 20.8 | 17.7 | 14.9
Bustleholm 132kV | BUSTLEHOLM 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 27.8 | 27.6 | 27.5 | 27.5 | 26.4 | 26.2 | 25.8 | 25.7 | 25.6 | 25.5 | 25.4 | 25.4 | 25.3 | 25.2 | 25.1 | 24.9 | 24.7 | 23.1 | 21
Bustleholm 132kV | Kingstanding 132/11kVDummy | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 56 | 55.3 | 55 | 54.7 | 54.5 | 54.7 | 55 | 54.9 | 54.8 | 54.8 | 54.7 | 54.7 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 53.4 | 52.3
Bustleholm 132kV | Kingstanding 132/11kVDummy | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 56 | 54.8 | 54.3 | 53.4 | 52.9 | 52.9 | 53.4 | 53.4 | 53.3 | 53.1 | 52.8 | 52.3 | 51.8 | 51.1 | 50.5 | 49.8 | 49 | 45 | 40.4
Bustleholm 132kV | Kingstanding 132/11kVDummy | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 56 | 54.5 | 53.3 | 52.7 | 51.9 | 51.6 | 53 | 52.2 | 51.6 | 50.8 | 50.1 | 49.5 | 48.8 | 48.1 | 47.5 | 46.9 | 46.3 | 42.2 | 37.3
Bustleholm 132kV | Kingstanding 132/11kVDummy | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 56 | 55.1 | 54.7 | 54.4 | 53.6 | 54.3 | 54.8 | 54.7 | 54.6 | 53.4 | 53.4 | 53.3 | 53.3 | 53.3 | 53.2 | 53.2 | 53.1 | 51.2 | 47.6
Bustleholm 132kV | Ladywood 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 56.8 | 56.8 | 56.7 | 56.7 | 56.9 | 56.9 | 53.5 | 53.4 | 53.3 | 51.9 | 49.1 | 48.9 | 48.6 | 48.5 | 48.3 | 48.2 | 48 | 47.2 | 46.9
Bustleholm 132kV | Ladywood 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 56.8 | 56.8 | 56.7 | 56.7 | 54.1 | 51.3 | 51.2 | 50.6 | 49.7 | 33.8 | 30.1 | 29.5 | 29.2 | 29.1 | 31.9 | 32.8 | 32.5 | 31 | 30.2
Bustleholm 132kV | Ladywood 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 56.8 | 56.8 | 56.7 | 56.7 | 52.6 | 51.2 | 51.1 | 49.9 | 48.9 | 30.1 | 28.9 | 28.7 | 28.6 | 32.5 | 32.4 | 32.3 | 32 | 30.4 | 26
Bustleholm 132kV | Ladywood 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 56.8 | 56.8 | 56.7 | 56.7 | 54.3 | 51.6 | 51.2 | 50.6 | 49.7 | 34.5 | 30.1 | 27.9 | 27.8 | 27.8 | 27.8 | 27.8 | 27.6 | 26.3 | 25.8
Bustleholm 132kV | Perry Barr 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 32 | 32 | 32 | 31.9 | 31.9 | 31.8 | 31 | 31 | 30.9 | 30.7 | 30.6 | 30.6 | 30.6 | 30.6 | 30.6 | 30.6 | 30.5 | 30.3 | 29.8
Bustleholm 132kV | Perry Barr 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 32 | 32 | 32 | 31.9 | 31.5 | 31.1 | 30.5 | 30.4 | 30.3 | 29.5 | 29.2 | 29.1 | 28.9 | 28.7 | 28.6 | 28.4 | 25.6 | 24.1 | 22.2
Bustleholm 132kV | Perry Barr 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 32 | 32 | 32 | 31.5 | 30.9 | 30.5 | 30 | 29.5 | 29.2 | 28.3 | 25.6 | 25.5 | 25.4 | 25.3 | 25.2 | 25 | 24.6 | 22.3 | 19.8
Bustleholm 132kV | Perry Barr 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 32 | 32 | 32 | 31.9 | 31.8 | 31.5 | 30.7 | 30.6 | 30.5 | 29.9 | 29.7 | 29.7 | 29.6 | 29.6 | 29.6 | 29.5 | 29.3 | 28.3 | 25.2
Bustleholm 132kV | Rushall 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29 | 29 | 28.9 | 28.8 | 28.7 | 28.6 | 28.3 | 28.2 | 28.1 | 28 | 27.9 | 27.8 | 28 | 28 | 27.9 | 27.9 | 27.9 | 28 | 27.6
Bustleholm 132kV | Rushall 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29 | 29 | 28.9 | 28.5 | 27.9 | 27.3 | 27.8 | 27.5 | 27.1 | 26.6 | 25.8 | 25.3 | 25.8 | 25.3 | 24.7 | 24.2 | 23.6 | 21.8 | 19.1
Bustleholm 132kV | Rushall 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29 | 29 | 28.6 | 27.9 | 27.2 | 26.6 | 27.4 | 26.4 | 25.5 | 24.9 | 24.2 | 23.7 | 24.1 | 23.6 | 23.1 | 22.6 | 22.1 | 20.2 | 17.3
Bustleholm 132kV | Rushall 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29 | 29 | 28.9 | 28.8 | 28.6 | 28.1 | 28 | 27.8 | 27.6 | 27.5 | 27.1 | 26.7 | 27.4 | 27.2 | 26.9 | 26.8 | 26.5 | 25.7 | 23.6
Bustleholm 132kV | Smethwick 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.5 | 27.5 | 27.5 | 27.5 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.3 | 27.3 | 27.3 | 27.2
Bustleholm 132kV | Smethwick 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.4 | 27.4 | 27.4 | 27.3 | 26.6 | 26.5 | 26.4 | 25.5 | 25.4 | 25.4 | 25.3 | 25.1 | 24.1 | 22.8
Bustleholm 132kV | Smethwick 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 27.6 | 27.6 | 27.6 | 27.6 | 27.4 | 27.3 | 27.4 | 27.2 | 27.2 | 25.5 | 25.3 | 25.2 | 25 | 24.9 | 24.7 | 24.5 | 24.2 | 22.8 | 21.2
Bustleholm 132kV | Smethwick 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.5 | 27.4 | 27.4 | 27.4 | 26.8 | 26.7 | 26.7 | 26.6 | 26.5 | 26.5 | 26.5 | 26.5 | 25.4 | 24.9
Bustleholm 132kV | Winson Green 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.6 | 29.6 | 29.6 | 29.5 | 29.5 | 29.5 | 28.9 | 28.8 | 28.7 | 28.4 | 28.2 | 28.1 | 28 | 27.9 | 28 | 27.8 | 27.3 | 23.6 | 23.1
Bustleholm 132kV | Winson Green 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.6 | 29.6 | 29.6 | 29.5 | 29.3 | 28.9 | 28.3 | 27.9 | 27.2 | 24.3 | 23.3 | 22.4 | 21.4 | 20.4 | 19.9 | 19 | 17.9 | 14.3 | 13.1
Bustleholm 132kV | Winson Green 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.6 | 29.6 | 29.6 | 29.3 | 28.9 | 28.5 | 27.9 | 26.3 | 24.9 | 21.8 | 20.3 | 19.5 | 18.7 | 18 | 17.7 | 16.9 | 16.2 | 13.1 | 11.5
Bustleholm 132kV | Winson Green 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.6 | 29.6 | 29.6 | 29.5 | 29.5 | 29.2 | 28.5 | 28 | 27.2 | 24.3 | 23.2 | 22.3 | 21.5 | 20.8 | 20.6 | 19.8 | 19.1 | 16.2 | 15.2
Cellarhead 132kV | BEARSTONE | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 7.2 | 7.1 | 7 | 6.6 | 6.5 | 6.3 | 5.9 | 5.5 | 5 | 4.4 | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 3.1 | 1.7 | 0
Cellarhead 132kV | BEARSTONE | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 7.1 | 7 | 6.4 | 5.8 | 5.3 | 4.6 | 3.9 | 3.2 | 2.4 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | BEARSTONE | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 7.1 | 7 | 6.5 | 6.2 | 5.8 | 5.3 | 4.5 | 3.8 | 3.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | BEARSTONE | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 7.2 | 7 | 7 | 6.5 | 6.2 | 5.8 | 5.2 | 4.7 | 4.1 | 3.5 | 3 | 2.6 | 2.2 | 1.9 | 1.6 | 1.3 | 0 | 0
Cellarhead 132kV | Boothen 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Boothen 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 14.9 | 14.8 | 14.4 | 13.9
Cellarhead 132kV | Boothen 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.8 | 14.7 | 14.6 | 14.6 | 0 | 0
Cellarhead 132kV | Boothen 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | BOOTHEN 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | BOOTHEN 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.9 | 51.8 | 51.8 | 51.5 | 51.1
Cellarhead 132kV | BOOTHEN 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.8 | 51.7 | 51.7 | 51.6 | 0 | 0
Cellarhead 132kV | BOOTHEN 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | Burslem 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 56.2 | 55.4 | 55.6 | 55.9 | 56.1 | 56.3 | 56.4 | 56.5 | 56.5 | 56.5 | 56.3 | 56.1 | 55.9 | 55.7 | 55.5 | 55.5 | 55.4 | 55.2 | 56.3
Cellarhead 132kV | Burslem 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 56.2 | 55 | 54.9 | 54.9 | 54.9 | 54.7 | 55.5 | 55.1 | 54.7 | 54.6 | 52.8 | 51.5 | 50.7 | 50.4 | 53.1 | 52.6 | 52.1 | 49.5 | 47
Cellarhead 132kV | Burslem 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 56.2 | 54.8 | 54.4 | 54.4 | 53.5 | 53.3 | 54.5 | 52.8 | 51.3 | 50.6 | 49.4 | 49 | 48.5 | 48.1 | 50.9 | 50.5 | 50 | 47.2 | 44.2
Cellarhead 132kV | Burslem 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 56.2 | 55.2 | 55.3 | 55.5 | 55.6 | 55.6 | 56 | 55.5 | 55.2 | 55.1 | 54.6 | 53.2 | 52.8 | 52.6 | 55.1 | 55.1 | 55 | 54.5 | 52.8
Cellarhead 132kV | CAULDON | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.3 | 10.3 | 10.2 | 10 | 9.9 | 9.8 | 9.9 | 9.7 | 9.5 | 9.3 | 9 | 8.5 | 8 | 7.6 | 7.3 | 7.2 | 7.1 | 6.3 | 5.4
Cellarhead 132kV | CAULDON | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.3 | 10.3 | 9.9 | 9.6 | 9.3 | 8.9 | 8.8 | 8.1 | 7.2 | 5.8 | 5 | 4.5 | 4.1 | 3.6 | 3.1 | 2.8 | 2.4 | 0.5 | 0
Cellarhead 132kV | CAULDON | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.3 | 10.2 | 9.8 | 9.6 | 9.4 | 9 | 8.6 | 7.5 | 6.5 | 5.7 | 5.2 | 4.8 | 4.4 | 3.9 | 3.5 | 3.2 | 2.9 | 1.2 | 0
Cellarhead 132kV | CAULDON | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.3 | 10.3 | 10.1 | 9.9 | 9.8 | 9.6 | 9.5 | 9 | 8.3 | 7 | 6.2 | 6 | 5.7 | 5.5 | 5.3 | 5.1 | 4.9 | 3.6 | 2.2
Cellarhead 132kV | CHEADLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.5 | 16.5 | 16.3 | 16 | 15.7 | 15.3 | 14.1 | 13.7 | 13.2 | 12.7 | 12 | 11.5 | 11.2 | 10.9 | 10.6 | 10.4 | 9.9 | 7.6 | 5
Cellarhead 132kV | CHEADLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.5 | 16.3 | 15.9 | 14.9 | 13.9 | 12.9 | 12.6 | 11.2 | 9.8 | 8.4 | 7 | 5.4 | 3.7 | 2 | 1.1 | 0 | 0 | 0 | 0
Cellarhead 132kV | CHEADLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.5 | 16.3 | 15.6 | 15.2 | 14.4 | 13.3 | 13.6 | 12.1 | 10.7 | 9.4 | 8 | 3.5 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | CHEADLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.5 | 16.4 | 16.1 | 15.6 | 15.2 | 14.4 | 13.8 | 13.2 | 12.2 | 11.1 | 9.9 | 9 | 8.1 | 7.2 | 6.7 | 6.3 | 4.4 | 0.5 | 0
Cellarhead 132kV | CHEDDLETON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.3 | 11.3 | 11.3 | 11.2 | 11.1 | 11 | 10.8 | 10.7 | 10.5 | 10.3 | 10 | 9.8 | 9.8 | 9.7 | 9.7 | 9.6 | 9.6 | 9.3 | 8.8
Cellarhead 132kV | CHEDDLETON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.3 | 11.2 | 11.1 | 10.8 | 10.5 | 10.2 | 9.7 | 9.3 | 8.8 | 8.3 | 8.1 | 7.8 | 7.6 | 7.4 | 7.3 | 7.1 | 6.9 | 5.9 | 0
Cellarhead 132kV | CHEDDLETON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.3 | 11.2 | 11 | 10.8 | 10.5 | 10.3 | 9.8 | 9.3 | 8.8 | 8.4 | 8.1 | 8 | 7.8 | 7.6 | 7.5 | 7.3 | 7.2 | 6.3 | 5.7
Cellarhead 132kV | CHEDDLETON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.3 | 11.3 | 11.2 | 11 | 10.7 | 10.4 | 10 | 9.7 | 9.2 | 8.8 | 8.6 | 8.5 | 8.4 | 8.4 | 8.3 | 8.3 | 8.2 | 7.5 | 6.6
Cellarhead 132kV | CONGLETON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17 | 17 | 17 | 16.9 | 16.7 | 16.5 | 16.3 | 15.9 | 15.6 | 15.3 | 14.8 | 14.5 | 14.3 | 14.1 | 14 | 13.7 | 13.5 | 12.5 | 11.3
Cellarhead 132kV | CONGLETON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17 | 17 | 16.6 | 16.1 | 15.6 | 15.2 | 14.3 | 13.7 | 13.1 | 12.6 | 12 | 11.4 | 10.5 | 9.6 | 14.3 | 14.1 | 13.9 | 10.4 | 7.1
Cellarhead 132kV | CONGLETON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17 | 16.8 | 16.3 | 15.7 | 15.5 | 14.7 | 14.1 | 13.3 | 12.7 | 12.2 | 11.5 | 10.7 | 10.2 | 14 | 13.7 | 13.5 | 13.3 | 10.4 | 1.8
Cellarhead 132kV | CONGLETON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17 | 17 | 16.8 | 16.6 | 16.3 | 16 | 15.2 | 11.2 | 10.7 | 10.2 | 9.7 | 9.3 | 8.9 | 8.3 | 8.1 | 7.9 | 7.7 | 2.7 | 0
Cellarhead 132kV | COTES HEATH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.7 | 7.7 | 7.7 | 7.6 | 7.5 | 7.5 | 7.3 | 7.2 | 7 | 6.8 | 6.6 | 6.4 | 6.3 | 6.2 | 6.2 | 6.1 | 8.9 | 8.4 | 7.8
Cellarhead 132kV | COTES HEATH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.7 | 7.7 | 7.6 | 7.4 | 7.2 | 7 | 6.8 | 6.5 | 6.2 | 6 | 5.7 | 5.4 | 5.1 | 4.8 | 4.6 | 4.4 | 7.1 | 6 | 4.6
Cellarhead 132kV | COTES HEATH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.7 | 7.7 | 7.6 | 7.5 | 7.4 | 7.3 | 7 | 6.8 | 6.5 | 6.2 | 5.9 | 5.6 | 5.4 | 5.1 | 4.9 | 4.8 | 7.5 | 6.5 | 6
Cellarhead 132kV | COTES HEATH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.7 | 7.7 | 7.6 | 7.6 | 7.5 | 7.4 | 7.2 | 6.9 | 6.7 | 6.5 | 6.3 | 6.1 | 5.9 | 5.8 | 5.7 | 5.6 | 8.4 | 7.6 | 6.5
Cellarhead 132kV | ECCLESHALL PRIMARY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 6.6 | 6.5 | 6.5 | 6.4 | 6.4 | 6.3 | 6.2 | 6.2 | 6.1 | 6 | 6 | 5.9 | 5.9 | 5.8 | 5.7 | 5.6 | 4.3 | 1.6
Cellarhead 132kV | ECCLESHALL PRIMARY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 6.6 | 6.5 | 6.4 | 6.3 | 6.2 | 6.2 | 5.8 | 3.8 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | ECCLESHALL PRIMARY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 6.6 | 6.4 | 6.3 | 6.2 | 6.2 | 6.1 | 6 | 4 | 2.7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | ECCLESHALL PRIMARY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 6.6 | 6.5 | 6.5 | 6.4 | 6.4 | 6.4 | 6.3 | 6.3 | 5.8 | 4.7 | 3.9 | 3.1 | 2.3 | 1.8 | 1.2 | 1.1 | 0 | 0
Cellarhead 132kV | ENDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17 | 17 | 16.9 | 16.7 | 16.6 | 16.5 | 16.7 | 16.5 | 16.4 | 15.9 | 15.6 | 15.3 | 15 | 14.9 | 14.7 | 14.6 | 14.5 | 13.5 | 12.3
Cellarhead 132kV | ENDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17 | 16.9 | 16.7 | 16.4 | 15.8 | 15.4 | 15.8 | 15.4 | 14.9 | 14.2 | 13.6 | 12.8 | 12 | 11.4 | 11 | 10.6 | 10.1 | 6.4 | 0
Cellarhead 132kV | ENDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17 | 16.8 | 16.5 | 16.4 | 16 | 15.7 | 16.3 | 15.6 | 14.9 | 14.3 | 13.6 | 13 | 12.5 | 11.9 | 11.6 | 11.2 | 10.9 | 8.7 | 6.3
Cellarhead 132kV | ENDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17 | 17 | 16.8 | 16.7 | 16.5 | 16.1 | 16.5 | 16.4 | 15.8 | 15.4 | 14.9 | 14.4 | 14 | 13.7 | 13.5 | 13.4 | 13.2 | 11.5 | 9.4
Cellarhead 132kV | FORSBROOK 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 76.8 | 76.1 | 75.7 | 75.1 | 74.5 | 73.7 | 72.7 | 71.3 | 69.8 | 68.3 | 66.5 | 65 | 63.9 | 63 | 62.2 | 61.6 | 60.9 | 56.9 | 52.2
Cellarhead 132kV | FORSBROOK 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 76.8 | 75.8 | 74.6 | 72.8 | 70.7 | 68.6 | 65.7 | 62.8 | 59.7 | 56.1 | 53.3 | 50.6 | 48 | 45.2 | 43.5 | 41.8 | 38.4 | 27.5 | 18.3
Cellarhead 132kV | FORSBROOK 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 76.8 | 75.6 | 74.1 | 73.1 | 71.4 | 69.3 | 66.6 | 63.2 | 59.9 | 57 | 54.6 | 49.3 | 47.2 | 42.4 | 41 | 39.5 | 37.7 | 29.4 | 24.8
Cellarhead 132kV | FORSBROOK 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 76.8 | 76 | 75.2 | 74.2 | 73.1 | 71.6 | 69.1 | 66.8 | 64.2 | 61.3 | 58.7 | 57.3 | 56 | 54.6 | 53.8 | 53 | 50.6 | 42.4 | 34.6
Cellarhead 132kV | FROGHALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
Cellarhead 132kV | FROGHALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 5.9 | 2.7
Cellarhead 132kV | FROGHALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 5.5
Cellarhead 132kV | FROGHALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.7 | 6.7
Cellarhead 132kV | GNOSALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.9 | 5.8 | 5.8 | 5.8 | 5.7 | 5.7 | 5.6 | 5.6 | 5.5 | 5.4 | 5.3 | 5.3 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 4.6 | 1.7
Cellarhead 132kV | GNOSALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.9 | 5.8 | 5.8 | 5.6 | 5.4 | 5.2 | 5 | 4.8 | 4 | 2.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | GNOSALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.9 | 5.8 | 5.7 | 5.6 | 5.4 | 5.2 | 5.1 | 4.9 | 4.3 | 2.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | GNOSALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.9 | 5.8 | 5.8 | 5.7 | 5.7 | 5.6 | 5.6 | 5.5 | 5.4 | 5.3 | 5 | 4.2 | 3.3 | 2.4 | 1.9 | 1.3 | 1.2 | 0 | 0
Cellarhead 132kV | GOLDENHILL BANK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.9 | 17.9 | 17.8 | 17.8 | 17.7 | 17.7 | 17.5 | 17.1 | 16.7 | 16.3 | 15.7 | 15.4 | 15.2 | 14.9 | 14.7 | 14.5 | 14.2 | 13.1 | 11.6
Cellarhead 132kV | GOLDENHILL BANK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.9 | 17.8 | 17.7 | 17.4 | 16.8 | 16.3 | 15.2 | 14.5 | 13.8 | 13.2 | 12.5 | 11.7 | 10.8 | 9.7 | 15.5 | 14.8 | 14 | 9.2 | 4.7
Cellarhead 132kV | GOLDENHILL BANK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.9 | 17.8 | 17.6 | 17.2 | 16.6 | 15.7 | 14.8 | 13.9 | 13.1 | 12.5 | 11.7 | 10.7 | 10.2 | 15.4 | 15.4 | 15.2 | 13.6 | 10.1 | 1.8
Cellarhead 132kV | GOLDENHILL BANK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.9 | 17.9 | 17.8 | 17.7 | 17.7 | 17.3 | 16.2 | 12.1 | 11.5 | 10.9 | 10.3 | 9.9 | 9.4 | 8.7 | 8.5 | 8.3 | 8 | 2.7 | 0
Cellarhead 132kV | HIGH OFFLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9 | 9 | 8.9 | 8.8 | 8.7 | 8.4 | 8 | 7.7 | 7.4 | 7 | 7 | 4.5 | 1.6
Cellarhead 132kV | HIGH OFFLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.1 | 9.1 | 9.1 | 9 | 8.9 | 8.8 | 8 | 6 | 4 | 2.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HIGH OFFLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.1 | 9.1 | 9.1 | 9 | 9 | 8.9 | 8.4 | 6.4 | 4.2 | 2.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HIGH OFFLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9 | 8.9 | 8.7 | 7 | 6 | 4.9 | 4.1 | 3.3 | 2.4 | 1.8 | 1.3 | 1.2 | 0 | 0
Cellarhead 132kV | HILL CHORLTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.8 | 5.8 | 5.8 | 5.7 | 5.7 | 5.6 | 5.5 | 5.3 | 5 | 4.8 | 4.5 | 4.3 | 4.2 | 4.1 | 4 | 3.9 | 3.8 | 3.1 | 2.4
Cellarhead 132kV | HILL CHORLTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.8 | 5.8 | 5.7 | 5.5 | 5.2 | 5 | 4.6 | 4.3 | 3.9 | 3.6 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HILL CHORLTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.8 | 5.8 | 5.7 | 5.7 | 5.5 | 5.3 | 5.1 | 4.7 | 4.4 | 4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HILL CHORLTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.8 | 5.8 | 5.7 | 5.7 | 5.6 | 5.4 | 5.2 | 4.9 | 4.6 | 4.4 | 4.1 | 3.8 | 3.6 | 3.4 | 3.3 | 3.2 | 3 | 0 | 0
Cellarhead 132kV | HINSTOCK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.1 | 10.1 | 10 | 10 | 10 | 10 | 10 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.5 | 9.1 | 8.7 | 8.3 | 8.4 | 5.4 | 2
Cellarhead 132kV | HINSTOCK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.1 | 10 | 9.9 | 9.9 | 9.9 | 9.8 | 9.5 | 7.2 | 4.8 | 3.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HINSTOCK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.1 | 10 | 9.9 | 9.8 | 9.8 | 9.7 | 9.7 | 7.6 | 5 | 3.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HINSTOCK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.1 | 10.1 | 10 | 10 | 9.9 | 9.9 | 9.8 | 9.8 | 8.3 | 7.2 | 5.8 | 4.9 | 3.9 | 2.8 | 2.2 | 1.5 | 1.4 | 0 | 0
Cellarhead 132kV | HOOKGATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.3 | 7.2 | 7.2 | 7 | 6.9 | 6.6 | 6.6 | 6.4 | 6.1 | 5.7 | 5.1 | 4.7 | 4.5 | 4.3 | 4.1 | 3.9 | 3.8 | 2.4 | 0.9
Cellarhead 132kV | HOOKGATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.3 | 7.2 | 7 | 6.5 | 5.9 | 5.4 | 5.3 | 4.6 | 3.9 | 3.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HOOKGATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.3 | 7.2 | 6.9 | 6.6 | 6.3 | 5.9 | 5.9 | 5.2 | 4.5 | 3.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | HOOKGATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.3 | 7.2 | 7.1 | 6.9 | 6.6 | 6.4 | 6.2 | 5.9 | 5.4 | 4.8 | 4.2 | 3.7 | 3.3 | 2.9 | 2.6 | 1.8 | 1.7 | 0 | 0
Cellarhead 132kV | KINGSLEY HOLT 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.2 | 10.1 | 10 | 9.9 | 9.8 | 9.7 | 9.6 | 9.4 | 9.2 | 8.9 | 8.6 | 8.4 | 8.3 | 8.2 | 8.1 | 8 | 7.9 | 7.2 | 6.5
Cellarhead 132kV | KINGSLEY HOLT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.2 | 10 | 9.8 | 9.5 | 9.2 | 8.9 | 8.6 | 8.2 | 7.8 | 7.4 | 7.1 | 6.6 | 6.2 | 5.9 | 5.6 | 5.4 | 5 | 3.5 | 2.1
Cellarhead 132kV | KINGSLEY HOLT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.2 | 10 | 9.7 | 9.6 | 9.3 | 9 | 8.7 | 8.3 | 7.9 | 7.6 | 7.2 | 7 | 6.7 | 6.4 | 6.2 | 5.9 | 5.6 | 4.3 | 3.5
Cellarhead 132kV | KINGSLEY HOLT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.2 | 10 | 9.9 | 9.8 | 9.6 | 9.4 | 9.2 | 8.9 | 8.6 | 8.3 | 8 | 7.8 | 7.6 | 7.4 | 7.3 | 7.2 | 7 | 5.8 | 4.5
Cellarhead 132kV | KNYPERSLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.1 | 3.8 | 3.7 | 3.7 | 3.6 | 3.4 | 2.6 | 2.4 | 2.1 | 1.9 | 1.5 | 1.2 | 1.1 | 0.9 | 0.7 | 0.5 | 0 | 0 | 0
Cellarhead 132kV | KNYPERSLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.1 | 3.7 | 3.5 | 3.1 | 2.8 | 2.4 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 3 | 2.6 | 0 | 0
Cellarhead 132kV | KNYPERSLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.1 | 3.6 | 3.3 | 3 | 2.7 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 3.8 | 3.5 | 2.1 | 0 | 0
Cellarhead 132kV | KNYPERSLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.1 | 3.8 | 3.6 | 3.5 | 3.3 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | LEEK 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.4 | 13.4 | 13.2 | 13.1 | 13 | 12.7 | 12.8 | 12.5 | 12 | 11.5 | 11 | 10.6 | 10.3 | 10.1 | 9.9 | 9.8 | 9.6 | 8.6 | 7.2
Cellarhead 132kV | LEEK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.4 | 13.3 | 13 | 12.6 | 12.3 | 11.7 | 10.8 | 10.1 | 9.3 | 8.6 | 7.8 | 6.9 | 6.2 | 5.5 | 5 | 4.5 | 4 | 1 | 0
Cellarhead 132kV | LEEK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.4 | 13.2 | 12.7 | 12.6 | 12.2 | 11.5 | 10.6 | 9.7 | 8.8 | 8.1 | 7.4 | 6.8 | 6.2 | 5.6 | 5.2 | 4.7 | 4.2 | 3.3 | 1.2
Cellarhead 132kV | LEEK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.4 | 13.3 | 13.2 | 13 | 12.7 | 12.5 | 12 | 11.3 | 10.6 | 10.1 | 9.4 | 8.9 | 8.6 | 8.4 | 8.2 | 8 | 7.8 | 5.8 | 3.4
Cellarhead 132kV | Longton 132/33/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 56 | 55.7 | 55.3 | 54.9 | 54.6 | 54.1 | 53.4 | 53.2 | 53 | 52.7 | 52.4 | 52.2 | 52 | 51.9 | 51.7 | 51.6 | 51.4 | 50.5 | 48.7
Cellarhead 132kV | Longton 132/33/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 56 | 55.3 | 54.5 | 53.8 | 52.8 | 51.2 | 51.8 | 51.3 | 50.8 | 49.5 | 48 | 46.4 | 44.6 | 43.7 | 42.9 | 42.1 | 44 | 39.8 | 35.8
Cellarhead 132kV | Longton 132/33/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 56 | 55 | 53.8 | 52.6 | 51.4 | 50.2 | 51.2 | 50.1 | 48 | 46 | 44.4 | 43.2 | 42.4 | 44.3 | 43.7 | 43 | 42.3 | 35.2 | 31.4
Cellarhead 132kV | Longton 132/33/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 56 | 55.6 | 55 | 54.6 | 53.8 | 52.6 | 52.5 | 52.2 | 51.9 | 50.2 | 49 | 47.9 | 46.7 | 46.2 | 46 | 45.8 | 45.6 | 43.1 | 40.1
Cellarhead 132kV | MARKET DRAYTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.1 | 15.1 | 15 | 14.9 | 14.9 | 14.8 | 15.6 | 15.2 | 15 | 14.6 | 13.2 | 12.3 | 11.7 | 11.2 | 10.7 | 10.2 | 10.3 | 6.6 | 2.4
Cellarhead 132kV | MARKET DRAYTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.1 | 15 | 14.8 | 14.6 | 14.5 | 14.4 | 11.7 | 8.8 | 5.8 | 3.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | MARKET DRAYTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.1 | 15 | 14.7 | 14.5 | 14.3 | 13.8 | 12.3 | 9.3 | 6.2 | 4.1 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | MARKET DRAYTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.1 | 15 | 14.9 | 14.7 | 14.6 | 14.5 | 13.7 | 12.5 | 10.2 | 8.8 | 7.2 | 6 | 4.8 | 3.5 | 2.7 | 1.8 | 1.7 | 0 | 0
Cellarhead 132kV | Meaford C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 16.8 | 16.8 | 16.7 | 16.7 | 16.6 | 16.6 | 16.6 | 16.5 | 16.4 | 15.9 | 15.6 | 15.5 | 15.4 | 15.4 | 15.4 | 15.3 | 15.3 | 14.8 | 14.2
Cellarhead 132kV | Meaford C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 16.8 | 16.7 | 16.6 | 16.4 | 15.5 | 15.1 | 14.6 | 14.1 | 13.7 | 13.2 | 12.7 | 12.4 | 12.2 | 11.9 | 11.6 | 11.4 | 11.2 | 9.8 | 4
Cellarhead 132kV | Meaford C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 16.8 | 16.7 | 16.5 | 16.4 | 16 | 15.7 | 15.2 | 14.7 | 14.1 | 13.7 | 13.4 | 13.1 | 12.8 | 12.5 | 12.3 | 12.1 | 11.9 | 10.6 | 9.6
Cellarhead 132kV | Meaford C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 16.8 | 16.8 | 16.7 | 16.6 | 16.5 | 16.4 | 15.9 | 15.4 | 15 | 14.6 | 14.1 | 13.9 | 13.7 | 13.6 | 13.5 | 13.4 | 13.3 | 12.4 | 11.2
Cellarhead 132kV | MEAFORD C 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 73 | 72.8 | 72.3 | 71.6 | 70.8 | 70.1 | 69.2 | 67.3 | 65.2 | 63.4 | 61.1 | 59.7 | 58.9 | 58.3 | 57.7 | 57 | 59.2 | 54.2 | 48.3
Cellarhead 132kV | MEAFORD C 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 73 | 72.4 | 71 | 68.8 | 65.3 | 62.6 | 57.5 | 53.3 | 49.1 | 45.8 | 42.5 | 39.4 | 36.4 | 33.2 | 31 | 28.7 | 29.2 | 16 | 4
Cellarhead 132kV | MEAFORD C 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 73 | 72 | 70.2 | 68.8 | 66.7 | 63.6 | 59.6 | 55.2 | 50.6 | 47.3 | 44 | 40.9 | 38.3 | 35.6 | 33.7 | 31.6 | 32.4 | 20.5 | 12.8
Cellarhead 132kV | MEAFORD C 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 73 | 72.7 | 71.7 | 70.5 | 69.3 | 67.6 | 63.4 | 59.8 | 56.2 | 53.7 | 50.8 | 49 | 47.4 | 45.9 | 44.9 | 43.8 | 45.5 | 36.4 | 26.4
Cellarhead 132kV | Newcastle 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 26.7 | 26.7 | 27.3 | 27.3 | 27.3 | 26.7 | 26.7 | 26.7 | 26.6 | 26.5 | 26.4 | 26.3 | 26.2 | 26.1 | 26.1 | 26.1 | 26 | 26.2 | 25.8
Cellarhead 132kV | Newcastle 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 26.7 | 26.6 | 26.5 | 26.3 | 26.1 | 25.8 | 25.6 | 25.1 | 24.8 | 24.5 | 24.2 | 24 | 23.8 | 23.6 | 25.4 | 25.3 | 25.1 | 22.4 | 20.8
Cellarhead 132kV | Newcastle 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 26.7 | 26.5 | 26.4 | 26.2 | 25.9 | 25.6 | 25.1 | 24.6 | 24.2 | 23.9 | 23.6 | 23.4 | 23.2 | 25.1 | 24.9 | 24.7 | 22.5 | 21.5 | 20.1
Cellarhead 132kV | Newcastle 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 26.7 | 26.6 | 26.6 | 26.5 | 26.3 | 26.1 | 25.9 | 25.5 | 25.1 | 24.8 | 24.6 | 24.5 | 24.4 | 24.3 | 24.2 | 24.2 | 24.1 | 23.9 | 22.8
Cellarhead 132kV | NEWCASTLE 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 19.7 | 19.6 | 19.6 | 19.5 | 19.3 | 19.2 | 18.1 | 17.9 | 17.3 | 16.8 | 16.1 | 15.6 | 15.2 | 15 | 14.8 | 14.6 | 14.4 | 12.9 | 11.1
Cellarhead 132kV | NEWCASTLE 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 19.7 | 19.6 | 19.3 | 18.4 | 17.8 | 17.1 | 16.3 | 15.4 | 14.5 | 13.6 | 12.6 | 11.6 | 10.6 | 9.7 | 9 | 8.3 | 7.7 | 3.6 | 0
Cellarhead 132kV | NEWCASTLE 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 19.7 | 19.5 | 19.2 | 18.4 | 17.9 | 17.4 | 16.5 | 15.5 | 14.5 | 13.5 | 12.6 | 11.8 | 10.9 | 10.1 | 9.6 | 9 | 8.4 | 4.8 | 2.6
Cellarhead 132kV | NEWCASTLE 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 19.7 | 19.6 | 19.5 | 19.3 | 18.5 | 18.2 | 17.5 | 16.8 | 16.1 | 15.3 | 14.5 | 13.9 | 13.4 | 12.9 | 12.6 | 12.3 | 12 | 9.1 | 6
Cellarhead 132kV | SCOT HAY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.7 | 7.6 | 7.6 | 7.5 | 7.4 | 7.2 | 7 | 6.7 | 6.4 | 6 | 5.5 | 5.2 | 5 | 4.9 | 4.8 | 4.7 | 4.5 | 3.5 | 2.4
Cellarhead 132kV | SCOT HAY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.7 | 7.6 | 7.4 | 7 | 6.6 | 6.2 | 5.7 | 5.1 | 4.6 | 4.1 | 3.5 | 2.8 | 2.3 | 1.7 | 1.3 | 0.9 | 0 | 0 | 0
Cellarhead 132kV | SCOT HAY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.7 | 7.5 | 7.3 | 7.1 | 6.9 | 6.5 | 6.1 | 5.5 | 4.9 | 4.4 | 3.9 | 3.3 | 2.8 | 2.3 | 1.9 | 1.6 | 1.2 | 0 | 0
Cellarhead 132kV | SCOT HAY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.7 | 7.6 | 7.5 | 7.4 | 7.2 | 6.9 | 6.5 | 6.1 | 5.6 | 5.2 | 4.7 | 4.4 | 4.1 | 3.8 | 3.6 | 3.4 | 3.2 | 1.3 | 0
Cellarhead 132kV | SIMPLEX 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.1 | 11.1 | 11 | 10.9 | 10.7 | 10.6 | 14.2 | 14.5 | 13.8 | 13.1 | 12.4 | 11.9 | 11.6 | 11.3 | 11 | 10.8 | 10.6 | 9 | 7.3
Cellarhead 132kV | SIMPLEX 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.1 | 10.9 | 10.6 | 10.2 | 9.5 | 8.9 | 12.2 | 11 | 9.8 | 8.6 | 7.5 | 6.4 | 5.4 | 3.7 | 2.7 | 1.5 | 0 | 0 | 0
Cellarhead 132kV | SIMPLEX 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.1 | 10.8 | 10.5 | 10 | 9.4 | 8.8 | 13 | 11.7 | 10.4 | 9.2 | 8.3 | 4.7 | 3.8 | 2.7 | 1.8 | 0.9 | 0 | 0 | 0
Cellarhead 132kV | SIMPLEX 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.1 | 11 | 10.7 | 10.4 | 9.9 | 9.3 | 13.5 | 12.4 | 11.4 | 10.3 | 9.4 | 8.8 | 8.2 | 7.7 | 7.5 | 7.2 | 5.4 | 2.2 | 0
Cellarhead 132kV | Stagefields 132/33/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 58.9 | 58.1 | 57.6 | 57.2 | 56.8 | 56.2 | 57.4 | 57.1 | 56.8 | 56.6 | 56.2 | 56 | 55.8 | 55.6 | 55.4 | 55.2 | 55 | 54.3 | 52.3
Cellarhead 132kV | Stagefields 132/33/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 58.9 | 57.7 | 56.8 | 56.1 | 54.7 | 52.5 | 55.3 | 54.4 | 53.3 | 51.9 | 49.9 | 47.6 | 44.7 | 43.6 | 42.9 | 42.2 | 41.4 | 37.7 | 34.1
Cellarhead 132kV | Stagefields 132/33/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 58.9 | 57.4 | 56.1 | 54.6 | 52.7 | 50.9 | 54.3 | 52.6 | 49.7 | 47.1 | 44.7 | 42.9 | 42.2 | 41.5 | 40.9 | 40.3 | 39.7 | 35.7 | 31.1
Cellarhead 132kV | Stagefields 132/33/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 58.9 | 58 | 57.3 | 56.8 | 55.9 | 54.5 | 56.3 | 55.4 | 55 | 54.5 | 53.1 | 51.6 | 50.1 | 49.3 | 48.6 | 48.1 | 47.8 | 45.1 | 42.1
Cellarhead 132kV | TALKE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.5 | 18.4 | 18.3 | 18.2 | 18.1 | 18 | 17.8 | 17.7 | 17.2 | 16.6 | 15.9 | 15.4 | 15.1 | 14.9 | 14.7 | 14.5 | 14.3 | 12.8 | 11
Cellarhead 132kV | TALKE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.5 | 18.3 | 18.2 | 17.9 | 17.7 | 17 | 16.1 | 15.2 | 14.4 | 13.5 | 12.5 | 11.5 | 10.5 | 9.6 | 8.9 | 8.3 | 7.6 | 3.6 | 0
Cellarhead 132kV | TALKE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.5 | 18.3 | 18 | 17.9 | 17.6 | 17.3 | 16.4 | 15.4 | 14.4 | 13.4 | 12.5 | 11.7 | 10.9 | 10 | 9.5 | 8.9 | 8.4 | 4.7 | 2.5
Cellarhead 132kV | TALKE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.5 | 18.4 | 18.3 | 18.2 | 18 | 17.8 | 17.3 | 16.6 | 15.9 | 15.2 | 14.4 | 13.8 | 13.3 | 12.8 | 12.5 | 12.2 | 11.9 | 9.1 | 5.9
Cellarhead 132kV | TEAN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.6 | 15.6 | 15.6 | 15.5 | 15.4 | 15.2 | 14.1 | 13.7 | 13.2 | 12.8 | 12 | 11.5 | 11.2 | 10.9 | 10.7 | 10.4 | 9.9 | 7.6 | 5
Cellarhead 132kV | TEAN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.6 | 15.6 | 15.5 | 14.9 | 13.9 | 12.9 | 12.2 | 11 | 9.8 | 8.5 | 7 | 5.4 | 3.8 | 2 | 1.1 | 0 | 0 | 0 | 0
Cellarhead 132kV | TEAN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.6 | 15.6 | 15.5 | 15.2 | 14.5 | 13.3 | 12.9 | 11.7 | 10.4 | 9.2 | 8 | 3.5 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0
Cellarhead 132kV | TEAN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.6 | 15.6 | 15.5 | 15.4 | 15.2 | 14.4 | 13.4 | 12.4 | 11.3 | 10.3 | 9.4 | 8.7 | 8.2 | 7.2 | 6.7 | 6.3 | 4.4 | 0.5 | 0
Cellarhead 132kV | WHITFIELD 132 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 143.5 | 137 | 136.1 | 135.3 | 134.3 | 133.3 | 132 | 130.6 | 128.9 | 127.1 | 125 | 123.6 | 122.7 | 122 | 121.4 | 120.7 | 120 | 116.1 | 110.8
Cellarhead 132kV | WHITFIELD 132 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 143.5 | 136.1 | 134.3 | 132 | 129.6 | 127.2 | 124.2 | 121.3 | 118.5 | 115.7 | 112.8 | 109.7 | 106.5 | 103.5 | 108.3 | 106.1 | 104 | 91.3 | 79.3
Cellarhead 132kV | WHITFIELD 132 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 143.5 | 135.6 | 133 | 131.3 | 128.9 | 126.2 | 123.2 | 119.7 | 116.3 | 113.3 | 110.4 | 107.5 | 105.4 | 109.7 | 108 | 106.2 | 103.2 | 93.9 | 79.5
Cellarhead 132kV | WHITFIELD 132 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 143.5 | 136.7 | 135.4 | 134.2 | 132.7 | 130.9 | 128.3 | 122.2 | 119.9 | 117.5 | 115.1 | 113.4 | 111.8 | 110.4 | 109.7 | 100 | 99.2 | 88.3 | 79
Cellarhead 132kV | Whitfield 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 17.5 | 17.5 | 17.4 | 17.3 | 17.3 | 17.2 | 17.1 | 17 | 17 | 16.9 | 16.9 | 16.9 | 16.9 | 15.5 | 15.5 | 15.5 | 15.5 | 15.4 | 15.2
Cellarhead 132kV | Whitfield 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 17.5 | 17.4 | 17.3 | 17.1 | 17 | 17 | 16.9 | 15.5 | 15.4 | 15.3 | 15.2 | 15 | 14.7 | 14.5 | 14.3 | 14.1 | 14 | 13 | 12
Cellarhead 132kV | Whitfield 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 17.5 | 17.3 | 17.1 | 17 | 17 | 15.4 | 15.5 | 15.3 | 15.1 | 14.8 | 14.6 | 14.3 | 14.1 | 14 | 13.8 | 13.7 | 13.5 | 12.5 | 11.6
Cellarhead 132kV | Whitfield 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 17.5 | 17.4 | 17.4 | 17.3 | 17.2 | 17.1 | 16.9 | 16.9 | 16.9 | 15.5 | 15.4 | 15.3 | 15.2 | 15.1 | 15.1 | 15.1 | 15.1 | 14.7 | 14
East Claydon 132kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.4 | 20.4 | 20.2 | 20.1 | 19.9 | 19.7 | 27.2 | 27 | 26.9 | 26.7 | 26.5 | 26.4 | 26.3 | 26.3 | 26.2 | 26.1 | 26 | 25.4 | 21
East Claydon 132kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.4 | 20.3 | 20 | 19.5 | 19 | 18.4 | 26.2 | 25.5 | 25 | 24.6 | 24.1 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.4 | 20.2 | 19.9 | 19.5 | 19 | 18.4 | 26.1 | 25.5 | 25 | 24.6 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.4 | 20.3 | 20.1 | 19.8 | 19.5 | 19 | 26.6 | 26.3 | 26 | 25.6 | 25.3 | 25 | 24.8 | 24.6 | 20.7 | 11.4 | 2.7 | 0 | 0
East Claydon 132kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.4 | 14.4 | 14.3 | 14.1 | 14 | 13.8 | 16 | 15.8 | 15.4 | 15.1 | 14.5 | 14 | 13.7 | 13.5 | 13.2 | 13.1 | 12.9 | 11.4 | 9.8
East Claydon 132kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.4 | 14.4 | 14.1 | 13.5 | 12.9 | 12.3 | 14.7 | 13.7 | 12.8 | 12.1 | 11.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.4 | 14.3 | 14 | 13.7 | 13.3 | 12.9 | 15.1 | 14.2 | 13.3 | 12.6 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.4 | 14.4 | 14.2 | 14 | 13.7 | 13.3 | 15.6 | 15.1 | 14.4 | 13.8 | 13.1 | 12.5 | 12.1 | 11.7 | 11.4 | 5.1 | 0 | 0 | 0
East Claydon 132kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.6 | 14.3 | 14.3 | 14.1 | 13.9 | 13.7 | 16 | 15.8 | 15.6 | 15.1 | 14.4 | 13.9 | 13.6 | 13.4 | 13.2 | 13 | 12.8 | 11.2 | 0
East Claydon 132kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.6 | 14.3 | 14 | 13.4 | 12.7 | 12 | 14.7 | 13.8 | 13 | 12.2 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.6 | 14.2 | 13.9 | 13.7 | 13.2 | 12.7 | 15.5 | 14.7 | 13.8 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.6 | 14.3 | 14.2 | 13.9 | 13.6 | 13.2 | 15.7 | 15.3 | 14.6 | 14 | 13.3 | 12.7 | 10.6 | 6 | 2.3 | 0 | 0 | 0 | 0
Feckenham 66kV | BEVINGTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 7.2 | 7.1 | 0 | 0 | 0 | 5.7 | 5.6 | 5.4 | 4.9 | 4.3 | 3.8 | 3.6 | 3.1 | 2.5 | 1.9 | 1.3 | 0 | 0
Feckenham 66kV | BEVINGTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 0 | 0 | 0 | 0 | 0 | 4.7 | 3.9 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BEVINGTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 0 | 0 | 0 | 0 | 0 | 5.4 | 4.6 | 2.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BEVINGTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 0 | 0 | 0 | 0 | 0 | 5.5 | 5.2 | 4.6 | 3.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.2 | 9 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BROADWAY 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.7 | 6.5 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BROADWAY 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BROADWAY 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BROADWAY 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BROTHERIDGE GRN 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BROTHERIDGE GRN 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BROTHERIDGE GRN 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | BROTHERIDGE GRN 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.2 | 9 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | EVESHAM 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.9 | 5.2 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | EVESHAM 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | EVESHAM 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | EVESHAM 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | Feckenham 66/11kVDUMMY | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10 | 9.7 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | Feckenham 66/11kVDUMMY | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | Feckenham 66/11kVDUMMY | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | Feckenham 66/11kVDUMMY | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | GREAT ALNE 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.5 | 16.4 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | GREAT ALNE 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | GREAT ALNE 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | GREAT ALNE 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | IPSLEY 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 27.8 | 27.5 | 27.4 | 27.1 | 26.9 | 26.6 | 25.8 | 25.3 | 25 | 24.8 | 24.4 | 24.3 | 24.2 | 24.2 | 24.1 | 24.1 | 24 | 23.5 | 22.8
Feckenham 66kV | IPSLEY 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 27.8 | 27.3 | 26.4 | 25.5 | 25.1 | 24.6 | 22.7 | 22.1 | 21.7 | 21.4 | 21 | 20.7 | 20.4 | 20.1 | 16.6 | 16.4 | 16.1 | 14.5 | 12.9
Feckenham 66kV | IPSLEY 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 27.8 | 27.2 | 26.2 | 25.4 | 24.9 | 23.6 | 22.4 | 22 | 21.5 | 21.1 | 20.7 | 20.4 | 20.2 | 16.7 | 16.5 | 16.3 | 16 | 14.5 | 16.6
Feckenham 66kV | IPSLEY 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 27.8 | 27.4 | 26.6 | 25.8 | 25.5 | 25.1 | 24.3 | 22.9 | 22.4 | 23.8 | 23.4 | 23.3 | 23.2 | 23.1 | 23.1 | 23 | 22.9 | 12.8 | 11.6
Feckenham 66kV | LEDBURY 66/11kV | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 15.9 | 15.7 | 15.6 | 15.4 | 15.3 | 15.2 | 15.2 | 15.2 | 15.2 | 15.1 | 15 | 14.7 | 14.3
Feckenham 66kV | LEDBURY 66/11kV | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 14.4 | 14.2 | 14 | 13.8 | 13.6 | 13.4 | 13.2 | 12.9 | 12.8 | 12.7 | 12.5 | 11.7 | 10.8
Feckenham 66kV | LEDBURY 66/11kV | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 14.6 | 14.3 | 14.1 | 13.9 | 13.6 | 13.2 | 13 | 12.8 | 12.7 | 12.6 | 12.5 | 11.7 | 11
Feckenham 66kV | LEDBURY 66/11kV | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 14.7 | 14.5 | 14.3 | 14.2 | 14 | 13.9 | 13.8 | 13.6 | 13.6 | 13.5 | 13.5 | 12.9 | 12.2
Feckenham 66kV | LONG MARSTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.9 | 12.9 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | LONG MARSTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | LONG MARSTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | LONG MARSTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | MORETON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.1 | 8.9 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | MORETON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | MORETON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | MORETON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | PERSHORE 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | PERSHORE 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | PERSHORE 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | PERSHORE 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.6 | 13.5 | 13.5 | 13.4 | 13.4 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.6 | 13.5 | 13.4 | 13.3 | 13.2 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.5 | 0 | 0 | 0
Feckenham 66kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.6 | 13.5 | 13.3 | 13.2 | 13.1 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.6 | 13.5 | 13.4 | 13.4 | 13.3 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | REDDITCH SOUTH 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 29.7 | 29.4 | 29.1 | 28.8 | 28.5 | 28 | 28.8 | 28.5 | 28.2 | 27.9 | 27.6 | 27.3 | 26.7 | 26.3 | 26 | 25.9 | 25.8 | 25.1 | 23.8
Feckenham 66kV | REDDITCH SOUTH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 29.7 | 29.2 | 28.6 | 27.9 | 26.7 | 25.8 | 27.6 | 26.7 | 25.6 | 24.3 | 23 | 21.8 | 20.5 | 19.3 | 18.3 | 17.8 | 17.3 | 14.4 | 11.5
Feckenham 66kV | REDDITCH SOUTH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 29.7 | 28.9 | 28.1 | 27.4 | 26.3 | 25.2 | 27.3 | 25.9 | 24.5 | 23.1 | 21.7 | 20.5 | 19.2 | 18.1 | 17.2 | 16.7 | 16.3 | 13.4 | 10.8
Feckenham 66kV | REDDITCH SOUTH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 29.7 | 29.4 | 29 | 28.4 | 27.7 | 26.6 | 28 | 27.5 | 26.6 | 25.5 | 24.3 | 23.4 | 22.4 | 21.6 | 21 | 20.9 | 20.7 | 18.9 | 16.7
Feckenham 66kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.2 | 8.9 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STOW 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.1 | 8.9 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STOW 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STOW 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STOW 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STRATFORD 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 27.9 | 27.9 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STRATFORD 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STRATFORD 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STRATFORD 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STRENSHAM 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STRENSHAM 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STRENSHAM 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | STRENSHAM 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | TEWKESBURY 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | TEWKESBURY 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | TEWKESBURY 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feckenham 66kV | TEWKESBURY 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | ALVESTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.4 | 15.9 | 15.8 | 15.7 | 15.5 | 15.3 | 15.1 | 14.8 | 14.4 | 14 | 13.6 | 13.2 | 13 | 12.6 | 12.1 | 11.5 | 10.8 | 7.4 | 3.4
Iron Acton 132kV | ALVESTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.4 | 15.8 | 15.6 | 15.2 | 14 | 12.4 | 13.6 | 13 | 11.6 | 9.7 | 7.6 | 5.4 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | ALVESTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.4 | 15.8 | 15.5 | 15.2 | 14.7 | 13.4 | 14 | 13.3 | 12.5 | 10.6 | 8.7 | 3.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | ALVESTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.4 | 15.9 | 15.7 | 15.5 | 15.3 | 14.9 | 14.5 | 14 | 13.6 | 13.1 | 12 | 10.8 | 9.5 | 7.9 | 7.2 | 6.5 | 4.4 | 0 | 0
Iron Acton 132kV | BERKELEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 8.2 | 7.9 | 7.5 | 7 | 6.4 | 6 | 5.6 | 5.3 | 5 | 4.3 | 3.2 | 0 | 0
Iron Acton 132kV | BERKELEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 2.4 | 1.6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | BERKELEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 5.7 | 4.8 | 4 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | BERKELEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 6.3 | 5.7 | 4.9 | 4.2 | 3.4 | 2.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | CAMP 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.3 | 14.3 | 14.2 | 14.1 | 14.1 | 14.1 | 14 | 13.9 | 13.1 | 13 | 12.9 | 12.9 | 12.9 | 12.8 | 12.8 | 12.8 | 12.8 | 12.5 | 12
Iron Acton 132kV | CAMP 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.3 | 14.2 | 14.1 | 14 | 14 | 13 | 13 | 12.8 | 12.7 | 12.5 | 12.3 | 12.2 | 12 | 11.8 | 11.6 | 11.5 | 11.3 | 10.2 | 7.9
Iron Acton 132kV | CAMP 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.3 | 14.2 | 14 | 14 | 13 | 12.9 | 12.8 | 12.6 | 12.4 | 12.2 | 12 | 11.8 | 11.7 | 11.5 | 11.4 | 11.2 | 11.1 | 10 | 9
Iron Acton 132kV | CAMP 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.3 | 14.3 | 14.2 | 14.1 | 14 | 14 | 13.1 | 13 | 13 | 12.9 | 12.7 | 12.7 | 12.6 | 12.6 | 12.5 | 12.5 | 12.4 | 11.7 | 10.8
Iron Acton 132kV | CHERINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.2 | 7.2 | 7.2 | 6.3 | 6.3 | 6.2 | 6.1 | 5.9 | 5.6 | 5.3 | 4.9 | 4.7 | 4.5 | 4.4 | 4.3 | 4.2 | 4 | 3.2 | 2.2
Iron Acton 132kV | CHERINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.2 | 7.2 | 6.3 | 6.1 | 5.8 | 5.4 | 4.9 | 4.5 | 4 | 3.5 | 3 | 2.5 | 2 | 1.5 | 1.1 | 0.7 | 0 | 0 | 0
Iron Acton 132kV | CHERINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.2 | 7.2 | 6.2 | 6.1 | 5.9 | 5.6 | 5.2 | 4.7 | 4.2 | 3.8 | 3.4 | 2.9 | 2.4 | 2 | 1.7 | 1.3 | 0.9 | 0 | 0
Iron Acton 132kV | CHERINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.2 | 7.2 | 6.3 | 6.3 | 6.2 | 6 | 5.7 | 5.3 | 5 | 4.6 | 4.2 | 3.9 | 3.6 | 3.4 | 3.2 | 3 | 2.8 | 1.4 | 0
Iron Acton 132kV | Chipping Sodbury 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 28.6 | 28.6 | 28.5 | 28.4 | 28.1 | 27.7 | 27.6 | 27.4 | 27.3 | 26.6 | 26.4 | 26.1 | 25.9 | 25.6 | 25.3 | 25 | 24.8 | 23.3 | 21.4
Iron Acton 132kV | Chipping Sodbury 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 28.6 | 28.5 | 27.9 | 26.6 | 25.7 | 24.6 | 25.9 | 24.7 | 23.5 | 22.4 | 21.1 | 20.1 | 19.3 | 18.3 | 17.6 | 16.9 | 16.2 | 2.3 | 0
Iron Acton 132kV | Chipping Sodbury 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 28.6 | 28.5 | 27.6 | 26.6 | 25.6 | 24.7 | 26 | 24.7 | 23.4 | 22.1 | 20.9 | 20.1 | 19.3 | 18.4 | 17.8 | 17.1 | 16.5 | 8.8 | 0
Iron Acton 132kV | Chipping Sodbury 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 28.6 | 28.6 | 28.3 | 27.6 | 26.7 | 26.1 | 26.6 | 26.3 | 25.7 | 24.9 | 23.9 | 23.2 | 22.6 | 21.9 | 21.5 | 21 | 20.6 | 17.7 | 14.4
Iron Acton 132kV | CHIPPING SODBURY 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 70.5 | 68.3 | 67.6 | 66.6 | 65.5 | 64.2 | 67.4 | 67 | 66.7 | 66.2 | 65.8 | 65.5 | 65.3 | 65.2 | 65.1 | 65 | 64.8 | 61.8 | 56
Iron Acton 132kV | CHIPPING SODBURY 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 70.5 | 67.8 | 65.6 | 62.8 | 59.8 | 56.7 | 65.1 | 64.5 | 64 | 63.4 | 61 | 58 | 55.1 | 52.1 | 50.1 | 44.6 | 42.3 | 2.3 | 0
Iron Acton 132kV | CHIPPING SODBURY 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 70.5 | 67.4 | 64.5 | 62.9 | 60.4 | 57.8 | 64.2 | 63.4 | 62.6 | 61.9 | 53.8 | 50.9 | 46.5 | 43.9 | 42.2 | 40.3 | 37.7 | 8.8 | 0
Iron Acton 132kV | CHIPPING SODBURY 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 70.5 | 68.2 | 66.7 | 65.3 | 63.8 | 61.6 | 66.2 | 65.7 | 65.2 | 64.7 | 64.2 | 64 | 63.7 | 62.4 | 61.5 | 57.3 | 56.1 | 46.4 | 30.4
Iron Acton 132kV | COWHORN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.2 | 15 | 14.9 | 14.6 | 14.4 | 14.1 | 18 | 17.9 | 17.8 | 17.7 | 17.5 | 17.4 | 17.4 | 17.4 | 17.3 | 17.3 | 17.3 | 16.3 | 15.2
Iron Acton 132kV | COWHORN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.2 | 14.8 | 14.2 | 13.6 | 13 | 12.3 | 17.3 | 17.2 | 17.1 | 16.3 | 16.1 | 15.9 | 15 | 11.7 | 9.4 | 7.1 | 3.7 | 0 | 0
Iron Acton 132kV | COWHORN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.2 | 14.7 | 13.9 | 13.5 | 12.9 | 12.3 | 16.4 | 16.2 | 15.9 | 15.5 | 15.2 | 14.5 | 11.3 | 9.7 | 8.5 | 7.4 | 5.4 | 0 | 0
Iron Acton 132kV | COWHORN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.2 | 14.9 | 14.5 | 14.3 | 13.9 | 13.4 | 17.6 | 17.4 | 17.3 | 17.2 | 16.3 | 16.3 | 16.3 | 16.2 | 16.2 | 16.1 | 16 | 10.4 | 0
Iron Acton 132kV | DUDBRIDGE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.8 | 14.8 | 14.6 | 14.6 | 14.5 | 14.4 | 14.3 | 14.2 | 14.2 | 14.1 | 14.1 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 13.1
Iron Acton 132kV | DUDBRIDGE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.8 | 14.7 | 14.4 | 14.3 | 14.1 | 14 | 13.1 | 13.1 | 13 | 13 | 12.9 | 12.9 | 12.8 | 12.8 | 12.7 | 12.6 | 12.5 | 11.6 | 10.6
Iron Acton 132kV | DUDBRIDGE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.8 | 14.6 | 14.3 | 14.1 | 13.9 | 12.9 | 12.8 | 12.7 | 12.6 | 12.5 | 12.3 | 12.2 | 12.2 | 12.1 | 12 | 12 | 11.9 | 10.8 | 8.6
Iron Acton 132kV | DUDBRIDGE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.8 | 14.7 | 14.6 | 14.4 | 14.2 | 14 | 13.9 | 13.9 | 13.9 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 12.7 | 12.1
Iron Acton 132kV | DURSLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 13.7 | 13.5 | 13.3 | 13.1 | 12.8 | 12.5 | 12.2 | 12 | 11.7 | 11.4 | 10.9 | 9.4 | 8.6
Iron Acton 132kV | DURSLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 11.8 | 11.2 | 10.6 | 8.5 | 5.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | DURSLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 11.3 | 10.3 | 9.6 | 9 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | DURSLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 11.9 | 11.2 | 10.6 | 10.1 | 9.3 | 8.8 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | HAMMERLEY DOWN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 17.6 | 16.5 | 16.4 | 15.9 | 15.7 | 15.4 | 15 | 14.5 | 13.9 | 13.3 | 12.5 | 12 | 11.7 | 11.5 | 11.3 | 11 | 10.5 | 7.2 | 3.4
Iron Acton 132kV | HAMMERLEY DOWN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 17.6 | 16.4 | 15.8 | 15.1 | 14.1 | 12.5 | 12.9 | 12 | 11.2 | 9.5 | 7.5 | 5.3 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | HAMMERLEY DOWN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 17.6 | 16.4 | 15.6 | 15.3 | 14.7 | 13.4 | 13.5 | 12.5 | 11.6 | 10.5 | 8.5 | 3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | HAMMERLEY DOWN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 17.6 | 16.5 | 16 | 15.7 | 15.4 | 14.9 | 14.3 | 13.6 | 12.9 | 12.2 | 11.4 | 10.6 | 9.3 | 7.8 | 7 | 6.4 | 4.4 | 0 | 0
Iron Acton 132kV | NAISHCOMBE HILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.7 | 9.6 | 9.5 | 9.3 | 9.1 | 8.8 | 8.5 | 8.3 | 8.2 | 7.9 | 7.4 | 7 | 6.7 | 6.5 | 6.4 | 6.2 | 6 | 4.7 | 3.2
Iron Acton 132kV | NAISHCOMBE HILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.7 | 9.5 | 9.1 | 8.6 | 8 | 7.5 | 7.6 | 6.9 | 6.2 | 5.6 | 4.8 | 4 | 3.2 | 2.5 | 2 | 1.4 | 0.6 | 0 | 0
Iron Acton 132kV | NAISHCOMBE HILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.7 | 9.5 | 8.8 | 8.6 | 8.1 | 7.7 | 8 | 7.3 | 6.6 | 5.9 | 5.2 | 4.5 | 3.8 | 3.1 | 2.7 | 2.2 | 1.4 | 0 | 0
Iron Acton 132kV | NAISHCOMBE HILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.7 | 9.6 | 9.3 | 9.1 | 8.8 | 8.4 | 8.3 | 8.1 | 7.6 | 7.1 | 6.5 | 6.1 | 5.7 | 5.3 | 5.1 | 4.9 | 4.5 | 2.3 | 0
Iron Acton 132kV | NETHERHILLS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 8.9 | 8.6 | 8.3 | 7.9 | 7.6 | 7.4 | 7.4 | 7.3 | 6.9 | 6.1 | 4.9 | 3.8
Iron Acton 132kV | NETHERHILLS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3.2 | 2.4 | 1.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | NETHERHILLS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 4.1 | 3.2 | 2.5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | NETHERHILLS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 4.2 | 3.6 | 2.9 | 2.3 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | OXBRIDGE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.8 | 15.8 | 15.7 | 15.5 | 15.3 | 15.1 | 11.9 | 11.7 | 11.6 | 11.4 | 11 | 10.8 | 10.7 | 10.6 | 10.5 | 10.4 | 10.3 | 9.5 | 8.7
Iron Acton 132kV | OXBRIDGE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.8 | 15.7 | 15.4 | 15 | 14.6 | 14.1 | 11.4 | 11 | 10.6 | 10.2 | 9.8 | 9.3 | 8.8 | 8.4 | 8.1 | 5.5 | 5.2 | 0.8 | 0
Iron Acton 132kV | OXBRIDGE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.8 | 15.6 | 15.3 | 15.1 | 14.7 | 14.3 | 11.7 | 11.4 | 11 | 10.6 | 5.6 | 5 | 5 | 4.6 | 4.3 | 4.1 | 4.1 | 0 | 0
Iron Acton 132kV | OXBRIDGE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.8 | 15.7 | 15.6 | 15.4 | 15.2 | 14.8 | 11.8 | 11.6 | 11.3 | 11 | 10.6 | 10.4 | 10.1 | 9.9 | 9.8 | 7.3 | 7.1 | 6.2 | 4.8
Iron Acton 132kV | Ryeford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 16.9 | 16.9 | 14.1 | 14 | 14 | 13.9 | 14 | 13.9 | 13.8 | 13.7 | 13.6 | 13.5 | 13.4 | 13.4 | 13.3 | 12.6 | 10.3 | 4.7 | 0.8
Iron Acton 132kV | Ryeford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 16.9 | 14.1 | 14 | 13.9 | 13.7 | 13.2 | 9 | 6.7 | 4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | Ryeford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 16.9 | 14.1 | 14 | 13.9 | 13.6 | 12.1 | 11.6 | 8.4 | 5.5 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | Ryeford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 16.9 | 14.1 | 14 | 13.9 | 13.7 | 13.5 | 12.9 | 10.8 | 8.7 | 6.7 | 4.3 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | RYEFORD 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 25.9 | 24.8 | 23.8 | 23.2 | 22.6 | 21.9 | 22.3 | 21.3 | 20.2 | 19 | 17.5 | 16.4 | 15.4 | 14.7 | 14.1 | 12.6 | 10.3 | 4.7 | 0.8
Iron Acton 132kV | RYEFORD 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 25.9 | 23.9 | 22.8 | 21.1 | 16.7 | 13.2 | 9 | 6.7 | 4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | RYEFORD 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 25.9 | 23.6 | 22.2 | 20.2 | 14.6 | 12.1 | 11.6 | 8.4 | 5.5 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iron Acton 132kV | RYEFORD 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 25.9 | 24.1 | 23.1 | 22 | 20.5 | 17.1 | 12.8 | 10.8 | 8.7 | 6.7 | 4.3 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BAYSTON HILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.6 | 9.1 | 8.8 | 8.7 | 8.5 | 8.2 | 9 | 8.7 | 8.4 | 8 | 7.6 | 7.3 | 7.1 | 7 | 6.7 | 6.5 | 6 | 4.5 | 4.5
Ironbr. & Shrewsb. 132kV | BAYSTON HILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.6 | 8.9 | 8.4 | 8 | 7.4 | 6.8 | 7.2 | 6.5 | 5.8 | 5.1 | 4.3 | 3.6 | 2.7 | 1.5 | 0.6 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BAYSTON HILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.6 | 8.7 | 8.1 | 7.6 | 7 | 6.2 | 6.5 | 5.6 | 4.7 | 3.9 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BAYSTON HILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.6 | 9 | 8.7 | 8.4 | 8.1 | 7.6 | 8.1 | 7.5 | 6.9 | 6.3 | 5.7 | 5.2 | 4.6 | 4 | 3.5 | 3 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BERRINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BERRINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 0.7 | 0.7 | 0.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BERRINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 0.7 | 0.7 | 0.6 | 0.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BERRINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.1 | 6.6 | 6.4 | 6.2 | 6 | 5.8 | 6.3 | 6 | 5.6 | 5.2 | 4.8 | 4.5 | 4.3 | 4.2 | 4 | 3.9 | 3.7 | 2.6 | 1.5
Ironbr. & Shrewsb. 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.1 | 6.5 | 6.1 | 5.6 | 5 | 4.3 | 4.5 | 3.8 | 3.2 | 2.5 | 1.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.1 | 6.3 | 5.8 | 5.4 | 4.8 | 4.3 | 4.4 | 3.7 | 3 | 2.4 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.1 | 6.5 | 6.3 | 6.1 | 5.8 | 5.4 | 5.7 | 5.2 | 4.8 | 4.3 | 3.8 | 3.5 | 3.2 | 2.8 | 2.5 | 2.2 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BROSELEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.1 | 6.6 | 6.4 | 6.2 | 5.9 | 5.6 | 5 | 4.3 | 3.7 | 3.1 | 2.3 | 1.7 | 1.3 | 1.1 | 0.9 | 0.8 | 0.7 | 1.6 | 0
Ironbr. & Shrewsb. 132kV | BROSELEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.1 | 6.3 | 5.9 | 4.9 | 3.8 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BROSELEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.1 | 6.2 | 5.5 | 4.8 | 3.7 | 2.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | BROSELEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.1 | 6.5 | 6 | 5.6 | 5 | 4.3 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | DONNINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.9 | 14.8 | 14.8 | 14.7 | 14.6 | 14.5 | 13.8 | 13.7 | 13.7 | 13.6 | 13.6 | 13.5 | 13.5 | 13.4 | 13.2 | 13 | 12.7 | 10.4 | 9.8
Ironbr. & Shrewsb. 132kV | DONNINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.9 | 14.8 | 14.6 | 14.5 | 14.4 | 14.2 | 13.6 | 13.4 | 13 | 12.6 | 12.1 | 11.4 | 10.7 | 10 | 9.4 | 8.7 | 8 | 5 | 3.9
Ironbr. & Shrewsb. 132kV | DONNINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.9 | 14.7 | 14.5 | 14.4 | 14.3 | 14.1 | 13.4 | 12.7 | 12 | 11.3 | 10.7 | 10.2 | 9.6 | 7.4 | 6.9 | 6.4 | 5.8 | 3.9 | 3.1
Ironbr. & Shrewsb. 132kV | DONNINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.9 | 14.8 | 14.7 | 14.6 | 14.6 | 14.5 | 13.7 | 13.5 | 13.2 | 12.8 | 12.2 | 11.6 | 10.9 | 10.4 | 9.9 | 9.4 | 8.8 | 6.2 | 5.4
Ironbr. & Shrewsb. 132kV | DOTHILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.4 | 5.3 | 5.2 | 5.2 | 5.1 | 5 | 3.8 | 3.8 | 3.7 | 3.6 | 3.1 | 2.4 | 1.8 | 1.2 | 0.7 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | DOTHILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.4 | 5.2 | 5.1 | 4.9 | 4.7 | 4.1 | 3.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | DOTHILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.4 | 5.2 | 5 | 4.7 | 4.4 | 3.9 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | DOTHILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.4 | 5.3 | 5.2 | 5 | 4.8 | 4.5 | 3.4 | 2.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | EASTHOPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.1 | 5.1 | 5.1 | 5 | 5 | 5 | 5 | 5 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.8 | 4.7
Ironbr. & Shrewsb. 132kV | EASTHOPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.1 | 5.1 | 5 | 5 | 4.9 | 4.9 | 4.9 | 4.8 | 4.8 | 4.8 | 4.7 | 4.7 | 4.7 | 4.6 | 4.6 | 4.5 | 4.4 | 4.1 | 3.9
Ironbr. & Shrewsb. 132kV | EASTHOPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.1 | 5 | 5 | 4.9 | 4.9 | 4.8 | 4.8 | 4.7 | 4.7 | 4.6 | 4.6 | 3.6 | 3.5 | 3.4 | 3.3 | 3.1 | 3 | 2.2 | 1.5
Ironbr. & Shrewsb. 132kV | EASTHOPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.1 | 5.1 | 5 | 5 | 5 | 5 | 5 | 4.9 | 4.9 | 4.9 | 4.9 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.7 | 4.5 | 4.3
Ironbr. & Shrewsb. 132kV | HALESFIELD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16.5 | 16 | 16 | 15.2 | 15.1 | 15.1 | 15.2 | 15.1 | 15 | 14.9 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.6
Ironbr. & Shrewsb. 132kV | HALESFIELD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16.5 | 15.2 | 15.2 | 15.1 | 15 | 14.9 | 14.8 | 14.7 | 14.6 | 14.5 | 14.3 | 14.3 | 14.2 | 14.1 | 14.1 | 14 | 13.9 | 13.4 | 12.7
Ironbr. & Shrewsb. 132kV | HALESFIELD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16.5 | 15.2 | 15.1 | 15 | 14.8 | 14.7 | 14.5 | 14.3 | 14.2 | 14 | 13.8 | 13.8 | 13.7 | 13.6 | 13.5 | 13.5 | 13.4 | 12.7 | 11.9
Ironbr. & Shrewsb. 132kV | HALESFIELD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16.5 | 16 | 15.2 | 15.1 | 15.1 | 15 | 15 | 14.9 | 14.8 | 14.7 | 14.6 | 14.6 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 12.6 | 12
Ironbr. & Shrewsb. 132kV | HARLESCOTT 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 2.1 | 2 | 1.8 | 1.7 | 1.5 | 2.1 | 1.7 | 1.4 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | HARLESCOTT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 2.1 | 1.7 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | HARLESCOTT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 1.9 | 1.5 | 1.1 | 0.7 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | HARLESCOTT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 2.1 | 1.9 | 1.6 | 1.4 | 1.1 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | HORTONWOOD 132 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 27.5 | 26.5 | 26.4 | 25.2 | 25.1 | 24.9 | 24.7 | 24.5 | 24.3 | 24.2 | 24 | 23.9 | 23.8 | 23.7 | 23.6 | 23.5 | 23.4 | 22.4 | 21.7
Ironbr. & Shrewsb. 132kV | HORTONWOOD 132 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 27.5 | 26.4 | 26 | 25.6 | 25.4 | 23.6 | 23.2 | 22.4 | 21.9 | 21.7 | 21.2 | 20.9 | 20.6 | 20.2 | 19.9 | 19.5 | 18.7 | 17 | 15.8
Ironbr. & Shrewsb. 132kV | HORTONWOOD 132 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 27.5 | 26 | 25.6 | 25.1 | 24.2 | 23 | 22.5 | 21.8 | 21.3 | 20.9 | 20.5 | 19.4 | 19.1 | 18.8 | 18.5 | 18.2 | 17.9 | 16.2 | 15
Ironbr. & Shrewsb. 132kV | HORTONWOOD 132 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 27.5 | 26.5 | 26 | 26 | 25.5 | 24 | 23.5 | 22.9 | 22.3 | 22.1 | 21.6 | 21.3 | 21 | 20.7 | 20.5 | 20.2 | 19 | 17.6 | 16.7
Ironbr. & Shrewsb. 132kV | IRONBRIDGE 132 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 39.2 | 37.9 | 37.5 | 37.2 | 36.8 | 36.5 | 35.2 | 34.9 | 34.6 | 34.3 | 34 | 36.6 | 36.6 | 36.3 | 36 | 35.7 | 35.4 | 35.3 | 32.5
Ironbr. & Shrewsb. 132kV | IRONBRIDGE 132 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 39.2 | 37.4 | 36.7 | 36.1 | 35.4 | 34.8 | 33.8 | 33.5 | 33.2 | 31 | 28.8 | 26.7 | 26.9 | 25 | 23.7 | 22.6 | 21.5 | 14 | 7.5
Ironbr. & Shrewsb. 132kV | IRONBRIDGE 132 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 39.2 | 37.1 | 36 | 35.2 | 34.4 | 33.7 | 32.9 | 32.1 | 31.4 | 30.6 | 29.9 | 24.7 | 24.2 | 23.7 | 23.3 | 22.9 | 22.4 | 14.7 | 10.9
Ironbr. & Shrewsb. 132kV | IRONBRIDGE 132 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 39.2 | 37.7 | 37.1 | 36.7 | 36.2 | 35.7 | 34.6 | 34.4 | 34.3 | 33.9 | 33.5 | 32.4 | 33.6 | 32.7 | 32 | 31.5 | 31 | 23.5 | 18.5
Ironbr. & Shrewsb. 132kV | Ketley 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 27.7 | 27.6 | 27.5 | 27.3 | 27.2 | 27.2 | 27.5 | 27.5 | 27.4 | 27.4 | 27.3 | 27.3 | 27.3 | 27.2 | 27.2 | 27.2 | 27.2 | 26.7 | 26.2
Ironbr. & Shrewsb. 132kV | Ketley 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 27.7 | 27.4 | 26.9 | 26.6 | 26.2 | 26 | 27.2 | 27.2 | 27.2 | 26.8 | 26.4 | 25.9 | 25.4 | 25.2 | 25 | 24.9 | 24.7 | 22.3 | 16.2
Ironbr. & Shrewsb. 132kV | Ketley 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 27.7 | 27.3 | 26.7 | 26.4 | 25.9 | 25.7 | 27.2 | 26.8 | 26.2 | 25.6 | 25.1 | 24.8 | 24.7 | 24.5 | 24.3 | 22.8 | 21.5 | 16.1 | 10
Ironbr. & Shrewsb. 132kV | Ketley 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 27.7 | 27.6 | 27.3 | 27.2 | 26.8 | 26.7 | 27.4 | 27.3 | 27.3 | 27.2 | 26.8 | 26.4 | 26 | 25.9 | 25.8 | 25.7 | 25.6 | 24.8 | 23.6
Ironbr. & Shrewsb. 132kV | KETLEY 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 72.3 | 71.2 | 70.6 | 70 | 69.4 | 68.8 | 66 | 64.6 | 63.4 | 62.4 | 61.1 | 60 | 59 | 58 | 57 | 55.5 | 54.5 | 51.7 | 49.3
Ironbr. & Shrewsb. 132kV | KETLEY 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 72.3 | 70.6 | 69.3 | 68 | 66.2 | 63.3 | 59.1 | 54.9 | 51.3 | 49.2 | 45.7 | 42.6 | 39 | 36.8 | 34.9 | 32.9 | 31.1 | 22.3 | 16.2
Ironbr. & Shrewsb. 132kV | KETLEY 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 72.3 | 70.2 | 68.4 | 66.3 | 63.8 | 60 | 54.7 | 50.1 | 45.5 | 42.6 | 38 | 36.1 | 29.9 | 25.9 | 24.4 | 22.8 | 21.5 | 16.1 | 10
Ironbr. & Shrewsb. 132kV | KETLEY 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 72.3 | 71 | 70.1 | 69.1 | 67.9 | 65.4 | 61.5 | 57.7 | 54.2 | 52.2 | 49 | 46.1 | 42.5 | 41 | 39.7 | 38.5 | 37.3 | 29.7 | 24.8
Ironbr. & Shrewsb. 132kV | LEATON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.4 | 3 | 3 | 2.9 | 2.8 | 2.7 | 2.5 | 2.2 | 1.9 | 1.6 | 1.1 | 0.8 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | LEATON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.4 | 3 | 2.9 | 2.7 | 2.3 | 1.9 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | LEATON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.4 | 2.9 | 2.9 | 2.8 | 2.5 | 2.3 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | LEATON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.4 | 3 | 3 | 2.9 | 2.7 | 2.5 | 2.1 | 1.6 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 6.6 | 6.6 | 6.5 | 6.5 | 6.5 | 6.4 | 6.4 | 6.4 | 6.3 | 6.3 | 6.3 | 6.2 | 6.2 | 6.3 | 6.3 | 6.3 | 6.2 | 6
Ironbr. & Shrewsb. 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 6.6 | 6.5 | 6.4 | 6.3 | 6.2 | 6.2 | 6.1 | 6 | 6 | 5.9 | 5.9 | 5.8 | 5.7 | 5.7 | 5.6 | 5.5 | 4.9 | 4.3
Ironbr. & Shrewsb. 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 6.6 | 6.4 | 6.3 | 6.2 | 6.1 | 6.1 | 6 | 5.9 | 5.8 | 5.8 | 3.6 | 3.5 | 3.4 | 3.3 | 3.2 | 3 | 2.2 | 1.5
Ironbr. & Shrewsb. 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 6.6 | 6.5 | 6.5 | 6.5 | 6.4 | 6.3 | 6.3 | 6.2 | 6.2 | 6.2 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6 | 5.8 | 5.5
Ironbr. & Shrewsb. 132kV | MADELEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.2 | 18 | 17.9 | 17.9 | 17.8 | 17.8 | 14.4 | 14.4 | 14.3 | 14.2 | 14.1 | 18.5 | 18.5 | 18.5 | 18.5 | 18.4 | 18.4 | 18.3 | 17.8
Ironbr. & Shrewsb. 132kV | MADELEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.2 | 17.9 | 17.8 | 14.2 | 14.2 | 14 | 14.1 | 13.9 | 13.8 | 13.6 | 13.3 | 17.8 | 14.3 | 14.3 | 14.2 | 14.1 | 14 | 12.6 | 10.5
Ironbr. & Shrewsb. 132kV | MADELEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.2 | 17.8 | 14.3 | 14.2 | 14 | 13.8 | 13.7 | 13.4 | 13 | 12.6 | 12.2 | 14 | 13.9 | 13.7 | 13.6 | 13.4 | 13.2 | 11.3 | 8.9
Ironbr. & Shrewsb. 132kV | MADELEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.2 | 17.9 | 17.8 | 17.8 | 14.2 | 14.2 | 14.3 | 14.2 | 14.1 | 14 | 13.8 | 18.1 | 18.1 | 18 | 18 | 18 | 18 | 14.3 | 13.3
Ironbr. & Shrewsb. 132kV | MALEHURST 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.2 | 2.3 | 2.1 | 1.9 | 1.8 | 1.6 | 2.3 | 1.8 | 1.4 | 1.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | MALEHURST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.2 | 2.2 | 1.8 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | MALEHURST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.2 | 2 | 1.6 | 1.2 | 0.7 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | MALEHURST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.2 | 2.2 | 2 | 1.7 | 1.5 | 1.1 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | NEWPORT 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.1 | 11.8 | 11.8 | 11.7 | 11.6 | 11.6 | 10.8 | 10.7 | 10.7 | 10.7 | 10.7 | 10.6 | 10.6 | 10.6 | 10.4 | 10.3 | 10.1 | 9.6 | 9
Ironbr. & Shrewsb. 132kV | NEWPORT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.1 | 11.7 | 11.5 | 11.3 | 11 | 10.7 | 10.3 | 9.8 | 9.1 | 8.7 | 7.7 | 7 | 6.4 | 5.9 | 5.5 | 5.1 | 4.7 | 3.1 | 1.5
Ironbr. & Shrewsb. 132kV | NEWPORT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.1 | 11.6 | 11.3 | 11.1 | 10.7 | 10.2 | 9.4 | 8.4 | 7.3 | 6.7 | 6.1 | 5.8 | 5 | 4.8 | 4.5 | 4.2 | 4 | 2.4 | 0.8
Ironbr. & Shrewsb. 132kV | NEWPORT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.1 | 11.8 | 11.7 | 11.6 | 11.5 | 11.3 | 10.6 | 10.5 | 10.1 | 9.8 | 9.1 | 8.5 | 8.1 | 7.8 | 7.7 | 7.6 | 7.3 | 6 | 4.8
Ironbr. & Shrewsb. 132kV | PRIESTWESTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.6 | 3.6 | 3.5 | 3.5 | 3.4 | 3.3 | 3.1 | 3 | 2.8 | 2.5 | 2.3 | 2.1 | 2 | 1.9 | 1.8 | 1.7 | 1.6 | 1 | 0
Ironbr. & Shrewsb. 132kV | PRIESTWESTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.6 | 3.6 | 3.4 | 3.2 | 2.9 | 2.7 | 2.3 | 2 | 1.7 | 1.3 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | PRIESTWESTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.6 | 3.6 | 3.3 | 3.2 | 3 | 2.8 | 2.5 | 2.2 | 1.8 | 1.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | PRIESTWESTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.6 | 3.6 | 3.5 | 3.4 | 3.3 | 3.1 | 2.9 | 2.6 | 2.4 | 2.1 | 1.8 | 1.6 | 1.5 | 1.3 | 1.2 | 1.1 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.1 | 6.6 | 6.4 | 6.2 | 5.9 | 5.6 | 5 | 4.3 | 3.7 | 3.1 | 2.3 | 1.7 | 1.3 | 1.1 | 0.9 | 0.8 | 0.7 | 1.6 | 0
Ironbr. & Shrewsb. 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.1 | 6.4 | 5.9 | 5 | 3.8 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.1 | 6.2 | 5.5 | 4.8 | 3.7 | 2.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.1 | 6.5 | 6.1 | 5.6 | 5.1 | 4.3 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | ROUSHILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 28.8 | 28.8 | 28.8 | 28.7 | 28.7 | 28.7 | 28.6 | 28.6 | 28.5 | 28.5 | 28.4 | 28.4 | 28.4 | 28.4 | 28.4 | 28.3 | 28.3 | 28.2 | 27.9
Ironbr. & Shrewsb. 132kV | ROUSHILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 28.8 | 28.8 | 28.8 | 28.7 | 28.7 | 28.5 | 28.3 | 28.2 | 28.2 | 28.1 | 27.9 | 27.9 | 27.8 | 27.7 | 21.7 | 14.6 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | ROUSHILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 28.8 | 28.8 | 28.8 | 28.6 | 28.4 | 28.2 | 28 | 27.8 | 27.7 | 27.5 | 27.4 | 14.1 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | ROUSHILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 28.8 | 28.8 | 28.8 | 28.7 | 28.7 | 28.7 | 28.6 | 28.5 | 28.4 | 28.3 | 28.2 | 28.2 | 28.2 | 28.2 | 28.1 | 28.1 | 27.8 | 20.2 | 4.3
Ironbr. & Shrewsb. 132kV | ROWTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3.2 | 2.2 | 2.1 | 1.9 | 1.8 | 1.6 | 2.3 | 1.8 | 1.4 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | ROWTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3.2 | 2.2 | 1.8 | 1.3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | ROWTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3.2 | 2 | 1.5 | 1.2 | 0.7 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | ROWTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3.2 | 2.2 | 2 | 1.7 | 1.4 | 1.1 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | SHIFNAL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.7 | 9.7 | 9.6 | 9.6 | 9.6 | 9.5 | 9.6 | 9 | 8.9 | 8.8 | 8.6 | 8.5 | 8.4 | 8.4 | 8.3 | 7.4 | 7.4 | 7.2 | 6.9
Ironbr. & Shrewsb. 132kV | SHIFNAL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.7 | 9.6 | 9.5 | 9.2 | 9.1 | 8.9 | 7.3 | 7 | 6.7 | 6.5 | 6.4 | 6.2 | 4.9 | 4.6 | 4.3 | 4 | 3.9 | 1.7 | 0.9
Ironbr. & Shrewsb. 132kV | SHIFNAL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.7 | 9.6 | 9.4 | 9.1 | 8.9 | 8 | 7.7 | 7.3 | 7.1 | 6.9 | 5.1 | 4.8 | 2.4 | 1.2 | 0.9 | 0.6 | 0.5 | 0 | 0
Ironbr. & Shrewsb. 132kV | SHIFNAL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.7 | 9.7 | 9.5 | 9.3 | 9.3 | 9.1 | 7.6 | 7.4 | 7.2 | 7 | 6.8 | 6.6 | 5.3 | 5.1 | 4.8 | 4.6 | 4.5 | 2.5 | 1.9
Ironbr. & Shrewsb. 132kV | Shrewsbury 132/33kVDUMMY | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 39.8 | 38.8 | 38.7 | 38.6 | 38.4 | 38.2 | 38.8 | 38.5 | 37.9 | 37.4 | 36.7 | 36.1 | 35.6 | 35.1 | 34.8 | 35.1 | 34.8 | 33.1 | 31.2
Ironbr. & Shrewsb. 132kV | Shrewsbury 132/33kVDUMMY | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 39.8 | 38.8 | 38.7 | 38.4 | 37.8 | 37.2 | 37.6 | 36.5 | 35.4 | 34.6 | 33.1 | 31.3 | 24 | 16.6 | 11 | 5.9 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | Shrewsbury 132/33kVDUMMY | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 39.8 | 38.8 | 38.6 | 38.5 | 38.1 | 38.2 | 38.2 | 36.9 | 35.3 | 34.5 | 31.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | Shrewsbury 132/33kVDUMMY | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 39.8 | 38.8 | 38.8 | 38.8 | 38.7 | 38.4 | 38.9 | 38.1 | 37.1 | 36.6 | 35.5 | 34.5 | 34.5 | 34.1 | 33.2 | 32.3 | 3.6 | 20.5 | 4.4
Ironbr. & Shrewsb. 132kV | SNEDSHILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 24.7 | 24.4 | 24.3 | 24.2 | 24.1 | 24 | 23.9 | 22.7 | 22.5 | 22.3 | 22 | 21.8 | 21.7 | 21.5 | 21.4 | 20.6 | 20.4 | 21 | 20.3
Ironbr. & Shrewsb. 132kV | SNEDSHILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 24.7 | 24.4 | 24.2 | 24 | 23.8 | 22.6 | 21.7 | 19.6 | 18.2 | 17.4 | 16.6 | 15.9 | 14.3 | 13.8 | 13.4 | 13 | 12.7 | 10.2 | 8.5
Ironbr. & Shrewsb. 132kV | SNEDSHILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 24.7 | 24.3 | 24.1 | 23.8 | 22.8 | 21.8 | 20.3 | 18.7 | 17.5 | 16.7 | 14.3 | 13.7 | 10.2 | 9 | 8.6 | 8.1 | 7.9 | 7.1 | 5.4
Ironbr. & Shrewsb. 132kV | SNEDSHILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 24.7 | 24.4 | 24.3 | 24.1 | 23.9 | 22.8 | 22.6 | 20.9 | 19.5 | 18.7 | 17.7 | 17.1 | 15.3 | 14.9 | 14.6 | 14.3 | 14.2 | 12.3 | 10.9
Ironbr. & Shrewsb. 132kV | SPRING GARDENS 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 29.5 | 28.8 | 28.6 | 28.3 | 28 | 27.7 | 28.5 | 28.1 | 27.9 | 27.7 | 27.4 | 27.3 | 27.2 | 26.7 | 26.7 | 25.5 | 25.2 | 24.2 | 22.5
Ironbr. & Shrewsb. 132kV | SPRING GARDENS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 29.5 | 28.6 | 28 | 27.2 | 26.4 | 25.6 | 26.2 | 25.5 | 24.8 | 24.1 | 23.3 | 22.6 | 20.3 | 16.7 | 11 | 5.9 | 0 | 7.4 | 0
Ironbr. & Shrewsb. 132kV | SPRING GARDENS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 29.5 | 28.3 | 27.5 | 26.6 | 25.8 | 24.2 | 25.8 | 24.8 | 23.9 | 23 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | SPRING GARDENS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 29.5 | 28.8 | 28.3 | 27.7 | 27.2 | 26.4 | 27.2 | 26.4 | 25.8 | 25.2 | 24.6 | 24.2 | 22.2 | 21.7 | 21.1 | 20.6 | 3.7 | 17.4 | 14.4
Ironbr. & Shrewsb. 132kV | STAR ALUMINIUM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6 | 6.6 | 6.4 | 6.2 | 5.9 | 5.6 | 5 | 4.3 | 3.7 | 3.1 | 2.3 | 1.7 | 1.3 | 1.1 | 0.9 | 0.8 | 0.7 | 1.6 | 0
Ironbr. & Shrewsb. 132kV | STAR ALUMINIUM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6 | 6.3 | 5.9 | 4.9 | 3.8 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | STAR ALUMINIUM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6 | 6.2 | 5.5 | 4.8 | 3.7 | 2.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | STAR ALUMINIUM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6 | 6.4 | 6 | 5.6 | 5 | 4.3 | 2.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | WEIR HILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.7 | 9.6 | 9.5 | 9.5 | 9.4 | 9.3 | 9.2 | 9 | 8.8 | 8.6 | 8.4 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.1 | 7.7
Ironbr. & Shrewsb. 132kV | WEIR HILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.7 | 9.5 | 9.2 | 8.9 | 8.4 | 8 | 7.5 | 7 | 6.5 | 6 | 5.6 | 5.4 | 5.3 | 4.4 | 3.3 | 2.2 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | WEIR HILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.7 | 9.4 | 9.1 | 8.8 | 8.3 | 7.9 | 7.3 | 6.8 | 6.3 | 5.8 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | WEIR HILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.7 | 9.5 | 9.3 | 9 | 8.6 | 8.3 | 7.8 | 7.4 | 7 | 6.5 | 6.1 | 6.1 | 6 | 6 | 5.9 | 5.9 | 1.8 | 3.1 | 0.7
Ironbr. & Shrewsb. 132kV | WORFIELD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 5.2 | 5.2 | 5.1 | 5.1 | 5.1 | 5 | 4.9 | 4.8 | 4.6 | 4.5 | 4.3 | 4.1 | 4.1 | 4 | 4 | 3.9 | 3.9 | 3.5 | 1.6
Ironbr. & Shrewsb. 132kV | WORFIELD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 5.2 | 5.1 | 5.1 | 5 | 4.8 | 4.7 | 4.5 | 4.2 | 2.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | WORFIELD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 5.2 | 5.1 | 5.1 | 5.1 | 5 | 4.9 | 4.7 | 4.5 | 3.7 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ironbr. & Shrewsb. 132kV | WORFIELD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 5.2 | 5.2 | 5.1 | 5.1 | 5 | 4.9 | 4.8 | 4.6 | 4.4 | 4.2 | 3.5 | 2.5 | 2.2 | 1.5 | 1 | 0.6 | 0 | 0 | 0
Kitwell 132kV | BARTLEY GREEN 132 11kV SUBSTN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.8 | 29.8 | 29.7 | 29.6 | 29.5 | 29.4 | 28.2 | 28.1 | 28.1 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 27.9
Kitwell 132kV | BARTLEY GREEN 132 11kV SUBSTN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.8 | 29.8 | 29.5 | 29.1 | 28.8 | 28.6 | 28 | 27.9 | 27.9 | 27.8 | 27.8 | 27.7 | 27.7 | 27.6 | 27.5 | 27.3 | 27.2 | 26.4 | 25.1
Kitwell 132kV | BARTLEY GREEN 132 11kV SUBSTN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.8 | 29.7 | 29.1 | 28.6 | 28.2 | 27.7 | 27.8 | 27.6 | 27.4 | 27.2 | 27.1 | 26.9 | 26.8 | 26.6 | 26.5 | 26.4 | 26.3 | 25.5 | 23.5
Kitwell 132kV | BARTLEY GREEN 132 11kV SUBSTN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.8 | 29.8 | 29.7 | 29.5 | 29.3 | 29.1 | 28.1 | 28.1 | 28 | 27.9 | 27.9 | 27.9 | 27.9 | 27.9 | 28 | 28 | 28 | 27.8 | 27.1
Kitwell 132kV | Bournville 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 28.5 | 28.3 | 28 | 27.6 | 27.5 | 27.3 | 28.1 | 28 | 28 | 27.9 | 27.9 | 27.9 | 27.9 | 27.9 | 27.9 | 27.9 | 27.9 | 27.9 | 27.7
Kitwell 132kV | Bournville 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 28.5 | 28 | 27.3 | 26.8 | 26.5 | 26.2 | 27.7 | 27.7 | 27.6 | 27.5 | 27.3 | 27.2 | 27.2 | 26.8 | 26.6 | 26.5 | 26.3 | 25.2 | 23.7
Kitwell 132kV | Bournville 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 28.5 | 27.6 | 26.8 | 26.5 | 26 | 25.6 | 27.5 | 27.2 | 26.7 | 26.3 | 26 | 25.8 | 25.7 | 25.5 | 25.3 | 25.1 | 25 | 23.7 | 21.9
Kitwell 132kV | Bournville 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 28.5 | 28.2 | 27.5 | 27.3 | 26.7 | 26.6 | 27.9 | 27.8 | 27.7 | 27.7 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.3 | 26.2
Kitwell 132kV | Chad Valley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 60.2 | 60.2 | 60.1 | 59.9 | 59.9 | 59.8 | 58.8 | 58.7 | 58.6 | 58.6 | 58.4 | 58.2 | 58 | 57.8 | 57.7 | 57.6 | 57.5 | 57.2 | 56.1
Kitwell 132kV | Chad Valley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 60.2 | 60.2 | 60.1 | 59.9 | 59.4 | 58.6 | 57.9 | 57.5 | 57.1 | 55.8 | 54.7 | 53.2 | 52.4 | 52 | 51.5 | 50.9 | 50.4 | 47.4 | 44.1
Kitwell 132kV | Chad Valley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 60.2 | 60.2 | 60.1 | 59.7 | 58.2 | 57.3 | 57 | 55.5 | 54.3 | 52.1 | 50.3 | 49.8 | 49.3 | 48.9 | 48.4 | 47.9 | 47.4 | 44.1 | 40
Kitwell 132kV | Chad Valley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 60.2 | 60.2 | 60.1 | 59.9 | 59.9 | 59.4 | 58.2 | 57.8 | 57.3 | 56.2 | 55.1 | 54.4 | 53.5 | 53.4 | 53.4 | 53.3 | 53.1 | 51.5 | 49
Kitwell 132kV | Halesowen 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 28.5 | 28.4 | 28.2 | 28 | 27.8 | 27.6 | 27.8 | 27.7 | 27.6 | 27.5 | 27.4 | 26.2 | 26.2 | 26.2 | 26.2 | 26.2 | 26.2 | 25.8 | 24.9
Kitwell 132kV | Halesowen 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 28.5 | 28.2 | 27.7 | 27.3 | 26.7 | 26.1 | 26.3 | 26.1 | 25.9 | 25.6 | 25.2 | 24.9 | 24.5 | 24 | 23.6 | 23.1 | 22.6 | 20 | 17.3
Kitwell 132kV | Halesowen 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 28.5 | 28.1 | 27.4 | 26.7 | 26.2 | 25.5 | 26 | 25.6 | 25.2 | 24.6 | 24.1 | 23.7 | 23.2 | 22.8 | 22.4 | 22 | 21.6 | 18.8 | 16.2
Kitwell 132kV | Halesowen 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 28.5 | 28.4 | 28 | 27.7 | 27.3 | 26.6 | 27.5 | 27.4 | 26.2 | 26.1 | 25.9 | 25.8 | 25.7 | 25.6 | 25.5 | 25.4 | 25.2 | 21.9 | 19.8
Kitwell 132kV | Hall Green 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 59.8 | 59.9 | 59.7 | 59.6 | 59.4 | 59.3 | 58.6 | 58.6 | 58.5 | 58.5 | 58.4 | 58.4 | 58.4 | 58.4 | 58.4 | 58.4 | 58.4 | 58.4 | 57.9
Kitwell 132kV | Hall Green 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 59.8 | 59.9 | 59.7 | 59.5 | 59.3 | 58.9 | 58.4 | 58.2 | 58.2 | 58.1 | 57.9 | 57.8 | 57.7 | 57.3 | 57 | 56.6 | 56.2 | 53.4 | 50.8
Kitwell 132kV | Hall Green 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 59.8 | 59.9 | 59.7 | 59 | 58.3 | 57.6 | 57.6 | 57.1 | 56.6 | 56.1 | 55.6 | 55 | 54.8 | 54.6 | 54.4 | 53.3 | 53.1 | 50.8 | 47
Kitwell 132kV | Hall Green 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 59.8 | 59.9 | 59.7 | 59.6 | 59.4 | 59.2 | 58.6 | 58.6 | 58.5 | 58.4 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 57.8 | 55.8
Kitwell 132kV | Highters Heath 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 55.6 | 55.5 | 55.2 | 55.1 | 54.9 | 54.7 | 55.2 | 55.1 | 55.1 | 55 | 54.9 | 54.9 | 54.8 | 54.8 | 54.8 | 54.6 | 54.6 | 54.5 | 53.4
Kitwell 132kV | Highters Heath 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 55.6 | 55.1 | 54.7 | 54.3 | 53.8 | 53.5 | 54.7 | 54.6 | 54.6 | 54.5 | 54.4 | 54.2 | 52.9 | 52.5 | 52.1 | 51.7 | 51.2 | 48.7 | 45.6
Kitwell 132kV | Highters Heath 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 55.6 | 54.9 | 54.2 | 53.7 | 53.1 | 52.6 | 54.4 | 53.8 | 53.5 | 53.1 | 51.4 | 51.1 | 50.7 | 50.3 | 50 | 49.6 | 49.2 | 46.5 | 43.2
Kitwell 132kV | Highters Heath 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 55.6 | 55.4 | 55.1 | 54.9 | 54.5 | 54.3 | 55 | 55 | 54.9 | 54.8 | 54.8 | 54.8 | 54.4 | 54.4 | 54.4 | 54.3 | 54.2 | 52.6 | 50.3
Kitwell 132kV | Longbridge 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.7 | 29.6 | 29.4 | 29.2 | 29 | 28.9 | 29 | 28.9 | 28.8 | 28.7 | 28.6 | 28.5 | 28.5 | 28.5 | 28.5 | 28.4 | 28.4 | 28.3 | 26
Kitwell 132kV | Longbridge 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.7 | 29.3 | 29 | 28.6 | 28.1 | 25.9 | 28.2 | 28.1 | 28 | 28 | 25.6 | 25 | 25 | 24.7 | 24.6 | 24.3 | 24 | 22 | 19.3
Kitwell 132kV | Longbridge 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.7 | 29.2 | 28.7 | 28.4 | 26 | 25.5 | 28 | 25.9 | 25.1 | 25 | 24.7 | 24.5 | 24.2 | 23.9 | 23.6 | 23.3 | 23 | 20.9 | 18.4
Kitwell 132kV | Longbridge 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.7 | 29.5 | 29.2 | 29 | 28.4 | 28.2 | 28.5 | 28.4 | 28.3 | 28.2 | 28.1 | 28.1 | 28.1 | 28 | 28 | 28 | 28 | 24.7 | 23.4
Kitwell 132kV | Rednal 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 28 | 27.5 | 27.2 | 26.9 | 26.7 | 26.5 | 27.6 | 27.6 | 27.5 | 27.4 | 27.4 | 27.3 | 27.4 | 27.4 | 27.3 | 27.3 | 27.2 | 26.1 | 24.8
Kitwell 132kV | Rednal 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 28 | 27.3 | 26.8 | 26.4 | 25.7 | 25 | 27.3 | 27.1 | 26.5 | 25.3 | 24.6 | 23.9 | 23.9 | 23.2 | 22.7 | 22 | 21.4 | 18.7 | 16
Kitwell 132kV | Rednal 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 28 | 27.2 | 26.5 | 26.1 | 25.3 | 24.7 | 27.2 | 26.3 | 25.5 | 24.2 | 23.4 | 22.9 | 23 | 22.5 | 22 | 21.5 | 21 | 18.4 | 16.2
Kitwell 132kV | Rednal 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 28 | 27.4 | 27.1 | 26.8 | 26.3 | 25.7 | 27.5 | 27.4 | 27.3 | 26.1 | 25.5 | 25.1 | 25.5 | 25.2 | 25 | 24.6 | 24.3 | 22.5 | 20.2
Kitwell 132kV | Selly Oak 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 27.1 | 27.1 | 26.6 | 26.5 | 26.6 | 26.4 | 24.7 | 24.6 | 24.5 | 24.4 | 24.1 | 24.1 | 24 | 24 | 24 | 24 | 24 | 24 | 23.7
Kitwell 132kV | Selly Oak 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 27.1 | 27.1 | 26.6 | 26.5 | 25.2 | 24.8 | 23.8 | 23.7 | 23.5 | 21.9 | 21.2 | 21 | 20.9 | 20.8 | 20.6 | 20.5 | 25.4 | 25 | 24.5
Kitwell 132kV | Selly Oak 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 27.1 | 27.1 | 27.1 | 26.6 | 25.2 | 24.8 | 23.8 | 23.4 | 23 | 20.9 | 20.5 | 20.4 | 20.3 | 25.3 | 25.2 | 25.2 | 25.1 | 24.7 | 17.7
Kitwell 132kV | Selly Oak 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 27.1 | 27.1 | 26.6 | 26.5 | 25.4 | 25.1 | 24 | 23.9 | 23.8 | 22.3 | 21.5 | 18 | 18 | 18 | 18 | 18 | 18 | 17.5 | 16.7
Kitwell 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29 | 28.5 | 28.4 | 28.2 | 28.1 | 27.9 | 28.2 | 28.1 | 27.9 | 27.8 | 27.6 | 27.4 | 27.3 | 27.2 | 26.8 | 26.5 | 26.2 | 25.2 | 24
Kitwell 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29 | 28.3 | 27.9 | 27.6 | 26.7 | 26.3 | 27.3 | 26.6 | 26.1 | 25.6 | 24.9 | 24.1 | 23.2 | 22.3 | 21.8 | 21.1 | 20.6 | 17.9 | 15.2
Kitwell 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29 | 28.2 | 27.7 | 27.4 | 26.8 | 26.3 | 27.2 | 26.3 | 25.6 | 24.9 | 24.2 | 23.4 | 22.8 | 22.3 | 21.8 | 21.4 | 20.9 | 18.3 | 16.3
Kitwell 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29 | 28.5 | 28.1 | 27.9 | 27.7 | 27.4 | 27.8 | 27.6 | 27.3 | 26.6 | 26.3 | 25.8 | 25.3 | 24.8 | 24.5 | 24.2 | 24 | 22.1 | 19.9
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 20.6 | 20.6 | 20.6 | 20.6 | 20.5 | 20.5 | 19.9 | 19.9 | 19.9 | 19.6 | 18.3 | 18 | 17.8 | 17.7 | 17.6 | 17.6 | 17.5 | 17.3 | 14.7
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 20.6 | 20.6 | 20.6 | 20.5 | 20.1 | 19.8 | 17.8 | 17.3 | 14.8 | 14.6 | 14.2 | 13.8 | 13.5 | 13.2 | 13 | 12.8 | 12.5 | 11.2 | 10
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 20.6 | 20.6 | 20.6 | 20.3 | 19.9 | 18.7 | 17.3 | 14.8 | 14.5 | 14.1 | 13.5 | 13.2 | 13 | 12.7 | 12.5 | 12.3 | 12.1 | 10.9 | 10.1
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 20.6 | 20.6 | 20.6 | 20.6 | 20.5 | 20.5 | 19.5 | 18.3 | 17.5 | 17.3 | 14.7 | 14.5 | 14.3 | 14.1 | 14 | 13.9 | 13.7 | 12.7 | 11.8
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.9 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 5.8 | 5.4 | 4.5 | 3.2 | 2.3 | 1.6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.9 | 6.6 | 6 | 5.4 | 4.5 | 2.8 | 1.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.9 | 6.4 | 5.7 | 4.8 | 3.4 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.9 | 6.7 | 6.4 | 6.1 | 5.5 | 4.3 | 3.4 | 2.6 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 26 | 25.5 | 25.5 | 25.3 | 25.2 | 25.2 | 25.2 | 25.1 | 25.1 | 25.1 | 25.1 | 25.3 | 25.4 | 25.3 | 24.7 | 24.4 | 24.4 | 26 | 26
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 26 | 25.4 | 24.9 | 24.3 | 23.8 | 23.8 | 23.8 | 23.7 | 23.7 | 23.9 | 22.2 | 22 | 22 | 22 | 21.9 | 21.9 | 21.6 | 23.8 | 23.7
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 26 | 25.4 | 24.9 | 24.3 | 23.7 | 23.8 | 23.8 | 23.8 | 23.8 | 22.1 | 22 | 21.4 | 21.4 | 21.4 | 21.4 | 21.3 | 21.3 | 23.5 | 23.4
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 26 | 25.4 | 24.9 | 24.3 | 23.8 | 23.8 | 23.8 | 23.7 | 23.7 | 23.8 | 22.2 | 22.1 | 22.1 | 22.1 | 22 | 22 | 21.7 | 24 | 23.9
Lea Marston 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 55.7 | 55.7 | 55.7 | 55.8 | 55.2 | 52.7 | 50.4 | 50.3 | 50.2 | 50.1 | 50 | 49.9 | 49.9 | 49.9 | 49.9 | 49.9 | 49.9 | 49.9 | 49.5
Lea Marston 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 55.7 | 55.7 | 52.9 | 51.5 | 51.4 | 51.2 | 49.9 | 49.7 | 49.6 | 49.4 | 49.1 | 48.9 | 48.7 | 48.5 | 48.3 | 48.1 | 47.8 | 46.2 | 50.3
Lea Marston 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 55.7 | 55.1 | 51.5 | 51.3 | 51.1 | 50.7 | 49.3 | 48.8 | 48.3 | 47.7 | 47.2 | 47 | 46.8 | 46.6 | 46.4 | 46.1 | 45.9 | 43.9 | 49
Lea Marston 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 55.7 | 55.7 | 55.7 | 55.1 | 52.6 | 51.4 | 50.1 | 50 | 49.8 | 49.6 | 49.5 | 49.4 | 49.4 | 49.5 | 49.5 | 49.5 | 49.5 | 48.9 | 51
Lea Marston 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | CHELMSLEY WOOD | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 28.7 | 28.1 | 28.1 | 27.9 | 27.8 | 27.7 | 28.2 | 28.1 | 28.1 | 28 | 27.9 | 27.8 | 27.8 | 27.7 | 27.6 | 27.3 | 26.4 | 25.5 | 24.8
Lea Marston 132kV | CHELMSLEY WOOD | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 28.7 | 27.9 | 27.4 | 27.2 | 26.7 | 26.6 | 27.7 | 27.5 | 27.3 | 26.6 | 26.3 | 25.8 | 24.5 | 22.9 | 22.3 | 21.6 | 21.3 | 19.9 | 18.4
Lea Marston 132kV | CHELMSLEY WOOD | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 28.7 | 27.8 | 27.2 | 26.7 | 26.4 | 26.1 | 27.4 | 26.5 | 25.9 | 25 | 24.2 | 22.6 | 22.1 | 21.4 | 21 | 20.7 | 20.4 | 18.8 | 17.2
Lea Marston 132kV | CHELMSLEY WOOD | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 28.7 | 28 | 27.5 | 27.4 | 27.3 | 26.8 | 27.8 | 27.6 | 27.4 | 26.7 | 26.4 | 26 | 25.2 | 23.7 | 23.1 | 22.8 | 22.7 | 21.7 | 20.5
Lea Marston 132kV | Copt Heath 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 55.5 | 55.5 | 55.3 | 55.1 | 54.8 | 54.6 | 55.2 | 55.1 | 55 | 54.9 | 54.6 | 54.4 | 53.7 | 53.6 | 53.4 | 53.3 | 53.1 | 52.2 | 50.9
Lea Marston 132kV | Copt Heath 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 55.5 | 55.3 | 55.1 | 54.6 | 54.3 | 53.4 | 54.9 | 54.4 | 53.5 | 52.8 | 52.1 | 51.4 | 50.7 | 49.9 | 49.5 | 49.1 | 48.7 | 46 | 43.4
Lea Marston 132kV | Copt Heath 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 55.5 | 55.2 | 54.9 | 54.6 | 54.3 | 53.4 | 54.8 | 53.7 | 53 | 52.3 | 51.7 | 51.1 | 50.5 | 50.1 | 49.8 | 49.4 | 49 | 46.7 | 45
Lea Marston 132kV | Copt Heath 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 55.5 | 55.4 | 55.2 | 54.9 | 54.6 | 54.3 | 55 | 54.9 | 54.4 | 53.6 | 53.1 | 52.6 | 52.1 | 51.9 | 51.8 | 51.7 | 51.5 | 49.6 | 47.4
Lea Marston 132kV | Elmdon 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 25.7 | 25.7 | 22.8 | 22.7 | 22.6 | 22.4 | 21.3 | 21.3 | 21.2 | 21 | 20.8 | 20.7 | 20.6 | 20.5 | 23.8 | 22.2 | 18.9 | 16.9 | 16.6
Lea Marston 132kV | Elmdon 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 25.7 | 25.7 | 25.7 | 22.6 | 22.4 | 22.1 | 24.3 | 24 | 23.7 | 23.5 | 23.2 | 23 | 19.4 | 14.4 | 13.4 | 12.1 | 11.3 | 10.6 | 9.9
Lea Marston 132kV | Elmdon 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 25.7 | 25.7 | 22.7 | 22.6 | 22.4 | 22 | 24.2 | 23.9 | 23.7 | 23.4 | 22.2 | 17.2 | 14.8 | 14.1 | 12.7 | 11.4 | 11.2 | 10.6 | 9.3
Lea Marston 132kV | Elmdon 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 25.7 | 25.7 | 25.7 | 22.6 | 22.5 | 22.3 | 24.3 | 24.2 | 23.9 | 23.4 | 23.2 | 23 | 21.2 | 15.7 | 13.4 | 12.3 | 10.9 | 9.6 | 9
Lea Marston 132kV | Hams Hall South 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 56.7 | 56.6 | 56.3 | 55.9 | 55.3 | 52.8 | 48.2 | 47.9 | 47.6 | 47.4 | 47.1 | 47 | 46.9 | 46.9 | 46.8 | 46.8 | 46.7 | 46.5 | 46.1
Lea Marston 132kV | Hams Hall South 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 56.7 | 56.6 | 56 | 55.1 | 46.1 | 40.2 | 43.7 | 41.8 | 40.1 | 38.4 | 37.1 | 36.3 | 35.8 | 35.1 | 34.8 | 34 | 33.6 | 31 | 28.1
Lea Marston 132kV | Hams Hall South 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 56.7 | 56.5 | 55.8 | 55.1 | 44.3 | 41.3 | 45.1 | 43.7 | 42.2 | 41 | 39.6 | 39.1 | 38.6 | 37.5 | 37.2 | 36.8 | 37.3 | 34.8 | 31.2
Lea Marston 132kV | Hams Hall South 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 56.7 | 56.6 | 56.1 | 55.4 | 46.9 | 41.5 | 44.8 | 43.2 | 41.8 | 40.2 | 39.1 | 38 | 37.7 | 37.3 | 37.1 | 36.6 | 36.4 | 34 | 31.4
Lea Marston 132kV | Kitts Green 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 58.1 | 58.1 | 58 | 57.9 | 57.8 | 57.7 | 57.2 | 57.2 | 57.1 | 57.1 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 56.8
Lea Marston 132kV | Kitts Green 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 58.1 | 58.1 | 58 | 57.9 | 57.7 | 57.4 | 57 | 56.9 | 56.9 | 56.8 | 56.7 | 56.6 | 56.6 | 56.5 | 56.3 | 56.1 | 55.8 | 54.7 | 52.2
Lea Marston 132kV | Kitts Green 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 58.1 | 58.1 | 58 | 57.5 | 57 | 56.7 | 56.5 | 56.2 | 55.9 | 55.6 | 55.3 | 55.2 | 55.1 | 54.9 | 54.8 | 54.7 | 54.6 | 52.3 | 50.1
Lea Marston 132kV | Kitts Green 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 58.1 | 58.1 | 58 | 57.9 | 57.8 | 57.7 | 57.2 | 57.1 | 57.1 | 57 | 56.9 | 57 | 57 | 57 | 57 | 57 | 57 | 56.6 | 55.4
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 4.3 | 4.2 | 4.1 | 4 | 3.9 | 3.8 | 3.5 | 3.3 | 2.7 | 2 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 4.3 | 4.1 | 3.7 | 3.3 | 2.7 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 4.3 | 4 | 3.5 | 3 | 2.2 | 1.4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 4.3 | 4.2 | 4 | 3.8 | 3.5 | 3 | 2.4 | 2 | 1.3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 28.3 | 28.1 | 28.1 | 28 | 28 | 27.9 | 27.8 | 27.7 | 27.6 | 27.5 | 27.4 | 27.3 | 27.2 | 27.2 | 27.1 | 26.8 | 26.7 | 26.4 | 26
Lea Marston 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 28.3 | 28.1 | 27.9 | 27.8 | 27.5 | 27.4 | 27.2 | 26.9 | 26.7 | 26.5 | 26.3 | 26 | 25.7 | 25.4 | 25.2 | 25 | 24.8 | 23.9 | 23
Lea Marston 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 28.3 | 28 | 27.8 | 27.7 | 27.6 | 27.4 | 27.1 | 26.8 | 26.5 | 26.3 | 26.1 | 25.8 | 25.6 | 25.4 | 25.2 | 25.1 | 24.9 | 24 | 23.3
Lea Marston 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 28.3 | 28.1 | 28 | 27.9 | 27.8 | 27.7 | 27.5 | 27.4 | 27.2 | 26.9 | 26.8 | 26.6 | 26.4 | 26.3 | 26.2 | 26.1 | 26 | 25.3 | 24.6
Lea Marston 132kV | Solihull 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 58.4 | 58.4 | 58.3 | 58.2 | 58.1 | 58 | 56.7 | 56.6 | 56.5 | 56.3 | 56.2 | 56 | 55.8 | 55.6 | 55.3 | 55 | 54.8 | 54.4 | 53.2
Lea Marston 132kV | Solihull 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 58.4 | 58.4 | 58.3 | 58.1 | 57.8 | 57.3 | 56.9 | 56.7 | 56.4 | 56.1 | 55.6 | 54.9 | 54.4 | 53.3 | 52.7 | 52.5 | 52.1 | 51 | 48.9
Lea Marston 132kV | Solihull 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 58.4 | 58.4 | 58.1 | 57.7 | 57.1 | 56.4 | 56.2 | 55.4 | 54.8 | 53.6 | 53.1 | 52.6 | 52.2 | 52.7 | 52.3 | 52 | 51.7 | 49.7 | 46.3
Lea Marston 132kV | Solihull 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 58.4 | 58.4 | 58.3 | 58.2 | 58.1 | 57.8 | 57.2 | 56.9 | 56.6 | 56 | 55.5 | 54.9 | 54.6 | 54.4 | 53.5 | 53.5 | 53.4 | 52.3 | 50.7
Lea Marston 132kV | Sutton Coldfield 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 36 | 35.9 | 35.6 | 24 | 23.9 | 23.7 | 55.2 | 55 | 55 | 54.9 | 54.7 | 54.6 | 54.6 | 54.5 | 54.5 | 54.1 | 53.8 | 50.4 | 49.1
Lea Marston 132kV | Sutton Coldfield 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 36 | 35.7 | 35.2 | 23.5 | 23.2 | 22.8 | 54.6 | 54.4 | 54.3 | 48.9 | 45.9 | 45.2 | 44.4 | 43.6 | 42.8 | 42 | 41.4 | 38.7 | 35.7
Lea Marston 132kV | Sutton Coldfield 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 36 | 35.5 | 34.9 | 23.1 | 22.7 | 22.1 | 54.3 | 52.9 | 52.2 | 44 | 42.9 | 42.3 | 41.5 | 40.8 | 40.1 | 39.9 | 39.5 | 36.8 | 33.3
Lea Marston 132kV | Sutton Coldfield 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 36 | 35.8 | 35.5 | 23.8 | 23.6 | 23.4 | 54.9 | 54.7 | 54.5 | 50.2 | 46.5 | 45.9 | 45.5 | 45.1 | 44.6 | 44.2 | 44 | 36.5 | 34.2
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 71 | 68.4 | 68.2 | 67.1 | 66.3 | 65.8 | 67.2 | 66.3 | 64.8 | 62.7 | 60.5 | 59.3 | 58.4 | 57.7 | 56.2 | 55.3 | 54.6 | 51.9 | 46.3
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 71 | 67.6 | 65.7 | 63.4 | 60.6 | 57.4 | 55.6 | 53.6 | 51.3 | 48.7 | 44.1 | 41.2 | 38.5 | 35.6 | 33.3 | 30.8 | 26.1 | 15.4 | 4.7
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 71 | 67.3 | 65 | 62.1 | 58.8 | 55.5 | 54 | 50.7 | 47.1 | 42.3 | 39 | 32 | 28.8 | 26.5 | 24.6 | 22.3 | 20.2 | 12 | 4.6
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 71 | 68 | 66.6 | 65.1 | 63 | 60.9 | 60.7 | 58.2 | 56.1 | 54 | 49.8 | 47.9 | 46.3 | 45 | 43.9 | 42.5 | 38.7 | 31.5 | 22.1
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 29.4 | 29.2 | 29.2 | 24.6 | 24.5 | 24.3 | 29.4 | 29.4 | 24.7 | 24.6 | 24.3 | 24.1 | 23.9 | 23.7 | 23.6 | 23.5 | 23.4 | 22.7 | 21.7
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 29.4 | 24.7 | 24.5 | 23.9 | 23 | 21.9 | 21.8 | 21 | 20.5 | 19.8 | 19.1 | 18.5 | 18 | 17.5 | 17.1 | 16.4 | 16 | 13.5 | 11.3
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 29.4 | 24.7 | 24.3 | 23.5 | 22.5 | 20.7 | 20.9 | 19.7 | 18.8 | 18 | 17.3 | 17 | 16.3 | 15.9 | 15.5 | 14.8 | 14.4 | 12.9 | 10.9
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 29.4 | 24.8 | 24.6 | 24.4 | 23.9 | 23.2 | 24 | 22.7 | 22.2 | 21.4 | 20.7 | 20.2 | 19.9 | 19.7 | 19.6 | 19.3 | 19 | 17.2 | 15.5
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 32.9 | 32.7 | 32.5 | 32.3 | 32.1 | 32 | 31.5 | 31.3 | 31 | 30.7 | 30.3 | 30 | 29.9 | 29.8 | 29.7 | 29.7 | 29.7 | 29.4 | 24.2
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 32.9 | 32.4 | 32 | 31.7 | 31.3 | 31 | 30.3 | 30.1 | 29.8 | 29.5 | 29.4 | 24.3 | 24.1 | 23.8 | 23.5 | 23.2 | 22.8 | 20.4 | 17.8
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 32.9 | 32.3 | 31.7 | 31.2 | 30.8 | 30.4 | 29.6 | 29.3 | 24.3 | 24 | 23.5 | 23.2 | 22.8 | 22.4 | 22.1 | 21.6 | 21.2 | 18.5 | 16.2
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 32.9 | 32.6 | 32.3 | 32.1 | 31.9 | 31.7 | 31.1 | 30.9 | 30.5 | 30.1 | 29.7 | 29.5 | 29.5 | 29.4 | 29.4 | 24.4 | 24.3 | 23.8 | 22.5
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 40.7 | 40.7 | 40.3 | 40.3 | 40.3 | 40.3 | 42 | 42 | 42 | 41.9 | 41.2 | 41.1 | 41 | 40.9 | 40.8 | 40.8 | 40.8 | 40.3 | 39.2
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 40.7 | 40.7 | 40.3 | 40.1 | 40 | 39.9 | 41 | 40.3 | 39.2 | 39.1 | 38.7 | 38.3 | 37.9 | 37.6 | 37.4 | 36.4 | 34.6 | 29 | 23.6
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 40.7 | 40.7 | 40.3 | 40.1 | 40 | 39.5 | 40.7 | 39.2 | 39 | 38.5 | 37.9 | 37.3 | 35.9 | 34.8 | 33.9 | 32.8 | 31.7 | 27 | 23.2
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 40.7 | 40.7 | 40.3 | 40.3 | 40.3 | 40.3 | 41.9 | 41.3 | 40.8 | 40.3 | 39.2 | 39 | 38.8 | 38.6 | 38.4 | 38.3 | 38.2 | 36.9 | 32.4
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 13.9 | 13.3 | 13.2 | 13.2 | 13.1 | 13 | 12.9 | 12.8 | 12.5 | 12 | 11.5 | 11.1 | 10.9 | 10.7 | 10.6 | 10.4 | 10.2 | 9 | 7.6
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 13.9 | 13.2 | 13.1 | 12.9 | 12.6 | 12.4 | 12.1 | 11.7 | 11 | 10.2 | 9.4 | 8.5 | 7.7 | 6.8 | 6.1 | 5.6 | 4.9 | 1.5 | 0
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 13.9 | 13.2 | 13 | 12.7 | 12.5 | 12.2 | 11.9 | 11.3 | 10.3 | 9.5 | 8.6 | 7.9 | 7.3 | 6.7 | 6.2 | 5.7 | 5.2 | 2.4 | 1
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 13.9 | 13.3 | 13.2 | 13.1 | 13 | 12.9 | 12.7 | 12.6 | 12.2 | 11.7 | 11 | 10.6 | 10.1 | 9.8 | 9.5 | 9.2 | 8.9 | 6.7 | 4.5
Nechells 132kV | Bordesley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 57 | 52 | 52 | 52 | 52.2 | 51.8 | 49.5 | 49.2 | 48.8 | 48.4 | 47.9 | 47.7 | 47.6 | 47.4 | 47.2 | 46.9 | 46 | 44.4 | 44.2
Nechells 132kV | Bordesley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 57 | 52 | 52 | 51.3 | 49.7 | 47.9 | 47.2 | 45.4 | 43.1 | 40.4 | 38 | 37.1 | 35.8 | 34.4 | 33.1 | 31.7 | 31 | 30.5 | 29.9
Nechells 132kV | Bordesley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 57 | 52 | 52 | 51.1 | 49.4 | 47.8 | 46.9 | 44.4 | 41.9 | 38.7 | 36.1 | 35 | 33.9 | 32.8 | 31.7 | 30.6 | 30.5 | 29.9 | 29.1
Nechells 132kV | Bordesley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 57 | 52 | 52 | 51.4 | 49.9 | 48.2 | 47.2 | 45.5 | 43.2 | 40.4 | 37.9 | 36.9 | 35.7 | 34.5 | 33.3 | 32.1 | 31.7 | 31.5 | 31.1
Nechells 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 55.3 | 55.3 | 55.3 | 55.3 | 53.2 | 53.1 | 50.1 | 50 | 50 | 49.9 | 49.8 | 49.8 | 49.7 | 49.7 | 49.7 | 49.7 | 49.7 | 49.8 | 49.4
Nechells 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 55.3 | 55.3 | 53.3 | 51.5 | 51.4 | 51.2 | 49.7 | 49.6 | 49.5 | 49.4 | 49 | 48.8 | 48.7 | 48.5 | 48.3 | 48.1 | 47.8 | 46.1 | 50.1
Nechells 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 55.3 | 54.7 | 51.5 | 51.4 | 51.1 | 50.7 | 49.3 | 48.8 | 48.3 | 47.7 | 47.2 | 47 | 46.8 | 46.6 | 46.3 | 46.1 | 45.8 | 43.9 | 48.9
Nechells 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 55.3 | 55.3 | 55.3 | 53.2 | 51.5 | 51.4 | 49.9 | 49.8 | 49.7 | 49.5 | 49.4 | 49.4 | 49.4 | 49.4 | 49.4 | 49.4 | 49.4 | 48.8 | 50.9
Nechells 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Cheapside 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 55.8 | 55.8 | 55.8 | 55.7 | 55.8 | 55.8 | 55.4 | 55.3 | 55.3 | 55.3 | 55.2 | 55 | 54.9 | 54.7 | 54.6 | 54.1 | 53.6 | 52.8 | 52.4
Nechells 132kV | Cheapside 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 55.8 | 55.8 | 55.8 | 55.7 | 54.8 | 53.7 | 54.9 | 54.7 | 53.3 | 50.7 | 48.9 | 46.3 | 44.7 | 44.4 | 44.1 | 43.9 | 43.7 | 42.9 | 41.7
Nechells 132kV | Cheapside 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 55.8 | 55.8 | 55.8 | 55.7 | 54.3 | 53.2 | 54.6 | 52.2 | 50.1 | 46.9 | 44.4 | 43.8 | 43.6 | 43.3 | 43.1 | 42.8 | 42.7 | 41.6 | 40.2
Nechells 132kV | Cheapside 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 55.8 | 55.8 | 55.8 | 55.7 | 55.1 | 54.1 | 54.9 | 54.6 | 52.9 | 50.2 | 48.2 | 45.8 | 45.3 | 45.2 | 45.1 | 45 | 45 | 44.6 | 43.8
Nechells 132kV | Chester Street 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.4 | 29.4 | 29.3 | 29.3 | 29.1 | 28.8 | 28.7 | 28.6 | 28.5 | 28.3 | 28.2 | 28.1 | 28.1 | 28 | 28 | 27.9 | 27.7 | 25.8 | 25.5
Nechells 132kV | Chester Street 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.4 | 29.4 | 29.3 | 29.1 | 28.4 | 27.8 | 28.2 | 28.1 | 27.8 | 26.2 | 25.5 | 25.2 | 25 | 24.9 | 24.8 | 24.7 | 24 | 20.7 | 19.8
Nechells 132kV | Chester Street 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.4 | 29.4 | 29.2 | 28.8 | 28 | 27.5 | 28 | 27.5 | 26.6 | 25.1 | 24.4 | 24.3 | 24.2 | 24.1 | 24 | 23.9 | 23.1 | 19.8 | 18.7
Nechells 132kV | Chester Street 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.4 | 29.4 | 29.3 | 29.2 | 28.7 | 28 | 28.3 | 28.2 | 28 | 26.4 | 25.7 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 24.9 | 22 | 21.4
Nechells 132kV | ERDINGTON 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | ERDINGTON 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | ERDINGTON 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | ERDINGTON 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nechells 132kV | Hockley 132/11kv | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 61.1 | 61.1 | 61.1 | 61 | 61 | 61 | 60.1 | 60 | 59.9 | 55.3 | 54.7 | 54.5 | 53.3 | 52.9 | 52.6 | 52.3 | 51.8 | 48.2 | 47.9
Nechells 132kV | Hockley 132/11kv | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 61.1 | 61.1 | 61.1 | 61 | 60.9 | 60.2 | 58.4 | 57.3 | 56.1 | 41.3 | 39.4 | 37.8 | 36.7 | 36.4 | 36 | 35.8 | 33.9 | 26 | 24.8
Nechells 132kV | Hockley 132/11kv | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 61.1 | 61.1 | 61.1 | 61 | 60.5 | 59.8 | 57.6 | 56.1 | 54.7 | 38.8 | 36.5 | 36 | 35.6 | 35.2 | 34.9 | 34.6 | 32.7 | 24.7 | 23.2
Nechells 132kV | Hockley 132/11kv | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 61.1 | 61.1 | 61.1 | 61 | 61 | 60.5 | 58.6 | 57.5 | 56.2 | 41.4 | 39.5 | 38 | 37.6 | 37.4 | 37.2 | 37.1 | 35.3 | 28 | 27.2
Nechells 132kV | Nechells West 132/25/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 47.4 | 47.3 | 47.1 | 47 | 46.9 | 46.7 | 45 | 45 | 45 | 45 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.8 | 44.7
Nechells 132kV | Nechells West 132/25/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 47.4 | 47.1 | 46.8 | 46.6 | 46 | 45.6 | 44.7 | 44.7 | 44.6 | 44.6 | 44.4 | 44.2 | 44 | 43.8 | 45.5 | 45.5 | 45.4 | 45.1 | 44.7
Nechells 132kV | Nechells West 132/25/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 47.4 | 47 | 46.5 | 46.2 | 45.3 | 45 | 44.5 | 44.1 | 43.8 | 43.3 | 42.9 | 42.7 | 42.5 | 45.2 | 45.1 | 45.1 | 45 | 44.9 | 39.1
Nechells 132kV | Nechells West 132/25/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 47.4 | 47.2 | 47 | 46.9 | 46.3 | 46 | 44.8 | 44.8 | 44.7 | 44.7 | 44.6 | 42.3 | 42.2 | 42.2 | 42.1 | 42.1 | 39.9 | 39.4 | 38.4
Nechells 132kV | Sparkbrook 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 59.3 | 59.3 | 58.9 | 58.6 | 58.2 | 57.8 | 58.3 | 58.2 | 58.1 | 57.9 | 57.7 | 57.7 | 57.7 | 57.8 | 57.8 | 57.8 | 57.8 | 57.8 | 57.4
Nechells 132kV | Sparkbrook 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 59.3 | 59.1 | 58.2 | 57.6 | 56.8 | 56.2 | 57.6 | 57.5 | 57.4 | 56.7 | 56.3 | 56.2 | 56.1 | 55.9 | 55.6 | 55.3 | 55.1 | 52.5 | 49.5
Nechells 132kV | Sparkbrook 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 59.3 | 58.8 | 57.7 | 56.9 | 55.8 | 55.1 | 57 | 56.4 | 56 | 54.8 | 53.1 | 53.1 | 52.9 | 52.7 | 52.4 | 52.2 | 51.9 | 49.1 | 45.7
Nechells 132kV | Sparkbrook 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 59.3 | 59.3 | 58.7 | 58.2 | 57.5 | 56.9 | 57.9 | 57.8 | 57.7 | 57.2 | 57.1 | 57.1 | 57.1 | 57.2 | 57.2 | 57.2 | 57.2 | 56.7 | 54.8
Nechells 132kV | Summer Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 28.5 | 28.4 | 28.4 | 28.4 | 27.9 | 27.9 | 27.9 | 27.9 | 27.9 | 27.9 | 27.9 | 27.6 | 27.5
Nechells 132kV | Summer Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 28.9 | 28 | 27.6 | 27.1 | 23.1 | 22.3 | 22.2 | 22.2 | 22.2 | 22.1 | 22.1 | 21.9 | 22.3 | 22
Nechells 132kV | Summer Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 28.8 | 27.9 | 27.4 | 26.8 | 22.2 | 22 | 21.9 | 21.9 | 23 | 23 | 22.9 | 22.7 | 21.9 | 20.2
Nechells 132kV | Summer Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 29 | 28.1 | 27.7 | 27.2 | 23.5 | 22.5 | 21.9 | 21.8 | 21.8 | 21.8 | 21.8 | 21.7 | 21 | 20.8
Ocker Hill 132kV | Black Lake 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 24.3 | 24.3 | 24.1 | 24 | 23.9 | 23.8 | 22.6 | 22.5 | 22.4 | 22.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.1 | 22 | 22 | 21.8 | 21.5
Ocker Hill 132kV | Black Lake 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 24.3 | 24.2 | 23.8 | 23.6 | 23.4 | 23.2 | 22.2 | 22.2 | 22.1 | 21.9 | 21.7 | 21.5 | 21 | 20.8 | 20.6 | 20.4 | 20.2 | 21.4 | 20.6
Ocker Hill 132kV | Black Lake 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 24.3 | 24.1 | 23.7 | 23.4 | 23.1 | 22.8 | 22.1 | 21.8 | 21.5 | 21.3 | 20.5 | 20.3 | 20.1 | 19.9 | 19.8 | 19.6 | 19.4 | 21 | 19.9
Ocker Hill 132kV | Black Lake 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 24.3 | 24.3 | 24 | 23.7 | 23.5 | 23.4 | 22.3 | 22.3 | 22.2 | 22.1 | 22 | 21.9 | 21.4 | 21.3 | 21.2 | 21.1 | 19.2 | 20.7 | 20
Ocker Hill 132kV | Ocker Hill B 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.6 | 29.6 | 29.5 | 29.4 | 29.3 | 29.2 | 28.8 | 28.8 | 28.8 | 28.8 | 28.7 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.5 | 28.3
Ocker Hill 132kV | Ocker Hill B 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.6 | 29.6 | 29.5 | 29.4 | 29.1 | 28.7 | 28.6 | 28.4 | 28.3 | 28.2 | 28 | 27.9 | 27.8 | 27.7 | 26.3 | 26.1 | 25.8 | 24.7 | 25.4
Ocker Hill 132kV | Ocker Hill B 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.6 | 29.6 | 29.5 | 29.2 | 28.7 | 28.2 | 28.3 | 27.9 | 27.7 | 26.3 | 25.9 | 25.8 | 25.7 | 25.6 | 25.4 | 25.2 | 24.9 | 23.2 | 23.6
Ocker Hill 132kV | Ocker Hill B 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.6 | 29.6 | 29.5 | 29.4 | 29.3 | 29 | 28.7 | 28.6 | 28.5 | 28.4 | 28.3 | 28.3 | 28.3 | 28.2 | 28.1 | 28 | 28 | 26.2 | 28.1
Ocker Hill 132kV | OCKER HILL B 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8
Ocker Hill 132kV | OCKER HILL B 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8
Ocker Hill 132kV | OCKER HILL B 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8
Ocker Hill 132kV | OCKER HILL B 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8
Oldbury 132kV | Birchfield Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.3 | 29.3 | 29.1 | 29 | 28.8 | 28.7 | 28.6 | 28.5 | 28.4 | 28.3 | 28.3 | 28.2 | 28.2 | 28.2 | 28.2 | 28.1 | 28.1 | 28 | 27.5
Oldbury 132kV | Birchfield Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.3 | 29.1 | 28.8 | 28.5 | 28.3 | 28 | 28.2 | 28.1 | 28 | 27.9 | 27.8 | 27.6 | 27.4 | 27.2 | 26.8 | 26.6 | 26.3 | 24.7 | 22.9
Oldbury 132kV | Birchfield Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.3 | 29 | 28.5 | 28.2 | 27.9 | 27.5 | 27.9 | 27.6 | 27.3 | 26.8 | 26.5 | 26.3 | 26 | 25.7 | 25.5 | 25.2 | 24.9 | 22.8 | 20.6
Oldbury 132kV | Birchfield Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.3 | 29.2 | 29 | 28.7 | 28.5 | 28.3 | 28.4 | 28.3 | 28.2 | 28.1 | 28 | 28 | 27.8 | 27.8 | 27.7 | 27.6 | 27.5 | 26.5 | 25.3
Oldbury 132kV | Oldbury B 11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 27.3 | 17.1 | 17 | 16.9 | 16.8 | 16.7 | 16.4 | 16.3 | 16.2 | 16 | 16 | 15.9 | 15.9 | 15.9 | 15.9 | 15.8 | 15.8 | 15.7 | 15.4
Oldbury 132kV | Oldbury B 11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 27.3 | 17 | 16.8 | 16.6 | 16.4 | 16.3 | 15.8 | 15.7 | 15.6 | 15.5 | 15.3 | 15.2 | 15.1 | 15 | 14.9 | 14.7 | 14.6 | 13.6 | 12.5
Oldbury 132kV | Oldbury B 11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 27.3 | 16.9 | 16.6 | 16.4 | 16.2 | 15.9 | 15.5 | 15.2 | 15 | 14.9 | 14.7 | 14.5 | 14.4 | 14 | 13.8 | 13.7 | 13.5 | 11.9 | 10.9
Oldbury 132kV | Oldbury B 11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 27.3 | 17.1 | 16.9 | 16.7 | 16.6 | 16.4 | 16 | 15.9 | 15.8 | 15.7 | 15.6 | 15.6 | 15.5 | 15.5 | 15.4 | 15.4 | 15.3 | 10.1 | 9.2
Oldbury 132kV | Tividale 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 72.3 | 71.8 | 71.7 | 71.6 | 71.6 | 71.5 | 71.7 | 71.6 | 71.5 | 71.4 | 72.1 | 72.1 | 72 | 72 | 72 | 72 | 72 | 71.9 | 71.7
Oldbury 132kV | Tividale 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 72.3 | 71.8 | 71.4 | 71.2 | 71.1 | 69.1 | 71.3 | 71.2 | 71.2 | 71.2 | 71.7 | 71.6 | 71.6 | 71.5 | 71.4 | 71.4 | 71.3 | 69.2 | 68.2
Oldbury 132kV | Tividale 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 72.3 | 71.7 | 71.3 | 71.1 | 69.2 | 69 | 71.1 | 71 | 69.3 | 69.2 | 71.3 | 71.3 | 71.2 | 71.2 | 71.1 | 71.1 | 69.2 | 68.2 | 67.2
Oldbury 132kV | Tividale 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 72.3 | 71.8 | 71.5 | 71.3 | 71.2 | 71.1 | 71.4 | 71.3 | 71.3 | 71.2 | 71.8 | 71.8 | 71.8 | 71.7 | 71.7 | 71.7 | 71.6 | 71.3 | 71.1
Penn 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 15.9 | 15.8 | 15.7 | 15.5 | 15.3 | 15.3 | 15.4 | 15.2 | 15 | 14.7 | 14.3 | 14.1 | 13.9 | 13.8 | 13.6 | 13.6 | 13.5 | 12.8 | 11.9
Penn 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 15.9 | 15.6 | 15.2 | 14.7 | 14.4 | 14.2 | 14 | 13.5 | 13 | 12.5 | 12 | 11.5 | 11.1 | 10.7 | 10.4 | 10.1 | 9.8 | 7.4 | 5.5
Penn 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 15.9 | 15.6 | 15 | 15.1 | 14.9 | 14.5 | 14.4 | 13.9 | 13.4 | 13 | 12.6 | 12.3 | 11.2 | 10.8 | 10.5 | 10.2 | 10 | 8.2 | 7.1
Penn 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 15.9 | 15.7 | 15.3 | 14.9 | 14.8 | 14.6 | 14.5 | 14.2 | 13.8 | 13.5 | 13.1 | 12.8 | 12.7 | 12.5 | 12.4 | 12.3 | 12.2 | 10.4 | 8.7
Penn 132kV | Coseley 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 18.8 | 18.6 | 18.4 | 18.4 | 18.2 | 18 | 16.7 | 16.7 | 16.6 | 16.6 | 16.5 | 16.5 | 16.5 | 16.4 | 16.4 | 16.4 | 16.4 | 16.3 | 15.6
Penn 132kV | Coseley 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 18.8 | 18.4 | 18 | 17.7 | 17.5 | 17.3 | 16.4 | 16.2 | 16 | 15.9 | 15.6 | 15.4 | 15.1 | 14.6 | 14.4 | 14.1 | 13.8 | 11.8 | 9.9
Penn 132kV | Coseley 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 18.8 | 18.2 | 17.7 | 17.2 | 16.9 | 16.6 | 15.6 | 15.1 | 14.7 | 14.4 | 14 | 13.4 | 13.2 | 12.9 | 12.7 | 12.4 | 12.1 | 9.9 | 7.5
Penn 132kV | Coseley 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 18.8 | 18.5 | 18.3 | 18 | 17.8 | 17.7 | 16.5 | 16.4 | 16.3 | 16.2 | 16.1 | 16 | 15.9 | 15.5 | 15.5 | 15.4 | 15.3 | 9 | 7.5
Penn 132kV | Dudley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 27.7 | 27.2 | 26.9 | 26.7 | 26.5 | 26.2 | 26.1 | 25.8 | 25.6 | 25.2 | 24.9 | 24.8 | 24.7 | 24.6 | 28.1 | 28.1 | 28.1 | 28.1 | 27.6
Penn 132kV | Dudley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 27.7 | 26.9 | 26.4 | 26 | 25.6 | 25.1 | 28.2 | 28 | 27.8 | 27.6 | 27.2 | 26.7 | 26.5 | 26.1 | 25.6 | 25.3 | 24.8 | 22.7 | 20.3
Penn 132kV | Dudley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 27.7 | 26.7 | 26 | 25.4 | 24.9 | 24 | 27.6 | 26.8 | 26.2 | 25.7 | 25 | 24.7 | 24.3 | 23.9 | 23.5 | 23.2 | 22.8 | 20.4 | 17.4
Penn 132kV | Dudley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 27.7 | 27.2 | 26.7 | 26.4 | 26.1 | 25.5 | 28.4 | 28.2 | 28 | 27.9 | 27.7 | 27.6 | 27.4 | 27.3 | 27.1 | 27.1 | 26.8 | 25.6 | 23.7
Penn 132kV | Hinksford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6
Penn 132kV | Hinksford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 21.6 | 21.6 | 21.6 | 21.6 | 21.1 | 20.4 | 21.6 | 21.6 | 21.6 | 21.6 | 21.3 | 18 | 14.4
Penn 132kV | Hinksford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 21.6 | 21.6 | 21.1 | 20.3 | 19.7 | 19 | 21.6 | 21.6 | 21.4 | 20.8 | 20.2 | 16.8 | 13.6
Penn 132kV | Hinksford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 20
Penn 132kV | HINKSFORD 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 21.4 | 20.2 | 21.4 | 21.4 | 21.4 | 21.4 | 20 | 20.1 | 20.2 | 21.4 | 21.5 | 21.7 | 21.8 | 21.8 | 21.9 | 22 | 22 | 22.5 | 23.2
Penn 132kV | HINKSFORD 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 21.4 | 20.2 | 21.4 | 21.4 | 21.5 | 21.7 | 21.4 | 21.6 | 21.9 | 22.2 | 22.5 | 22.8 | 23.1 | 23.5 | 23.6 | 23.8 | 24 | 25.2 | 26.5
Penn 132kV | HINKSFORD 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 21.4 | 20.2 | 21.4 | 21.4 | 21.4 | 21.6 | 20.2 | 21.5 | 21.6 | 21.9 | 22.1 | 22.3 | 22.6 | 22.9 | 23 | 23.2 | 23.4 | 24 | 24.5
Penn 132kV | HINKSFORD 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 21.4 | 20.2 | 21.4 | 21.4 | 21.4 | 21.5 | 20.1 | 21.4 | 21.5 | 21.6 | 21.8 | 22 | 22.1 | 22.3 | 22.4 | 22.4 | 22.5 | 23.4 | 24.5
Penn 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.3 | 9.3 | 9.3 | 9.3 | 9.2 | 9.1 | 8.8 | 8.6 | 8.4 | 8.2 | 7.9 | 7.7 | 7.6 | 7.5 | 7.4 | 7.4 | 7.3 | 6.7 | 6
Penn 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.3 | 9.3 | 9.3 | 9.1 | 8.8 | 8.5 | 8.1 | 7.8 | 7.4 | 7.1 | 6.8 | 6.4 | 6.1 | 5.8 | 5.6 | 5.4 | 5.2 | 4 | 2.6
Penn 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.3 | 9.3 | 9.2 | 9.2 | 8.9 | 8.7 | 8.4 | 8.1 | 7.7 | 7.5 | 7.2 | 6.9 | 6.6 | 6.4 | 6.2 | 6 | 5.8 | 5.2 | 4.6
Penn 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.3 | 9.3 | 9.3 | 9.2 | 9.1 | 8.9 | 8.5 | 8.3 | 8 | 7.8 | 7.5 | 7.3 | 7.1 | 7 | 6.9 | 6.8 | 6.7 | 5.8 | 4.7
Penn 132kV | Lye 11kV DUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 21.3 | 21.1 | 20.9 | 20.8 | 20.7 | 20.5 | 20.4 | 20.3 | 20.1 | 20 | 19.8 | 19.7 | 19.7 | 19.7 | 19.7 | 19.6 | 19.6 | 19.2 | 18.6
Penn 132kV | Lye 11kV DUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 21.3 | 20.9 | 20.6 | 20.4 | 20.1 | 19.8 | 19.6 | 19.4 | 19.2 | 19 | 18.8 | 18.7 | 18.5 | 18.2 | 18.1 | 17.7 | 17.4 | 15.8 | 14.3
Penn 132kV | Lye 11kV DUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 21.3 | 20.8 | 20.4 | 20.1 | 19.7 | 19.4 | 19 | 18.7 | 18.4 | 18.1 | 17.8 | 17.6 | 17.4 | 17.1 | 16.9 | 16.7 | 16.5 | 14.7 | 12.9
Penn 132kV | Lye 11kV DUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 21.3 | 21.1 | 20.8 | 20.6 | 20.4 | 20.2 | 20 | 19.8 | 19.6 | 19.4 | 19.3 | 19.2 | 19.2 | 19.1 | 19 | 18.9 | 18.8 | 17.7 | 16.5
Penn 132kV | PATTINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 16 | 16 | 15.9 | 15.9 | 15.9 | 15.8 | 16.1 | 16 | 15.9 | 15.8 | 15.7 | 15.6 | 15.5 | 15.5 | 15.5 | 15.4 | 15.4 | 15.1 | 14.8
Penn 132kV | PATTINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 16 | 15.9 | 15.9 | 15.8 | 15.7 | 15.5 | 15.7 | 15.5 | 15.4 | 15.2 | 15.1 | 14.8 | 14.2 | 13.6 | 13.2 | 12.8 | 12.3 | 9.3 | 6.6
Penn 132kV | PATTINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 16 | 15.9 | 15.9 | 15.8 | 15.7 | 15.7 | 15.8 | 15.7 | 15.5 | 15.4 | 15.2 | 15.1 | 14.5 | 14 | 13.6 | 13.2 | 12.8 | 10.5 | 9
Penn 132kV | PATTINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 16 | 16 | 15.9 | 15.9 | 15.8 | 15.8 | 16 | 15.9 | 15.7 | 15.6 | 15.5 | 15.4 | 15.3 | 15.3 | 15.2 | 15.2 | 15.1 | 13.4 | 11.1
Penn 132kV | Wolverhampton West 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 13.6 | 13.6 | 13.4 | 13.3 | 13.2 | 13.1 | 25.7 | 25.5 | 25.4 | 25.2 | 25 | 24.9 | 24.8 | 24.8 | 24.7 | 24.7 | 24.7 | 24.5 | 24.1
Penn 132kV | Wolverhampton West 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 13.6 | 13.4 | 13.2 | 13 | 12.8 | 12.6 | 25 | 24.8 | 24.5 | 24.2 | 24.1 | 22.1 | 22.1 | 21.7 | 21.6 | 21.4 | 21 | 19.1 | 16.9
Penn 132kV | Wolverhampton West 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 13.6 | 13.3 | 13 | 12.8 | 12.5 | 12.2 | 24.6 | 24.1 | 22.2 | 22.1 | 21.7 | 21.6 | 21.3 | 21 | 20.8 | 20.5 | 20.1 | 18.1 | 15.8
Penn 132kV | Wolverhampton West 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 13.6 | 13.5 | 13.4 | 13.2 | 13.1 | 12.9 | 25.3 | 25.1 | 24.8 | 24.6 | 24.4 | 24.3 | 24.2 | 24.2 | 24.2 | 24.1 | 24.1 | 21.6 | 20.1
Penn 132kV | WOLVERHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 86 | 85.8 | 85.3 | 84.9 | 84.5 | 84.2 | 84.9 | 84.3 | 83.7 | 83.1 | 82.6 | 79.5 | 79.4 | 79 | 79 | 78.9 | 78.9 | 77.8 | 75.2
Penn 132kV | WOLVERHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 86 | 85.2 | 84.4 | 83.4 | 82.9 | 82.6 | 82.3 | 79.1 | 78 | 77.1 | 75.8 | 74.6 | 73.6 | 72.5 | 71.8 | 70.8 | 69.7 | 62.7 | 55.5
Penn 132kV | WOLVERHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 86 | 85 | 83.8 | 83.4 | 82.8 | 79.3 | 79.6 | 78.1 | 77.2 | 76.1 | 75 | 74 | 72.3 | 71.1 | 70.3 | 69.3 | 68.3 | 61.7 | 55.8
Penn 132kV | WOLVERHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 86 | 85.5 | 84.8 | 84.1 | 83.7 | 83.2 | 83.3 | 82.5 | 79.5 | 78.9 | 77.9 | 77.6 | 77.2 | 76.8 | 76.7 | 76.4 | 76 | 72 | 66.5
Penn 132kV | Woodside 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 57.1 | 57 | 56.7 | 56.5 | 56.4 | 56.1 | 56.5 | 56.4 | 56.2 | 56.1 | 55.9 | 55.8 | 55.7 | 55.6 | 55.5 | 55.4 | 55.3 | 55 | 52.9
Penn 132kV | Woodside 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 57.1 | 56.8 | 56.2 | 55.9 | 55.6 | 55.1 | 55.8 | 55.6 | 55.4 | 55.1 | 53.1 | 52.8 | 52.6 | 52.1 | 51.6 | 50.9 | 50.3 | 48.1 | 46.2
Penn 132kV | Woodside 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 57.1 | 56.7 | 55.9 | 55.5 | 55.1 | 53 | 55.4 | 54.9 | 53.1 | 52.7 | 52.1 | 51.6 | 51.2 | 50.7 | 50 | 49.3 | 48.7 | 46.2 | 43.9
Penn 132kV | Woodside 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 57.1 | 57 | 56.5 | 56.3 | 56 | 55.4 | 56.1 | 55.8 | 55.7 | 55.5 | 55.1 | 54.9 | 53.1 | 52.9 | 52.8 | 52.4 | 52 | 50.6 | 49.3
Port Ham 132kV | ALDERTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 6.6 | 6.6 | 6.5 | 6.5 | 6.4 | 6.3 | 6.1 | 5.9 | 5.6 | 5.4 | 5.1 | 4.8 | 4.6 | 4.4 | 4.2 | 4.2 | 4.1 | 3.4 | 2.6
Port Ham 132kV | ALDERTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 6.6 | 6.5 | 6.4 | 6.2 | 5.9 | 5.7 | 5.4 | 4.6 | 3.9 | 3.6 | 3 | 2.4 | 2 | 1.7 | 1.4 | 1.1 | 0.8 | 0 | 0
Port Ham 132kV | ALDERTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 6.6 | 6.5 | 6.3 | 6.2 | 6 | 5.8 | 5 | 4.2 | 3.6 | 3.2 | 2.8 | 2.4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ALDERTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 6.6 | 6.6 | 6.5 | 6.4 | 6.3 | 6.1 | 5.9 | 5.2 | 4.6 | 4.3 | 3.8 | 3.4 | 3.1 | 2.9 | 2.8 | 2.7 | 2.6 | 0.7 | 0
Port Ham 132kV | BILSON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.3 | 7.3 | 7.2 | 7.2 | 7.1 | 7.1 | 11.2 | 11 | 10.8 | 10.7 | 10.4 | 9.5 | 8.5 | 7 | 4 | 2.8 | 3.3 | 2.1 | 0
Port Ham 132kV | BILSON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.3 | 7.3 | 7.1 | 7 | 6.9 | 6.9 | 10.5 | 9.4 | 8 | 7.4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BILSON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.3 | 7.2 | 7 | 6.9 | 6.6 | 6.4 | 9.2 | 7.4 | 2.8 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BILSON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.3 | 7.3 | 7.2 | 7.1 | 7.1 | 7 | 11 | 9.8 | 8.5 | 8.3 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BISHOPS CLEEVE 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 2.1 | 2 | 1.8 | 1.5 | 1.3 | 1 | 3.5 | 3.1 | 2.5 | 2 | 1.3 | 0.7 | 0 | 0 | 0 | 1.9 | 1.8 | 1.1 | 3.8
Port Ham 132kV | BISHOPS CLEEVE 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 2.1 | 1.9 | 1.5 | 0.9 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BISHOPS CLEEVE 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 2.1 | 1.8 | 1.3 | 0.8 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BISHOPS CLEEVE 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 2.1 | 2 | 1.6 | 1.1 | 0.6 | 0 | 1.9 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BIXHEAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.4 | 9.3 | 9.2 | 9.2 | 9.1 | 9 | 7.5 | 7.4 | 7.3 | 7.2 | 7.1 | 7 | 6.9 | 6.8 | 6.8 | 6.5 | 11.3 | 11.2 | 10.9
Port Ham 132kV | BIXHEAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.4 | 9.3 | 9.1 | 9 | 8.8 | 8.7 | 7.1 | 6.8 | 6.6 | 6.5 | 6.2 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BIXHEAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.4 | 9.2 | 9 | 8.8 | 8.6 | 8.4 | 6.5 | 6.2 | 5.9 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BIXHEAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.4 | 9.3 | 9.2 | 9.1 | 9 | 8.9 | 7.3 | 7 | 6.8 | 6.2 | 6 | 5.8 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | BROCKWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 14.8 | 14.7 | 14.5 | 14.4 | 14.2 | 14.1 | 13.7 | 13.5 | 13.2 | 13 | 12.6 | 12.1 | 11.6 | 11.1 | 10.7 | 10.6 | 10.5 | 10.2 | 9.6
Port Ham 132kV | BROCKWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 14.8 | 14.6 | 14.3 | 14 | 13.7 | 12.9 | 12.4 | 11.4 | 10.1 | 9.8 | 8 | 6.8 | 6.4 | 6.1 | 5.8 | 5.5 | 5.2 | 4 | 2.8
Port Ham 132kV | BROCKWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 14.8 | 14.5 | 14.1 | 13.7 | 13.2 | 12.8 | 11.4 | 9.9 | 8.1 | 7.6 | 6.3 | 6 | 5.7 | 5.4 | 5.2 | 4.9 | 4.6 | 3.3 | 1.9
Port Ham 132kV | BROCKWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 14.8 | 14.6 | 14.4 | 14.2 | 13.9 | 13.2 | 12.7 | 11.7 | 10.5 | 10.2 | 8.7 | 7.5 | 7.1 | 6.9 | 6.7 | 6.4 | 6.2 | 4.7 | 3.7
Port Ham 132kV | CASTLE MEADS 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | CASTLE MEADS 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | CASTLE MEADS 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | CASTLE MEADS 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Cheltenham 132/66/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.9 | 29.9 | 29.6 | 28.9 | 28.7 | 28.7 | 29.1 | 29.1 | 29 | 28.9 | 28.7 | 28.5 | 28.3 | 28.2 | 28.1 | 28.1 | 28.1 | 25.2 | 24.7
Port Ham 132kV | Cheltenham 132/66/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.9 | 29.6 | 28.6 | 28 | 27.7 | 26.3 | 28.3 | 28.1 | 24.7 | 24.6 | 23.5 | 21.9 | 21.4 | 20.9 | 20.7 | 20.4 | 20.1 | 18.5 | 16.9
Port Ham 132kV | Cheltenham 132/66/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.9 | 29.1 | 28.4 | 27.9 | 27.6 | 26.2 | 28.1 | 24.7 | 23.5 | 23.1 | 21.2 | 20.6 | 20.1 | 19.9 | 19.7 | 19.4 | 19.1 | 17.5 | 16
Port Ham 132kV | Cheltenham 132/66/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.9 | 29.9 | 28.8 | 28.3 | 28 | 27.7 | 28.5 | 28.2 | 25.3 | 24.8 | 24.1 | 23.1 | 22.4 | 22.1 | 22 | 21.9 | 21.8 | 20.8 | 19.6
Port Ham 132kV | CHELTENHAM 66kV S STN | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 33.8 | 33.7 | 33.4 | 33.2 | 32.9 | 32.6 | 31.2 | 30.9 | 30.7 | 30.4 | 30 | 29.5 | 29.1 | 28.7 | 28.5 | 30.8 | 30.7 | 29.9 | 32.5
Port Ham 132kV | CHELTENHAM 66kV S STN | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 33.8 | 33.5 | 33.1 | 32.5 | 31.8 | 31 | 29.7 | 28.7 | 27 | 26.1 | 24.6 | 23 | 25.7 | 24.7 | 24 | 25.8 | 25.3 | 20.6 | 16.9
Port Ham 132kV | CHELTENHAM 66kV S STN | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 33.8 | 33.5 | 33 | 32.4 | 31.8 | 31 | 29.6 | 27.8 | 26.2 | 25.3 | 24.2 | 23.1 | 24.6 | 22.3 | 21.6 | 23.5 | 22.9 | 20.9 | 16.4
Port Ham 132kV | CHELTENHAM 66kV S STN | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 33.8 | 33.6 | 33.2 | 32.8 | 32.2 | 31.5 | 29.8 | 29.1 | 27.8 | 26.9 | 25.5 | 24.5 | 26.6 | 26.2 | 25.9 | 28 | 27.7 | 23.6 | 20.3
Port Ham 132kV | COMMERCIAL RD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 11.8 | 11.7 | 10.9 | 10.7 | 10.5 | 10.3 | 10.1 | 9.8 | 9.4 | 9.1 | 8.6 | 8.3 | 8 | 7.8 | 7.7 | 8.6 | 8.5 | 7.7 | 6.7
Port Ham 132kV | COMMERCIAL RD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 11.8 | 11 | 10.6 | 10.2 | 9.7 | 9.2 | 8.7 | 7.9 | 7.1 | 6.6 | 5.7 | 4.9 | 4.4 | 3.9 | 3.5 | 4.1 | 3.7 | 1.4 | 0
Port Ham 132kV | COMMERCIAL RD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 11.8 | 10.9 | 10.4 | 10 | 9.5 | 9 | 8.1 | 7.1 | 6 | 5.4 | 4.6 | 4.1 | 3.6 | 3.1 | 2.8 | 3.4 | 3 | 2.2 | 0
Port Ham 132kV | COMMERCIAL RD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 11.8 | 11.1 | 10.8 | 10.6 | 10.3 | 9.9 | 9.5 | 8.8 | 8 | 7.5 | 6.7 | 6.1 | 5.8 | 5.5 | 5.3 | 6.2 | 6 | 4.3 | 2.4
Port Ham 132kV | Eastern Avenue 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.1 | 29.1 | 29 | 29 | 28.7 | 28.6 | 28.4 | 28.3 | 28.2 | 28.2 | 28 | 28 | 27.9 | 27.8 | 27.8 | 27.7 | 27.7 | 27.6 | 27.4
Port Ham 132kV | Eastern Avenue 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.1 | 29 | 28.9 | 28.5 | 28.4 | 28.2 | 28 | 27.6 | 27.3 | 27.3 | 23.2 | 17.6 | 13.5 | 9.1 | 5.7 | 4.1 | 1.3 | 0 | 0
Port Ham 132kV | Eastern Avenue 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.1 | 29 | 28.6 | 28.4 | 28.2 | 28 | 27.5 | 27.2 | 26.7 | 26.5 | 22.1 | 17.8 | 14.6 | 11.3 | 8.5 | 7 | 4.5 | 0 | 0
Port Ham 132kV | Eastern Avenue 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.1 | 29.1 | 29 | 28.7 | 28.6 | 28.5 | 28.3 | 28 | 27.7 | 27.6 | 27.4 | 23.8 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ELTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 3 | 2.5 | 2.5 | 2.4 | 2.3 | 2.1 | 4.9 | 4.6 | 4.2 | 3.9 | 3.4 | 3.1 | 2.8 | 2.7 | 2.5 | 2.4 | 2.3 | 1.2 | 0
Port Ham 132kV | ELTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 3 | 2.5 | 2.4 | 2.1 | 1.7 | 1.3 | 3.8 | 3.2 | 2.6 | 2.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ELTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 3 | 2.5 | 2.4 | 2.3 | 2 | 1.8 | 4.3 | 3.7 | 3.1 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ELTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 3 | 2.5 | 2.5 | 2.4 | 2.2 | 1.9 | 4.5 | 4.1 | 3.6 | 3.2 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | HEREFORD 132kV S STN | Bulk Supply Point | 66 | Counterfactual | Headroom (MW) | 77.2 | 77.1 | 76.9 | 76.6 | 76.3 | 76 | 76.3 | 75.4 | 74.7 | 73.9 | 73 | 72.4 | 71.9 | 71.6 | 71.2 | 70.9 | 70.5 | 68.8 | 66.5
Port Ham 132kV | HEREFORD 132kV S STN | Bulk Supply Point | 66 | Electric Engagement | Headroom (MW) | 77.2 | 76.9 | 76.4 | 75.6 | 74.8 | 73.6 | 71.5 | 70.2 | 69 | 67.8 | 66.6 | 65.5 | 64.3 | 62.8 | 61.8 | 60.6 | 61.4 | 55.9 | 50.6
Port Ham 132kV | HEREFORD 132kV S STN | Bulk Supply Point | 66 | Holistic Transition | Headroom (MW) | 77.2 | 76.8 | 76 | 74.9 | 73.9 | 71.7 | 70.9 | 69.3 | 67.7 | 66.5 | 65.2 | 63.7 | 62.3 | 62.9 | 61.9 | 60.8 | 59.8 | 52.5 | 47.6
Port Ham 132kV | HEREFORD 132kV S STN | Bulk Supply Point | 66 | Hydrogen Evolution | Headroom (MW) | 77.2 | 77.1 | 76.7 | 76.2 | 75.6 | 74.7 | 73 | 71 | 69.9 | 68.9 | 67.9 | 67.3 | 66.7 | 66 | 65.4 | 64.9 | 64.4 | 60.7 | 57
Port Ham 132kV | Hereford Central 66/11kv | Primary Substation | 11 | Counterfactual | Headroom (MW) | 32.6 | 32.6 | 32.5 | 32.5 | 32.4 | 32.4 | 31.6 | 31.5 | 31.4 | 31.3 | 31.2 | 31.1 | 31 | 31 | 30.9 | 30.9 | 30.8 | 30.6 | 30.2
Port Ham 132kV | Hereford Central 66/11kv | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 32.6 | 32.6 | 32.5 | 32.5 | 32.4 | 32.1 | 31.1 | 30.9 | 30.7 | 30.4 | 30.2 | 30 | 29.8 | 29.6 | 29.4 | 29.1 | 28.9 | 27.7 | 21.8
Port Ham 132kV | Hereford Central 66/11kv | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 32.6 | 32.6 | 32.5 | 32.2 | 31.9 | 31.6 | 30.5 | 30.2 | 29.9 | 29.6 | 29.2 | 29 | 28.7 | 28.5 | 28.3 | 28 | 27.8 | 21.8 | 21.4
Port Ham 132kV | Hereford Central 66/11kv | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 32.6 | 32.6 | 32.5 | 32.5 | 32.4 | 32.4 | 31.4 | 31.2 | 31 | 30.9 | 30.7 | 30.6 | 30.4 | 30.3 | 30.3 | 30.1 | 30 | 29.3 | 28.5
Port Ham 132kV | HEREFORD NORTH 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 29.2 | 29.2 | 29.1 | 29 | 28.9 | 28.8 | 30.2 | 29.8 | 29.7 | 29.4 | 29.2 | 29.1 | 29 | 28.9 | 28.9 | 28.8 | 28.8 | 28.6 | 28.3
Port Ham 132kV | HEREFORD NORTH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 29.2 | 29.1 | 28.9 | 28.6 | 28.5 | 28.3 | 28.5 | 28.2 | 28 | 27.8 | 26.2 | 26 | 25.9 | 25.6 | 25.5 | 25.3 | 25.2 | 23 | 19
Port Ham 132kV | HEREFORD NORTH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 29.2 | 29 | 28.8 | 28.4 | 28.2 | 27.6 | 28.4 | 28.1 | 27.8 | 26.2 | 25.9 | 25.6 | 25.4 | 25.2 | 25.1 | 24.9 | 24.8 | 20.8 | 17.3
Port Ham 132kV | HEREFORD NORTH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 29.2 | 29.2 | 29 | 28.8 | 28.6 | 28.4 | 28.6 | 28.4 | 28.1 | 27.9 | 27.7 | 27.7 | 26 | 26 | 25.9 | 25.9 | 25.8 | 25.4 | 23.3
Port Ham 132kV | HEREFORD SOUTH 66 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 18.6 | 18.4 | 18.2 | 17.9 | 17.6 | 17.3 | 16.2 | 15.7 | 15.4 | 15.1 | 14.7 | 14.4 | 14.2 | 14 | 13.7 | 13.4 | 13.2 | 11.8 | 10.1
Port Ham 132kV | HEREFORD SOUTH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 18.6 | 18.2 | 17.8 | 17.1 | 16.4 | 15.5 | 14.5 | 13.6 | 12.9 | 12.3 | 11.6 | 10.9 | 10.3 | 9.5 | 8.9 | 8.2 | 9.3 | 5.8 | 2.4
Port Ham 132kV | HEREFORD SOUTH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 18.6 | 18.1 | 17.4 | 16.8 | 16.1 | 15.1 | 14.4 | 13.4 | 12.5 | 12 | 11.4 | 10.8 | 10 | 11.1 | 10.5 | 9.8 | 9.2 | 4 | 1.3
Port Ham 132kV | HEREFORD SOUTH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 18.6 | 18.4 | 18 | 17.6 | 17.2 | 16.5 | 15.2 | 14 | 13.3 | 12.9 | 12.4 | 12 | 11.7 | 11.4 | 11 | 10.7 | 10.3 | 7.9 | 5.7
Port Ham 132kV | Lydney 33/11kVDUMMY | Primary Substation | 11 | Counterfactual | Headroom (MW) | 8.3 | 8.3 | 8.2 | 8.2 | 8 | 8 | 8.2 | 8 | 7.7 | 7.5 | 7 | 6.1 | 5.2 | 4.3 | 3.5 | 3.4 | 3.4 | 3.1 | 2.6
Port Ham 132kV | Lydney 33/11kVDUMMY | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 8.3 | 8.2 | 8 | 7.9 | 7.6 | 7.4 | 7.4 | 5.9 | 3.9 | 3.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Lydney 33/11kVDUMMY | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 8.3 | 8.2 | 8 | 7.8 | 7.6 | 7.3 | 6.1 | 3.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Lydney 33/11kVDUMMY | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 8.3 | 8.3 | 8.2 | 8 | 7.9 | 7.7 | 7.8 | 6.4 | 4.6 | 4.3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | LYDNEY 33kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 68.1 | 67.5 | 67 | 66.4 | 65.8 | 65.2 | 63 | 62 | 60.4 | 59.1 | 56.6 | 52.7 | 48.6 | 43.9 | 38.6 | 36.4 | 40.4 | 37.9 | 34.6
Port Ham 132kV | LYDNEY 33kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 68.1 | 67.1 | 66.1 | 64.8 | 63.3 | 61.7 | 58.3 | 52.8 | 45.3 | 42.7 | 30.4 | 17.6 | 11.3 | 5.4 | 1.6 | 0 | 2.3 | 0 | 0
Port Ham 132kV | LYDNEY 33kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 68.1 | 66.8 | 65.4 | 64.4 | 62.9 | 61.2 | 53.6 | 44.7 | 32.8 | 29 | 11.7 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | LYDNEY 33kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 68.1 | 67.4 | 66.7 | 66 | 65.1 | 64.1 | 61.2 | 56.2 | 49.4 | 46.7 | 36.1 | 25.4 | 17.7 | 13.2 | 10.1 | 8.2 | 12.3 | 4.8 | 0
Port Ham 132kV | Marle Hill 132/66/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 20.5 | 20.2 | 20 | 20 | 19.9 | 19.8 | 19.4 | 19.3 | 19.3 | 19.2 | 19.1 | 19.1 | 19 | 19 | 19 | 18.9 | 18.9 | 18.8 | 18.5
Port Ham 132kV | Marle Hill 132/66/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 20.5 | 20.1 | 19.9 | 19.7 | 19.1 | 19 | 18.7 | 18.5 | 18.5 | 18.4 | 18.4 | 18.4 | 18.3 | 18.3 | 18.3 | 14 | 14 | 13.6 | 13
Port Ham 132kV | Marle Hill 132/66/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 20.5 | 20 | 19.7 | 19.5 | 19.3 | 19.1 | 18.7 | 18.6 | 18.5 | 18.4 | 18.4 | 18.4 | 18.3 | 18.3 | 14 | 14 | 14 | 13.6 | 12.9
Port Ham 132kV | Marle Hill 132/66/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 20.5 | 20.1 | 20 | 19.9 | 19.7 | 19.6 | 19.2 | 19.1 | 19 | 18.9 | 18.9 | 18.8 | 18.8 | 18.8 | 18.7 | 18.7 | 18.7 | 18.4 | 14
Port Ham 132kV | MEAD LA 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 12.5 | 12.5 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.3 | 12.2 | 12 | 11.8 | 11.6 | 11.3 | 11.1 | 10.9 | 10.7 | 10.7 | 10.6
Port Ham 132kV | MEAD LA 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 12.5 | 12.5 | 12.4 | 12.4 | 12.3 | 12.2 | 12.2 | 11.9 | 11.4 | 11.1 | 10.2 | 9.6 | 9.1 | 8.7 | 8.5 | 8.2 | 8.1 | 7.7 | 7.4
Port Ham 132kV | MEAD LA 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 12.5 | 12.5 | 12.4 | 12.4 | 12.3 | 12.2 | 12 | 11.5 | 10.6 | 10.2 | 9 | 8.5 | 8.2 | 8 | 7.9 | 7.9 | 7.8 | 7.5 | 7.3
Port Ham 132kV | MEAD LA 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 12.5 | 12.5 | 12.4 | 12.4 | 12.4 | 12.3 | 12.3 | 12.1 | 11.7 | 11.5 | 10.8 | 10.2 | 9.7 | 9.3 | 9.1 | 8.8 | 8.7 | 8.5 | 8.3
Port Ham 132kV | MITCHELDEAN 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 10.8 | 10.8 | 10.8 | 10.7 | 10.6 | 10.6 | 10.5 | 10.4 | 10.3 | 10.3 | 10 | 9.7 | 9.4 | 8.2 | 4.7 | 3.2 | 3.8 | 2.4 | 0.6
Port Ham 132kV | MITCHELDEAN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 10.8 | 10.8 | 10.7 | 10.5 | 10.4 | 10.3 | 10 | 9.8 | 9.3 | 8.6 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | MITCHELDEAN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 10.8 | 10.8 | 10.6 | 10.5 | 10.4 | 10.3 | 9.9 | 9.2 | 3.3 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | MITCHELDEAN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 10.8 | 10.8 | 10.7 | 10.7 | 10.6 | 10.5 | 10.4 | 10 | 9.7 | 9.6 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Montpellier 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 73.1 | 72.7 | 72.3 | 72 | 71.7 | 71.5 | 72.3 | 72.2 | 72 | 71.4 | 70.7 | 70.1 | 69.6 | 69.2 | 68.8 | 68.6 | 68.4 | 67 | 65.3
Port Ham 132kV | Montpellier 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 73.1 | 72.3 | 71.6 | 71.1 | 70.7 | 69.5 | 69.9 | 68.2 | 66.5 | 65.2 | 63.2 | 61.8 | 61.1 | 60.3 | 59.6 | 58.9 | 58.2 | 50.7 | 46.5
Port Ham 132kV | Montpellier 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 73.1 | 72.1 | 71.1 | 70.6 | 69.3 | 68.6 | 68.1 | 66 | 63.9 | 62.5 | 60.8 | 59.9 | 51.9 | 51.2 | 50.5 | 49.9 | 49.6 | 47.7 | 43.1
Port Ham 132kV | Montpellier 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 73.1 | 72.6 | 72.1 | 71.7 | 71.3 | 70.9 | 70.6 | 69.3 | 67.9 | 67.1 | 65.6 | 64.3 | 63.5 | 63.1 | 62.7 | 62.3 | 61.9 | 55.1 | 51.7
Port Ham 132kV | PRINCESS ROYAL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 9.5 | 9.5 | 9.4 | 9.4 | 9.4 | 9.4 | 9.6 | 9.5 | 9.4 | 9.4 | 8.4 | 8 | 7.5 | 6.7 | 6 | 5.8 | 5.7 | 5.5 | 5.1
Port Ham 132kV | PRINCESS ROYAL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 9.5 | 9.4 | 9.4 | 9.3 | 9.3 | 8.7 | 9.3 | 8.2 | 7.4 | 7.1 | 5.3 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | PRINCESS ROYAL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 9.5 | 9.4 | 9.3 | 9.3 | 8.7 | 8.6 | 8.1 | 7.1 | 5.5 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | PRINCESS ROYAL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 9.5 | 9.5 | 9.4 | 9.4 | 9.3 | 9.3 | 9.5 | 8.4 | 7.8 | 7.5 | 5.9 | 4.2 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | ROTOL 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 28.2 | 26.6 | 27.4 | 26.6 | 26.5 | 26.6 | 27.4 | 26.2 | 26 | 25.7 | 25.3 | 24.8 | 24.4 | 24 | 23.7 | 23.6 | 23.4 | 22.6 | 21.5
Port Ham 132kV | ROTOL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 28.2 | 26.6 | 26.4 | 26 | 25.7 | 25 | 24.1 | 22.4 | 21 | 20.3 | 19.1 | 18.1 | 17.6 | 17 | 16.6 | 16.1 | 15.7 | 13.7 | 11.4
Port Ham 132kV | ROTOL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 28.2 | 26.5 | 26.2 | 26.1 | 25.7 | 25.2 | 23.2 | 21.5 | 20 | 19.3 | 18.5 | 18 | 17.5 | 17 | 16.6 | 16.2 | 15.8 | 13.7 | 11.8
Port Ham 132kV | ROTOL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 28.2 | 26.6 | 26.5 | 26.2 | 26 | 25.4 | 24.6 | 23.1 | 21.7 | 21.2 | 20.1 | 19.3 | 18.8 | 18.5 | 18.2 | 17.9 | 17.7 | 15.4 | 13.4
Port Ham 132kV | STOWFIELD 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.5 | 7.5 | 7.5 | 7.4 | 7.4 | 7.3 | 7.2 | 7.1 | 7 | 4.3 | 2.9 | 3.4 | 2.2 | 0.5
Port Ham 132kV | STOWFIELD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7.6 | 7.6 | 7.6 | 7.5 | 7.5 | 7.4 | 7.4 | 7.2 | 6.8 | 6.8 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | STOWFIELD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7.6 | 7.6 | 7.5 | 7.5 | 7.4 | 7.4 | 7.2 | 6.7 | 3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | STOWFIELD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7.6 | 7.6 | 7.6 | 7.6 | 7.5 | 7.5 | 7.5 | 7.3 | 7 | 7 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | Tewkesbury Grid 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 27.3 | 26.4 | 26.3 | 26.2 | 26 | 26 | 24.9 | 24.8 | 24.6 | 24.4 | 24.2 | 24.1 | 24 | 24 | 23.9 | 23.8 | 23.8 | 23 | 22.2
Port Ham 132kV | Tewkesbury Grid 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 27.3 | 26.3 | 25.9 | 25.4 | 25.1 | 24.8 | 24 | 23.4 | 22.6 | 21.9 | 21 | 20.7 | 20.4 | 20 | 19.7 | 19.4 | 19.2 | 17.5 | 15.7
Port Ham 132kV | Tewkesbury Grid 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 27.3 | 26.3 | 25.7 | 25.5 | 25.1 | 24.7 | 23.7 | 22.8 | 22 | 21.2 | 20.7 | 20.4 | 20.1 | 19.7 | 19.4 | 19.2 | 18.9 | 18.8 | 17
Port Ham 132kV | Tewkesbury Grid 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 27.3 | 26.3 | 26 | 25.6 | 25.4 | 25.1 | 24.2 | 23.9 | 23.6 | 23.1 | 22.5 | 22.2 | 21.9 | 21.7 | 21.5 | 21.3 | 21 | 19.5 | 18
Port Ham 132kV | TUFFLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | Headroom (MW) | 7 | 6.1 | 5.8 | 5.6 | 5.2 | 4.8 | 2.9 | 2.6 | 2.2 | 1.8 | 1.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | TUFFLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | Headroom (MW) | 7 | 5.9 | 5.5 | 4.8 | 4 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | TUFFLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | Headroom (MW) | 7 | 5.8 | 5.2 | 4.6 | 3.8 | 2.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Ham 132kV | TUFFLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | Headroom (MW) | 7 | 6 | 5.7 | 5.1 | 4.5 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugeley 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 57.3 | 57.3 | 57.2 | 57.1 | 57 | 56.9 | 56.7 | 56.6 | 56.4 | 56.3 | 56.1 | 55.9 | 55.8 | 55.7 | 55.6 | 55.6 | 55.5 | 55 | 53.3
Rugeley 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 57.3 | 57.3 | 57.2 | 56.8 | 56.3 | 55.8 | 56.2 | 55.7 | 54.8 | 54.6 | 52.9 | 52.2 | 51.8 | 51.3 | 50.9 | 50.4 | 49.9 | 46.7 | 43.5
Rugeley 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 57.3 | 57.3 | 57 | 56.4 | 55.8 | 55.3 | 55.6 | 54.6 | 52.8 | 52.2 | 51.5 | 51 | 50.6 | 50.1 | 49.7 | 49.3 | 48.8 | 45.3 | 42.3
Rugeley 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 57.3 | 57.3 | 57.2 | 57.1 | 56.9 | 56.5 | 56.5 | 56 | 55.7 | 55.4 | 54.7 | 53.3 | 53.2 | 53 | 52.9 | 52.8 | 52.7 | 51.2 | 49.3
Rugeley 132kV | Cannock 132/11kV | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 51.3 | 51.3 | 51.1 | 51 | 50.8 | 50.6 | 48.3 | 47.8 | 47.2 | 46.7 | 45.9 | 44.7 | 48.5 | 47.1 | 45.3 | 44.4 | 44.3 | 46.8 | 44.9
Rugeley 132kV | Cannock 132/11kV | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 51.3 | 51.2 | 50.9 | 50.4 | 49.9 | 49.1 | 45.9 | 44 | 41.7 | 40.8 | 37.2 | 33.1 | 36.5 | 34.3 | 32.3 | 31.5 | 30.7 | 30.1 | 25.6
Rugeley 132kV | Cannock 132/11kV | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 51.3 | 51.1 | 50.6 | 50 | 49.3 | 48.2 | 43.7 | 40.8 | 37 | 36 | 31.1 | 29 | 32.4 | 30.4 | 29.7 | 28.7 | 28 | 27.4 | 23.2
Rugeley 132kV | Cannock 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 51.3 | 51.2 | 51 | 50.8 | 50.4 | 49.8 | 46.8 | 45.3 | 43.2 | 42.5 | 39.4 | 36.1 | 39 | 37.4 | 35.8 | 35.5 | 35.1 | 35.8 | 32.2
Rugeley 132kV | Lichfield 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 56.6 | 56.3 | 55.7 | 55.1 | 54.6 | 53.2 | 49 | 48.4 | 47.7 | 47.1 | 46.3 | 45.8 | 45.4 | 45.2 | 44.9 | 44.7 | 44.2 | 40.9 | 37.3
Rugeley 132kV | Lichfield 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 56.6 | 55.8 | 54.6 | 52.2 | 49 | 44.3 | 44.5 | 40.5 | 37.9 | 35.4 | 32.8 | 30.6 | 28.4 | 26.2 | 25.1 | 23.5 | 21.9 | 14.6 | 6.6
Rugeley 132kV | Lichfield 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 56.6 | 55.6 | 53.4 | 50.6 | 47.8 | 44.4 | 44.7 | 41.9 | 39.2 | 37.1 | 35.2 | 33.1 | 31.2 | 29.7 | 28.6 | 27.2 | 25.7 | 18.7 | 14.2
Rugeley 132kV | Lichfield 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 56.6 | 56.1 | 55.1 | 53.4 | 51.7 | 48 | 46.3 | 45.1 | 43.4 | 41.3 | 39.2 | 37.7 | 36.3 | 34.8 | 34 | 33.1 | 32.1 | 26.3 | 20.1
Rugeley 132kV | RUGELEY TOWN 132 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 29.1 | 28.9 | 28.6 | 28.2 | 27.8 | 27.3 | 27.4 | 26.6 | 26.3 | 26 | 25.5 | 24.8 | 24 | 23.2 | 22.2 | 21.7 | 21.4 | 19.3 | 16.6
Rugeley 132kV | RUGELEY TOWN 132 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 29.1 | 28.4 | 27.7 | 26.4 | 24.8 | 23.2 | 25.1 | 23.5 | 21.7 | 20.5 | 17.9 | 15.3 | 13.5 | 11.7 | 10.4 | 9.1 | 8.2 | 2.7 | 0
Rugeley 132kV | RUGELEY TOWN 132 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 29.1 | 28.3 | 27.3 | 26.1 | 24.6 | 23.6 | 25.3 | 23.1 | 20.4 | 19 | 16.4 | 14.7 | 13 | 11.3 | 10.5 | 9.4 | 8.5 | 3.5 | 0
Rugeley 132kV | RUGELEY TOWN 132 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 29.1 | 28.7 | 28.2 | 27.7 | 26.7 | 25.5 | 26 | 25.4 | 23.9 | 22.8 | 20.5 | 18.4 | 16.9 | 15.8 | 14.9 | 14.3 | 13.8 | 9.7 | 5
Rugeley 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 56.5 | 56.3 | 56 | 55.5 | 55.1 | 54.5 | 53.5 | 53.1 | 52.6 | 52.2 | 51.6 | 51.2 | 50.9 | 50.4 | 50 | 48.5 | 46.3 | 43.5 | 40.9
Rugeley 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 56.5 | 56.1 | 55.4 | 54.2 | 52.5 | 50.5 | 50.9 | 48.7 | 46.8 | 45.2 | 43.7 | 42.1 | 37.7 | 33 | 32.1 | 30.9 | 29.8 | 23.5 | 18
Rugeley 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 56.5 | 56 | 55 | 53.7 | 52.4 | 50.5 | 51 | 48.6 | 46.8 | 45.3 | 42.7 | 36.3 | 34.8 | 33.3 | 32.3 | 31.3 | 30.2 | 24.2 | 20.9
Rugeley 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 56.5 | 56.3 | 55.6 | 54.8 | 53.6 | 51.8 | 51.8 | 50.7 | 49 | 47.7 | 46.4 | 45.5 | 43.2 | 38.6 | 37.2 | 36.7 | 36 | 31.5 | 26.9
Rugeley 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 53.1 | 53 | 52.8 | 52.6 | 52.3 | 52 | 50.4 | 50.1 | 49.8 | 49.4 | 49 | 48.6 | 48.3 | 48.2 | 48 | 47.8 | 50.2 | 49.3 | 47.3
Rugeley 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 53.1 | 52.7 | 52.3 | 51.6 | 50.8 | 49.9 | 48.9 | 48.1 | 47.3 | 46.4 | 45.4 | 44.4 | 43.3 | 42.2 | 41.4 | 40.6 | 43.1 | 38.2 | 33
Rugeley 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 53.1 | 52.5 | 51.9 | 51.3 | 50.6 | 49.7 | 48.8 | 47.7 | 46.6 | 45.5 | 44.4 | 43.4 | 42.4 | 41.4 | 40.7 | 39.9 | 42.5 | 37.8 | 34.2
Rugeley 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 53.1 | 52.9 | 52.6 | 52.3 | 51.8 | 51.2 | 49.7 | 49.3 | 48.9 | 48.3 | 47.5 | 47 | 46.4 | 46 | 45.7 | 45.4 | 48.5 | 45 | 40.7
Willenhall 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 62.3 | 62.3 | 62.2 | 62 | 61.9 | 61.8 | 60.6 | 60.5 | 60.4 | 60.1 | 59.7 | 59.3 | 59 | 58.6 | 58.4 | 58.3 | 58.2 | 57.7 | 56.8
Willenhall 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 62.3 | 62.3 | 62.2 | 62 | 61.9 | 61.3 | 59.9 | 58.6 | 57.1 | 56.6 | 55.5 | 52.2 | 51.9 | 51.5 | 51.1 | 50.7 | 50.2 | 47.6 | 45
Willenhall 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 62.3 | 62.3 | 62.2 | 61.9 | 61.1 | 60.4 | 58.1 | 56 | 52.4 | 51.8 | 50.9 | 50.4 | 50 | 49.5 | 49 | 48.6 | 48.1 | 45.1 | 42.1
Willenhall 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 62.3 | 62.3 | 62.2 | 62 | 61.9 | 61.8 | 60.6 | 59.3 | 58.1 | 57.6 | 56.3 | 55.6 | 55.4 | 52.4 | 52.4 | 52.3 | 52.2 | 50.8 | 48.9
Willenhall 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 57.9 | 57.9 | 57.8 | 57.7 | 57.6 | 57.6 | 56.8 | 56.7 | 56.7 | 56.6 | 56.5 | 56.3 | 56.2 | 56 | 56 | 55.9 | 55.8 | 55.3 | 54.7
Willenhall 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 57.9 | 57.9 | 57.8 | 57.5 | 57 | 56.5 | 56.5 | 56 | 55.2 | 54.9 | 53.2 | 52.6 | 52.3 | 51.8 | 51.4 | 51 | 50.6 | 47.7 | 44.5
Willenhall 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 57.9 | 57.9 | 57.6 | 57.1 | 56.6 | 56.1 | 55.9 | 54.8 | 53.1 | 52.7 | 52 | 51.6 | 51.2 | 50.8 | 50.4 | 50 | 49.6 | 46.4 | 43.4
Willenhall 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 57.9 | 57.9 | 57.8 | 57.7 | 57.6 | 57.1 | 56.7 | 56.4 | 56 | 55.7 | 55 | 54.7 | 53.3 | 53.2 | 53.2 | 53.1 | 53 | 51.7 | 50
Willenhall 132kV | Willenhall 132/25/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 28.1 | 28 | 27.9 | 27.7 | 27.6 | 27.5 | 27.9 | 27.8 | 27.8 | 27.7 | 27.7 | 27.6 | 27.6 | 27.5 | 27.5 | 27.5 | 27.5 | 27.4 | 26.7
Willenhall 132kV | Willenhall 132/25/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 28.1 | 27.9 | 27.5 | 27.4 | 27.3 | 26.6 | 27.7 | 27.5 | 27.4 | 26.7 | 26.3 | 26.1 | 25.8 | 25.4 | 25.2 | 25 | 24.7 | 23.3 | 22
Willenhall 132kV | Willenhall 132/25/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 28.1 | 27.8 | 27.3 | 26.7 | 26.5 | 26.2 | 27.4 | 26.4 | 25.9 | 25.5 | 25.1 | 24.6 | 24.4 | 24.1 | 23.9 | 23.7 | 23.4 | 21.8 | 20.1
Willenhall 132kV | Willenhall 132/25/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 28.1 | 28 | 27.7 | 27.6 | 27.4 | 27.4 | 27.8 | 27.6 | 27.5 | 27.4 | 27.3 | 26.7 | 26.5 | 26.1 | 26.1 | 26.1 | 25.2 | 24.4 | 23.4
Willenhall 132kV | Wolverhampton 132/33/11kV DUMMY | Bulk Supply Point | 11 | Counterfactual | Headroom (MW) | 17.3 | 17.2 | 17.2 | 17.2 | 17.1 | 17.1 | 0.8 | 1.4 | 2.1 | 2.3 | 2.5 | 2.7 | 2.7 | 2.8 | 2.8 | 3 | 2.9 | 8.8 | 7.2
Willenhall 132kV | Wolverhampton 132/33/11kV DUMMY | Bulk Supply Point | 11 | Electric Engagement | Headroom (MW) | 17.3 | 17.2 | 17.1 | 17.1 | 17 | 16.9 | 4.8 | 11.2 | 12.2 | 12.4 | 12.5 | 12.7 | 12.9 | 13.1 | 13.1 | 13.2 | 11.6 | 13.7 | 14.3
Willenhall 132kV | Wolverhampton 132/33/11kV DUMMY | Bulk Supply Point | 11 | Holistic Transition | Headroom (MW) | 17.3 | 17.2 | 17.1 | 17 | 16.9 | 16.8 | 4.4 | 10.9 | 11.9 | 12 | 12.3 | 12.4 | 12.7 | 12.9 | 12.9 | 12.9 | 11.2 | 13.3 | 13.5
Willenhall 132kV | Wolverhampton 132/33/11kV DUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | Headroom (MW) | 17.3 | 17.2 | 17.2 | 17.1 | 17 | 16.9 | 4.5 | 11 | 12 | 12.2 | 12.3 | 12.4 | 12.5 | 12.6 | 12.5 | 12.6 | 10.7 | 12.3 | 13
Willenhall 132kV | WOLVERHAMPTON 132kV S STN | Bulk Supply Point | 33 | Counterfactual | Headroom (MW) | 32.9 | 32.7 | 32.1 | 31.4 | 30.4 | 29.2 | 0.8 | 1.4 | 2.1 | 2.3 | 2.5 | 2.7 | 2.7 | 2.8 | 2.9 | 3 | 2.9 | 8.8 | 7.2
Willenhall 132kV | WOLVERHAMPTON 132kV S STN | Bulk Supply Point | 33 | Electric Engagement | Headroom (MW) | 32.9 | 32.1 | 30.5 | 27.9 | 24.7 | 20.7 | 4.8 | 11.2 | 12.2 | 12.4 | 12.5 | 12.7 | 12.9 | 13.1 | 13.1 | 13.2 | 11.6 | 13.7 | 14.4
Willenhall 132kV | WOLVERHAMPTON 132kV S STN | Bulk Supply Point | 33 | Holistic Transition | Headroom (MW) | 32.9 | 32.1 | 30.2 | 27.9 | 24.8 | 20.7 | 4.4 | 10.9 | 11.9 | 12 | 12.3 | 12.4 | 12.7 | 12.9 | 12.9 | 12.9 | 11.2 | 13.3 | 13.5
Willenhall 132kV | WOLVERHAMPTON 132kV S STN | Bulk Supply Point | 33 | Hydrogen Evolution | Headroom (MW) | 32.9 | 32.2 | 30.6 | 28.4 | 25.4 | 21.5 | 4.5 | 11 | 12 | 12.2 | 12.3 | 12.4 | 12.5 | 12.6 | 12.6 | 12.6 | 10.7 | 12.3 | 13

## Fault Level Contribution
[6 empty] | Break contribution (kA) | [17 empty] | Make contribution (kA)
Licence Area | Associated GSP | Substation | Supply Level | Voltage Level (kV) | Scenario | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050
West Midlands | Bishops Wood 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.21772 | 0.24041 | 0.26476 | 0.29366 | 0.32872 | 0.3702 | 0.4171 | 0.48766 | 0.54525 | 0.60356 | 0.6615 | 0.72311 | 0.79771 | 0.87168 | 0.94354 | 1.0178 | 1.3692 | 1.5322 | 0.52617 | 0.5747 | 0.62569 | 0.6858 | 0.75844 | 0.84435 | 0.9415 | 1.0862 | 1.205 | 1.3252 | 1.4441 | 1.5698 | 1.7219 | 1.8731 | 2.0202 | 2.1716 | 2.8898 | 3.229
West Midlands | Bishops Wood 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.23749 | 0.2945 | 0.35758 | 0.43122 | 0.51547 | 0.61669 | 0.73333 | 0.86697 | 0.99276 | 1.1032 | 1.2011 | 1.3007 | 1.3892 | 1.4523 | 1.4852 | 1.5152 | 1.679 | 1.7965 | 0.56894 | 0.69109 | 0.82371 | 0.97681 | 1.1518 | 1.361 | 1.6014 | 1.875 | 2.1332 | 2.3603 | 2.5625 | 2.768 | 2.955 | 3.0911 | 3.1624 | 3.2281 | 3.5904 | 3.855
West Midlands | Bishops Wood 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.2314 | 0.27335 | 0.31507 | 0.3654 | 0.4163 | 0.49446 | 0.57338 | 0.68279 | 0.77643 | 0.87813 | 0.99021 | 1.1026 | 1.2272 | 1.3399 | 1.4331 | 1.5126 | 1.7731 | 1.9259 | 0.55838 | 0.6532 | 0.74414 | 0.85215 | 0.96077 | 1.1251 | 1.2907 | 1.5176 | 1.7125 | 1.9232 | 2.1553 | 2.3889 | 2.6502 | 2.8873 | 3.0813 | 3.248 | 3.808 | 4.1466
West Midlands | Bishops Wood 132kV | BISHOPS CASTLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.22547 | 0.25664 | 0.29269 | 0.34218 | 0.39615 | 0.46144 | 0.54028 | 0.64649 | 0.74077 | 0.85389 | 0.96275 | 1.0657 | 1.1893 | 1.2914 | 1.3771 | 1.4466 | 1.6886 | 1.8261 | 0.5428 | 0.61031 | 0.68669 | 0.78954 | 0.90154 | 1.037 | 1.1998 | 1.417 | 1.6105 | 1.8413 | 2.0632 | 2.2742 | 2.5302 | 2.7426 | 2.9183 | 3.0618 | 3.5708 | 3.868
West Midlands | Bishops Wood 132kV | BODENHAM 66 11kV S STN | Primary Substation | 11 | Counterfactual | 1.6006 | 1.6295 | 1.6632 | 1.6947 | 1.73 | 1.7704 | 1.8166 | 1.8883 | 1.9473 | 2.0149 | 2.0796 | 2.1452 | 2.2147 | 2.2832 | 2.3515 | 2.4207 | 2.76 | 2.8991 | 3.9733 | 4.0342 | 4.1046 | 4.1701 | 4.2436 | 4.3277 | 4.4239 | 4.5714 | 4.6938 | 4.8348 | 4.9687 | 5.1033 | 5.2452 | 5.3849 | 5.5241 | 5.6652 | 6.3609 | 6.6549
West Midlands | Bishops Wood 132kV | BODENHAM 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.6226 | 1.6863 | 1.7721 | 1.863 | 1.9604 | 2.0669 | 2.1911 | 2.3472 | 2.4957 | 2.6262 | 2.7412 | 2.8534 | 2.9303 | 2.9719 | 2.9977 | 3.0225 | 3.2124 | 3.3222 | 4.021 | 4.1551 | 4.3393 | 4.5337 | 4.7404 | 4.9656 | 5.2256 | 5.5515 | 5.8639 | 6.1387 | 6.3815 | 6.6184 | 6.7861 | 6.8776 | 6.9344 | 6.9912 | 7.4452 | 7.7008
West Midlands | Bishops Wood 132kV | BODENHAM 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.6158 | 1.66 | 1.7177 | 1.774 | 1.8364 | 1.9064 | 1.9849 | 2.0955 | 2.1991 | 2.314 | 2.4319 | 2.6818 | 2.7799 | 2.8678 | 2.9525 | 3.0249 | 3.2289 | 3.3366 | 4.0094 | 4.1062 | 4.2332 | 4.3567 | 4.493 | 4.6434 | 4.8099 | 5.0412 | 5.2595 | 5.5 | 5.747 | 6.325 | 6.5287 | 6.7115 | 6.888 | 7.0398 | 7.4842 | 7.7326
West Midlands | Bishops Wood 132kV | BODENHAM 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.6091 | 1.6463 | 1.6912 | 1.734 | 1.7834 | 1.8428 | 1.9148 | 2.0194 | 2.1161 | 2.2289 | 2.34 | 2.4472 | 2.5435 | 2.6265 | 2.7057 | 2.7734 | 3.0161 | 3.1042 | 3.9915 | 4.0707 | 4.1652 | 4.2543 | 4.3574 | 4.4813 | 4.6307 | 4.8456 | 5.0458 | 5.2794 | 5.508 | 5.7285 | 5.9259 | 6.096 | 6.2584 | 6.3977 | 6.9438 | 7.1447
West Midlands | Bishops Wood 132kV | BROMYARD 66/11kV | Primary Substation | 11 | Counterfactual | 0.52082 | 0.5778 | 0.65934 | 0.74964 | 0.84422 | 0.95308 | 1.0943 | 1.2754 | 1.4402 | 1.6337 | 1.8205 | 1.986 | 2.1489 | 2.3053 | 2.4644 | 2.6297 | 3.4835 | 3.9781 | 1.2592 | 1.3793 | 1.5518 | 1.7425 | 1.9428 | 2.1743 | 2.4825 | 2.8669 | 3.2201 | 3.6385 | 4.0369 | 4.3846 | 4.7231 | 5.046 | 5.3768 | 5.7212 | 7.5095 | 8.5763
West Midlands | Bishops Wood 132kV | BROMYARD 66/11kV | Primary Substation | 11 | Electric Engagement | 0.56309 | 0.69086 | 0.89554 | 1.1302 | 1.3758 | 1.6888 | 2.0013 | 2.3839 | 2.7598 | 3.1224 | 3.4794 | 3.8032 | 4.0457 | 4.1909 | 4.3078 | 4.4213 | 5.0045 | 5.4632 | 1.3503 | 1.6214 | 2.068 | 2.5731 | 3.0986 | 3.7853 | 4.4502 | 5.2618 | 6.0636 | 6.8404 | 7.6111 | 8.3131 | 8.8509 | 9.1713 | 9.4303 | 9.6869 | 11.0205 | 12.1122
West Midlands | Bishops Wood 132kV | BROMYARD 66/11kV | Primary Substation | 11 | Holistic Transition | 0.54951 | 0.64212 | 0.769 | 0.92972 | 1.1176 | 1.3102 | 1.5427 | 1.8426 | 2.1532 | 2.4928 | 2.8757 | 3.1969 | 3.4772 | 3.6986 | 3.9133 | 4.104 | 4.7892 | 5.0866 | 1.3266 | 1.5319 | 1.809 | 2.1585 | 2.5763 | 2.9937 | 3.5005 | 4.1437 | 4.8183 | 5.5491 | 6.3817 | 7.0739 | 7.6777 | 8.1464 | 8.6016 | 9.009 | 10.5284 | 11.2068
West Midlands | Bishops Wood 132kV | BROMYARD 66/11kV | Primary Substation | 11 | Hydrogen Evolution | 0.53823 | 0.61466 | 0.73135 | 0.86093 | 1.0025 | 1.2236 | 1.4307 | 1.7083 | 1.982 | 2.3115 | 2.6314 | 2.9203 | 3.1787 | 3.3825 | 3.5761 | 3.7471 | 4.3224 | 4.7316 | 1.2962 | 1.4601 | 1.7106 | 1.9865 | 2.2899 | 2.78 | 3.222 | 3.8069 | 4.3879 | 5.0906 | 5.7649 | 6.3735 | 6.9193 | 7.3436 | 7.7463 | 8.1052 | 9.3803 | 10.3345
West Midlands | Bishops Wood 132kV | CLEOBURY MORTIMER 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.4758 | 0.50017 | 0.53045 | 0.56691 | 0.61136 | 0.66713 | 0.73217 | 0.82804 | 0.90796 | 0.9921 | 1.0701 | 1.1467 | 1.2305 | 1.3105 | 1.3884 | 1.4685 | 1.8914 | 2.1042 | 1.1573 | 1.2085 | 1.2723 | 1.3492 | 1.4429 | 1.561 | 1.6998 | 1.9022 | 2.0726 | 2.2536 | 2.419 | 2.5789 | 2.752 | 2.9168 | 3.0774 | 3.2422 | 4.1244 | 4.587
West Midlands | Bishops Wood 132kV | CLEOBURY MORTIMER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.49927 | 0.55968 | 0.66033 | 0.78215 | 0.91587 | 1.0655 | 1.2325 | 1.4304 | 1.6207 | 1.7857 | 1.9387 | 2.088 | 2.2092 | 2.2947 | 2.3474 | 2.4092 | 2.7269 | 2.988 | 1.2082 | 1.335 | 1.557 | 1.8237 | 2.1142 | 2.4382 | 2.7965 | 3.2199 | 3.6303 | 3.9862 | 4.3183 | 4.6428 | 4.9144 | 5.1051 | 5.2235 | 5.3653 | 6.096 | 6.7147
West Midlands | Bishops Wood 132kV | CLEOBURY MORTIMER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.49226 | 0.53231 | 0.59225 | 0.67321 | 0.75384 | 0.85872 | 0.97069 | 1.1198 | 1.2578 | 1.3981 | 1.5527 | 1.7044 | 1.8478 | 1.9761 | 2.0959 | 2.2028 | 2.5815 | 2.7756 | 1.1961 | 1.2844 | 1.4183 | 1.5983 | 1.7775 | 2.0062 | 2.2501 | 2.5698 | 2.8694 | 3.1696 | 3.5014 | 3.8277 | 4.1359 | 4.4069 | 4.6613 | 4.8899 | 5.7282 | 6.1694
West Midlands | Bishops Wood 132kV | CLEOBURY MORTIMER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.48481 | 0.51648 | 0.5581 | 0.61629 | 0.68133 | 0.76588 | 0.86561 | 0.99765 | 1.1179 | 1.2591 | 1.3926 | 1.5178 | 1.6398 | 1.7449 | 1.8483 | 1.9387 | 2.2634 | 2.489 | 1.1767 | 1.2437 | 1.3317 | 1.455 | 1.5935 | 1.7744 | 1.9867 | 2.264 | 2.5182 | 2.8171 | 3.0963 | 3.3585 | 3.6128 | 3.8306 | 4.0454 | 4.2351 | 4.9453 | 5.4619
West Midlands | Bishops Wood 132kV | CRAVEN ARMS 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.66791 | 0.70859 | 0.7538 | 0.80453 | 0.86577 | 0.94361 | 1.0565 | 1.1808 | 1.2807 | 1.388 | 1.5007 | 1.6332 | 1.7767 | 1.9155 | 2.0621 | 2.197 | 2.817 | 3.1438 | 1.6369 | 1.7234 | 1.8184 | 1.9232 | 2.0493 | 2.2124 | 2.4587 | 2.7121 | 2.9169 | 3.1366 | 3.3675 | 3.6394 | 3.9325 | 4.2169 | 4.5222 | 4.7972 | 6.0597 | 6.7314
West Midlands | Bishops Wood 132kV | CRAVEN ARMS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.70366 | 0.80513 | 0.92885 | 1.0653 | 1.2193 | 1.5092 | 1.7298 | 1.9975 | 2.242 | 2.4566 | 2.6563 | 2.9202 | 3.0405 | 3.1188 | 3.1907 | 3.2784 | 3.5316 | 3.7226 | 1.7141 | 1.9307 | 2.1944 | 2.4792 | 2.8 | 3.4446 | 3.9012 | 4.4533 | 4.9587 | 5.4022 | 5.8169 | 6.3861 | 6.6383 | 6.8063 | 6.9624 | 7.1483 | 7.7135 | 8.1442
West Midlands | Bishops Wood 132kV | CRAVEN ARMS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.69225 | 0.76457 | 0.85054 | 0.94157 | 1.0785 | 1.26 | 1.4295 | 1.6429 | 1.828 | 2.1064 | 2.329 | 2.5291 | 2.7024 | 2.8611 | 3.0345 | 3.2046 | 3.3676 | 3.6062 | 1.6942 | 1.8567 | 2.047 | 2.2425 | 2.5506 | 2.9443 | 3.3014 | 3.7448 | 4.1305 | 4.7406 | 5.2044 | 5.6194 | 5.9775 | 6.3072 | 6.6695 | 7.0216 | 7.2835 | 7.8145
West Midlands | Bishops Wood 132kV | CRAVEN ARMS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.6822 | 0.74014 | 0.81277 | 0.89865 | 0.9924 | 1.2199 | 1.3743 | 1.5886 | 1.7734 | 1.9873 | 2.2077 | 2.4638 | 2.6403 | 2.7884 | 2.954 | 3.1132 | 3.4884 | 3.6887 | 1.6674 | 1.7932 | 1.9492 | 2.1271 | 2.3207 | 2.8356 | 3.155 | 3.5955 | 3.9756 | 4.413 | 4.8649 | 5.4118 | 5.7709 | 6.0744 | 6.4156 | 6.7409 | 7.5285 | 7.9605
West Midlands | Bishops Wood 132kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Counterfactual | 5.3464 | 5.495 | 5.6875 | 5.9109 | 6.1988 | 6.5156 | 6.8606 | 7.3721 | 7.7663 | 8.1977 | 8.6446 | 9.0779 | 9.5494 | 10.0103 | 10.4071 | 10.7823 | 12.525 | 13.2545 | 13.2166 | 13.5274 | 13.9289 | 14.3944 | 14.9954 | 15.6586 | 16.3836 | 17.457 | 18.2843 | 19.1973 | 20.1417 | 21.0497 | 22.0308 | 22.9871 | 23.802 | 24.5703 | 28.1661 | 29.7396
West Midlands | Bishops Wood 132kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 5.4867 | 5.8506 | 6.2989 | 6.9008 | 7.6082 | 8.2295 | 9.0376 | 9.9578 | 10.7215 | 11.3928 | 12.0427 | 12.6355 | 13.066 | 13.3198 | 13.5048 | 13.6768 | 14.3844 | 15.0603 | 13.5226 | 14.2886 | 15.2356 | 16.5084 | 18.0478 | 19.3569 | 21.0857 | 23.0278 | 24.6238 | 26.05 | 27.4383 | 28.6932 | 29.6227 | 30.1778 | 30.5934 | 30.983 | 32.5852 | 34.1197
West Midlands | Bishops Wood 132kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 5.4509 | 5.7075 | 6.0727 | 6.517 | 6.9052 | 7.4489 | 8.0288 | 8.7146 | 9.2768 | 9.9055 | 10.5639 | 11.1481 | 11.6939 | 12.2077 | 12.6891 | 13.1178 | 14.352 | 15.0489 | 13.461 | 14.0208 | 14.8048 | 15.7622 | 16.5967 | 17.8005 | 19.0697 | 20.5365 | 21.7328 | 23.0682 | 24.4613 | 25.6785 | 26.817 | 27.8911 | 28.8988 | 29.8006 | 32.4723 | 34.0432
West Midlands | Bishops Wood 132kV | DROITWICH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 5.393 | 5.5851 | 5.8473 | 6.2051 | 6.7316 | 7.183 | 7.7895 | 8.4898 | 9.0594 | 9.71 | 10.3615 | 10.9761 | 11.5631 | 12.0565 | 12.4924 | 12.8728 | 15.5076 | 16.207 | 13.3177 | 13.7247 | 14.2778 | 15.0364 | 16.2045 | 17.1686 | 18.4857 | 19.9747 | 21.1731 | 22.5552 | 23.9266 | 25.2123 | 26.436 | 27.4577 | 28.3581 | 29.1472 | 35.3824 | 36.977
West Midlands | Bishops Wood 132kV | DYMOCK 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.69744 | 0.71819 | 0.74146 | 0.77045 | 0.80393 | 0.84126 | 0.88318 | 0.95094 | 1.0045 | 1.0613 | 1.1204 | 1.1851 | 1.257 | 1.3269 | 1.3954 | 1.4653 | 1.8496 | 2.0624 | 1.714 | 1.7577 | 1.8063 | 1.8668 | 1.9365 | 2.0142 | 2.1015 | 2.2411 | 2.3521 | 2.4703 | 2.5924 | 2.7253 | 2.8722 | 3.0149 | 3.1548 | 3.2974 | 4.0842 | 4.5257
West Midlands | Bishops Wood 132kV | DYMOCK 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.71638 | 0.76535 | 0.84983 | 0.95715 | 1.0704 | 1.1958 | 1.3367 | 1.5135 | 1.6863 | 1.84 | 1.9822 | 2.1218 | 2.234 | 2.3033 | 2.3461 | 2.4041 | 2.6175 | 2.7783 | 1.755 | 1.8585 | 2.0453 | 2.2805 | 2.5268 | 2.7971 | 3.0963 | 3.4717 | 3.841 | 4.1662 | 4.4671 | 4.7643 | 5.0116 | 5.1662 | 5.2593 | 5.3891 | 5.882 | 6.2613
West Midlands | Bishops Wood 132kV | DYMOCK 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.71005 | 0.74392 | 0.80238 | 0.87659 | 0.9559 | 1.044 | 1.1354 | 1.2596 | 1.3771 | 1.504 | 1.6424 | 1.7769 | 1.8967 | 1.9953 | 2.0911 | 2.1834 | 2.4405 | 2.5782 | 1.7438 | 1.8191 | 1.9519 | 2.1172 | 2.2937 | 2.4843 | 2.6779 | 2.9379 | 3.1853 | 3.4484 | 3.7374 | 4.019 | 4.2709 | 4.4784 | 4.6801 | 4.8748 | 5.4417 | 5.7574
West Midlands | Bishops Wood 132kV | DYMOCK 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.70546 | 0.73143 | 0.76575 | 0.81453 | 0.86914 | 0.93776 | 1.0219 | 1.1379 | 1.2462 | 1.3727 | 1.5008 | 1.6233 | 1.7328 | 1.8203 | 1.9054 | 1.9806 | 2.1771 | 2.2882 | 1.731 | 1.7864 | 1.8583 | 1.9599 | 2.074 | 2.2166 | 2.3906 | 2.6287 | 2.8513 | 3.1106 | 3.3725 | 3.6236 | 3.8483 | 4.0278 | 4.2029 | 4.3582 | 4.7806 | 5.0297
West Midlands | Bishops Wood 132kV | KENSWICK 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.65778 | 0.68812 | 0.73189 | 0.78514 | 0.84626 | 0.92234 | 1.0153 | 1.1505 | 1.2652 | 1.3943 | 1.5055 | 1.6063 | 1.7108 | 1.8127 | 1.9134 | 2.0151 | 2.384 | 2.6998 | 1.6052 | 1.6691 | 1.7633 | 1.8783 | 2.0108 | 2.1774 | 2.3836 | 2.6799 | 2.9345 | 3.2251 | 3.4707 | 3.688 | 3.9096 | 4.1244 | 4.3366 | 4.551 | 5.2798 | 5.9958
West Midlands | Bishops Wood 132kV | KENSWICK 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.68463 | 0.75749 | 0.88126 | 1.0253 | 1.1831 | 1.355 | 1.5568 | 1.7973 | 2.0255 | 2.2404 | 2.4571 | 2.6584 | 2.8173 | 2.9111 | 2.9881 | 3.0627 | 3.1066 | 3.4932 | 1.6634 | 1.8171 | 2.0913 | 2.4075 | 2.7519 | 3.1295 | 3.5706 | 4.0921 | 4.5891 | 5.0624 | 5.5464 | 5.9947 | 6.3575 | 6.5726 | 6.7531 | 6.9299 | 7.0001 | 7.9372
West Midlands | Bishops Wood 132kV | KENSWICK 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.67664 | 0.72409 | 0.78051 | 0.87089 | 0.95567 | 1.079 | 1.241 | 1.4493 | 1.6506 | 1.8518 | 2.069 | 2.206 | 2.3498 | 2.4822 | 2.6068 | 2.7182 | 2.9911 | 3.2014 | 1.6497 | 1.7546 | 1.8756 | 2.0754 | 2.2624 | 2.5383 | 2.9041 | 3.365 | 3.8152 | 4.259 | 4.7398 | 5.0233 | 5.3273 | 5.6089 | 5.8744 | 6.1134 | 6.7026 | 7.192
West Midlands | Bishops Wood 132kV | KENSWICK 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.66785 | 0.70535 | 0.76047 | 0.83796 | 0.92634 | 1.044 | 1.1829 | 1.3644 | 1.5336 | 1.7332 | 1.9182 | 2.0931 | 2.252 | 2.3821 | 2.5054 | 2.6177 | 2.8563 | 3.2265 | 1.6268 | 1.7065 | 1.8257 | 1.9946 | 2.1896 | 2.4515 | 2.7594 | 3.1548 | 3.525 | 3.9648 | 4.3648 | 4.7421 | 5.0833 | 5.3591 | 5.6216 | 5.8629 | 6.3768 | 7.2655
West Midlands | Bishops Wood 132kV | Kidderminster 132/33/11kV | Bulk Supply Point | 11 | Counterfactual | 1.2724 | 1.5299 | 1.9249 | 2.2798 | 2.6828 | 3.1463 | 3.6914 | 4.5492 | 5.3122 | 6.0744 | 6.7707 | 7.4883 | 8.2843 | 9.07 | 9.827 | 10.5783 | 13.9135 | 14.9511 | 2.9027 | 3.4418 | 4.2555 | 4.9921 | 5.8278 | 6.79 | 7.9227 | 9.6983 | 11.286 | 12.8762 | 14.3228 | 15.805 | 17.4408 | 19.0523 | 20.6002 | 22.1342 | 28.9671 | 31.1862
West Midlands | Bishops Wood 132kV | Kidderminster 132/33/11kV | Bulk Supply Point | 11 | Electric Engagement | 1.5137 | 2.2368 | 3.0192 | 3.8689 | 4.8964 | 6.0043 | 7.3954 | 9.0075 | 10.371 | 11.5062 | 12.5357 | 13.5115 | 14.1617 | 14.5594 | 14.8294 | 15.0709 | 16.1834 | 17.1965 | 3.4279 | 4.9365 | 6.5737 | 8.3443 | 10.4879 | 12.7994 | 15.7216 | 19.066 | 21.8787 | 24.2441 | 26.4039 | 28.4382 | 29.8201 | 30.6839 | 31.291 | 31.8389 | 34.3994 | 36.7357
West Midlands | Bishops Wood 132kV | Kidderminster 132/33/11kV | Bulk Supply Point | 11 | Holistic Transition | 1.4413 | 1.95 | 2.4182 | 3.0036 | 3.6772 | 4.5105 | 5.4352 | 6.6215 | 7.6075 | 8.643 | 9.7256 | 10.7865 | 11.8325 | 12.7932 | 13.6961 | 14.4926 | 16.7136 | 17.7718 | 3.3034 | 4.401 | 5.4032 | 6.6589 | 8.1014 | 9.9132 | 11.8964 | 14.3906 | 16.458 | 18.6277 | 20.8876 | 23.1038 | 25.2894 | 27.2908 | 29.1764 | 30.8462 | 35.6871 | 38.1038
West Midlands | Bishops Wood 132kV | Kidderminster 132/33/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | 1.3631 | 1.7967 | 2.2515 | 2.7784 | 3.4039 | 4.0928 | 4.9935 | 6.1692 | 7.111 | 8.1252 | 9.1691 | 10.1783 | 11.1627 | 12.0667 | 12.9169 | 13.6569 | 15.5151 | 16.4206 | 3.0997 | 4.0075 | 4.963 | 6.0705 | 7.3888 | 8.8402 | 10.7565 | 13.2146 | 15.1661 | 17.2712 | 19.4286 | 21.5066 | 23.5322 | 25.3907 | 27.1412 | 28.6689 | 32.6586 | 34.705
West Midlands | Bishops Wood 132kV | KINGTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | 1.1078 | 1.1528 | 1.2008 | 1.2547 | 1.3195 | 1.3994 | 1.4924 | 1.6324 | 1.7531 | 1.8802 | 2.0004 | 2.1212 | 2.2523 | 2.379 | 2.5032 | 2.6326 | 3.3053 | 3.6603 | 2.7388 | 2.8365 | 2.9383 | 3.0525 | 3.1897 | 3.3587 | 3.5565 | 3.8502 | 4.1067 | 4.3781 | 4.6317 | 4.8831 | 5.1531 | 5.4143 | 5.6705 | 5.9372 | 7.3335 | 8.0918
West Midlands | Bishops Wood 132kV | KINGTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.1397 | 1.2409 | 1.3753 | 1.5406 | 1.7143 | 1.9277 | 2.1861 | 2.499 | 2.8043 | 3.0767 | 3.3314 | 3.5733 | 3.7536 | 3.8713 | 3.966 | 4.062 | 4.5643 | 4.8817 | 2.8091 | 3.0273 | 3.3164 | 3.6712 | 4.0433 | 4.4962 | 5.0411 | 5.6987 | 6.3444 | 6.9194 | 7.4578 | 7.9701 | 8.3624 | 8.6198 | 8.8254 | 9.0378 | 10.1545 | 10.8988
West Midlands | Bishops Wood 132kV | KINGTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.1334 | 1.213 | 1.303 | 1.4152 | 1.5399 | 1.7068 | 1.889 | 2.133 | 2.3635 | 2.6167 | 2.8691 | 3.1062 | 3.3264 | 3.5133 | 3.698 | 3.8599 | 4.439 | 4.7335 | 2.7995 | 2.9801 | 3.1809 | 3.4307 | 3.708 | 4.0681 | 4.4577 | 4.9747 | 5.4651 | 6.0018 | 6.5316 | 7.031 | 7.4961 | 7.8893 | 8.2781 | 8.6213 | 9.883 | 10.5523
West Midlands | Bishops Wood 132kV | KINGTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.12 | 1.1767 | 1.2392 | 1.3221 | 1.4185 | 1.5407 | 1.6913 | 1.8982 | 2.1053 | 2.3365 | 2.5608 | 2.7675 | 2.9623 | 3.1146 | 3.2683 | 3.4228 | 3.82 | 4.1056 | 2.7654 | 2.8879 | 3.0199 | 3.1939 | 3.3972 | 3.6533 | 3.968 | 4.3961 | 4.8274 | 5.3104 | 5.7752 | 6.2036 | 6.6062 | 6.9205 | 7.2374 | 7.5702 | 8.4294 | 9.0659
West Midlands | Bishops Wood 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.9022 | 0.93863 | 0.97783 | 1.0243 | 1.0787 | 1.1456 | 1.228 | 1.3489 | 1.4507 | 1.5712 | 1.6819 | 1.7857 | 1.892 | 1.9925 | 2.0912 | 2.1895 | 2.6867 | 2.9343 | 2.2099 | 2.2876 | 2.3722 | 2.4729 | 2.5909 | 2.7376 | 2.9204 | 3.1848 | 3.4106 | 3.6806 | 3.9239 | 4.147 | 4.3718 | 4.583 | 4.7908 | 4.9973 | 6.0594 | 6.6256
West Midlands | Bishops Wood 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.92961 | 1.0133 | 1.1297 | 1.2619 | 1.4057 | 1.5874 | 1.7903 | 2.0298 | 2.2389 | 2.4247 | 2.607 | 2.7812 | 2.9124 | 2.9845 | 3.04 | 3.0941 | 3.3989 | 3.7461 | 2.2695 | 2.4486 | 2.706 | 2.9957 | 3.3089 | 3.7066 | 4.1487 | 4.6663 | 5.1193 | 5.5265 | 5.9322 | 6.3174 | 6.6163 | 6.7818 | 6.9134 | 7.0424 | 7.7749 | 8.6168
West Midlands | Bishops Wood 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.92123 | 0.98868 | 1.0412 | 1.1212 | 1.2511 | 1.364 | 1.5039 | 1.679 | 1.8345 | 1.9936 | 2.17 | 2.3497 | 2.5226 | 2.6592 | 2.7903 | 2.9087 | 3.0524 | 3.2383 | 2.2551 | 2.4056 | 2.5189 | 2.6966 | 2.9822 | 3.2338 | 3.5485 | 3.9341 | 4.2786 | 4.6276 | 5.0159 | 5.4104 | 5.79 | 6.0832 | 6.3655 | 6.6223 | 6.8946 | 7.332
West Midlands | Bishops Wood 132kV | KINVER 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.91275 | 0.96585 | 1.0293 | 1.097 | 1.1927 | 1.3066 | 1.4338 | 1.5979 | 1.738 | 1.8996 | 2.0492 | 2.1916 | 2.3261 | 2.4372 | 2.5427 | 2.6362 | 2.9825 | 3.283 | 2.2326 | 2.3474 | 2.4847 | 2.6325 | 2.8433 | 3.0964 | 3.3779 | 3.7347 | 4.0406 | 4.3951 | 4.7172 | 5.0227 | 5.31 | 5.5437 | 5.7662 | 5.965 | 6.7576 | 7.4801
West Midlands | Bishops Wood 132kV | KNIGHTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.56399 | 0.60559 | 0.6463 | 0.6939 | 0.75342 | 0.82611 | 0.91587 | 1.0394 | 1.1448 | 1.2651 | 1.3735 | 1.475 | 1.5832 | 1.6886 | 1.7977 | 1.9055 | 2.4365 | 2.7225 | 1.3681 | 1.4616 | 1.5507 | 1.655 | 1.7858 | 1.9452 | 2.1446 | 2.4142 | 2.6471 | 2.9157 | 3.1532 | 3.3705 | 3.598 | 3.8204 | 4.052 | 4.2787 | 5.4127 | 6.0551
West Midlands | Bishops Wood 132kV | KNIGHTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.58936 | 0.6919 | 0.81556 | 0.96653 | 1.1219 | 1.3124 | 1.5203 | 1.7533 | 1.9754 | 2.1782 | 2.3746 | 2.582 | 2.7479 | 2.8595 | 2.9674 | 3.0481 | 3.5116 | 3.9087 | 1.4232 | 1.6536 | 1.9309 | 2.268 | 2.6099 | 3.0293 | 3.483 | 3.9874 | 4.4706 | 4.9144 | 5.3496 | 5.8102 | 6.1842 | 6.4363 | 6.6761 | 6.862 | 7.927 | 8.8891
West Midlands | Bishops Wood 132kV | KNIGHTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.58163 | 0.67401 | 0.74832 | 0.845 | 0.94479 | 1.0905 | 1.2469 | 1.4411 | 1.6083 | 1.8009 | 1.9947 | 2.188 | 2.3792 | 2.5417 | 2.7202 | 2.8515 | 3.4515 | 3.7227 | 1.4099 | 1.6279 | 1.7968 | 2.0153 | 2.2401 | 2.5631 | 2.9134 | 3.3405 | 3.7097 | 4.1368 | 4.5611 | 4.9858 | 5.4062 | 5.7595 | 6.1421 | 6.4294 | 7.7902 | 8.4177
West Midlands | Bishops Wood 132kV | KNIGHTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.57363 | 0.62897 | 0.68462 | 0.77024 | 0.8624 | 0.98555 | 1.1238 | 1.2994 | 1.4539 | 1.643 | 1.8148 | 1.9857 | 2.1527 | 2.287 | 2.4298 | 2.534 | 3.0089 | 3.3916 | 1.3888 | 1.5142 | 1.6362 | 1.8251 | 2.0275 | 2.3003 | 2.6032 | 2.9819 | 3.3162 | 3.7246 | 4.0913 | 4.4609 | 4.8162 | 5.1014 | 5.401 | 5.6224 | 6.6745 | 7.5702
West Midlands | Bishops Wood 132kV | LEDBURY 66/11kV | Primary Substation | 11 | Counterfactual | 0.60727 | 0.7015 | 0.83019 | 0.98195 | 1.149 | 1.3064 | 1.5138 | 1.7436 | 1.9129 | 2.0937 | 2.2738 | 2.4615 | 2.6657 | 2.8663 | 3.0753 | 3.2941 | 4.3388 | 4.8215 | 1.4391 | 1.6383 | 1.9109 | 2.2275 | 2.5781 | 2.908 | 3.3602 | 3.8363 | 4.1891 | 4.5671 | 4.9406 | 5.3264 | 5.7438 | 6.1532 | 6.5845 | 7.0392 | 9.1877 | 10.2052
West Midlands | Bishops Wood 132kV | LEDBURY 66/11kV | Primary Substation | 11 | Electric Engagement | 0.66979 | 0.87366 | 1.1558 | 1.4725 | 1.8172 | 2.3089 | 2.6983 | 3.1576 | 3.562 | 3.923 | 4.2587 | 4.5935 | 4.8242 | 4.9446 | 5.0329 | 5.1079 | 5.4761 | 5.814 | 1.5745 | 2.0086 | 2.6176 | 3.2875 | 4.0176 | 5.1111 | 5.9222 | 6.8719 | 7.7081 | 8.4571 | 9.158 | 9.8642 | 10.3613 | 10.6213 | 10.8168 | 10.9861 | 11.8371 | 12.6231
West Midlands | Bishops Wood 132kV | LEDBURY 66/11kV | Primary Substation | 11 | Holistic Transition | 0.65209 | 0.8029 | 1.0246 | 1.2478 | 1.5827 | 1.8282 | 2.1092 | 2.4666 | 2.78 | 3.1335 | 3.5519 | 3.895 | 4.2091 | 4.4731 | 4.7236 | 4.9398 | 5.5752 | 5.8859 | 1.5451 | 1.8793 | 2.3733 | 2.8528 | 3.607 | 4.1317 | 4.7301 | 5.4793 | 6.1385 | 6.8824 | 7.7812 | 8.499 | 9.1565 | 9.7066 | 10.2294 | 10.6837 | 12.0749 | 12.7852
West Midlands | Bishops Wood 132kV | LEDBURY 66/11kV | Primary Substation | 11 | Hydrogen Evolution | 0.63123 | 0.75873 | 0.95153 | 1.1654 | 1.4031 | 1.7893 | 2.0534 | 2.3977 | 2.6935 | 3.0278 | 3.366 | 3.698 | 4.0158 | 4.2695 | 4.5036 | 4.7029 | 5.234 | 5.533 | 1.4905 | 1.7654 | 2.186 | 2.641 | 3.1503 | 4.0269 | 4.5809 | 5.2937 | 5.9062 | 6.5969 | 7.292 | 7.9782 | 8.6418 | 9.1646 | 9.6454 | 10.0571 | 11.2044 | 11.8868
West Midlands | Bishops Wood 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.46255 | 0.49988 | 0.54218 | 0.59183 | 0.65477 | 0.72879 | 0.81357 | 0.9398 | 1.0378 | 1.1357 | 1.2326 | 1.334 | 1.4487 | 1.5592 | 1.6665 | 1.7765 | 2.3326 | 2.5684 | 1.1141 | 1.1928 | 1.2808 | 1.3835 | 1.5136 | 1.6667 | 1.8426 | 2.1012 | 2.303 | 2.504 | 2.7023 | 2.9086 | 3.1414 | 3.3655 | 3.5831 | 3.8059 | 4.9387 | 5.4311
West Midlands | Bishops Wood 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.49829 | 0.59261 | 0.71022 | 0.85705 | 1.0242 | 1.207 | 1.4112 | 1.6513 | 1.8763 | 2.0661 | 2.2322 | 2.3942 | 2.5068 | 2.5764 | 2.6219 | 2.6692 | 2.9116 | 3.1085 | 1.1915 | 1.3904 | 1.6399 | 1.9498 | 2.3014 | 2.6856 | 3.1091 | 3.6043 | 4.071 | 4.4643 | 4.8088 | 5.1448 | 5.3843 | 5.5357 | 5.6355 | 5.7419 | 6.2895 | 6.7383
West Midlands | Bishops Wood 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.48736 | 0.55114 | 0.63621 | 0.73837 | 0.8379 | 0.96287 | 1.0922 | 1.2746 | 1.4328 | 1.6016 | 1.7863 | 1.9656 | 2.1355 | 2.2882 | 2.44 | 2.5723 | 2.9757 | 3.2062 | 1.1727 | 1.314 | 1.5006 | 1.7219 | 1.9383 | 2.2033 | 2.4746 | 2.8529 | 3.1824 | 3.5317 | 3.9143 | 4.2858 | 4.6383 | 4.9556 | 5.2714 | 5.5488 | 6.4207 | 6.9388
West Midlands | Bishops Wood 132kV | LEEBOTWOOD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.47598 | 0.52646 | 0.5869 | 0.66985 | 0.76024 | 0.87464 | 1.0065 | 1.1772 | 1.3293 | 1.5027 | 1.6754 | 1.8379 | 1.9984 | 2.1339 | 2.2714 | 2.388 | 2.7331 | 2.9218 | 1.143 | 1.2507 | 1.3777 | 1.5504 | 1.7383 | 1.9785 | 2.2515 | 2.5999 | 2.9119 | 3.2656 | 3.6172 | 3.9486 | 4.276 | 4.553 | 4.8347 | 5.0749 | 5.8034 | 6.2152
West Midlands | Bishops Wood 132kV | LEOMINSTER 66 11kV S STN | Primary Substation | 11 | Counterfactual | 1.2097 | 1.3007 | 1.4062 | 1.5303 | 1.6726 | 1.828 | 2.0012 | 2.2505 | 2.4507 | 2.6317 | 2.8214 | 3.0265 | 3.2537 | 3.4777 | 3.7128 | 3.9604 | 5.0708 | 5.5323 | 2.9562 | 3.148 | 3.3675 | 3.6247 | 3.92 | 4.2421 | 4.6066 | 5.1161 | 5.5277 | 5.897 | 6.2837 | 6.7012 | 7.1621 | 7.6164 | 8.0998 | 8.6124 | 10.8768 | 11.8335
West Midlands | Bishops Wood 132kV | LEOMINSTER 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.2818 | 1.4861 | 1.752 | 2.0728 | 2.4453 | 2.8977 | 3.324 | 3.8205 | 4.2757 | 4.6605 | 5.0074 | 5.3783 | 5.6501 | 5.7897 | 5.8709 | 5.9541 | 6.3343 | 6.6597 | 3.1121 | 3.5433 | 4.1094 | 4.792 | 5.5831 | 6.56 | 7.4485 | 8.4765 | 9.4245 | 10.2233 | 10.9441 | 11.7313 | 12.3264 | 12.632 | 12.8095 | 12.9994 | 13.8808 | 14.6325
West Midlands | Bishops Wood 132kV | LEOMINSTER 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.259 | 1.4013 | 1.5924 | 1.8234 | 2.1075 | 2.3872 | 2.6602 | 3.005 | 3.3152 | 3.671 | 4.1062 | 4.4558 | 4.7804 | 5.0684 | 5.3416 | 5.5788 | 6.2502 | 6.6071 | 3.0726 | 3.3865 | 3.808 | 4.3111 | 4.9373 | 5.5368 | 6.1107 | 6.8233 | 7.4669 | 8.2092 | 9.1402 | 9.8644 | 10.5374 | 11.1358 | 11.7045 | 12.2011 | 13.6617 | 14.4811
West Midlands | Bishops Wood 132kV | LEOMINSTER 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.2378 | 1.3539 | 1.4974 | 1.6928 | 1.9148 | 2.2156 | 2.4743 | 2.8079 | 3.1072 | 3.4422 | 3.7923 | 4.1476 | 4.5045 | 4.7878 | 5.0447 | 5.263 | 5.7884 | 6.022 | 3.0164 | 3.2634 | 3.5639 | 3.9742 | 4.4412 | 5.093 | 5.6271 | 6.3055 | 6.9163 | 7.5977 | 8.3097 | 9.0405 | 9.7867 | 10.369 | 10.8932 | 11.3403 | 12.4494 | 12.9642
West Midlands | Bishops Wood 132kV | LOWER CHADNOR 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.26667 | 0.28466 | 0.30498 | 0.32831 | 0.35576 | 0.38735 | 0.42428 | 0.48369 | 0.53619 | 0.58945 | 0.63689 | 0.68986 | 0.74789 | 0.80527 | 0.86214 | 0.91952 | 1.2299 | 1.3874 | 0.64793 | 0.68552 | 0.72751 | 0.77559 | 0.83208 | 0.89701 | 0.97287 | 1.0938 | 1.2016 | 1.3108 | 1.4072 | 1.5147 | 1.6322 | 1.7483 | 1.8634 | 1.9795 | 2.6088 | 2.9312
West Midlands | Bishops Wood 132kV | LOWER CHADNOR 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.28447 | 0.32873 | 0.37973 | 0.44333 | 0.51262 | 0.59762 | 0.70341 | 0.83313 | 0.95539 | 1.0641 | 1.1621 | 1.2544 | 1.3132 | 1.3457 | 1.3694 | 1.3871 | 1.4642 | 1.534 | 0.6864 | 0.77899 | 0.88424 | 1.0151 | 1.1572 | 1.3318 | 1.5486 | 1.8132 | 2.0631 | 2.2847 | 2.4847 | 2.6732 | 2.7944 | 2.8626 | 2.9131 | 2.9516 | 3.1258 | 3.2817
West Midlands | Bishops Wood 132kV | LOWER CHADNOR 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.27876 | 0.30745 | 0.33969 | 0.38012 | 0.42448 | 0.48526 | 0.55966 | 0.65995 | 0.75545 | 0.85838 | 0.96328 | 1.063 | 1.1514 | 1.2256 | 1.2957 | 1.3544 | 1.513 | 1.5942 | 0.67643 | 0.73937 | 0.80812 | 0.89354 | 0.98693 | 1.1142 | 1.2692 | 1.4757 | 1.673 | 1.884 | 2.0985 | 2.3029 | 2.4843 | 2.6371 | 2.7816 | 2.9034 | 3.2442 | 3.4275
West Midlands | Bishops Wood 132kV | LOWER CHADNOR 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.27381 | 0.29727 | 0.32632 | 0.3637 | 0.40603 | 0.4635 | 0.53619 | 0.63646 | 0.73084 | 0.83367 | 0.93759 | 1.0371 | 1.1249 | 1.1967 | 1.2646 | 1.3206 | 1.4538 | 1.5146 | 0.66317 | 0.7126 | 0.77284 | 0.84988 | 0.93699 | 1.0556 | 1.2051 | 1.4097 | 1.6029 | 1.8116 | 2.0222 | 2.2242 | 2.4025 | 2.5486 | 2.6868 | 2.8013 | 3.0815 | 3.215
West Midlands | Bishops Wood 132kV | Ludlow 132/66/33/11kV | Bulk Supply Point | 11 | Counterfactual | 1.2458 | 1.3338 | 1.4353 | 1.5544 | 1.6854 | 1.8388 | 2.0303 | 2.2799 | 2.4775 | 2.6806 | 2.8768 | 3.0759 | 3.2974 | 3.5156 | 3.7399 | 3.9517 | 5.0063 | 5.4455 | 3.0123 | 3.1982 | 3.4098 | 3.6574 | 3.9306 | 4.2512 | 4.6592 | 5.177 | 5.5899 | 6.0155 | 6.4232 | 6.8328 | 7.2856 | 7.7328 | 8.198 | 8.6301 | 10.8006 | 11.742
West Midlands | Bishops Wood 132kV | Ludlow 132/66/33/11kV | Bulk Supply Point | 11 | Electric Engagement | 1.3139 | 1.5159 | 1.7813 | 2.0805 | 2.4079 | 2.8126 | 3.2286 | 3.7073 | 4.143 | 4.5099 | 4.8364 | 5.1937 | 5.4214 | 5.5589 | 5.6475 | 5.7448 | 6.3163 | 6.7732 | 3.1596 | 3.588 | 4.1582 | 4.7972 | 5.4933 | 6.3666 | 7.2419 | 8.2427 | 9.1587 | 9.9318 | 10.6236 | 11.3955 | 11.8926 | 12.1986 | 12.3988 | 12.6231 | 13.9592 | 15.027
West Midlands | Bishops Wood 132kV | Ludlow 132/66/33/11kV | Bulk Supply Point | 11 | Holistic Transition | 1.2924 | 1.4364 | 1.6126 | 1.8169 | 2.0353 | 2.2898 | 2.5611 | 2.9214 | 3.2282 | 3.6282 | 3.9796 | 4.324 | 4.7835 | 5.0763 | 5.3636 | 5.6185 | 6.4086 | 6.8441 | 3.1222 | 3.4414 | 3.8284 | 4.2749 | 4.7563 | 5.3043 | 5.8846 | 6.6434 | 7.2938 | 8.1639 | 8.9035 | 9.6291 | 10.6481 | 11.2616 | 11.8652 | 12.4044 | 14.1393 | 15.1308
West Midlands | Bishops Wood 132kV | Ludlow 132/66/33/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | 1.272 | 1.3909 | 1.5348 | 1.7085 | 1.892 | 2.151 | 2.41 | 2.7458 | 3.034 | 3.3657 | 3.6913 | 4.0388 | 4.3408 | 4.6002 | 4.8592 | 5.085 | 5.8309 | 6.2346 | 3.0686 | 3.3238 | 3.6289 | 3.9946 | 4.381 | 4.9434 | 5.4875 | 6.1827 | 6.7817 | 7.4704 | 8.1416 | 8.8758 | 9.4973 | 10.0303 | 10.5639 | 11.0321 | 12.6599 | 13.5707
West Midlands | Bishops Wood 132kV | MADLEY 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.16756 | 0.18441 | 0.20401 | 0.22602 | 0.2572 | 0.28943 | 0.32316 | 0.37713 | 0.41931 | 0.46484 | 0.51111 | 0.56174 | 0.61725 | 0.67115 | 0.72414 | 0.77892 | 1.081 | 1.238 | 0.40204 | 0.43744 | 0.47822 | 0.52399 | 0.59089 | 0.65898 | 0.72898 | 0.8397 | 0.92673 | 1.0208 | 1.116 | 1.2194 | 1.3323 | 1.4419 | 1.5495 | 1.6609 | 2.2773 | 2.602
West Midlands | Bishops Wood 132kV | MADLEY 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.18407 | 0.22647 | 0.27579 | 0.34624 | 0.42957 | 0.50826 | 0.60493 | 0.72418 | 0.83728 | 0.9435 | 1.0434 | 1.1367 | 1.1992 | 1.2345 | 1.2615 | 1.2825 | 1.3833 | 1.4645 | 0.43783 | 0.52691 | 0.62985 | 0.77994 | 0.95928 | 1.1216 | 1.3204 | 1.5644 | 1.7963 | 2.0144 | 2.2203 | 2.4126 | 2.5432 | 2.6179 | 2.6762 | 2.7224 | 2.9516 | 3.1372
West Midlands | Bishops Wood 132kV | MADLEY 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.17922 | 0.20797 | 0.25698 | 0.29656 | 0.34021 | 0.39717 | 0.46565 | 0.55888 | 0.64779 | 0.74824 | 0.85341 | 0.95366 | 1.0423 | 1.1152 | 1.1854 | 1.2444 | 1.415 | 1.5028 | 0.42952 | 0.49291 | 0.60441 | 0.68869 | 0.78129 | 0.90107 | 1.0445 | 1.2371 | 1.4217 | 1.6289 | 1.8458 | 2.0532 | 2.2369 | 2.3882 | 2.534 | 2.6573 | 3.0276 | 3.2253
West Midlands | Bishops Wood 132kV | MADLEY 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.17383 | 0.19633 | 0.22335 | 0.26749 | 0.32432 | 0.377 | 0.44133 | 0.53118 | 0.61563 | 0.71567 | 0.81671 | 0.91252 | 0.99729 | 1.0654 | 1.1307 | 1.1842 | 1.3236 | 1.3994 | 0.41549 | 0.46313 | 0.51959 | 0.61469 | 0.73956 | 0.84926 | 0.98189 | 1.1656 | 1.3386 | 1.5431 | 1.7491 | 1.9447 | 2.118 | 2.2573 | 2.3908 | 2.501 | 2.7996 | 2.9687
West Midlands | Bishops Wood 132kV | Malvern 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 0.74786 | 0.91256 | 1.1095 | 1.3415 | 1.6039 | 1.9001 | 2.2353 | 2.7454 | 3.1464 | 3.6039 | 4.0813 | 4.5747 | 5.103 | 5.6272 | 6.1333 | 6.6287 | 8.8118 | 9.5429 | 1.7116 | 2.0565 | 2.4656 | 2.947 | 3.4913 | 4.1062 | 4.8019 | 5.8534 | 6.6841 | 7.6353 | 8.6275 | 9.6474 | 10.7341 | 11.8101 | 12.847 | 13.861 | 18.3393 | 19.8982
West Midlands | Bishops Wood 132kV | Malvern 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 0.89442 | 1.2874 | 1.7628 | 2.3173 | 2.9442 | 3.6611 | 4.5653 | 5.6391 | 6.5379 | 7.2899 | 7.9685 | 8.6041 | 9.016 | 9.2676 | 9.4335 | 9.5911 | 10.3068 | 10.9983 | 2.0299 | 2.8538 | 3.847 | 5.003 | 6.308 | 7.8051 | 9.698 | 11.929 | 13.7894 | 15.3573 | 16.7797 | 18.1064 | 18.9821 | 19.5292 | 19.9036 | 20.2614 | 21.9124 | 23.5018
West Midlands | Bishops Wood 132kV | Malvern 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 0.84861 | 1.1445 | 1.4478 | 1.8156 | 2.3183 | 2.8958 | 3.5341 | 4.2796 | 4.929 | 5.606 | 6.3199 | 7.0106 | 7.6734 | 8.2815 | 8.8454 | 9.3483 | 10.7531 | 11.4663 | 1.9513 | 2.5993 | 3.2488 | 4.0372 | 5.1162 | 6.3645 | 7.7333 | 9.2981 | 10.6645 | 12.0824 | 13.5741 | 15.018 | 16.404 | 17.672 | 18.8503 | 19.9062 | 22.9646 | 24.5927
West Midlands | Bishops Wood 132kV | Malvern 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 0.79988 | 1.0434 | 1.325 | 1.6481 | 2.0451 | 2.5233 | 3.1127 | 3.868 | 4.488 | 5.1534 | 5.8415 | 6.5017 | 7.1277 | 7.7055 | 8.241 | 8.7132 | 9.8856 | 10.5008 | 1.8237 | 2.3409 | 2.9318 | 3.6101 | 4.4466 | 5.4566 | 6.7049 | 8.2788 | 9.5665 | 10.9495 | 12.3717 | 13.7325 | 15.0205 | 16.2082 | 17.3108 | 18.2865 | 20.7982 | 22.1873
West Midlands | Bishops Wood 132kV | NEWENT 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.96535 | 1.0204 | 1.0901 | 1.1751 | 1.273 | 1.3924 | 1.5319 | 1.7599 | 1.9311 | 2.1349 | 2.3375 | 2.5344 | 2.7397 | 2.9353 | 3.1153 | 3.2956 | 4.2301 | 4.7521 | 2.3576 | 2.4728 | 2.6216 | 2.8027 | 3.0126 | 3.2703 | 3.5746 | 4.0724 | 4.4458 | 4.898 | 5.3433 | 5.7676 | 6.2041 | 6.6166 | 6.9919 | 7.3673 | 9.3454 | 10.497
West Midlands | Bishops Wood 132kV | NEWENT 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.0124 | 1.1326 | 1.3302 | 1.557 | 1.8038 | 2.0892 | 2.4997 | 2.9488 | 3.3069 | 3.6685 | 4.0188 | 4.3266 | 4.562 | 4.7017 | 4.8153 | 4.9212 | 5.5941 | 6.1381 | 2.4591 | 2.7121 | 3.1432 | 3.6342 | 4.1663 | 4.7831 | 5.694 | 6.6739 | 7.4419 | 8.2371 | 9.0143 | 9.6883 | 10.2173 | 10.5327 | 10.7945 | 11.0425 | 12.6601 | 13.9743
West Midlands | Bishops Wood 132kV | NEWENT 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.99578 | 1.0772 | 1.1788 | 1.3194 | 1.4698 | 1.7658 | 2.0808 | 2.4381 | 2.7328 | 3.0374 | 3.3642 | 3.8325 | 4.2639 | 4.5024 | 4.7295 | 4.9316 | 5.6124 | 5.9059 | 2.4296 | 2.6089 | 2.8273 | 3.1347 | 3.4622 | 4.1406 | 4.8568 | 5.648 | 6.2967 | 6.9614 | 7.6733 | 8.7407 | 9.7227 | 10.2337 | 10.7215 | 11.159 | 12.7052 | 13.3879
West Midlands | Bishops Wood 132kV | NEWENT 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.98735 | 1.0534 | 1.1576 | 1.2886 | 1.4456 | 1.6469 | 1.9481 | 2.3052 | 2.5738 | 2.9179 | 3.2428 | 3.54 | 3.8072 | 4.0282 | 4.238 | 4.4235 | 5.193 | 5.6746 | 2.4041 | 2.5442 | 2.7666 | 3.0479 | 3.3887 | 3.8276 | 4.5045 | 5.2864 | 5.863 | 6.6171 | 7.3175 | 7.9512 | 8.5166 | 8.9795 | 9.4206 | 9.8141 | 11.5877 | 12.7403
West Midlands | Bishops Wood 132kV | PETERCHURCH 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.41397 | 0.44036 | 0.47038 | 0.50755 | 0.54145 | 0.57962 | 0.6225 | 0.69035 | 0.7414 | 0.7958 | 0.8528 | 0.91436 | 0.98247 | 1.0502 | 1.1171 | 1.185 | 1.5123 | 1.6581 | 1.0026 | 1.0579 | 1.12 | 1.1967 | 1.2663 | 1.3445 | 1.4323 | 1.57 | 1.6739 | 1.7846 | 1.9004 | 2.0254 | 2.1632 | 2.3001 | 2.4356 | 2.5731 | 3.2378 | 3.5385
West Midlands | Bishops Wood 132kV | PETERCHURCH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.43518 | 0.49345 | 0.57343 | 0.66922 | 0.76125 | 0.86172 | 0.97848 | 1.1241 | 1.2586 | 1.371 | 1.4716 | 1.5711 | 1.6404 | 1.682 | 1.711 | 1.7359 | 1.8466 | 1.9451 | 1.0483 | 1.1708 | 1.341 | 1.5444 | 1.7383 | 1.9488 | 2.1909 | 2.4922 | 2.7727 | 3.0062 | 3.2152 | 3.4227 | 3.5718 | 3.663 | 3.7249 | 3.7815 | 4.0375 | 4.2641
West Midlands | Bishops Wood 132kV | PETERCHURCH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.42783 | 0.46724 | 0.52272 | 0.58594 | 0.64493 | 0.71072 | 0.78205 | 0.8828 | 0.97319 | 1.0704 | 1.1741 | 1.2758 | 1.3699 | 1.4537 | 1.5385 | 1.6074 | 1.8025 | 1.901 | 1.0353 | 1.1219 | 1.2435 | 1.3811 | 1.5091 | 1.6491 | 1.798 | 2.0059 | 2.1933 | 2.3935 | 2.6076 | 2.8177 | 3.0123 | 3.1861 | 3.3618 | 3.5055 | 3.9285 | 4.1549
West Midlands | Bishops Wood 132kV | PETERCHURCH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.42304 | 0.45639 | 0.50014 | 0.55258 | 0.60132 | 0.65907 | 0.72896 | 0.83001 | 0.92004 | 1.0197 | 1.1244 | 1.2273 | 1.3224 | 1.4057 | 1.4859 | 1.5523 | 1.712 | 1.7774 | 1.0219 | 1.0926 | 1.1839 | 1.2929 | 1.3933 | 1.5118 | 1.6547 | 1.8597 | 2.0432 | 2.2456 | 2.4584 | 2.6676 | 2.8611 | 3.0306 | 3.1939 | 3.3294 | 3.6654 | 3.8103
West Midlands | Bishops Wood 132kV | PONTRILAS 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.3725 | 0.39034 | 0.41624 | 0.44896 | 0.48844 | 0.53952 | 0.60434 | 0.69693 | 0.77707 | 0.8741 | 0.95623 | 1.0295 | 1.102 | 1.1704 | 1.2377 | 1.3067 | 1.7086 | 1.996 | 0.91675 | 0.9549 | 1.0124 | 1.0851 | 1.173 | 1.2877 | 1.4353 | 1.6434 | 1.8259 | 2.0494 | 2.2347 | 2.3957 | 2.5522 | 2.6987 | 2.8431 | 2.9909 | 3.8707 | 4.5227
West Midlands | Bishops Wood 132kV | PONTRILAS 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.38723 | 0.42676 | 0.51526 | 0.61824 | 0.7264 | 0.85419 | 1.0016 | 1.1775 | 1.3458 | 1.508 | 1.6755 | 1.8317 | 1.9634 | 2.0418 | 2.1083 | 2.1748 | 2.5256 | 2.8876 | 0.94836 | 1.0321 | 1.2342 | 1.4664 | 1.7086 | 1.9959 | 2.3253 | 2.7159 | 3.0915 | 3.4559 | 3.8368 | 4.1915 | 4.4978 | 4.6795 | 4.8348 | 4.9926 | 5.8357 | 6.7213
West Midlands | Bishops Wood 132kV | PONTRILAS 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.38204 | 0.40899 | 0.44354 | 0.50482 | 0.56902 | 0.65952 | 0.78004 | 0.92584 | 1.0733 | 1.2185 | 1.3771 | 1.5342 | 1.6776 | 1.7766 | 1.8731 | 1.9607 | 2.3199 | 2.4736 | 0.93904 | 0.99912 | 1.075 | 1.2137 | 1.3584 | 1.5636 | 1.8401 | 2.1686 | 2.5046 | 2.8301 | 3.1873 | 3.5425 | 3.8671 | 4.0855 | 4.2986 | 4.494 | 5.3305 | 5.6936
West Midlands | Bishops Wood 132kV | PONTRILAS 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.37914 | 0.4005 | 0.43712 | 0.48688 | 0.55038 | 0.638 | 0.7409 | 0.87181 | 0.99522 | 1.1451 | 1.278 | 1.4034 | 1.5143 | 1.599 | 1.6818 | 1.7562 | 2.0885 | 2.3912 | 0.93072 | 0.97622 | 1.0565 | 1.1664 | 1.3085 | 1.506 | 1.7369 | 2.0257 | 2.2994 | 2.634 | 2.9251 | 3.1989 | 3.4402 | 3.6217 | 3.7998 | 3.9619 | 4.7377 | 5.473
West Midlands | Bishops Wood 132kV | PRESTEIGNE 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.31513 | 0.3365 | 0.36047 | 0.38784 | 0.41927 | 0.45488 | 0.49622 | 0.55896 | 0.60822 | 0.6622 | 0.71647 | 0.77204 | 0.83269 | 0.89194 | 0.95009 | 1.0093 | 1.3029 | 1.4216 | 0.77017 | 0.8161 | 0.86653 | 0.92403 | 0.99018 | 1.065 | 1.1521 | 1.2825 | 1.3857 | 1.4994 | 1.6126 | 1.7272 | 1.8512 | 1.9724 | 2.0914 | 2.2125 | 2.8166 | 3.0696
West Midlands | Bishops Wood 132kV | PRESTEIGNE 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.33372 | 0.38781 | 0.44805 | 0.5202 | 0.59749 | 0.68664 | 0.79359 | 0.92334 | 1.042 | 1.1463 | 1.243 | 1.3338 | 1.395 | 1.4307 | 1.4566 | 1.4797 | 1.5944 | 1.6882 | 0.81047 | 0.92659 | 1.0541 | 1.2067 | 1.3686 | 1.5552 | 1.7782 | 2.0468 | 2.2933 | 2.5109 | 2.714 | 2.9042 | 3.035 | 3.1125 | 3.1705 | 3.223 | 3.4886 | 3.7106
West Midlands | Bishops Wood 132kV | PRESTEIGNE 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.32958 | 0.36992 | 0.4089 | 0.45603 | 0.50787 | 0.57301 | 0.64703 | 0.74571 | 0.83205 | 0.92584 | 1.0263 | 1.1242 | 1.216 | 1.2955 | 1.3717 | 1.4379 | 1.6319 | 1.7247 | 0.80436 | 0.89569 | 0.98065 | 1.0828 | 1.1946 | 1.3342 | 1.4924 | 1.6996 | 1.8815 | 2.0778 | 2.2884 | 2.4937 | 2.6866 | 2.853 | 3.0128 | 3.1525 | 3.5791 | 3.7932
West Midlands | Bishops Wood 132kV | PRESTEIGNE 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.32194 | 0.3527 | 0.38814 | 0.42917 | 0.47409 | 0.52882 | 0.59495 | 0.68703 | 0.76876 | 0.86238 | 0.95675 | 1.0461 | 1.1303 | 1.2016 | 1.27 | 1.328 | 1.4847 | 1.5711 | 0.7848 | 0.85146 | 0.92647 | 1.0136 | 1.1083 | 1.2236 | 1.3622 | 1.5528 | 1.7224 | 1.9165 | 2.111 | 2.2951 | 2.4684 | 2.6151 | 2.7558 | 2.8758 | 3.2146 | 3.4123
West Midlands | Bishops Wood 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.6674 | 2.6963 | 2.7331 | 2.7791 | 2.835 | 2.8915 | 2.9568 | 3.0541 | 3.1344 | 3.2256 | 3.3153 | 3.4066 | 3.5047 | 3.5977 | 3.6876 | 3.7772 | 1.7019 | 1.8872 | 6.6427 | 6.7034 | 6.7804 | 6.8768 | 6.9937 | 7.1125 | 7.2503 | 7.4536 | 7.6229 | 7.8164 | 8.0048 | 8.1947 | 8.3972 | 8.5885 | 8.7733 | 8.9571 | 3.5777 | 3.9789
West Midlands | Bishops Wood 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.694 | 2.7649 | 2.857 | 2.9672 | 3.0949 | 3.2477 | 3.4195 | 3.6186 | 3.7973 | 3.9516 | 4.0921 | 1.7059 | 1.7953 | 1.8503 | 1.8916 | 1.9329 | 2.1594 | 2.3541 | 6.7002 | 6.8491 | 7.0442 | 7.2766 | 7.5456 | 7.8684 | 8.2295 | 8.6453 | 9.0192 | 9.3443 | 9.6429 | 3.6258 | 3.8187 | 3.939 | 4.032 | 4.1254 | 4.6419 | 5.0958
West Midlands | Bishops Wood 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.6859 | 2.7331 | 2.7875 | 2.8617 | 2.9598 | 3.0828 | 3.2037 | 3.3479 | 3.483 | 3.6264 | 3.7724 | 1.3999 | 1.5408 | 1.6632 | 1.7837 | 1.8913 | 4.7499 | 4.9207 | 6.6864 | 6.7899 | 6.9062 | 7.0659 | 7.2774 | 7.542 | 7.8027 | 8.1074 | 8.3964 | 8.7007 | 9.0096 | 3.022 | 3.32 | 3.5761 | 3.8288 | 4.0559 | 11.0969 | 11.4825
West Midlands | Bishops Wood 132kV | QUATT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.6775 | 2.7165 | 2.7674 | 2.8351 | 2.9222 | 3.0285 | 3.1431 | 3.2866 | 3.4115 | 3.5542 | 3.6898 | 1.2957 | 1.4179 | 1.5227 | 1.6279 | 1.7204 | 4.5399 | 4.7289 | 6.6643 | 6.7472 | 6.8545 | 6.9976 | 7.183 | 7.4103 | 7.6538 | 7.9539 | 8.2163 | 8.5162 | 8.7981 | 2.7598 | 3.0127 | 3.2286 | 3.446 | 3.6386 | 10.5881 | 11.0188
West Midlands | Bishops Wood 132kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Counterfactual | 9.2651 | 9.4152 | 9.5754 | 9.7572 | 9.9874 | 10.2109 | 10.4613 | 10.8229 | 11.1221 | 11.4432 | 11.7688 | 12.0816 | 12.3865 | 12.6883 | 12.9906 | 13.2993 | 14.658 | 15.1336 | 22.8975 | 23.2167 | 23.5509 | 23.9299 | 24.4227 | 24.8887 | 25.4117 | 26.1599 | 26.7836 | 27.4547 | 28.1318 | 28.7776 | 29.3999 | 30.0152 | 30.6331 | 31.2633 | 34.0559 | 35.0726
West Midlands | Bishops Wood 132kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 9.3665 | 9.6966 | 10.047 | 10.4434 | 10.8895 | 11.3778 | 11.9474 | 12.6252 | 13.235 | 13.7477 | 14.234 | 14.6821 | 14.9509 | 6.6177 | 6.7493 | 6.8714 | 7.4797 | 7.9718 | 23.1187 | 23.8276 | 24.5649 | 25.397 | 26.3309 | 27.3541 | 28.5426 | 29.9477 | 31.2161 | 32.2893 | 33.3127 | 34.2527 | 34.8236 | 13.932 | 14.2233 | 14.4958 | 15.8736 | 17.0023
West Midlands | Bishops Wood 132kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 9.3371 | 9.5849 | 9.8202 | 10.0907 | 10.3919 | 10.7448 | 11.1402 | 11.6559 | 12.1091 | 12.5787 | 13.0908 | 13.5673 | 5.4788 | 5.8594 | 6.2366 | 6.5725 | 7.5729 | 16.5502 | 23.0683 | 23.6223 | 24.1279 | 24.7106 | 25.3577 | 26.1138 | 26.9586 | 28.0435 | 29.0028 | 29.9918 | 31.068 | 32.0702 | 11.6806 | 12.4729 | 13.2612 | 13.9667 | 16.1387 | 38.4707
West Midlands | Bishops Wood 132kV | REDDITCH NORTH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 9.3056 | 9.5117 | 9.7272 | 9.9747 | 10.253 | 10.5795 | 10.9535 | 11.4554 | 16.141 | 16.613 | 17.099 | 17.5486 | 17.9421 | 18.2969 | 18.6459 | 18.9537 | 19.7604 | 20.1853 | 22.9859 | 23.4348 | 23.8887 | 24.4109 | 24.9993 | 25.69 | 26.4774 | 27.5209 | 39.0563 | 40.0401 | 41.0475 | 41.9779 | 42.7851 | 43.5117 | 44.2291 | 44.8643 | 46.5916 | 47.5477
West Midlands | Bishops Wood 132kV | ROSS ON WYE 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.63036 | 0.72403 | 0.83513 | 0.95557 | 1.0943 | 1.2644 | 1.5138 | 1.7834 | 2.0134 | 2.2402 | 2.4688 | 2.7093 | 2.9926 | 3.2994 | 3.6364 | 4.0037 | 5.2678 | 5.7473 | 1.4909 | 1.6874 | 1.9184 | 2.1683 | 2.456 | 2.8091 | 3.3516 | 3.906 | 4.3829 | 4.8528 | 5.3247 | 5.8181 | 6.3991 | 7.0301 | 7.742 | 8.5282 | 11.1292 | 12.1356
West Midlands | Bishops Wood 132kV | ROSS ON WYE 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.70864 | 0.92269 | 1.1789 | 1.4714 | 1.8325 | 2.4529 | 2.9483 | 3.5028 | 3.9889 | 4.3917 | 4.7581 | 5.219 | 5.5925 | 5.7802 | 5.9224 | 6.051 | 6.4696 | 6.8179 | 1.6609 | 2.1111 | 2.6469 | 3.2557 | 4.0094 | 5.3848 | 6.4174 | 7.5613 | 8.5651 | 9.3967 | 10.1578 | 11.1601 | 11.9931 | 12.3982 | 12.7111 | 12.9971 | 13.9505 | 14.7494
West Midlands | Bishops Wood 132kV | ROSS ON WYE 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.68497 | 0.83166 | 0.99882 | 1.2035 | 1.5397 | 1.8627 | 2.2191 | 2.6441 | 3.0124 | 3.4465 | 4.0815 | 4.4698 | 4.8554 | 5.2218 | 5.5712 | 5.878 | 6.6397 | 6.9984 | 1.6202 | 1.9422 | 2.3003 | 2.7381 | 3.488 | 4.1787 | 4.9372 | 5.8256 | 6.5986 | 7.5266 | 8.9488 | 9.7576 | 10.5623 | 11.3282 | 12.0598 | 12.7059 | 14.3578 | 15.1728
West Midlands | Bishops Wood 132kV | ROSS ON WYE 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.66108 | 0.78261 | 0.93524 | 1.1239 | 1.3617 | 1.852 | 2.1918 | 2.6039 | 2.9549 | 3.3212 | 3.6953 | 4.11 | 4.6117 | 4.9923 | 5.3237 | 5.6124 | 6.2482 | 6.559 | 1.5572 | 1.8152 | 2.1355 | 2.5313 | 3.0329 | 4.1417 | 4.8563 | 5.7086 | 6.4354 | 7.1887 | 7.9552 | 8.828 | 9.9202 | 10.7217 | 11.4074 | 12.0082 | 13.3666 | 14.0657
West Midlands | Bishops Wood 132kV | ST WEONARDS 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.64814 | 0.66778 | 0.69321 | 0.72397 | 0.76025 | 0.80798 | 0.86477 | 0.95051 | 1.0211 | 1.1011 | 1.1754 | 1.2502 | 1.3285 | 1.4037 | 1.4786 | 1.5543 | 2.0063 | 2.2966 | 1.5932 | 1.6342 | 1.6884 | 1.754 | 1.8316 | 1.934 | 2.0573 | 2.2409 | 2.3939 | 2.5694 | 2.7291 | 2.8869 | 3.0505 | 3.2063 | 3.3618 | 3.5187 | 4.4658 | 5.0896
West Midlands | Bishops Wood 132kV | ST WEONARDS 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.66725 | 0.71509 | 0.80224 | 0.91519 | 1.0347 | 1.1721 | 1.3327 | 1.5313 | 1.7267 | 1.9141 | 2.0655 | 2.2013 | 2.3082 | 2.3643 | 2.4078 | 2.4566 | 2.7687 | 3.0297 | 1.6345 | 1.7345 | 1.928 | 2.1748 | 2.4342 | 2.7318 | 3.0764 | 3.5014 | 3.921 | 4.3226 | 4.6383 | 4.9201 | 5.1494 | 5.2676 | 5.3588 | 5.4674 | 6.1868 | 6.8115
West Midlands | Bishops Wood 132kV | ST WEONARDS 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.66256 | 0.69316 | 0.73867 | 0.81119 | 0.88607 | 0.98267 | 1.102 | 1.2548 | 1.3255 | 1.4384 | 1.6009 | 1.7718 | 1.9221 | 2.0331 | 2.1401 | 2.2335 | 2.5742 | 2.7208 | 1.6274 | 1.6945 | 1.7955 | 1.9551 | 2.1198 | 2.3305 | 2.5911 | 2.9196 | 3.0446 | 3.2655 | 3.6083 | 3.9763 | 4.301 | 4.5368 | 4.7646 | 4.9655 | 5.7268 | 6.0637
West Midlands | Bishops Wood 132kV | ST WEONARDS 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.65564 | 0.68093 | 0.71716 | 0.76778 | 0.82806 | 0.91427 | 1.0185 | 1.1569 | 1.292 | 1.4555 | 1.6121 | 1.7603 | 1.888 | 1.987 | 2.0824 | 2.1648 | 2.4533 | 2.6696 | 1.6092 | 1.6625 | 1.7397 | 1.8474 | 1.977 | 2.1621 | 2.3848 | 2.6765 | 2.9626 | 3.3099 | 3.6378 | 3.9483 | 4.2156 | 4.4211 | 4.6199 | 4.7934 | 5.4376 | 5.9466
West Midlands | Bishops Wood 132kV | STOCKTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.18101 | 0.20759 | 0.24381 | 0.28927 | 0.34278 | 0.40619 | 0.48281 | 0.59275 | 0.68624 | 0.78968 | 0.88237 | 0.96815 | 1.0575 | 1.144 | 1.2291 | 1.3149 | 1.7703 | 2.0304 | 0.42173 | 0.47783 | 0.55555 | 0.65317 | 0.76844 | 0.90612 | 1.0747 | 1.3139 | 1.5199 | 1.7511 | 1.954 | 2.1377 | 2.3266 | 2.5082 | 2.6869 | 2.867 | 3.8418 | 4.4265
West Midlands | Bishops Wood 132kV | STOCKTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.20269 | 0.2684 | 0.37018 | 0.48924 | 0.62472 | 0.77575 | 0.94322 | 1.1441 | 1.3327 | 1.5088 | 1.6866 | 1.8526 | 1.9847 | 2.0677 | 2.1377 | 2.2075 | 2.5786 | 2.9049 | 0.4687 | 0.6082 | 0.83273 | 1.0922 | 1.3856 | 1.7149 | 2.078 | 2.5112 | 2.9198 | 3.305 | 3.699 | 4.0661 | 4.3648 | 4.5519 | 4.7121 | 4.873 | 5.7342 | 6.5221
West Midlands | Bishops Wood 132kV | STOCKTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.19559 | 0.24419 | 0.29239 | 0.37463 | 0.45645 | 0.55759 | 0.68777 | 0.85457 | 1.0184 | 1.1811 | 1.3566 | 1.5286 | 1.6897 | 1.8131 | 1.9319 | 2.0407 | 2.4547 | 2.6259 | 0.45627 | 0.56381 | 0.66726 | 0.84733 | 1.0264 | 1.25 | 1.5418 | 1.9088 | 2.2741 | 2.632 | 3.0188 | 3.3993 | 3.7552 | 4.0212 | 4.2777 | 4.5142 | 5.4486 | 5.8441
West Midlands | Bishops Wood 132kV | STOCKTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.18975 | 0.22415 | 0.27548 | 0.3488 | 0.42929 | 0.52771 | 0.64007 | 0.78681 | 0.92367 | 1.0846 | 1.2327 | 1.3745 | 1.5055 | 1.6145 | 1.7192 | 1.8159 | 2.1848 | 2.4828 | 0.44041 | 0.51396 | 0.62462 | 0.7837 | 0.96033 | 1.1773 | 1.4241 | 1.7413 | 2.0393 | 2.3917 | 2.7104 | 3.0146 | 3.2944 | 3.524 | 3.7455 | 3.9519 | 4.7884 | 5.4983
West Midlands | Bishops Wood 132kV | Stourport 132/66/33/11kV | Bulk Supply Point | 11 | Counterfactual | 1.1308 | 2.9899 | 3.1362 | 3.3057 | 3.4999 | 3.7514 | 4.0607 | 4.504 | 4.8779 | 5.8976 | 6.2343 | 6.5803 | 6.9607 | 7.3337 | 7.7005 | 8.0762 | 9.8384 | 10.5614 | 2.7126 | 7.3098 | 7.6153 | 7.9687 | 8.3736 | 8.8991 | 9.5474 | 10.469 | 11.2518 | 13.6688 | 14.3697 | 15.0831 | 15.8633 | 16.6267 | 17.377 | 18.1452 | 21.7769 | 23.3211
West Midlands | Bishops Wood 132kV | Stourport 132/66/33/11kV | Bulk Supply Point | 11 | Electric Engagement | 1.2461 | 3.9936 | 4.4426 | 4.9078 | 5.4984 | 6.1584 | 6.8454 | 7.64 | 8.3495 | 8.9574 | 9.5115 | 10.0461 | 10.4408 | 10.6921 | 10.8542 | 11.0273 | 11.8503 | 12.5514 | 2.9626 | 9.7054 | 10.6681 | 11.6618 | 12.9204 | 14.3265 | 15.7781 | 17.4437 | 18.9365 | 20.2217 | 21.3997 | 22.5346 | 23.397 | 23.9538 | 24.3166 | 24.7132 | 26.6104 | 28.2434
West Midlands | Bishops Wood 132kV | Stourport 132/66/33/11kV | Bulk Supply Point | 11 | Holistic Transition | 1.2106 | 2.1345 | 2.4008 | 2.7414 | 3.1698 | 3.6292 | 4.0707 | 4.6367 | 5.1265 | 5.6551 | 6.2236 | 6.7757 | 7.3175 | 7.803 | 8.2704 | 8.69 | 9.9829 | 10.6524 | 2.901 | 5.1419 | 5.7252 | 6.4701 | 7.4043 | 8.403 | 9.3518 | 10.5444 | 11.5819 | 12.6942 | 13.8912 | 15.0557 | 16.1998 | 17.2187 | 18.2011 | 19.0885 | 21.9281 | 23.4555
West Midlands | Bishops Wood 132kV | Stourport 132/66/33/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | 1.1763 | 3.7911 | 4.0379 | 4.3174 | 4.6734 | 5.0498 | 5.4597 | 6.0041 | 6.465 | 6.9937 | 7.5299 | 8.0444 | 8.5413 | 8.9806 | 9.4066 | 9.7788 | 10.7976 | 11.3736 | 2.8106 | 9.2771 | 9.7979 | 10.3869 | 11.1415 | 11.9386 | 12.8032 | 13.9322 | 14.8894 | 15.9904 | 17.0989 | 18.161 | 19.1849 | 20.0884 | 20.9657 | 21.7366 | 23.9262 | 25.2264
West Midlands | Bishops Wood 132kV | TENBURY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.35996 | 0.39579 | 0.44469 | 0.50355 | 0.57276 | 0.65937 | 0.76232 | 0.91438 | 1.0417 | 1.1897 | 1.3281 | 1.461 | 1.5986 | 1.7306 | 1.8601 | 1.9881 | 2.6475 | 2.9929 | 0.85911 | 0.9345 | 1.0388 | 1.1647 | 1.3131 | 1.4999 | 1.7242 | 2.0516 | 2.3289 | 2.655 | 2.9543 | 3.2369 | 3.5262 | 3.8021 | 4.0729 | 4.3404 | 5.7383 | 6.5079
West Midlands | Bishops Wood 132kV | TENBURY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.39365 | 0.48127 | 0.61694 | 0.78163 | 0.96364 | 1.1838 | 1.4404 | 1.749 | 2.0326 | 2.2873 | 2.5366 | 2.7681 | 2.9282 | 3.0324 | 3.1174 | 3.2011 | 3.6405 | 4.0471 | 0.93226 | 1.1164 | 1.4124 | 1.768 | 2.159 | 2.6345 | 3.1859 | 3.8458 | 4.4541 | 5.0048 | 5.5502 | 6.0559 | 6.4107 | 6.6451 | 6.84 | 7.0338 | 8.0597 | 9.0364
West Midlands | Bishops Wood 132kV | TENBURY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.38334 | 0.43963 | 0.50603 | 0.61129 | 0.75804 | 0.91705 | 1.1164 | 1.3581 | 1.5976 | 1.8289 | 2.0643 | 2.305 | 2.5279 | 2.7028 | 2.8707 | 3.022 | 3.5591 | 3.7991 | 0.91453 | 1.0385 | 1.1808 | 1.4105 | 1.7302 | 2.0788 | 2.52 | 3.0457 | 3.5729 | 4.0752 | 4.5833 | 5.109 | 5.5955 | 5.9696 | 6.3296 | 6.6564 | 7.8653 | 8.4182
West Midlands | Bishops Wood 132kV | TENBURY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.37241 | 0.41711 | 0.48352 | 0.57184 | 0.69035 | 0.84254 | 1.0186 | 1.2445 | 1.4501 | 1.6819 | 1.8983 | 2.1008 | 2.2874 | 2.4418 | 2.5913 | 2.7266 | 3.2063 | 3.5775 | 0.886 | 0.9807 | 1.1229 | 1.313 | 1.5707 | 1.9032 | 2.2861 | 2.7704 | 3.2134 | 3.7146 | 4.1751 | 4.6055 | 5.0004 | 5.3239 | 5.6382 | 5.9256 | 7.0057 | 7.8841
West Midlands | Bishops Wood 132kV | Timberdine 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.5905 | 1.7098 | 1.8512 | 2.0115 | 2.2571 | 2.532 | 2.8456 | 3.3058 | 3.6772 | 4.0721 | 4.4626 | 4.8583 | 5.2861 | 5.7145 | 6.1321 | 6.5503 | 8.411 | 8.9217 | 3.3384 | 3.5868 | 3.8805 | 4.2138 | 4.7253 | 5.2991 | 5.9559 | 6.9126 | 7.69 | 8.5194 | 9.3362 | 10.1576 | 11.0413 | 11.9245 | 12.785 | 13.6466 | 17.495 | 18.6019
West Midlands | Bishops Wood 132kV | Timberdine 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.706 | 1.9958 | 2.3489 | 2.8665 | 3.4547 | 4.0824 | 4.8339 | 5.7067 | 6.4878 | 7.1628 | 7.7998 | 8.4124 | 8.867 | 9.067 | 9.2015 | 9.3288 | 9.9966 | 10.574 | 3.5894 | 4.1928 | 4.932 | 6.021 | 7.2589 | 8.5816 | 10.164 | 11.9879 | 13.622 | 15.0462 | 16.3986 | 17.6963 | 18.6765 | 19.1127 | 19.4164 | 19.7056 | 21.2267 | 22.5642
West Midlands | Bishops Wood 132kV | Timberdine 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.6707 | 1.8514 | 2.1565 | 2.5261 | 2.921 | 3.3943 | 3.9438 | 4.62 | 5.2292 | 5.8578 | 6.5229 | 7.1815 | 7.7019 | 8.1734 | 8.6121 | 9.0004 | 10.1515 | 10.6556 | 3.5286 | 3.9208 | 4.5741 | 5.3689 | 6.2169 | 7.2415 | 8.4263 | 9.8611 | 11.1606 | 12.4943 | 13.9026 | 15.2981 | 16.3906 | 17.3735 | 18.2898 | 19.1048 | 21.6032 | 22.7536
West Midlands | Bishops Wood 132kV | Timberdine 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.6328 | 1.7858 | 1.9762 | 2.2747 | 2.6052 | 2.9901 | 3.4658 | 4.0745 | 4.6099 | 5.1855 | 5.7688 | 6.3396 | 6.8918 | 7.4053 | 7.8869 | 8.3259 | 9.4741 | 9.9549 | 3.4297 | 3.751 | 4.1486 | 4.7794 | 5.4802 | 6.2983 | 7.3103 | 8.5858 | 9.7108 | 10.9213 | 12.1388 | 13.3284 | 14.4776 | 15.5444 | 16.547 | 17.4646 | 19.9441 | 21.0489
West Midlands | Bishops Wood 132kV | Upton Warren 132/66/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.5926 | 1.817 | 2.1029 | 2.4309 | 2.7506 | 3.1172 | 3.5371 | 4.1731 | 4.7007 | 5.2635 | 5.7846 | 6.2692 | 6.8112 | 7.3623 | 7.9785 | 8.536 | 11.1675 | 12.3551 | 3.5051 | 3.9807 | 4.5818 | 5.271 | 5.9454 | 6.721 | 7.614 | 8.9524 | 10.0726 | 11.2764 | 12.3774 | 13.3861 | 14.5044 | 15.6455 | 16.9453 | 18.0948 | 23.5799 | 26.1661
West Midlands | Bishops Wood 132kV | Upton Warren 132/66/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.7526 | 2.2539 | 2.9045 | 3.612 | 4.3686 | 5.2053 | 6.2121 | 7.4074 | 8.4818 | 9.3932 | 10.2165 | 11.0961 | 11.6466 | 11.9973 | 12.2754 | 12.5303 | 13.9392 | 15.205 | 3.8515 | 4.9195 | 6.311 | 7.8176 | 9.4224 | 11.1977 | 13.3306 | 15.8426 | 18.1073 | 20.0446 | 21.8103 | 23.7338 | 24.938 | 25.7128 | 26.337 | 26.915 | 30.1885 | 33.1675
West Midlands | Bishops Wood 132kV | Upton Warren 132/66/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.7038 | 2.0729 | 2.4925 | 2.9707 | 3.4546 | 4.0781 | 4.7981 | 5.7237 | 6.5454 | 7.5213 | 8.3752 | 9.1959 | 10.0012 | 10.7101 | 11.4133 | 12.0471 | 14.0701 | 15.1083 | 3.7674 | 4.5879 | 5.4949 | 6.5333 | 7.5807 | 8.9364 | 10.5039 | 12.4818 | 14.2505 | 16.3901 | 18.211 | 19.9659 | 21.6869 | 23.1835 | 24.6741 | 26.0254 | 30.5101 | 32.8775
West Midlands | Bishops Wood 132kV | Upton Warren 132/66/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.6545 | 1.9524 | 2.3426 | 2.7799 | 3.2477 | 3.8004 | 4.4689 | 5.3552 | 6.1286 | 6.9662 | 7.7532 | 8.6132 | 9.331 | 9.9709 | 10.6133 | 11.1796 | 12.9153 | 14.0798 | 3.6377 | 4.2781 | 5.1085 | 6.0409 | 7.0429 | 8.2283 | 9.6596 | 11.5281 | 13.1643 | 14.9389 | 16.5837 | 18.4281 | 19.9219 | 21.2466 | 22.583 | 23.7685 | 27.5943 | 30.2832
West Midlands | Bishops Wood 132kV | Warndon 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.0318 | 1.2322 | 1.4889 | 1.7627 | 2.0673 | 2.4171 | 2.7914 | 3.3933 | 3.853 | 4.3628 | 4.9161 | 5.4852 | 6.1135 | 6.7279 | 7.292 | 7.8581 | 10.3741 | 11.0597 | 2.3827 | 2.7996 | 3.3294 | 3.8951 | 4.5247 | 5.2492 | 6.022 | 7.2604 | 8.2047 | 9.2625 | 10.4228 | 11.609 | 12.91 | 14.1763 | 15.3237 | 16.4743 | 21.6015 | 23.0563
West Midlands | Bishops Wood 132kV | Warndon 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.2231 | 1.7048 | 2.2882 | 2.9301 | 3.6703 | 4.5065 | 5.5361 | 6.8167 | 7.8337 | 8.7963 | 9.6679 | 10.4106 | 10.8941 | 11.1958 | 11.391 | 11.5789 | 12.4801 | 13.4638 | 2.7988 | 3.8018 | 5.0116 | 6.3423 | 7.8754 | 9.6189 | 11.775 | 14.4545 | 16.5373 | 18.5794 | 20.4227 | 21.9526 | 22.9626 | 23.6061 | 24.0367 | 24.4518 | 26.46 | 28.6104
West Midlands | Bishops Wood 132kV | Warndon 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.1654 | 1.4688 | 1.8459 | 2.2494 | 2.7302 | 3.379 | 4.1385 | 5.1504 | 5.8569 | 6.6683 | 7.5055 | 8.3232 | 9.1339 | 9.8841 | 10.5847 | 11.2114 | 12.9306 | 13.9675 | 2.6998 | 3.3578 | 4.1624 | 5.0225 | 6.0552 | 7.4693 | 9.1274 | 11.3017 | 12.7666 | 14.4719 | 16.2035 | 17.8958 | 19.5743 | 21.1259 | 22.5769 | 23.8787 | 27.5569 | 29.8486
West Midlands | Bishops Wood 132kV | Warndon 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.1013 | 1.3602 | 1.7079 | 2.0754 | 2.5 | 2.9944 | 3.6754 | 4.6024 | 5.3149 | 6.1797 | 7.0676 | 7.8724 | 8.6239 | 9.3177 | 9.9677 | 10.5438 | 11.9413 | 12.7457 | 2.5334 | 3.0775 | 3.8008 | 4.5685 | 5.4563 | 6.4877 | 7.9464 | 9.9032 | 11.3782 | 13.2092 | 15.0721 | 16.7319 | 18.2673 | 19.6847 | 21.0136 | 22.1937 | 25.135 | 26.8776
West Midlands | Bishops Wood 132kV | WOOFFERTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.55505 | 0.57943 | 0.60701 | 0.63937 | 0.67738 | 0.72111 | 0.77053 | 0.8494 | 0.91162 | 0.9783 | 1.0458 | 1.1199 | 1.2009 | 1.2801 | 1.3583 | 1.4382 | 1.8921 | 2.157 | 1.3636 | 1.4152 | 1.473 | 1.5407 | 1.62 | 1.7112 | 1.8143 | 1.9767 | 2.1056 | 2.2442 | 2.3836 | 2.5356 | 2.7009 | 2.8624 | 3.0218 | 3.1847 | 4.1127 | 4.6614
West Midlands | Bishops Wood 132kV | WOOFFERTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.57736 | 0.63532 | 0.72544 | 0.83994 | 0.96061 | 1.0975 | 1.2563 | 1.4543 | 1.649 | 1.8281 | 1.9935 | 2.1521 | 2.2728 | 2.3449 | 2.3907 | 2.4371 | 2.6404 | 2.8107 | 1.4118 | 1.5336 | 1.7305 | 1.9786 | 2.2381 | 2.5301 | 2.8643 | 3.2802 | 3.6918 | 4.0672 | 4.4141 | 4.7483 | 5.0109 | 5.1698 | 5.2688 | 5.3743 | 5.8443 | 6.243
West Midlands | Bishops Wood 132kV | WOOFFERTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.57008 | 0.60873 | 0.66901 | 0.74481 | 0.82663 | 0.92203 | 1.0271 | 1.1698 | 1.3077 | 1.4627 | 1.6265 | 1.7826 | 1.919 | 2.0294 | 2.1361 | 2.2255 | 2.4981 | 2.6449 | 1.399 | 1.4843 | 1.6199 | 1.7873 | 1.9676 | 2.1723 | 2.3936 | 2.6907 | 2.9788 | 3.2995 | 3.6395 | 3.9643 | 4.2492 | 4.4799 | 4.7032 | 4.8919 | 5.4904 | 5.8273
West Midlands | Bishops Wood 132kV | WOOFFERTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.56403 | 0.59513 | 0.63382 | 0.68726 | 0.74732 | 0.82572 | 0.92355 | 1.0588 | 1.1889 | 1.3429 | 1.4983 | 1.6449 | 1.7725 | 1.8733 | 1.9705 | 2.0491 | 2.2603 | 2.3749 | 1.3828 | 1.4487 | 1.5296 | 1.6404 | 1.7651 | 1.9275 | 2.1291 | 2.4056 | 2.6722 | 2.9872 | 3.3041 | 3.6032 | 3.8642 | 4.0701 | 4.269 | 4.4308 | 4.8823 | 5.1393
West Midlands | Bishops Wood 132kV | Worcester 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.1328 | 1.3055 | 1.5137 | 1.7417 | 1.9862 | 2.2598 | 2.5869 | 3.0963 | 3.501 | 3.9369 | 4.3875 | 4.8499 | 5.3604 | 5.8705 | 6.3635 | 6.8555 | 9.0165 | 9.6599 | 2.5316 | 2.8932 | 3.3243 | 3.7967 | 4.3025 | 4.8684 | 5.5454 | 6.5911 | 7.4266 | 8.3287 | 9.2582 | 10.208 | 11.252 | 12.2939 | 13.2997 | 14.3026 | 18.7225 | 20.0955
West Midlands | Bishops Wood 132kV | Worcester 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.2914 | 1.7079 | 2.2032 | 2.7501 | 3.3587 | 4.0516 | 4.893 | 5.911 | 6.8008 | 7.5305 | 8.2028 | 8.8424 | 9.2629 | 9.5158 | 9.6804 | 9.8356 | 10.6132 | 11.2968 | 2.876 | 3.7494 | 4.7807 | 5.9177 | 7.1782 | 8.6166 | 10.3618 | 12.4589 | 14.2925 | 15.8055 | 17.2056 | 18.5346 | 19.4236 | 19.9701 | 20.3382 | 20.6872 | 22.471 | 24.0264
West Midlands | Bishops Wood 132kV | Worcester 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.2436 | 1.5167 | 1.8276 | 2.1761 | 2.6366 | 3.1006 | 3.6428 | 4.3831 | 5.0212 | 5.6872 | 6.4046 | 7.1489 | 7.8904 | 8.5136 | 9.0917 | 9.6059 | 11.0223 | 11.7113 | 2.7943 | 3.3926 | 4.0565 | 4.8025 | 5.7879 | 6.78 | 7.9314 | 9.4776 | 10.8161 | 12.206 | 13.6988 | 15.2686 | 16.8392 | 18.1337 | 19.3369 | 20.4112 | 23.4735 | 25.0371
West Midlands | Bishops Wood 132kV | Worcester 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.1909 | 1.4144 | 1.704 | 2.0158 | 2.3904 | 2.8163 | 3.3336 | 4.0507 | 4.659 | 5.3146 | 5.9958 | 6.6618 | 7.3033 | 7.893 | 8.4422 | 8.9271 | 10.1512 | 10.7255 | 2.6571 | 3.1296 | 3.7341 | 4.3862 | 5.1715 | 6.0631 | 7.1457 | 8.6269 | 9.8851 | 11.2392 | 12.6395 | 14.0066 | 15.3219 | 16.5301 | 17.6561 | 18.6533 | 21.2761 | 22.5644
West Midlands | Bishops Wood 132kV | WRIBBENHALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.29782 | 0.3615 | 0.43661 | 0.5225 | 0.61801 | 0.73496 | 0.87486 | 1.0865 | 1.2597 | 1.4452 | 1.6258 | 1.8032 | 1.9948 | 2.1825 | 2.3669 | 2.5542 | 3.4739 | 3.8473 | 0.69033 | 0.82462 | 0.98316 | 1.1648 | 1.3671 | 1.6159 | 1.9158 | 2.364 | 2.7348 | 3.136 | 3.5201 | 3.8917 | 4.2891 | 4.677 | 5.0582 | 5.4453 | 7.372 | 8.2041
West Midlands | Bishops Wood 132kV | WRIBBENHALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.35546 | 0.51823 | 0.72714 | 0.96023 | 1.2108 | 1.4915 | 1.8233 | 2.222 | 2.5817 | 2.8998 | 3.2018 | 3.4898 | 3.6973 | 3.8182 | 3.9073 | 3.9975 | 4.4919 | 4.9524 | 0.81583 | 1.1602 | 1.6087 | 2.1058 | 2.637 | 3.234 | 3.9362 | 4.7742 | 5.5336 | 6.2127 | 6.8653 | 7.4859 | 7.9446 | 8.2149 | 8.4207 | 8.6302 | 9.7847 | 10.8856
West Midlands | Bishops Wood 132kV | WRIBBENHALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.33802 | 0.45182 | 0.55828 | 0.70003 | 0.84898 | 1.0352 | 1.2637 | 1.5641 | 1.8388 | 2.1265 | 2.4371 | 2.7443 | 3.0414 | 3.2907 | 3.5271 | 3.7422 | 4.4441 | 4.7578 | 0.78576 | 1.0373 | 1.2656 | 1.5737 | 1.896 | 2.3006 | 2.8002 | 3.4442 | 4.0396 | 4.6573 | 5.3248 | 5.9862 | 6.6249 | 7.1518 | 7.6531 | 8.1121 | 9.6762 | 10.4026
West Midlands | Bishops Wood 132kV | WRIBBENHALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.31958 | 0.41217 | 0.52037 | 0.63661 | 0.77522 | 0.9483 | 1.153 | 1.4314 | 1.6747 | 1.9584 | 2.2337 | 2.5001 | 2.7557 | 2.9782 | 3.1898 | 3.3816 | 3.9916 | 4.4015 | 0.73768 | 0.93554 | 1.1655 | 1.4133 | 1.7105 | 2.0836 | 2.5224 | 3.1099 | 3.6266 | 4.2317 | 4.8108 | 5.3702 | 5.9051 | 6.3668 | 6.8068 | 7.2086 | 8.562 | 9.5283
West Midlands | Bushbury 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.85826 | 0.94791 | 1.048 | 1.1663 | 1.2914 | 1.4427 | 1.6203 | 1.8915 | 2.1116 | 2.3677 | 2.6247 | 2.88 | 3.1498 | 3.4097 | 3.6592 | 3.9046 | 5.0298 | 5.5412 | 2.0497 | 2.2434 | 2.4588 | 2.7111 | 2.9735 | 3.2927 | 3.67 | 4.2395 | 4.7066 | 5.2554 | 5.7991 | 6.3329 | 6.8921 | 7.4286 | 7.943 | 8.4482 | 10.7862 | 11.9033
West Midlands | Bushbury 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.957 | 1.1889 | 1.4773 | 1.7619 | 2.0815 | 2.4896 | 2.949 | 3.5032 | 3.9946 | 4.4055 | 4.7892 | 5.1426 | 5.3819 | 5.5191 | 5.6229 | 5.7222 | 6.3087 | 6.8372 | 2.2725 | 2.7799 | 3.4106 | 4.0124 | 4.6852 | 5.5516 | 6.5214 | 7.6847 | 8.7207 | 9.5926 | 10.4155 | 11.1696 | 11.6929 | 11.9961 | 12.2338 | 12.4634 | 13.8443 | 15.1004
West Midlands | Bushbury 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.93317 | 1.1191 | 1.245 | 1.42 | 1.7259 | 1.9841 | 2.2909 | 2.6943 | 3.048 | 3.3989 | 3.7776 | 4.2743 | 4.6291 | 4.9276 | 5.2143 | 5.4691 | 6.2772 | 6.6506 | 2.2308 | 2.6555 | 2.9227 | 3.2991 | 3.9593 | 4.5157 | 5.1801 | 6.0409 | 6.8024 | 7.5479 | 8.3535 | 9.4596 | 10.2172 | 10.8452 | 11.4503 | 11.9916 | 13.783 | 14.6451
West Midlands | Bushbury 132kV | ALBRIGHTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.91421 | 1.0725 | 1.2543 | 1.4119 | 1.6428 | 1.9053 | 2.199 | 2.5955 | 2.9387 | 3.3099 | 3.6688 | 4.0061 | 4.3258 | 4.6014 | 4.8642 | 5.0982 | 5.8623 | 6.3358 | 2.1789 | 2.534 | 2.9346 | 3.2676 | 3.7605 | 4.323 | 4.9485 | 5.7816 | 6.5071 | 7.292 | 8.0414 | 8.7432 | 9.4065 | 9.9737 | 10.5162 | 11.0033 | 12.7024 | 13.8103
West Midlands | Bushbury 132kV | Bushbury B-C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.7988 | 2.6236 | 3.007 | 3.2952 | 3.6422 | 4.0813 | 4.5678 | 5.2932 | 5.8667 | 6.5014 | 7.1722 | 7.9349 | 8.7783 | 9.6352 | 10.5516 | 11.4467 | 15.0458 | 16.2612 | 4.1575 | 5.8337 | 6.6193 | 7.2164 | 7.9385 | 8.8579 | 9.8717 | 11.3607 | 12.5456 | 13.8607 | 15.2465 | 16.8129 | 18.5396 | 20.2928 | 22.1769 | 24.0152 | 31.3863 | 33.9477
West Midlands | Bushbury 132kV | Bushbury B-C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 2.0291 | 3.2933 | 4.0077 | 4.7663 | 5.6862 | 6.7617 | 7.9862 | 9.5588 | 10.9295 | 12.0872 | 13.18 | 14.2792 | 15.0497 | 15.5692 | 15.9368 | 16.261 | 17.3253 | 18.3766 | 4.6583 | 7.2597 | 8.7406 | 10.3215 | 12.2533 | 14.508 | 17.045 | 20.2855 | 23.1127 | 25.5125 | 27.7961 | 30.0982 | 31.7402 | 32.8623 | 33.675 | 34.4058 | 36.8642 | 39.2576
West Midlands | Bushbury 132kV | Bushbury B-C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.959 | 3.0171 | 3.5068 | 3.9788 | 4.6771 | 5.4458 | 6.3425 | 7.4727 | 8.4466 | 9.531 | 10.7276 | 12.0732 | 13.1989 | 14.2348 | 15.1531 | 15.9647 | 18.0336 | 19.0708 | 4.5377 | 6.7422 | 7.7915 | 8.8075 | 10.3156 | 11.957 | 13.8651 | 16.2306 | 18.2781 | 20.5521 | 23.0773 | 25.9688 | 28.3165 | 30.4734 | 32.3842 | 34.0803 | 38.5615 | 40.9169
West Midlands | Bushbury 132kV | Bushbury B-C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.8862 | 2.8819 | 3.3157 | 3.7365 | 4.3371 | 5.0186 | 5.8436 | 6.9962 | 7.9976 | 9.0995 | 10.2576 | 11.4113 | 12.5495 | 13.5835 | 14.5042 | 15.2983 | 17.1522 | 18.0363 | 4.3466 | 6.3928 | 7.2938 | 8.178 | 9.4628 | 10.8998 | 12.6443 | 15.0303 | 17.1041 | 19.384 | 21.773 | 24.1553 | 26.51 | 28.6428 | 30.5382 | 32.1822 | 36.1427 | 38.1342
West Midlands | Bushbury 132kV | FOUR ASHES 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.7389 | 1.8501 | 2.007 | 2.1732 | 2.3713 | 2.2212 | 2.4902 | 2.8452 | 3.0214 | 3.2312 | 3.4498 | 3.6802 | 3.981 | 4.2615 | 4.5246 | 4.7722 | 5.7472 | 6.1937 | 3.8859 | 4.1394 | 4.4939 | 4.8773 | 5.3369 | 5.1115 | 5.7378 | 6.5496 | 6.9322 | 7.3906 | 7.8613 | 8.3514 | 8.9875 | 9.5796 | 10.1349 | 10.6563 | 12.7267 | 13.7281
West Midlands | Bushbury 132kV | FOUR ASHES 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.8395 | 2.1326 | 2.5538 | 3.0499 | 3.6367 | 3.9735 | 4.7342 | 5.5783 | 5.9864 | 6.3486 | 6.7334 | 7.1451 | 7.4904 | 7.6369 | 7.7311 | 7.8186 | 8.7096 | 9.2195 | 4.12 | 4.7962 | 5.7725 | 6.9349 | 8.3141 | 9.2348 | 11.0061 | 12.9505 | 13.8245 | 14.6077 | 15.4489 | 16.3474 | 17.1134 | 17.4432 | 17.6627 | 17.8693 | 19.8377 | 21.0644
West Midlands | Bushbury 132kV | FOUR ASHES 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.8233 | 2.083 | 2.4285 | 2.8393 | 3.4391 | 3.7013 | 4.3957 | 5.1622 | 5.5086 | 5.8619 | 6.2304 | 6.5941 | 6.9083 | 7.1429 | 7.3716 | 7.5753 | 8.6736 | 9.0413 | 4.0918 | 4.7088 | 5.5257 | 6.5091 | 7.9239 | 8.6942 | 10.3412 | 12.134 | 12.8921 | 13.6594 | 14.4601 | 15.2515 | 15.934 | 16.4354 | 16.9253 | 17.3652 | 19.7429 | 20.6054
West Midlands | Bushbury 132kV | FOUR ASHES 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.808 | 2.0368 | 2.3685 | 2.7647 | 3.2956 | 3.5298 | 4.1727 | 4.9058 | 5.2059 | 5.5436 | 5.9081 | 6.2821 | 6.6305 | 6.836 | 7.0334 | 7.2042 | 7.9594 | 8.3693 | 4.0512 | 4.5907 | 5.3693 | 6.3144 | 7.5768 | 8.281 | 9.8042 | 11.5129 | 12.1573 | 12.8835 | 13.662 | 14.4616 | 15.2042 | 15.6327 | 16.0451 | 16.4048 | 18.0471 | 19.0159
West Midlands | Bushbury 132kV | I54 Busines Park 33/11kv | Primary Substation | 11 | Counterfactual | 0.50102 | 0.5201 | 0.53896 | 0.56279 | 0.61359 | 0.68498 | 0.74256 | 0.81336 | 0.85769 | 0.90478 | 0.9497 | 0.99619 | 1.0476 | 1.1008 | 1.1667 | 1.2368 | 1.4699 | 1.5373 | 1.2369 | 1.2763 | 1.3152 | 1.3642 | 1.4803 | 1.6455 | 1.7728 | 1.9256 | 2.018 | 2.1148 | 2.2071 | 2.3023 | 2.4071 | 2.5151 | 2.6569 | 2.8093 | 3.2925 | 3.4358
West Midlands | Bushbury 132kV | I54 Busines Park 33/11kv | Primary Substation | 11 | Electric Engagement | 0.51784 | 0.5616 | 0.6094 | 0.7101 | 0.90976 | 1.0776 | 1.2139 | 1.3239 | 1.4165 | 1.4896 | 1.5591 | 1.6581 | 1.7398 | 1.7831 | 1.8948 | 1.9132 | 1.9934 | 2.0789 | 1.2734 | 1.3641 | 1.463 | 1.6899 | 2.1617 | 2.5505 | 2.852 | 3.0801 | 3.2699 | 3.4206 | 3.564 | 3.7822 | 3.97 | 4.0691 | 4.3429 | 4.3833 | 4.5612 | 4.7503
West Midlands | Bushbury 132kV | I54 Busines Park 33/11kv | Primary Substation | 11 | Holistic Transition | 0.51248 | 0.54017 | 0.63661 | 0.72139 | 0.85619 | 0.95135 | 1.0128 | 1.0864 | 1.1502 | 1.4123 | 1.5413 | 1.6492 | 1.7229 | 1.7895 | 1.8541 | 1.9122 | 2.0701 | 2.1538 | 1.2641 | 1.3236 | 1.5539 | 1.7539 | 2.075 | 2.2949 | 2.4269 | 2.5797 | 2.7122 | 3.3397 | 3.6297 | 3.8669 | 4.0192 | 4.1564 | 4.2899 | 4.4105 | 4.7477 | 4.9346
West Midlands | Bushbury 132kV | I54 Busines Park 33/11kv | Primary Substation | 11 | Hydrogen Evolution | 0.50707 | 0.53114 | 0.5597 | 0.62843 | 0.79654 | 0.91589 | 1.0493 | 1.1307 | 1.1904 | 1.2578 | 1.3274 | 1.4061 | 1.5134 | 1.6068 | 1.7693 | 1.8199 | 1.9428 | 2.0044 | 1.25 | 1.3001 | 1.3593 | 1.519 | 1.9248 | 2.2037 | 2.5155 | 2.6853 | 2.8081 | 2.9464 | 3.0888 | 3.2542 | 3.4919 | 3.6979 | 4.0766 | 4.1803 | 4.4381 | 4.5751
West Midlands | Bushbury 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.1304 | 1.3433 | 1.6428 | 2.0026 | 2.4101 | 2.8226 | 3.2761 | 3.8402 | 4.2792 | 4.7861 | 5.2959 | 5.8066 | 6.3505 | 6.8796 | 7.5336 | 8.2727 | 10.5978 | 11.5341 | 2.4655 | 2.9142 | 3.5421 | 4.2953 | 5.1571 | 6.0324 | 6.9979 | 8.1844 | 9.1139 | 10.1941 | 11.2704 | 12.3379 | 13.4671 | 14.5627 | 15.9771 | 17.6034 | 22.4829 | 24.5145
West Midlands | Bushbury 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.2597 | 1.6942 | 2.2997 | 3.045 | 3.8802 | 4.7779 | 5.8171 | 6.9506 | 7.8836 | 8.6861 | 9.4444 | 10.4911 | 11.4019 | 11.7626 | 12.0411 | 12.3046 | 13.5632 | 14.5127 | 2.7453 | 3.6664 | 4.9596 | 6.5564 | 8.3517 | 10.2803 | 12.499 | 14.8957 | 16.8635 | 18.5677 | 20.1921 | 22.5492 | 24.6585 | 25.4553 | 26.0806 | 26.6771 | 29.5512 | 31.7883
West Midlands | Bushbury 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.2195 | 1.5704 | 2.0405 | 2.5692 | 3.2498 | 3.9712 | 4.7843 | 5.6161 | 6.3358 | 7.1998 | 8.543 | 9.3644 | 10.1149 | 10.7617 | 11.3817 | 11.9412 | 13.732 | 14.5027 | 2.6756 | 3.447 | 4.4775 | 5.621 | 7.1068 | 8.6831 | 10.4596 | 12.2387 | 13.7899 | 15.6835 | 18.7567 | 20.5356 | 22.1459 | 23.5147 | 24.8296 | 26.0232 | 29.9651 | 31.7258
West Midlands | Bushbury 132kV | Stafford 132/25/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.1794 | 1.4798 | 1.8941 | 2.4088 | 3.0452 | 3.6875 | 4.4501 | 5.2999 | 5.9809 | 6.7196 | 7.4412 | 8.2908 | 9.4026 | 10.1242 | 10.6927 | 11.2006 | 12.6871 | 13.5646 | 2.5706 | 3.2144 | 4.0979 | 5.2059 | 6.5914 | 7.9772 | 9.6283 | 11.4332 | 12.8787 | 14.4455 | 15.9582 | 17.8009 | 20.3074 | 21.8632 | 23.0496 | 24.1161 | 27.3698 | 29.3972
West Midlands | Bushbury 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Counterfactual | 2.1967 | 2.3953 | 2.6344 | 2.9068 | 3.2167 | 3.5617 | 3.9591 | 4.5829 | 5.0841 | 5.6197 | 6.1493 | 6.686 | 7.2809 | 7.8739 | 8.4604 | 7.7819 | 10.4709 | 11.4141 | 5.2699 | 5.6838 | 6.1812 | 6.7479 | 7.3939 | 8.1139 | 8.9444 | 10.2345 | 11.2801 | 12.4019 | 13.5013 | 14.606 | 15.8238 | 17.0363 | 18.2373 | 16.2755 | 21.8114 | 23.8507
West Midlands | Bushbury 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | 2.3871 | 2.8671 | 3.4734 | 4.1539 | 4.9228 | 5.765 | 6.7638 | 7.9671 | 9.0523 | 9.9538 | 10.779 | 11.5755 | 12.1014 | 12.4061 | 12.6011 | 11.5761 | 12.5111 | 13.4594 | 5.6834 | 6.6853 | 7.9593 | 9.3864 | 10.9952 | 12.7554 | 14.832 | 17.318 | 19.5697 | 21.4524 | 23.1904 | 24.8687 | 26.0007 | 26.6696 | 27.1162 | 24.4931 | 26.6809 | 28.9046
West Midlands | Bushbury 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | 2.3276 | 2.6325 | 3.0024 | 3.4152 | 3.9113 | 4.4543 | 5.1004 | 6.0048 | 6.8087 | 7.6519 | 8.5386 | 9.3929 | 10.2223 | 10.9602 | 11.6473 | 11.0496 | 12.7977 | 13.6225 | 5.5809 | 6.2448 | 7.0393 | 7.9265 | 8.9895 | 10.1514 | 11.5319 | 13.4341 | 15.1386 | 16.9176 | 18.783 | 20.5831 | 22.3297 | 23.8714 | 25.3104 | 23.5489 | 27.3852 | 29.285
West Midlands | Bushbury 132kV | STAFFORD SOUTH 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | 2.2681 | 2.5225 | 2.8572 | 3.2387 | 3.6975 | 4.2158 | 4.8252 | 5.6732 | 6.42 | 7.2335 | 8.0641 | 8.8797 | 9.6551 | 10.3569 | 11.0095 | 10.3525 | 11.8354 | 12.6551 | 5.4238 | 5.9597 | 6.6615 | 7.4652 | 8.4364 | 9.5306 | 10.809 | 12.5652 | 14.121 | 15.8152 | 17.5314 | 19.2188 | 20.8174 | 22.2593 | 23.6023 | 21.6968 | 24.907 | 26.8042
West Midlands | Bushbury 132kV | Wednesfield 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 2.0653 | 2.3599 | 3.1362 | 3.553 | 3.9742 | 4.4589 | 5.0035 | 5.8659 | 6.5409 | 7.2685 | 8.0281 | 8.824 | 9.7077 | 10.5885 | 11.4781 | 12.3391 | 16.5292 | 17.6225 | 4.9461 | 5.5605 | 7.1377 | 7.9989 | 8.867 | 9.8654 | 10.9859 | 12.748 | 14.1333 | 15.6282 | 17.1888 | 18.8201 | 20.6257 | 22.426 | 24.2541 | 26.0093 | 34.6095 | 36.9179
West Midlands | Bushbury 132kV | Wednesfield 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 2.3381 | 3.0449 | 4.3051 | 5.2375 | 6.2708 | 7.4405 | 8.8568 | 10.5785 | 12.0815 | 13.3248 | 14.4433 | 15.5844 | 16.3017 | 16.7444 | 17.0537 | 17.3619 | 18.7628 | 19.87 | 5.5391 | 7.0176 | 9.6018 | 11.5319 | 13.6643 | 16.0833 | 19.0107 | 22.548 | 25.636 | 28.2057 | 30.5267 | 32.9156 | 34.4271 | 35.3811 | 36.0706 | 36.7596 | 39.9248 | 42.4587
West Midlands | Bushbury 132kV | Wednesfield 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 2.2534 | 2.7117 | 3.6875 | 4.2811 | 4.9893 | 5.8399 | 6.8111 | 8.0869 | 9.193 | 10.4078 | 11.61 | 12.7901 | 13.9455 | 15.0125 | 16.0325 | 16.9446 | 19.6069 | 20.7231 | 5.3934 | 6.3923 | 8.42 | 9.6861 | 11.1937 | 13.0104 | 15.0678 | 17.7263 | 20.0389 | 22.5978 | 25.0921 | 27.5439 | 29.9453 | 32.161 | 34.2866 | 36.1946 | 41.9882 | 44.5322
West Midlands | Bushbury 132kV | Wednesfield 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 2.1676 | 2.5495 | 3.4575 | 4.0079 | 4.6309 | 5.3612 | 6.2522 | 7.4946 | 8.5429 | 9.6721 | 10.8632 | 12.0822 | 13.2153 | 14.2447 | 15.2247 | 16.0917 | 18.2574 | 19.2037 | 5.1668 | 5.9744 | 7.8336 | 8.9831 | 10.2828 | 11.8074 | 13.668 | 16.2313 | 18.3959 | 20.7236 | 23.1735 | 25.704 | 28.0309 | 30.1436 | 32.1597 | 33.9486 | 38.5497 | 40.6933
West Midlands | Bustleholm 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.4704 | 1.6437 | 1.846 | 2.0793 | 2.3634 | 2.6854 | 3.0443 | 3.6266 | 4.0594 | 4.5439 | 5.0725 | 5.6281 | 6.2425 | 6.8334 | 7.3717 | 7.9079 | 10.3234 | 11.2553 | 3.0613 | 3.4252 | 3.8441 | 4.3271 | 4.9142 | 5.5792 | 6.32 | 7.531 | 8.4223 | 9.4313 | 10.5454 | 11.7088 | 12.9882 | 14.2131 | 15.313 | 16.4072 | 21.343 | 23.292
West Midlands | Bustleholm 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.6244 | 2.0263 | 2.5009 | 3.1069 | 3.8016 | 4.5292 | 5.553 | 6.7292 | 7.6452 | 8.5429 | 9.3632 | 10.0891 | 10.5591 | 10.8832 | 11.1181 | 11.3325 | 12.314 | 13.1824 | 3.3937 | 4.2385 | 5.2219 | 6.4827 | 7.9276 | 9.4353 | 11.6268 | 14.1155 | 16.003 | 17.9131 | 19.6557 | 21.1619 | 22.1476 | 22.8389 | 23.3499 | 23.8191 | 26.0049 | 27.9256
West Midlands | Bustleholm 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.5728 | 1.8458 | 2.2252 | 2.6478 | 3.0915 | 3.8192 | 4.5734 | 5.5294 | 6.2411 | 7.0011 | 7.7613 | 8.5425 | 9.3053 | 10.0296 | 10.709 | 11.3112 | 13.0306 | 13.974 | 3.3027 | 3.9025 | 4.7137 | 5.6174 | 6.5629 | 8.1832 | 9.8482 | 11.9024 | 13.3944 | 14.9936 | 16.5707 | 18.1894 | 19.7714 | 21.274 | 22.6853 | 23.9413 | 27.6357 | 29.7428
West Midlands | Bustleholm 132kV | Bentley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.5363 | 1.7566 | 2.0515 | 2.4061 | 2.8157 | 3.2951 | 4.0179 | 4.9483 | 5.6282 | 6.4602 | 7.3183 | 8.1069 | 8.8057 | 9.4494 | 10.0548 | 10.5822 | 11.9673 | 12.6882 | 3.201 | 3.6677 | 4.281 | 5.0212 | 5.8762 | 6.8779 | 8.447 | 10.433 | 11.84 | 13.6031 | 15.4103 | 17.0473 | 18.4809 | 19.8028 | 21.0468 | 22.134 | 25.0649 | 26.6433
West Midlands | Bustleholm 132kV | BUSTLEHOLM 11kV S STN | Bulk Supply Point | 11 | Counterfactual | 0.80643 | 1.0461 | 1.349 | 1.6829 | 2.0465 | 2.4537 | 2.9585 | 3.7278 | 4.3552 | 4.987 | 5.6391 | 6.3225 | 7.0842 | 7.8474 | 8.599 | 9.3404 | 12.6567 | 13.5719 | 1.8064 | 2.3046 | 2.9296 | 3.6189 | 4.3678 | 5.2057 | 6.2458 | 7.8163 | 9.1066 | 10.4031 | 11.7393 | 13.1365 | 14.6893 | 16.2449 | 17.7764 | 19.2861 | 26.0467 | 27.9874
West Midlands | Bustleholm 132kV | BUSTLEHOLM 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | 1.0505 | 1.6656 | 2.3975 | 3.2033 | 4.1386 | 5.1694 | 6.3986 | 7.8951 | 9.2178 | 10.2916 | 11.2748 | 12.2354 | 12.8675 | 13.2582 | 13.5077 | 13.7555 | 14.8885 | 15.9699 | 2.3376 | 3.6187 | 5.1351 | 6.8012 | 8.7331 | 10.8633 | 13.392 | 16.4547 | 19.1674 | 21.3772 | 23.4073 | 25.3899 | 26.7151 | 27.5529 | 28.1063 | 28.6553 | 31.1839 | 33.593
West Midlands | Bustleholm 132kV | BUSTLEHOLM 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | 0.97653 | 1.367 | 1.8212 | 2.3273 | 2.9275 | 3.6194 | 4.4279 | 5.5106 | 6.4517 | 7.4419 | 8.5219 | 9.5952 | 10.6514 | 11.642 | 12.5554 | 13.3772 | 15.6579 | 16.7813 | 2.2111 | 3.0576 | 4.0243 | 5.1026 | 6.3788 | 7.8452 | 9.5465 | 11.7922 | 13.754 | 15.8092 | 18.0448 | 20.2664 | 22.4533 | 24.504 | 26.3983 | 28.108 | 33.0079 | 35.5361
West Midlands | Bustleholm 132kV | BUSTLEHOLM 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | 0.89405 | 1.2262 | 1.6622 | 2.1149 | 2.6423 | 3.2697 | 4.0077 | 5.0464 | 5.9398 | 6.8848 | 7.8881 | 8.8846 | 9.8631 | 10.7729 | 11.6157 | 12.3763 | 14.2059 | 15.0735 | 1.9961 | 2.6946 | 3.6026 | 4.5465 | 5.646 | 6.9536 | 8.4843 | 10.6162 | 12.4566 | 14.3953 | 16.4478 | 18.4873 | 20.4902 | 22.3532 | 24.0805 | 25.6423 | 29.498 | 31.4192
West Midlands | Bustleholm 132kV | Kingstanding 132/11kVDummy | Bulk Supply Point | 11 | Counterfactual | 1.2546 | 1.5629 | 1.9279 | 2.3294 | 2.5833 | 3.0661 | 3.6216 | 4.5023 | 5.1922 | 5.9289 | 6.6867 | 7.484 | 8.3676 | 9.2511 | 10.1168 | 10.9746 | 14.8002 | 15.8768 | 2.807 | 3.4497 | 4.2049 | 5.0354 | 5.4773 | 6.4723 | 7.616 | 9.413 | 10.8305 | 12.344 | 13.8969 | 15.5248 | 17.3229 | 19.1196 | 20.8797 | 22.6227 | 30.4068 | 32.7047
West Midlands | Bustleholm 132kV | Kingstanding 132/11kVDummy | Bulk Supply Point | 11 | Electric Engagement | 1.5575 | 2.3156 | 3.2016 | 4.2016 | 5.1259 | 6.3514 | 7.816 | 9.6177 | 11.2028 | 12.4768 | 13.612 | 14.7223 | 15.4005 | 15.7774 | 15.9735 | 16.1595 | 17.0243 | 18.1151 | 3.4661 | 5.0469 | 6.8855 | 8.9556 | 10.7809 | 13.3096 | 16.3186 | 20.0023 | 23.2513 | 25.8695 | 28.2148 | 30.5056 | 31.9293 | 32.7422 | 33.1905 | 33.6179 | 35.6335 | 38.1279
West Midlands | Bustleholm 132kV | Kingstanding 132/11kVDummy | Bulk Supply Point | 11 | Holistic Transition | 1.4657 | 1.9459 | 2.4998 | 3.116 | 3.6179 | 4.4123 | 5.3489 | 6.6219 | 7.7172 | 8.885 | 10.1264 | 11.3816 | 12.6183 | 13.7544 | 14.795 | 15.6903 | 17.9076 | 19.0567 | 3.3092 | 4.3529 | 5.5352 | 6.8498 | 7.8454 | 9.527 | 11.4972 | 14.1338 | 16.4157 | 18.837 | 21.4055 | 24.0046 | 26.5652 | 28.9146 | 31.0702 | 32.9286 | 37.7086 | 40.354
West Midlands | Bustleholm 132kV | Kingstanding 132/11kVDummy | Bulk Supply Point | 11 | Hydrogen Evolution | 1.3625 | 1.7623 | 2.2539 | 2.7926 | 3.2206 | 3.935 | 4.7862 | 6.0121 | 7.0508 | 8.1554 | 9.3124 | 10.443 | 11.5584 | 12.583 | 13.5219 | 14.3457 | 16.1058 | 16.9911 | 3.0405 | 3.8818 | 4.9071 | 6.0309 | 6.845 | 8.3322 | 10.0946 | 12.608 | 14.746 | 17.0096 | 19.3723 | 21.6788 | 23.956 | 26.0463 | 27.9628 | 29.6473 | 33.3654 | 35.3666
West Midlands | Bustleholm 132kV | Ladywood 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.5423 | 1.6812 | 1.9011 | 2.2344 | 2.4468 | 2.6853 | 2.9019 | 3.1839 | 3.8451 | 4.5539 | 4.8187 | 5.0999 | 5.3887 | 5.6695 | 5.9503 | 6.2521 | 7.6359 | 7.9807 | 3.7926 | 4.0849 | 4.5396 | 5.2724 | 5.7373 | 6.2463 | 6.6953 | 7.2763 | 8.8203 | 10.4633 | 11.0115 | 11.593 | 12.1874 | 12.7637 | 13.3385 | 13.9568 | 16.797 | 17.5113
West Midlands | Bustleholm 132kV | Ladywood 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.6041 | 1.8456 | 2.1922 | 2.965 | 3.5148 | 3.9275 | 4.4039 | 4.9965 | 7.1443 | 7.9738 | 8.4821 | 8.8991 | 9.1504 | 8.342 | 8.1493 | 8.3732 | 9.385 | 10.0186 | 3.9278 | 4.4425 | 5.1694 | 6.9554 | 8.2088 | 9.0787 | 10.0777 | 11.3172 | 16.4629 | 18.3216 | 19.3823 | 20.2451 | 20.7585 | 18.647 | 18.0814 | 18.5522 | 20.683 | 22.005
West Midlands | Bustleholm 132kV | Ladywood 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.5858 | 1.78 | 2.0511 | 2.8825 | 3.1894 | 3.5883 | 4.0534 | 4.5813 | 6.9747 | 7.5131 | 7.8685 | 8.2277 | 7.1975 | 7.5418 | 7.8715 | 8.2268 | 9.4451 | 11.2368 | 3.8956 | 4.32 | 4.899 | 6.869 | 7.5615 | 8.4194 | 9.4157 | 10.533 | 16.3213 | 17.4692 | 18.1966 | 18.9292 | 16.1902 | 16.8924 | 17.5649 | 18.3014 | 20.8559 | 25.1073
West Midlands | Bustleholm 132kV | Ladywood 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.5725 | 1.7478 | 2.0377 | 2.7249 | 3.1828 | 3.5565 | 3.955 | 4.4786 | 6.4672 | 7.3795 | 8.4358 | 8.7683 | 9.0714 | 9.3591 | 9.6405 | 9.9629 | 11.0007 | 11.4132 | 3.8587 | 4.2353 | 4.8453 | 6.4495 | 7.5139 | 8.3183 | 9.1622 | 10.2642 | 15.0448 | 17.1121 | 19.5607 | 20.2376 | 20.8508 | 21.4328 | 22.0017 | 22.6668 | 24.8301 | 25.6937
West Midlands | Bustleholm 132kV | Perry Barr 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 0.7027 | 0.99535 | 1.4233 | 1.8217 | 2.1932 | 2.5933 | 3.0395 | 3.7598 | 4.3806 | 4.9775 | 5.6038 | 6.2669 | 7.0116 | 7.758 | 8.5218 | 9.3066 | 12.8876 | 13.767 | 1.5666 | 2.1785 | 3.0594 | 3.8854 | 4.6546 | 5.479 | 6.3938 | 7.8575 | 9.1572 | 10.3761 | 11.6546 | 13.0056 | 14.5188 | 16.035 | 17.5904 | 19.1902 | 26.5067 | 28.3658
West Midlands | Bustleholm 132kV | Perry Barr 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 0.96175 | 1.7197 | 2.5095 | 3.4299 | 4.3914 | 5.3979 | 6.606 | 8.1015 | 9.5852 | 10.6442 | 11.5867 | 12.5049 | 13.0532 | 13.3541 | 13.5285 | 13.7477 | 14.6831 | 15.459 | 2.131 | 3.7109 | 5.3512 | 7.2693 | 9.2671 | 11.3378 | 13.8127 | 16.8638 | 19.9744 | 22.1456 | 24.0872 | 25.9762 | 27.1209 | 27.7677 | 28.1636 | 28.6598 | 30.8107 | 32.5844
West Midlands | Bustleholm 132kV | Perry Barr 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 0.88354 | 1.4079 | 1.9275 | 2.5508 | 3.1233 | 3.7924 | 4.5756 | 5.6507 | 6.7411 | 7.7213 | 8.7262 | 9.7428 | 10.7399 | 11.6627 | 12.5141 | 13.3223 | 15.3835 | 16.2742 | 1.9969 | 3.1263 | 4.238 | 5.5851 | 6.8056 | 8.2197 | 9.8633 | 12.0864 | 14.4235 | 16.4524 | 18.5234 | 20.6209 | 22.6792 | 24.5841 | 26.3451 | 28.0305 | 32.4824 | 34.5416
West Midlands | Bustleholm 132kV | Perry Barr 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 0.80001 | 1.2545 | 1.7203 | 2.2697 | 2.8179 | 3.419 | 4.1316 | 5.1675 | 6.2095 | 7.1398 | 8.1264 | 9.0753 | 10.0048 | 10.8591 | 11.6522 | 12.414 | 14.1328 | 14.7619 | 1.778 | 2.7305 | 3.706 | 4.8645 | 6.0202 | 7.2693 | 8.7406 | 10.8599 | 13.074 | 14.9748 | 16.9877 | 18.9198 | 20.814 | 22.5547 | 24.1732 | 25.7414 | 29.3852 | 30.7995
West Midlands | Bustleholm 132kV | Rushall 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 2.4987 | 2.8245 | 3.2355 | 3.6927 | 4.2514 | 4.8797 | 5.579 | 6.6251 | 7.4253 | 8.2823 | 9.1713 | 9.4356 | 10.4527 | 11.4679 | 12.4411 | 13.4147 | 17.0757 | 18.4843 | 6.0215 | 6.7023 | 7.5519 | 8.4972 | 9.6525 | 10.9515 | 12.3961 | 14.5441 | 16.1904 | 17.9584 | 19.7947 | 20.0453 | 22.1282 | 24.2044 | 26.1882 | 28.1712 | 35.3318 | 38.3102
West Midlands | Bustleholm 132kV | Rushall 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 2.8097 | 3.6023 | 4.573 | 5.8132 | 7.2129 | 8.6013 | 10.2963 | 12.3455 | 14.0897 | 15.5536 | 16.8953 | 17.5185 | 18.4072 | 18.9906 | 19.3794 | 19.7547 | 20.7755 | 22.3044 | 6.6962 | 8.3536 | 10.3744 | 12.966 | 15.8879 | 18.7705 | 22.298 | 26.5379 | 30.131 | 33.1773 | 35.9735 | 36.9824 | 38.8586 | 40.1128 | 40.9679 | 41.7991 | 43.9062 | 47.3278
West Midlands | Bustleholm 132kV | Rushall 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 2.7158 | 3.2313 | 3.9968 | 4.8626 | 5.6922 | 6.7136 | 7.8655 | 9.3494 | 10.5714 | 11.896 | 13.3411 | 14.1055 | 15.5049 | 16.8136 | 18.0304 | 19.1214 | 21.5036 | 23.113 | 6.5348 | 7.6603 | 9.3015 | 11.1578 | 12.93 | 15.1265 | 17.5854 | 20.6938 | 23.2442 | 26.0061 | 29.0056 | 30.3137 | 33.2214 | 35.939 | 38.4696 | 40.7468 | 45.6321 | 49.2492
West Midlands | Bustleholm 132kV | Rushall 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 2.616 | 3.0432 | 3.6156 | 4.3189 | 5.1119 | 6.028 | 7.1336 | 8.6006 | 9.7894 | 11.1056 | 12.4641 | 13.1196 | 14.4227 | 15.6288 | 16.749 | 17.7492 | 19.5419 | 20.796 | 6.2738 | 7.1749 | 8.3663 | 9.8388 | 11.5003 | 13.4195 | 15.7443 | 18.7867 | 21.2374 | 23.9623 | 26.7589 | 27.8064 | 30.4784 | 32.9525 | 35.2522 | 37.3104 | 40.8406 | 43.6099
West Midlands | Bustleholm 132kV | Smethwick 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 0.34547 | 0.46723 | 0.6049 | 0.76214 | 0.94802 | 1.1873 | 1.5067 | 1.9392 | 2.4491 | 2.7469 | 3.0585 | 3.3814 | 3.7443 | 4.0918 | 4.4427 | 4.7805 | 6.307 | 6.9401 | 0.77468 | 1.0345 | 1.3203 | 1.6485 | 2.0337 | 2.5299 | 3.1941 | 4.0859 | 5.2 | 5.8131 | 6.454 | 7.1153 | 7.8567 | 8.567 | 9.2904 | 9.9785 | 13.0985 | 14.4206
West Midlands | Bustleholm 132kV | Smethwick 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 0.44709 | 0.7834 | 1.1752 | 1.5527 | 2.077 | 2.65 | 3.2408 | 3.9075 | 4.8241 | 5.3332 | 5.812 | 6.3066 | 6.6196 | 6.8389 | 7.0098 | 7.1562 | 7.8499 | 8.4236 | 0.99392 | 1.7154 | 2.5357 | 3.3263 | 4.4252 | 5.6257 | 6.8513 | 8.2208 | 10.2493 | 11.3033 | 12.2977 | 13.3366 | 13.9913 | 14.4572 | 14.826 | 15.1454 | 16.6928 | 17.9657
West Midlands | Bustleholm 132kV | Smethwick 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 0.41583 | 0.67417 | 0.90919 | 1.2521 | 1.6463 | 2.0508 | 2.4808 | 3.0028 | 3.7691 | 4.2785 | 4.7762 | 5.2751 | 5.7643 | 6.2275 | 6.6717 | 7.0635 | 8.2129 | 8.866 | 0.93952 | 1.517 | 2.0219 | 2.7641 | 3.6117 | 4.4741 | 5.3863 | 6.4733 | 8.2057 | 9.2857 | 10.3177 | 11.3533 | 12.3698 | 13.3324 | 14.2568 | 15.0757 | 17.5508 | 19.0071
West Midlands | Bustleholm 132kV | Smethwick 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 0.38665 | 0.5995 | 0.85986 | 1.1695 | 1.5288 | 1.889 | 2.2791 | 2.7679 | 3.5197 | 3.994 | 4.4858 | 4.998 | 5.4581 | 5.8736 | 6.2683 | 6.6117 | 7.5172 | 8.0085 | 0.86229 | 1.3243 | 1.8726 | 2.5297 | 3.2885 | 4.0452 | 4.8588 | 5.8615 | 7.5507 | 8.5263 | 9.5358 | 10.6027 | 11.5464 | 12.3993 | 13.21 | 13.9181 | 15.8358 | 16.9077
West Midlands | Bustleholm 132kV | Winson Green 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.1503 | 1.3489 | 1.602 | 1.8681 | 2.1632 | 2.5679 | 3.0307 | 3.6596 | 4.3219 | 4.8802 | 5.4304 | 6.0352 | 6.6959 | 7.0648 | 7.7899 | 8.7253 | 13.3376 | 14.0444 | 2.5624 | 2.9805 | 3.5044 | 4.0564 | 4.6682 | 5.5089 | 6.4697 | 7.7649 | 9.1935 | 10.3547 | 11.4947 | 12.7472 | 14.1123 | 14.739 | 16.2428 | 18.197 | 27.8646 | 29.3463
West Midlands | Bustleholm 132kV | Winson Green 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.304 | 1.757 | 2.2958 | 2.8753 | 3.5532 | 4.5303 | 5.6401 | 7.0213 | 8.5695 | 9.6254 | 10.6694 | 11.763 | 12.5776 | 12.9388 | 13.5371 | 14.1451 | 16.3316 | 17.2452 | 2.8962 | 3.8541 | 4.9761 | 6.1845 | 7.6001 | 9.6604 | 11.9912 | 14.8843 | 18.2605 | 20.4898 | 22.6939 | 25.0065 | 26.7467 | 27.4218 | 28.726 | 30.053 | 34.839 | 36.8183
West Midlands | Bustleholm 132kV | Winson Green 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.2577 | 1.5822 | 1.9565 | 2.3826 | 2.8414 | 3.8199 | 4.9597 | 6.2001 | 7.6674 | 8.8739 | 9.8827 | 10.8925 | 11.8862 | 12.5305 | 13.4499 | 14.2553 | 16.8266 | 17.7675 | 2.8161 | 3.5305 | 4.3301 | 5.2475 | 6.2296 | 8.344 | 10.8004 | 13.4394 | 16.6918 | 19.2704 | 21.3918 | 23.514 | 25.604 | 26.8385 | 28.7769 | 30.4766 | 36.0092 | 38.0809
West Midlands | Bustleholm 132kV | Winson Green 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.2116 | 1.4802 | 1.8462 | 2.2369 | 2.6749 | 3.4772 | 4.3668 | 5.5391 | 6.8798 | 7.9308 | 9.0323 | 10.0451 | 11.0219 | 11.6372 | 12.5335 | 13.3738 | 15.7796 | 16.4787 | 2.6946 | 3.2676 | 4.0328 | 4.8554 | 5.78 | 7.4946 | 9.3875 | 11.8634 | 14.8217 | 17.0416 | 19.3586 | 21.4832 | 23.5312 | 24.6982 | 26.5828 | 28.3548 | 33.5031 | 35.0073
West Midlands | Cellarhead 132kV | BEARSTONE | Primary Substation | 11 | Counterfactual | 0.096953 | 0.10793 | 0.12134 | 0.13808 | 0.15784 | 0.18485 | 0.21676 | 0.26263 | 0.30151 | 0.34339 | 0.38183 | 0.41837 | 0.45784 | 0.49448 | 0.53056 | 0.56711 | 0.7612 | 0.86339 | 0.22927 | 0.25268 | 0.28133 | 0.3172 | 0.35954 | 0.41738 | 0.48643 | 0.58471 | 0.66897 | 0.76081 | 0.84358 | 0.92099 | 1.0037 | 1.08 | 1.1551 | 1.2311 | 1.6416 | 1.8687
West Midlands | Cellarhead 132kV | BEARSTONE | Primary Substation | 11 | Electric Engagement | 0.10712 | 0.13493 | 0.17411 | 0.22483 | 0.28265 | 0.34817 | 0.42307 | 0.50999 | 0.59258 | 0.66782 | 0.7415 | 0.81088 | 0.86562 | 0.90232 | 0.93424 | 0.96739 | 1.1498 | 1.2809 | 0.25137 | 0.31067 | 0.39606 | 0.50499 | 0.62853 | 0.769 | 0.92889 | 1.1137 | 1.29 | 1.4519 | 1.6122 | 1.7629 | 1.8841 | 1.9652 | 2.0365 | 2.1107 | 2.5202 | 2.8309
West Midlands | Cellarhead 132kV | BEARSTONE | Primary Substation | 11 | Holistic Transition | 0.10421 | 0.12385 | 0.14353 | 0.17771 | 0.2109 | 0.25904 | 0.31526 | 0.38636 | 0.45525 | 0.52385 | 0.59918 | 0.67237 | 0.74234 | 0.79899 | 0.85574 | 0.90737 | 1.111 | 1.2008 | 0.24647 | 0.29066 | 0.33319 | 0.40744 | 0.47953 | 0.58412 | 0.70803 | 0.86216 | 1.0138 | 1.1628 | 1.3263 | 1.486 | 1.638 | 1.7586 | 1.8795 | 1.9902 | 2.4391 | 2.6423
West Midlands | Cellarhead 132kV | BEARSTONE | Primary Substation | 11 | Hydrogen Evolution | 0.10069 | 0.11509 | 0.13343 | 0.15884 | 0.18914 | 0.23113 | 0.27962 | 0.34107 | 0.39788 | 0.46452 | 0.5264 | 0.58495 | 0.64214 | 0.68943 | 0.73835 | 0.78245 | 0.95839 | 1.0879 | 0.23734 | 0.26834 | 0.30771 | 0.36237 | 0.4281 | 0.51924 | 0.62412 | 0.75513 | 0.8773 | 1.021 | 1.1524 | 1.2768 | 1.3975 | 1.4964 | 1.5988 | 1.692 | 2.0802 | 2.3796
West Midlands | Cellarhead 132kV | Boothen 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 2.6603 | 2.8385 | 3.3611 | 3.6076 | 3.9448 | 4.3069 | 4.6982 | 5.2918 | 5.7252 | 6.228 | 6.7944 | 7.3967 | 8.065 | 8.7395 | 9.4017 | 10.0324 | 12.7855 | 13.4827 | 6.5206 | 6.8933 | 7.9537 | 8.464 | 9.166 | 9.9218 | 10.7312 | 11.9609 | 12.8537 | 13.9033 | 15.1003 | 16.3636 | 17.7578 | 19.1589 | 20.5198 | 21.8144 | 27.4635 | 28.9333
West Midlands | Cellarhead 132kV | Boothen 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 2.8269 | 3.5318 | 4.0789 | 4.8155 | 5.69 | 6.5315 | 7.6129 | 8.8399 | 9.9159 | 11.0405 | 12.2353 | 13.3479 | 13.9952 | 12.4924 | 12.7769 | 13.0693 | 14.4458 | 15.658 | 6.8825 | 8.3335 | 9.4688 | 11.0169 | 12.8715 | 14.6269 | 16.9198 | 19.5103 | 21.7362 | 24.1408 | 26.6784 | 29.0134 | 30.3727 | 26.4682 | 27.0745 | 27.6968 | 30.6442 | 33.237
West Midlands | Cellarhead 132kV | Boothen 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 2.7776 | 3.3404 | 3.8625 | 4.4125 | 4.9402 | 5.6679 | 6.437 | 7.6968 | 8.6698 | 9.6472 | 10.6664 | 11.5295 | 10.4965 | 11.2839 | 12.0267 | 12.7051 | 16.6684 | 17.7847 | 6.798 | 7.9768 | 9.1012 | 10.2859 | 11.4172 | 13.0157 | 14.7095 | 17.4402 | 19.4962 | 21.5652 | 23.6915 | 25.4719 | 22.522 | 24.1442 | 25.6757 | 27.0779 | 36.182 | 38.5996
West Midlands | Cellarhead 132kV | Boothen 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 2.7224 | 3.2288 | 3.5909 | 4.0142 | 4.5297 | 5.0543 | 5.7472 | 6.688 | 8.4108 | 9.3975 | 10.5107 | 11.5185 | 12.3936 | 13.1698 | 13.8452 | 14.4757 | 16.2512 | 17.0992 | 6.6544 | 7.6931 | 8.4427 | 9.336 | 10.4409 | 11.5423 | 13.0278 | 15.0321 | 19.0118 | 21.1159 | 23.4702 | 25.5753 | 27.3808 | 28.9795 | 30.3639 | 31.6592 | 35.3811 | 37.1969
West Midlands | Cellarhead 132kV | Burslem 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 2.3682 | 2.5813 | 2.8418 | 3.1257 | 3.4843 | 3.883 | 4.3191 | 5.0025 | 5.492 | 6.0554 | 6.662 | 7.3043 | 8.0311 | 8.7291 | 9.3821 | 10.0233 | 12.7387 | 12.3671 | 5.7325 | 6.18 | 6.7188 | 7.306 | 8.0477 | 8.8719 | 9.7716 | 11.1831 | 12.1873 | 13.3533 | 14.6174 | 15.9497 | 17.451 | 18.888 | 20.2211 | 21.5278 | 27.0578 | 25.8096
West Midlands | Cellarhead 132kV | Burslem 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 2.5785 | 3.0995 | 3.7124 | 4.4671 | 5.3266 | 6.213 | 7.3838 | 8.7527 | 9.9485 | 11.0662 | 12.1154 | 13.0759 | 13.5949 | 12.8033 | 13.0564 | 13.2931 | 14.3603 | 15.2669 | 6.1919 | 7.2866 | 8.5567 | 10.1265 | 11.9128 | 13.7465 | 16.2152 | 19.0725 | 21.5396 | 23.8925 | 26.1019 | 28.1003 | 29.1794 | 27.0629 | 27.6119 | 28.1277 | 30.4865 | 32.4808
West Midlands | Cellarhead 132kV | Burslem 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 2.5184 | 2.8668 | 3.3422 | 3.8605 | 4.3842 | 5.1374 | 5.9709 | 7.1598 | 8.1185 | 9.0516 | 9.97 | 10.8738 | 11.7693 | 11.4517 | 12.2422 | 12.9462 | 14.8885 | 15.8409 | 6.0885 | 6.8546 | 7.8704 | 8.9794 | 10.0949 | 11.7466 | 13.5567 | 16.0824 | 18.0981 | 20.0535 | 21.9507 | 23.8154 | 25.6654 | 24.5084 | 26.1441 | 27.6063 | 31.7525 | 33.8775
West Midlands | Cellarhead 132kV | Burslem 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 2.4549 | 2.7353 | 3.1071 | 3.5573 | 4.0668 | 4.6401 | 5.4203 | 6.4202 | 7.2614 | 8.2246 | 9.2786 | 10.2673 | 11.0892 | 10.686 | 11.3812 | 11.9906 | 13.4136 | 14.0655 | 5.9226 | 6.5163 | 7.2886 | 8.2301 | 9.2962 | 10.4924 | 12.1604 | 14.2608 | 16.001 | 18.0171 | 20.2169 | 22.2647 | 23.9442 | 22.592 | 24.0118 | 25.2581 | 28.238 | 29.6606
West Midlands | Cellarhead 132kV | CAULDON | Primary Substation | 11 | Counterfactual | 0.14055 | 0.16766 | 0.19382 | 0.22391 | 0.25914 | 0.30425 | 0.35942 | 0.43788 | 0.50402 | 0.58019 | 0.68211 | 0.77723 | 0.87367 | 0.95577 | 1.0196 | 1.0849 | 1.4143 | 1.6005 | 0.31657 | 0.37751 | 0.43476 | 0.5005 | 0.5773 | 0.6758 | 0.79805 | 0.9685 | 1.114 | 1.2834 | 1.5156 | 1.7295 | 1.9433 | 2.1221 | 2.2563 | 2.3931 | 3.0952 | 3.5105
West Midlands | Cellarhead 132kV | CAULDON | Primary Substation | 11 | Electric Engagement | 0.15704 | 0.22509 | 0.30198 | 0.38934 | 0.48438 | 0.60482 | 0.7676 | 0.97056 | 1.2046 | 1.3587 | 1.4835 | 1.5985 | 1.6948 | 1.7726 | 1.8239 | 1.8829 | 2.1476 | 2.3697 | 0.35219 | 0.50544 | 0.67633 | 0.86796 | 1.0749 | 1.3389 | 1.7029 | 2.1575 | 2.6958 | 3.0406 | 3.3161 | 3.5685 | 3.7835 | 3.9538 | 4.0711 | 4.2036 | 4.8165 | 5.3526
West Midlands | Cellarhead 132kV | CAULDON | Primary Substation | 11 | Holistic Transition | 0.15208 | 0.21361 | 0.25588 | 0.31459 | 0.39473 | 0.51781 | 0.68336 | 0.86711 | 1.013 | 1.1266 | 1.248 | 1.3642 | 1.4826 | 1.5953 | 1.6885 | 1.7816 | 2.0973 | 2.2551 | 0.34365 | 0.48917 | 0.5835 | 0.71494 | 0.89349 | 1.1772 | 1.5656 | 1.9882 | 2.3217 | 2.5709 | 2.8365 | 3.0916 | 3.3506 | 3.5914 | 3.7932 | 3.9946 | 4.7071 | 5.0753
West Midlands | Cellarhead 132kV | CAULDON | Primary Substation | 11 | Hydrogen Evolution | 0.14717 | 0.18465 | 0.22477 | 0.27156 | 0.33402 | 0.41552 | 0.52535 | 0.6842 | 0.87512 | 1.0355 | 1.1439 | 1.2415 | 1.3393 | 1.4279 | 1.5072 | 1.5806 | 1.85 | 2.0549 | 0.33072 | 0.41574 | 0.50358 | 0.60567 | 0.74265 | 0.92332 | 1.1708 | 1.5291 | 1.9735 | 2.3357 | 2.5673 | 2.7753 | 2.9823 | 3.1678 | 3.335 | 3.4902 | 4.0923 | 4.5732
West Midlands | Cellarhead 132kV | CHEADLE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.25719 | 0.31108 | 0.37811 | 0.45352 | 0.53016 | 0.62439 | 0.74345 | 0.90968 | 1.0448 | 1.1942 | 1.3437 | 1.4933 | 1.6563 | 1.8152 | 1.9789 | 2.1527 | 2.8766 | 3.1517 | 0.5915 | 0.70637 | 0.84801 | 1.0066 | 1.1676 | 1.3658 | 1.6225 | 1.9698 | 2.2549 | 2.5721 | 2.886 | 3.1965 | 3.5323 | 3.859 | 4.1998 | 4.5637 | 6.0665 | 6.6661
West Midlands | Cellarhead 132kV | CHEADLE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.30584 | 0.44322 | 0.61613 | 0.80621 | 1.0096 | 1.3001 | 1.5826 | 1.9245 | 2.2227 | 2.4734 | 2.7076 | 2.9539 | 3.1296 | 3.2286 | 3.2982 | 3.3639 | 3.7037 | 3.9903 | 0.69699 | 0.9903 | 1.3605 | 1.7621 | 2.1893 | 2.8193 | 3.4123 | 4.1256 | 4.7491 | 5.2771 | 5.775 | 6.3063 | 6.6957 | 6.9129 | 7.0707 | 7.2211 | 8.0079 | 8.6884
West Midlands | Cellarhead 132kV | CHEADLE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.29124 | 0.38786 | 0.49245 | 0.61466 | 0.80782 | 0.97255 | 1.1592 | 1.4028 | 1.6189 | 1.8544 | 2.1444 | 2.3806 | 2.6085 | 2.8127 | 3.0099 | 3.1821 | 3.7077 | 3.9338 | 0.67197 | 0.88896 | 1.1168 | 1.3815 | 1.8075 | 2.1619 | 2.5647 | 3.0803 | 3.542 | 4.0457 | 4.6787 | 5.1805 | 5.6641 | 6.0932 | 6.508 | 6.8726 | 8.0312 | 8.5533
West Midlands | Cellarhead 132kV | CHEADLE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.27501 | 0.3498 | 0.44801 | 0.55397 | 0.68704 | 0.88777 | 1.0627 | 1.2991 | 1.4992 | 1.721 | 1.9414 | 2.1635 | 2.3959 | 2.5885 | 2.7677 | 2.9224 | 3.3613 | 3.6178 | 0.62983 | 0.79165 | 1.0023 | 1.2268 | 1.5102 | 1.9544 | 2.3252 | 2.8188 | 3.2384 | 3.7037 | 4.1614 | 4.6268 | 5.12 | 5.5208 | 5.8909 | 6.2123 | 7.1702 | 7.7661
West Midlands | Cellarhead 132kV | CHEDDLETON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.11775 | 0.14612 | 0.18083 | 0.22026 | 0.26582 | 0.32015 | 0.38397 | 0.48079 | 0.56651 | 0.64651 | 0.72505 | 0.80339 | 0.88814 | 0.97106 | 1.0514 | 1.1319 | 1.5162 | 1.6655 | 0.26872 | 0.32944 | 0.40373 | 0.48852 | 0.5866 | 0.70397 | 0.84254 | 1.0494 | 1.2353 | 1.4065 | 1.5724 | 1.7356 | 1.9106 | 2.0813 | 2.2468 | 2.4121 | 3.2103 | 3.5377
West Midlands | Cellarhead 132kV | CHEDDLETON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.14612 | 0.22063 | 0.31697 | 0.42798 | 0.55355 | 0.70406 | 0.87574 | 1.078 | 1.2579 | 1.3932 | 1.517 | 1.6351 | 1.7165 | 1.767 | 1.8038 | 1.8381 | 2.0107 | 2.1682 | 0.33113 | 0.49146 | 0.70105 | 0.94228 | 1.2147 | 1.5423 | 1.9132 | 2.346 | 2.7331 | 3.019 | 3.2838 | 3.5353 | 3.7132 | 3.8247 | 3.9088 | 3.988 | 4.3934 | 4.7699
West Midlands | Cellarhead 132kV | CHEDDLETON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.13828 | 0.19085 | 0.24956 | 0.32326 | 0.41923 | 0.53207 | 0.65543 | 0.80804 | 0.94564 | 1.066 | 1.1925 | 1.3192 | 1.442 | 1.5511 | 1.6548 | 1.747 | 2.0183 | 2.1299 | 0.31763 | 0.43642 | 0.56663 | 0.73173 | 0.94582 | 1.1978 | 1.4731 | 1.8064 | 2.1101 | 2.3655 | 2.6346 | 2.9044 | 3.1656 | 3.395 | 3.6134 | 3.8089 | 4.41 | 4.6699
West Midlands | Cellarhead 132kV | CHEDDLETON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.13035 | 0.17327 | 0.2287 | 0.29586 | 0.3843 | 0.49084 | 0.60729 | 0.75621 | 0.88562 | 1.0056 | 1.1222 | 1.2343 | 1.3421 | 1.4398 | 1.5329 | 1.6143 | 1.8461 | 1.9807 | 0.29679 | 0.39107 | 0.5127 | 0.66097 | 0.85684 | 1.0935 | 1.3502 | 1.6719 | 1.9537 | 2.2064 | 2.4493 | 2.6827 | 2.9063 | 3.1082 | 3.3011 | 3.4704 | 3.9799 | 4.2975
West Midlands | Cellarhead 132kV | CONGLETON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.74778 | 0.87262 | 1.0157 | 1.1632 | 1.3261 | 1.5094 | 1.7192 | 2.0504 | 2.3088 | 2.5871 | 2.8714 | 3.1666 | 3.4967 | 3.8241 | 4.1472 | 4.4668 | 5.9097 | 6.3284 | 1.6403 | 1.9029 | 2.2005 | 2.5069 | 2.8443 | 3.2239 | 3.6586 | 4.3372 | 4.8704 | 5.4451 | 6.0298 | 6.6334 | 7.3057 | 7.9725 | 8.6325 | 9.2823 | 12.2283 | 13.1149
West Midlands | Cellarhead 132kV | CONGLETON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.85763 | 1.1494 | 1.4898 | 1.8588 | 2.2699 | 2.7258 | 3.2714 | 3.9347 | 4.5233 | 5.0087 | 5.4453 | 5.8744 | 6.1431 | 6.2978 | 6.3927 | 6.4776 | 6.8664 | 7.1906 | 1.8793 | 2.4942 | 3.2061 | 3.9745 | 4.8273 | 5.7721 | 6.899 | 8.2613 | 9.4734 | 10.4776 | 11.386 | 12.2805 | 12.8484 | 13.1835 | 13.3976 | 13.5917 | 14.4988 | 15.2636
West Midlands | Cellarhead 132kV | CONGLETON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.82483 | 1.0235 | 1.2423 | 1.4737 | 1.7301 | 2.0378 | 2.3879 | 2.8699 | 3.2851 | 3.7342 | 4.2013 | 4.6439 | 5.0761 | 5.4782 | 5.8571 | 6.1879 | 7.0649 | 7.4058 | 1.823 | 2.2608 | 2.7309 | 3.2277 | 3.7757 | 4.4295 | 5.1694 | 6.172 | 7.041 | 7.9808 | 8.9514 | 9.8667 | 10.7621 | 11.5967 | 12.3844 | 13.0756 | 14.9905 | 15.7834
West Midlands | Cellarhead 132kV | CONGLETON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.79081 | 0.95095 | 1.1455 | 1.355 | 1.5912 | 1.8668 | 2.1982 | 2.6668 | 3.0657 | 3.5022 | 3.9519 | 4.3958 | 4.8167 | 5.1937 | 5.5488 | 5.8538 | 6.5663 | 6.8474 | 1.7334 | 2.074 | 2.482 | 2.9197 | 3.4128 | 3.9879 | 4.6764 | 5.6391 | 6.4615 | 7.3585 | 8.2794 | 9.1926 | 10.0536 | 10.8245 | 11.5512 | 12.1775 | 13.699 | 14.3396
West Midlands | Cellarhead 132kV | COTES HEATH 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.1206 | 1.1343 | 1.1526 | 1.1739 | 1.1989 | 1.2295 | 1.2675 | 1.3256 | 1.3759 | 1.4329 | 1.4843 | 1.5327 | 1.5838 | 1.633 | 1.681 | 0.72416 | 0.98822 | 1.1453 | 2.7842 | 2.8131 | 2.8523 | 2.8981 | 2.9519 | 3.0186 | 3.1021 | 3.2281 | 3.3385 | 3.4651 | 3.5771 | 3.68 | 3.7874 | 3.8901 | 3.9904 | 1.578 | 2.1395 | 2.487
West Midlands | Cellarhead 132kV | COTES HEATH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.1336 | 1.1672 | 1.2207 | 1.2815 | 1.3482 | 1.4258 | 1.5176 | 1.6281 | 1.7328 | 1.83 | 1.9277 | 2.018 | 2.0893 | 2.1334 | 2.1703 | 1.1989 | 1.3792 | 1.5539 | 2.8123 | 2.883 | 3.0003 | 3.1324 | 3.2765 | 3.4449 | 3.6432 | 3.8803 | 4.106 | 4.3174 | 4.5325 | 4.7309 | 4.8911 | 4.99 | 5.0743 | 2.6392 | 3.0633 | 3.4822
West Midlands | Cellarhead 132kV | COTES HEATH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.1296 | 1.1521 | 1.1767 | 1.2138 | 1.254 | 1.3097 | 1.3812 | 1.4746 | 1.5653 | 1.6562 | 1.7558 | 1.8529 | 1.9437 | 2.0141 | 2.0825 | 1.1378 | 1.3597 | 1.4621 | 2.8053 | 2.8548 | 2.9073 | 2.9892 | 3.0771 | 3.2003 | 3.3603 | 3.5649 | 3.7659 | 3.9649 | 4.1833 | 4.3967 | 4.5965 | 4.7477 | 4.8948 | 2.5128 | 3.0155 | 3.2501
West Midlands | Cellarhead 132kV | COTES HEATH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.1257 | 1.1439 | 1.1695 | 1.2019 | 1.2418 | 1.2939 | 1.3559 | 1.4387 | 1.5161 | 1.607 | 1.6925 | 1.7728 | 1.8477 | 1.9091 | 1.969 | 1.0159 | 1.2103 | 1.3685 | 2.7951 | 2.8336 | 2.8884 | 2.9582 | 3.0453 | 3.1596 | 3.295 | 3.4727 | 3.64 | 3.8373 | 4.0196 | 4.1908 | 4.3498 | 4.4789 | 4.605 | 2.2024 | 2.6429 | 3.0177
West Midlands | Cellarhead 132kV | ECCLESHALL PRIMARY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.99482 | 1.0261 | 1.0595 | 1.0946 | 1.1326 | 1.1735 | 1.2185 | 1.2834 | 1.3393 | 1.397 | 1.4552 | 1.5157 | 1.5821 | 1.6486 | 1.7223 | 1.802 | 2.1308 | 2.3026 | 2.4543 | 2.5257 | 2.6009 | 2.6795 | 2.764 | 2.8545 | 2.9535 | 3.0923 | 3.2135 | 3.3382 | 3.4636 | 3.5935 | 3.7352 | 3.8768 | 4.0373 | 4.2124 | 4.9178 | 5.3052
West Midlands | Cellarhead 132kV | ECCLESHALL PRIMARY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.0115 | 1.0686 | 1.1306 | 1.1992 | 1.2751 | 1.3584 | 1.4563 | 1.5734 | 1.6836 | 1.7804 | 1.8703 | 1.9782 | 2.0627 | 2.1067 | 2.1673 | 2.1991 | 2.365 | 2.5259 | 2.4905 | 2.616 | 2.7507 | 2.8984 | 3.0608 | 3.2383 | 3.4452 | 3.6907 | 3.9227 | 4.1277 | 4.3192 | 4.5572 | 4.7485 | 4.8473 | 4.9793 | 5.0536 | 5.4457 | 5.8295
West Midlands | Cellarhead 132kV | ECCLESHALL PRIMARY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.0065 | 1.0501 | 1.0954 | 1.1444 | 1.1978 | 1.2593 | 1.3281 | 1.4225 | 1.51 | 1.6124 | 1.747 | 1.8418 | 1.9329 | 2.017 | 2.1241 | 2.1966 | 2.4422 | 2.6216 | 2.4818 | 2.5823 | 2.6847 | 2.7948 | 2.9136 | 3.0489 | 3.1991 | 3.401 | 3.5895 | 3.8119 | 4.1127 | 4.3156 | 4.511 | 4.6917 | 4.9184 | 5.076 | 5.6335 | 6.0594
West Midlands | Cellarhead 132kV | ECCLESHALL PRIMARY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.001 | 1.0305 | 1.0638 | 1.1014 | 1.1438 | 1.1923 | 1.2501 | 1.3304 | 1.4054 | 1.488 | 1.5737 | 1.6663 | 1.7724 | 1.8501 | 1.9303 | 1.9884 | 2.1486 | 2.2414 | 2.4677 | 2.5327 | 2.6049 | 2.6859 | 2.7769 | 2.8801 | 3.0021 | 3.169 | 3.3263 | 3.4985 | 3.6766 | 3.8736 | 4.106 | 4.2712 | 4.4378 | 4.56 | 4.9098 | 5.1202
West Midlands | Cellarhead 132kV | ENDON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.24337 | 0.30068 | 0.37277 | 0.45346 | 0.54201 | 0.64795 | 0.7735 | 0.96911 | 1.1285 | 1.3177 | 1.5016 | 1.6851 | 1.8858 | 2.0782 | 2.2653 | 2.448 | 3.2881 | 3.5757 | 0.55501 | 0.67539 | 0.82707 | 0.99734 | 1.1843 | 1.4091 | 1.6771 | 2.0893 | 2.4289 | 2.8355 | 3.2252 | 3.6092 | 4.0255 | 4.4231 | 4.8096 | 5.1866 | 6.9365 | 7.5795
West Midlands | Cellarhead 132kV | ENDON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.30096 | 0.4465 | 0.63924 | 0.85534 | 1.0953 | 1.3632 | 1.6821 | 2.0747 | 2.4518 | 2.7777 | 3.0942 | 3.4236 | 3.6075 | 3.7165 | 3.7919 | 3.8653 | 4.2361 | 4.5956 | 0.68039 | 0.986 | 1.3977 | 1.8565 | 2.3632 | 2.9306 | 3.6023 | 4.4245 | 5.2197 | 5.9131 | 6.5942 | 7.3027 | 7.7072 | 7.9505 | 8.1257 | 8.2976 | 9.1739 | 10.0398
West Midlands | Cellarhead 132kV | ENDON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.28392 | 0.37794 | 0.47942 | 0.60839 | 0.74978 | 0.92399 | 1.1602 | 1.4859 | 1.7842 | 2.0901 | 2.4036 | 2.6912 | 2.9692 | 3.2077 | 3.4301 | 3.6284 | 4.2125 | 4.4377 | 0.65148 | 0.85843 | 1.0759 | 1.3558 | 1.6611 | 2.0387 | 2.5531 | 3.2505 | 3.895 | 4.5501 | 5.2209 | 5.8362 | 6.4303 | 6.9328 | 7.4027 | 7.8239 | 9.1234 | 9.6531
West Midlands | Cellarhead 132kV | ENDON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.26374 | 0.33915 | 0.43608 | 0.54585 | 0.67676 | 0.83875 | 1.031 | 1.2987 | 1.5573 | 1.8444 | 2.1366 | 2.4251 | 2.6858 | 2.8939 | 3.0888 | 3.2637 | 3.7494 | 4.0478 | 0.59915 | 0.75905 | 0.96431 | 1.1978 | 1.4778 | 1.8257 | 2.2362 | 2.7993 | 3.3483 | 3.959 | 4.5741 | 5.181 | 5.7262 | 6.1559 | 6.5595 | 6.9237 | 7.9984 | 8.7115
West Midlands | Cellarhead 132kV | FROGHALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00011547 | 0.00017321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00023094 | 0.00034641
West Midlands | Cellarhead 132kV | FROGHALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00011547 | 0.00011547 | 0.00011547 | 0.00011547 | 0.00011547 | 0.00011547 | 0.00011547 | 0.00011547 | 0.00011547 | 0.00017845 | 0.00024144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00023094 | 0.00023094 | 0.00023094 | 0.00023094 | 0.00023094 | 0.00023094 | 0.00023094 | 0.00023094 | 0.00023094 | 0.0003884 | 0.00054586
West Midlands | Cellarhead 132kV | FROGHALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Midlands | Cellarhead 132kV | FROGHALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7735e-05 | 5.7735e-05 | 5.7735e-05 | 5.7735e-05 | 5.7735e-05 | 5.7735e-05 | 5.7735e-05 | 5.7735e-05 | 5.7735e-05 | 0.00017845 | 0.00029917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00011547 | 0.00011547 | 0.00011547 | 0.00011547 | 0.00011547 | 0.00011547 | 0.00011547 | 0.00011547 | 0.00011547 | 0.0003884 | 0.00066133
West Midlands | Cellarhead 132kV | GNOSALL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.66473 | 0.68772 | 0.71509 | 0.74584 | 0.78079 | 0.82102 | 0.86756 | 0.94405 | 1.0071 | 1.0737 | 1.1397 | 1.2074 | 1.283 | 1.3584 | 1.4326 | 1.5063 | 1.8739 | 2.0408 | 1.6341 | 1.6819 | 1.7387 | 1.8025 | 1.875 | 1.9585 | 2.0555 | 2.2132 | 2.3444 | 2.4836 | 2.6202 | 2.7593 | 2.9139 | 3.0675 | 3.219 | 3.3694 | 4.1233 | 4.4757
West Midlands | Cellarhead 132kV | GNOSALL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.68812 | 0.74541 | 0.84836 | 0.96715 | 1.0943 | 1.2292 | 1.3785 | 1.5666 | 1.7499 | 1.9006 | 2.0362 | 2.1701 | 2.2765 | 2.3411 | 2.3713 | 2.414 | 2.6126 | 2.8035 | 1.6847 | 1.8039 | 2.0321 | 2.2949 | 2.5734 | 2.8671 | 3.1869 | 3.5894 | 3.9858 | 4.3092 | 4.6005 | 4.8901 | 5.1288 | 5.2752 | 5.3419 | 5.4417 | 5.9107 | 6.3615
West Midlands | Cellarhead 132kV | GNOSALL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.68042 | 0.71537 | 0.7832 | 0.85858 | 0.94205 | 1.0245 | 1.11 | 1.2338 | 1.3481 | 1.4673 | 1.5891 | 1.7063 | 1.8249 | 1.9289 | 2.0265 | 2.1131 | 2.3764 | 2.5199 | 1.6713 | 1.7472 | 1.9015 | 2.0719 | 2.2597 | 2.4408 | 2.6236 | 2.8852 | 3.1281 | 3.3781 | 3.6316 | 3.876 | 4.1271 | 4.3459 | 4.552 | 4.7361 | 5.3189 | 5.6518
West Midlands | Cellarhead 132kV | GNOSALL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.6736 | 0.70359 | 0.7419 | 0.78648 | 0.83872 | 0.90241 | 0.97924 | 1.0898 | 1.1924 | 1.307 | 1.4248 | 1.5376 | 1.6407 | 1.7326 | 1.8175 | 1.8999 | 2.0986 | 2.2106 | 1.6531 | 1.716 | 1.7959 | 1.889 | 1.9982 | 2.1315 | 2.2913 | 2.519 | 2.7317 | 2.9688 | 3.2111 | 3.4429 | 3.6535 | 3.8411 | 4.0146 | 4.187 | 4.6137 | 4.8686
West Midlands | Cellarhead 132kV | GOLDENHILL BANK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.14724 | 0.19057 | 0.24012 | 0.29879 | 0.36379 | 0.43982 | 0.52324 | 0.65601 | 0.75774 | 0.86758 | 0.98202 | 1.0995 | 1.2329 | 1.3626 | 1.4896 | 1.6154 | 2.1891 | 2.3423 | 0.33372 | 0.42369 | 0.52631 | 0.64787 | 0.78235 | 0.93944 | 1.1121 | 1.3839 | 1.5938 | 1.8208 | 2.0562 | 2.2969 | 2.569 | 2.8334 | 3.0923 | 3.3486 | 4.5197 | 4.8476
West Midlands | Cellarhead 132kV | GOLDENHILL BANK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.19012 | 0.2962 | 0.41988 | 0.56582 | 0.7308 | 0.91212 | 1.1286 | 1.3949 | 1.6277 | 1.8178 | 1.9913 | 2.1588 | 2.2666 | 2.3264 | 2.3641 | 2.3996 | 2.5623 | 2.7209 | 0.42701 | 0.64757 | 0.90469 | 1.2078 | 1.5496 | 1.9255 | 2.3721 | 2.9185 | 3.3972 | 3.7897 | 4.15 | 4.4975 | 4.7251 | 4.8549 | 4.9399 | 5.0206 | 5.3948 | 5.7592
West Midlands | Cellarhead 132kV | GOLDENHILL BANK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.17737 | 0.24368 | 0.31909 | 0.41369 | 0.51661 | 0.63623 | 0.77977 | 0.97064 | 1.1395 | 1.3131 | 1.5 | 1.6875 | 1.8705 | 2.038 | 2.1887 | 2.3253 | 2.6772 | 2.8324 | 0.40534 | 0.54889 | 0.70978 | 0.9115 | 1.1307 | 1.3849 | 1.6881 | 2.0856 | 2.4389 | 2.8003 | 3.1887 | 3.5784 | 3.9586 | 4.3055 | 4.6185 | 4.9032 | 5.6638 | 6.0208
West Midlands | Cellarhead 132kV | GOLDENHILL BANK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.1628 | 0.21876 | 0.28631 | 0.37025 | 0.46376 | 0.57341 | 0.70587 | 0.8901 | 1.0444 | 1.2122 | 1.385 | 1.5586 | 1.7253 | 1.8756 | 2.0168 | 2.1427 | 2.4284 | 2.5567 | 0.36742 | 0.48467 | 0.62566 | 0.80113 | 0.99703 | 1.2268 | 1.5025 | 1.8817 | 2.2005 | 2.5461 | 2.9006 | 3.2566 | 3.5978 | 3.9054 | 4.1946 | 4.4529 | 5.0604 | 5.352
West Midlands | Cellarhead 132kV | HIGH OFFLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.22968 | 0.23956 | 0.25165 | 0.26626 | 0.28306 | 0.3032 | 0.32684 | 0.36516 | 0.39744 | 0.43288 | 0.46692 | 0.50145 | 0.54024 | 0.5795 | 0.61817 | 0.65606 | 0.85236 | 0.9668 | 0.55954 | 0.58002 | 0.6054 | 0.63604 | 0.67137 | 0.71389 | 0.76421 | 0.84479 | 0.91339 | 0.98937 | 1.0613 | 1.1332 | 1.2135 | 1.2945 | 1.3743 | 1.4524 | 1.86 | 2.1034
West Midlands | Cellarhead 132kV | HIGH OFFLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.23964 | 0.26293 | 0.3022 | 0.34907 | 0.40009 | 0.45993 | 0.5264 | 0.6086 | 0.69295 | 0.77229 | 0.84792 | 0.91745 | 0.96852 | 1.0003 | 1.0233 | 1.0468 | 1.1594 | 1.2612 | 0.58103 | 0.62947 | 0.71506 | 0.81646 | 0.92603 | 1.054 | 1.1953 | 1.3695 | 1.5495 | 1.719 | 1.8813 | 2.0308 | 2.1436 | 2.2143 | 2.2652 | 2.3188 | 2.5775 | 2.8165
West Midlands | Cellarhead 132kV | HIGH OFFLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.23619 | 0.25069 | 0.27564 | 0.30531 | 0.33728 | 0.37525 | 0.42105 | 0.49242 | 0.5646 | 0.63171 | 0.70224 | 0.76902 | 0.83096 | 0.88093 | 0.92798 | 0.96935 | 1.11 | 1.1791 | 0.57488 | 0.60633 | 0.66056 | 0.72581 | 0.79596 | 0.87849 | 0.97783 | 1.1307 | 1.2868 | 1.4294 | 1.5795 | 1.7223 | 1.8549 | 1.9603 | 2.0597 | 2.1478 | 2.459 | 2.6156
West Midlands | Cellarhead 132kV | HIGH OFFLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.23404 | 0.24642 | 0.26728 | 0.28939 | 0.31579 | 0.35039 | 0.39184 | 0.44938 | 0.50779 | 0.57539 | 0.6448 | 0.71177 | 0.76896 | 0.815 | 0.85883 | 0.89728 | 1.0171 | 1.101 | 0.56875 | 0.59471 | 0.63826 | 0.68491 | 0.74092 | 0.81454 | 0.90225 | 1.0224 | 1.1454 | 1.2879 | 1.4328 | 1.5728 | 1.6918 | 1.7868 | 1.8774 | 1.9575 | 2.22 | 2.4131
West Midlands | Cellarhead 132kV | HILL CHORLTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.047038 | 0.056507 | 0.069067 | 0.085002 | 0.1039 | 0.1306 | 0.16386 | 0.21045 | 0.25132 | 0.30046 | 0.34256 | 0.37908 | 0.41572 | 0.45016 | 0.4839 | 0.51814 | 0.70647 | 0.83143 | 0.10611 | 0.12678 | 0.15451 | 0.18984 | 0.23188 | 0.29134 | 0.36662 | 0.47108 | 0.56379 | 0.67672 | 0.77141 | 0.85167 | 0.93087 | 1.0046 | 1.0769 | 1.1502 | 1.5639 | 1.8512
West Midlands | Cellarhead 132kV | HILL CHORLTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.055641 | 0.080294 | 0.12215 | 0.1737 | 0.22986 | 0.29472 | 0.36914 | 0.45573 | 0.53748 | 0.61558 | 0.69787 | 0.7742 | 0.83985 | 0.88225 | 0.92059 | 0.95982 | 1.172 | 1.3526 | 0.12504 | 0.1792 | 0.27443 | 0.38954 | 0.51385 | 0.6586 | 0.82418 | 1.0159 | 1.1976 | 1.3731 | 1.5601 | 1.7332 | 1.8846 | 1.9812 | 2.0692 | 2.1597 | 2.6517 | 3.0912
West Midlands | Cellarhead 132kV | HILL CHORLTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.053079 | 0.072326 | 0.087988 | 0.12072 | 0.15395 | 0.20194 | 0.26444 | 0.33808 | 0.41248 | 0.48301 | 0.56144 | 0.63908 | 0.71263 | 0.7663 | 0.81917 | 0.8687 | 1.079 | 1.16 | 0.12049 | 0.165 | 0.19897 | 0.27189 | 0.34598 | 0.45408 | 0.5976 | 0.76396 | 0.9343 | 1.0936 | 1.2712 | 1.4475 | 1.614 | 1.7317 | 1.8477 | 1.9571 | 2.4365 | 2.6248
West Midlands | Cellarhead 132kV | HILL CHORLTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.051358 | 0.065844 | 0.083779 | 0.10843 | 0.1399 | 0.18509 | 0.23654 | 0.2997 | 0.35804 | 0.4279 | 0.48861 | 0.5464 | 0.60045 | 0.64373 | 0.68712 | 0.72809 | 0.91514 | 1.0797 | 0.11572 | 0.14813 | 0.18768 | 0.24253 | 0.31347 | 0.41546 | 0.53149 | 0.67177 | 0.80231 | 0.9599 | 1.0941 | 1.2214 | 1.3394 | 1.4321 | 1.5252 | 1.6142 | 2.0445 | 2.4395
West Midlands | Cellarhead 132kV | HINSTOCK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.13031 | 0.14728 | 0.16383 | 0.18164 | 0.20688 | 0.23619 | 0.26877 | 0.31636 | 0.35266 | 0.39072 | 0.42959 | 0.47089 | 0.51685 | 0.56055 | 0.60257 | 0.64641 | 0.87206 | 0.98368 | 0.30877 | 0.34514 | 0.37946 | 0.41635 | 0.46855 | 0.5292 | 0.59649 | 0.69388 | 0.76842 | 0.84642 | 0.9259 | 1.0101 | 1.1034 | 1.1921 | 1.2775 | 1.3663 | 1.8254 | 2.0554
West Midlands | Cellarhead 132kV | HINSTOCK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.14361 | 0.18642 | 0.22417 | 0.27888 | 0.34169 | 0.40557 | 0.48374 | 0.58001 | 0.66638 | 0.74344 | 0.81293 | 0.87818 | 0.92211 | 0.9496 | 0.97188 | 0.99093 | 1.091 | 1.1581 | 0.33761 | 0.43027 | 0.50852 | 0.62232 | 0.75311 | 0.88449 | 1.0453 | 1.2428 | 1.4198 | 1.5777 | 1.7204 | 1.8538 | 1.9444 | 2.0023 | 2.05 | 2.0913 | 2.3127 | 2.4624
West Midlands | Cellarhead 132kV | HINSTOCK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.13981 | 0.17285 | 0.20425 | 0.24508 | 0.27832 | 0.32741 | 0.3865 | 0.46659 | 0.53167 | 0.60161 | 0.67702 | 0.74863 | 0.81458 | 0.87291 | 0.93288 | 0.98357 | 1.1432 | 1.2346 | 0.33107 | 0.40591 | 0.47349 | 0.5608 | 0.63134 | 0.73412 | 0.85799 | 1.0242 | 1.1589 | 1.3027 | 1.4578 | 1.6053 | 1.7414 | 1.8624 | 1.9867 | 2.0927 | 2.4353 | 2.6375
West Midlands | Cellarhead 132kV | HINSTOCK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.13535 | 0.16161 | 0.18441 | 0.21965 | 0.25798 | 0.30431 | 0.36288 | 0.44102 | 0.50633 | 0.5814 | 0.65507 | 0.7221 | 0.7871 | 0.83888 | 0.8936 | 0.9377 | 1.0745 | 1.1496 | 0.31963 | 0.37767 | 0.42532 | 0.49869 | 0.57844 | 0.67468 | 0.79613 | 0.95673 | 1.0905 | 1.2432 | 1.393 | 1.5294 | 1.6618 | 1.7678 | 1.8799 | 1.9708 | 2.259 | 2.4207
West Midlands | Cellarhead 132kV | HOOKGATE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.12935 | 0.16221 | 0.207 | 0.246 | 0.28594 | 0.33858 | 0.40188 | 0.49436 | 0.57285 | 0.66291 | 0.74474 | 0.8211 | 0.90126 | 0.97732 | 1.0522 | 1.1275 | 1.5199 | 1.7489 | 0.29753 | 0.36709 | 0.46246 | 0.54624 | 0.63256 | 0.74679 | 0.88589 | 1.0868 | 1.2593 | 1.4599 | 1.6383 | 1.8018 | 1.9711 | 2.1306 | 2.2876 | 2.4456 | 3.284 | 3.7956
West Midlands | Cellarhead 132kV | HOOKGATE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.14859 | 0.21515 | 0.31808 | 0.42575 | 0.53876 | 0.66767 | 0.81742 | 0.99583 | 1.1629 | 1.3182 | 1.4754 | 1.6213 | 1.7383 | 1.8135 | 1.8785 | 1.9431 | 2.2844 | 2.5639 | 0.33919 | 0.48125 | 0.70743 | 0.94132 | 1.1852 | 1.4651 | 1.7889 | 2.1727 | 2.5334 | 2.8721 | 3.2187 | 3.5399 | 3.8028 | 3.971 | 4.1181 | 4.2651 | 5.0486 | 5.7202
West Midlands | Cellarhead 132kV | HOOKGATE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.14239 | 0.19266 | 0.25066 | 0.32302 | 0.3913 | 0.48539 | 0.60444 | 0.75162 | 0.89598 | 1.0391 | 1.1955 | 1.3461 | 1.4881 | 1.5982 | 1.7048 | 1.8022 | 2.1835 | 2.3387 | 0.32835 | 0.43989 | 0.56494 | 0.72322 | 0.87264 | 1.0801 | 1.3464 | 1.6698 | 1.9912 | 2.3054 | 2.6493 | 2.982 | 3.2953 | 3.5319 | 3.7616 | 3.9726 | 4.828 | 5.1843
West Midlands | Cellarhead 132kV | HOOKGATE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.13662 | 0.17868 | 0.23787 | 0.29484 | 0.35788 | 0.44474 | 0.54501 | 0.67438 | 0.79405 | 0.93429 | 1.0643 | 1.1876 | 1.3033 | 1.3988 | 1.4925 | 1.5782 | 1.9067 | 2.1638 | 0.31308 | 0.40363 | 0.53138 | 0.65493 | 0.7931 | 0.98403 | 1.2036 | 1.4826 | 1.7425 | 2.0486 | 2.3274 | 2.5914 | 2.8377 | 3.0385 | 3.236 | 3.4184 | 4.1576 | 4.7658
West Midlands | Cellarhead 132kV | KINGSLEY HOLT 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.41632 | 0.45911 | 0.50941 | 0.5679 | 0.62204 | 0.68335 | 0.75628 | 0.86848 | 0.96077 | 1.0641 | 1.1645 | 1.2615 | 1.3654 | 1.4665 | 1.5652 | 1.6636 | 2.1221 | 2.3041 | 1.0049 | 1.0964 | 1.2026 | 1.3262 | 1.441 | 1.5716 | 1.7282 | 1.9658 | 2.1636 | 2.387 | 2.6008 | 2.8041 | 3.0198 | 3.2288 | 3.4329 | 3.6363 | 4.5965 | 5.0031
West Midlands | Cellarhead 132kV | KINGSLEY HOLT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.4474 | 0.54617 | 0.66678 | 0.80614 | 0.94561 | 1.102 | 1.2859 | 1.5084 | 1.7085 | 1.8776 | 2.0383 | 2.1876 | 2.2789 | 2.3306 | 2.3688 | 2.419 | 2.6024 | 2.7653 | 1.0727 | 1.2857 | 1.5454 | 1.8436 | 2.14 | 2.4737 | 2.8638 | 3.3329 | 3.7563 | 4.1174 | 4.4647 | 4.7864 | 4.9848 | 5.0978 | 5.1846 | 5.2937 | 5.7156 | 6.1045
West Midlands | Cellarhead 132kV | KINGSLEY HOLT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.43809 | 0.51168 | 0.5822 | 0.67408 | 0.76742 | 0.87819 | 1.0103 | 1.178 | 1.3272 | 1.4753 | 1.6131 | 1.74 | 1.8683 | 1.9895 | 2.1041 | 2.2231 | 2.5183 | 2.6483 | 1.0568 | 1.2229 | 1.3752 | 1.5755 | 1.7784 | 2.02 | 2.3094 | 2.6698 | 2.9931 | 3.3108 | 3.599 | 3.8634 | 4.133 | 4.3878 | 4.6293 | 4.8795 | 5.525 | 5.8283
West Midlands | Cellarhead 132kV | KINGSLEY HOLT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.42817 | 0.48688 | 0.55375 | 0.63423 | 0.71763 | 0.8188 | 0.93645 | 1.096 | 1.2331 | 1.3838 | 1.5296 | 1.6671 | 1.7919 | 1.9053 | 2.0119 | 2.1354 | 2.4364 | 2.6274 | 1.0307 | 1.1592 | 1.302 | 1.4744 | 1.6538 | 1.8724 | 2.1252 | 2.463 | 2.7547 | 3.0757 | 3.3818 | 3.67 | 3.928 | 4.1617 | 4.3811 | 4.6449 | 5.3121 | 5.7659
West Midlands | Cellarhead 132kV | KNYPERSLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 5.0068 | 5.0803 | 5.1672 | 5.262 | 5.3697 | 5.4974 | 5.6558 | 5.8887 | 6.0766 | 6.2845 | 6.4996 | 6.7249 | 6.9951 | 7.2542 | 7.5125 | 7.7692 | 8.8414 | 9.2037 | 12.451 | 12.6061 | 12.7889 | 12.9874 | 13.2131 | 13.481 | 13.8185 | 14.3031 | 14.6978 | 15.1361 | 15.5857 | 16.0527 | 16.6113 | 17.1452 | 17.6818 | 18.2164 | 20.4316 | 21.2155
West Midlands | Cellarhead 132kV | KNYPERSLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 5.0789 | 5.2663 | 5.4972 | 5.7529 | 6.0401 | 6.4189 | 6.8236 | 7.3085 | 7.737 | 8.0884 | 8.42 | 8.7777 | 9.0579 | 6.7888 | 6.8854 | 6.9666 | 7.6707 | 8.021 | 12.6075 | 13.0035 | 13.4938 | 14.0314 | 14.6329 | 15.4444 | 16.2916 | 17.2946 | 18.1826 | 18.9118 | 19.6056 | 20.3619 | 20.9695 | 15.2571 | 15.4734 | 15.659 | 17.3511 | 18.1802
West Midlands | Cellarhead 132kV | KNYPERSLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 5.0567 | 5.1805 | 5.317 | 5.4744 | 5.7063 | 5.9629 | 6.2501 | 6.6095 | 6.877 | 7.1874 | 7.5593 | 7.8806 | 5.8514 | 6.1358 | 6.4118 | 7.0572 | 7.7394 | 10.2222 | 12.5691 | 12.8435 | 13.1388 | 13.4787 | 13.9855 | 14.5388 | 15.152 | 15.9062 | 16.4544 | 17.0996 | 17.8889 | 18.5517 | 13.342 | 13.9316 | 14.5041 | 16.0203 | 17.5162 | 23.6752
West Midlands | Cellarhead 132kV | KNYPERSLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 5.0346 | 5.1351 | 5.261 | 5.3991 | 5.5784 | 5.8406 | 7.3637 | 7.7305 | 8.0414 | 8.3721 | 8.7166 | 9.0674 | 9.4338 | 9.7062 | 9.9605 | 10.1793 | 11.8508 | 12.147 | 12.5109 | 12.7262 | 12.9939 | 13.2856 | 13.6664 | 14.2393 | 17.9471 | 18.7149 | 19.3683 | 20.0605 | 20.7768 | 21.5109 | 22.285 | 22.8482 | 23.3715 | 23.8242 | 27.8157 | 28.5068
West Midlands | Cellarhead 132kV | LEEK 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.4758 | 1.5875 | 1.7228 | 1.8882 | 2.0699 | 2.2639 | 2.4867 | 2.8229 | 3.0863 | 3.3811 | 3.6955 | 4.0132 | 4.3548 | 4.6831 | 5.0002 | 5.315 | 6.7067 | 7.1809 | 3.6041 | 3.8419 | 4.126 | 4.4728 | 4.8539 | 5.2621 | 5.7321 | 6.4328 | 6.9865 | 7.6091 | 8.2678 | 8.9268 | 9.63 | 10.303 | 10.9532 | 11.5975 | 14.4622 | 15.4843
West Midlands | Cellarhead 132kV | LEEK 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.5749 | 1.8555 | 2.1972 | 2.5828 | 3.0111 | 3.4865 | 4.0459 | 4.7218 | 5.309 | 5.8115 | 6.3049 | 6.7434 | 7.0096 | 7.1774 | 7.2868 | 7.3828 | 7.8788 | 8.309 | 3.8192 | 4.4176 | 5.1429 | 5.9578 | 6.8594 | 7.8618 | 9.0351 | 10.4434 | 11.6655 | 12.7181 | 13.7628 | 14.685 | 15.2557 | 15.6196 | 15.8674 | 16.0862 | 17.2385 | 18.2573
West Midlands | Cellarhead 132kV | LEEK 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.5448 | 1.7436 | 1.9546 | 2.2058 | 2.5155 | 2.8635 | 3.2605 | 3.7649 | 4.1721 | 4.6147 | 5.0684 | 5.4818 | 5.8901 | 6.2836 | 6.6489 | 6.9708 | 7.2262 | 7.6422 | 3.7674 | 4.2132 | 4.6685 | 5.2137 | 5.8838 | 6.6357 | 7.4887 | 8.5529 | 9.4055 | 10.3322 | 11.2813 | 12.1435 | 12.9981 | 13.8205 | 14.586 | 15.2646 | 15.6211 | 16.5898
West Midlands | Cellarhead 132kV | LEEK 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.5132 | 1.6656 | 1.8574 | 2.0831 | 2.3551 | 2.6644 | 3.0296 | 3.528 | 3.9436 | 4.4003 | 4.8911 | 5.3037 | 5.6954 | 6.0616 | 6.4023 | 6.6938 | 7.4476 | 7.828 | 3.6848 | 4.013 | 4.4191 | 4.8977 | 5.4765 | 6.136 | 6.9103 | 7.9529 | 8.8216 | 9.7727 | 10.7933 | 11.642 | 12.4469 | 13.1991 | 13.899 | 14.4985 | 16.1206 | 16.9967
West Midlands | Cellarhead 132kV | Longton 132/33/11kV | Bulk Supply Point | 11 | Counterfactual | 2.4049 | 2.6717 | 2.9954 | 3.3539 | 3.7794 | 4.258 | 4.7813 | 5.5946 | 6.2403 | 6.9647 | 7.7192 | 8.5134 | 9.419 | 10.3242 | 11.2035 | 12.0673 | 15.6841 | 16.6279 | 5.6894 | 6.2476 | 6.9182 | 7.6607 | 8.5476 | 9.5465 | 10.6304 | 12.2955 | 13.6259 | 15.1228 | 16.6789 | 18.3109 | 20.1677 | 22.0225 | 23.8233 | 25.5895 | 32.9864 | 34.9966
West Midlands | Cellarhead 132kV | Longton 132/33/11kV | Bulk Supply Point | 11 | Electric Engagement | 2.6703 | 3.3367 | 4.1275 | 5.0856 | 6.2301 | 7.3935 | 8.763 | 10.3909 | 11.9852 | 13.3621 | 14.6661 | 16.0182 | 16.6941 | 17.0698 | 17.2942 | 16.5625 | 17.5522 | 18.3976 | 6.2662 | 7.6605 | 9.3047 | 11.3076 | 13.7194 | 16.1405 | 18.971 | 22.3104 | 25.6096 | 28.4805 | 31.2187 | 34.0624 | 35.4909 | 36.3025 | 36.809 | 34.9318 | 37.2236 | 39.1892
West Midlands | Cellarhead 132kV | Longton 132/33/11kV | Bulk Supply Point | 11 | Holistic Transition | 2.5903 | 3.0173 | 3.6001 | 4.2212 | 4.9055 | 5.6784 | 6.5405 | 8.0367 | 9.3699 | 10.6338 | 11.8964 | 13.0004 | 13.152 | 14.1493 | 15.0781 | 15.8977 | 19.0088 | 19.8998 | 6.1293 | 7.0644 | 8.3292 | 9.6679 | 11.1375 | 12.7839 | 14.6063 | 17.7561 | 20.5762 | 23.2285 | 25.8656 | 28.1591 | 28.0825 | 30.1527 | 32.0834 | 33.7952 | 40.8629 | 42.9251
West Midlands | Cellarhead 132kV | Longton 132/33/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | 2.5009 | 2.8498 | 3.2879 | 3.8156 | 4.4791 | 5.1688 | 5.9662 | 7.106 | 8.7014 | 9.8903 | 11.2008 | 12.5238 | 13.6255 | 14.5719 | 15.4353 | 16.1827 | 17.8966 | 18.5908 | 5.8969 | 6.6335 | 7.5476 | 8.6605 | 10.0823 | 11.5335 | 13.1916 | 15.5369 | 19.061 | 21.5291 | 24.2494 | 26.9998 | 29.2673 | 31.2047 | 32.9719 | 34.5046 | 38.1448 | 39.7246
West Midlands | Cellarhead 132kV | MARKET DRAYTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.5399 | 2.6227 | 2.7216 | 2.8292 | 2.9481 | 3.1044 | 3.3192 | 3.5733 | 3.7436 | 3.9352 | 4.1415 | 4.3567 | 4.5926 | 4.8247 | 5.0486 | 5.2729 | 6.3897 | 6.8621 | 6.2883 | 6.4641 | 6.6718 | 6.8949 | 7.1409 | 7.4783 | 7.9546 | 8.4937 | 8.8442 | 9.2393 | 9.6647 | 10.1075 | 10.5911 | 11.0667 | 11.5255 | 11.9841 | 14.2834 | 15.2777
West Midlands | Cellarhead 132kV | MARKET DRAYTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.6026 | 2.7966 | 3.0276 | 3.2682 | 3.5383 | 4.088 | 4.5627 | 5.1358 | 5.5367 | 5.8767 | 6.1978 | 6.5092 | 6.7221 | 6.8531 | 6.9562 | 7.0538 | 7.5639 | 7.908 | 6.424 | 6.8387 | 7.3289 | 7.8287 | 8.3892 | 9.6332 | 10.6653 | 11.8998 | 12.7282 | 13.4327 | 14.1026 | 14.7516 | 15.2003 | 15.4809 | 15.7065 | 15.9212 | 17.0554 | 17.8263
West Midlands | Cellarhead 132kV | MARKET DRAYTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.5831 | 2.7317 | 2.8961 | 3.0646 | 3.3485 | 3.7084 | 4.0771 | 4.5324 | 4.8412 | 5.2215 | 5.5669 | 5.8874 | 6.1943 | 6.472 | 6.7456 | 6.9912 | 7.7781 | 8.1911 | 6.3903 | 6.7222 | 7.0831 | 7.4436 | 8.078 | 8.8923 | 9.7165 | 10.7148 | 11.3633 | 12.1768 | 12.8966 | 13.5634 | 14.2029 | 14.782 | 15.3538 | 15.87 | 17.5692 | 18.4951
West Midlands | Cellarhead 132kV | MARKET DRAYTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.5634 | 2.6867 | 2.8443 | 2.9986 | 3.1767 | 3.6151 | 3.9638 | 4.4135 | 4.7104 | 5.0366 | 5.3805 | 5.6982 | 6.0073 | 6.2685 | 6.5281 | 6.7565 | 7.4546 | 7.8049 | 6.3387 | 6.6067 | 6.9463 | 7.2693 | 7.6424 | 8.6582 | 9.4327 | 10.4127 | 11.0287 | 11.7027 | 12.4136 | 13.0698 | 13.7076 | 14.2463 | 14.7823 | 15.2567 | 16.7464 | 17.5164
West Midlands | Cellarhead 132kV | Meaford C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.8949 | 1.9948 | 2.116 | 2.2402 | 2.3925 | 2.5854 | 2.8112 | 3.1257 | 3.3708 | 3.6544 | 3.9086 | 4.1908 | 4.5054 | 4.8209 | 5.1269 | 5.4369 | 6.8562 | 7.477 | 4.3801 | 4.5893 | 4.8418 | 5.1006 | 5.4223 | 5.8366 | 6.3253 | 6.985 | 7.4992 | 8.1056 | 8.6336 | 9.213 | 9.8556 | 10.4991 | 11.1234 | 11.7557 | 14.675 | 15.9931
West Midlands | Cellarhead 132kV | Meaford C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.9831 | 2.2178 | 2.5104 | 2.984 | 3.4275 | 3.918 | 4.4282 | 5.0669 | 5.6487 | 6.1504 | 6.5737 | 6.9774 | 7.251 | 7.4229 | 7.543 | 7.6505 | 8.2022 | 8.7042 | 4.571 | 5.063 | 5.679 | 6.7305 | 7.6903 | 8.7562 | 9.8383 | 11.1763 | 12.3981 | 13.4604 | 14.3511 | 15.1985 | 15.7852 | 16.1585 | 16.4273 | 16.6711 | 17.9416 | 19.1092
West Midlands | Cellarhead 132kV | Meaford C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.9551 | 2.1093 | 2.3327 | 2.5714 | 2.8785 | 3.1879 | 3.5379 | 4.0164 | 4.4344 | 4.8524 | 5.3118 | 5.7539 | 6.1808 | 6.5598 | 6.9143 | 7.2264 | 8.1657 | 8.6147 | 4.5223 | 4.8601 | 5.3505 | 5.8744 | 6.5664 | 7.2459 | 8.0116 | 9.0375 | 9.9362 | 10.8162 | 11.7817 | 12.7126 | 13.6117 | 14.4032 | 15.1454 | 15.8025 | 17.8568 | 18.8788
West Midlands | Cellarhead 132kV | Meaford C 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.9287 | 2.0584 | 2.2239 | 2.4255 | 2.7108 | 3.0222 | 3.3652 | 3.8398 | 4.2781 | 4.7892 | 5.2626 | 5.7022 | 6.1267 | 6.509 | 6.8637 | 7.1789 | 8.0341 | 8.4816 | 4.4526 | 4.7269 | 5.0746 | 5.505 | 6.1359 | 6.8168 | 7.557 | 8.558 | 9.482 | 10.5692 | 11.5547 | 12.4602 | 13.3335 | 14.118 | 14.847 | 15.4972 | 17.3349 | 18.3598
West Midlands | Cellarhead 132kV | Newcastle 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 5.3676 | 5.6694 | 6.0166 | 6.3985 | 6.8388 | 7.3387 | 7.8969 | 8.7426 | 9.412 | 10.0848 | 10.7845 | 11.5718 | 12.4421 | 13.3034 | 14.1334 | 14.9624 | 18.0276 | 19.3285 | 12.9924 | 13.6369 | 14.3656 | 15.1659 | 16.0874 | 17.1345 | 18.3035 | 20.0583 | 21.456 | 22.8472 | 24.293 | 25.9086 | 27.6874 | 29.4452 | 31.1349 | 32.8216 | 38.774 | 41.4924
West Midlands | Cellarhead 132kV | Newcastle 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 5.6118 | 6.4038 | 7.2571 | 8.2055 | 9.2861 | 10.4835 | 11.9342 | 13.6816 | 15.2061 | 16.4162 | 17.5271 | 18.597 | 19.3028 | 16.8503 | 17.1624 | 17.445 | 21.1081 | 22.5913 | 13.5232 | 15.2295 | 17.0369 | 19.0389 | 21.317 | 23.8422 | 26.906 | 30.5435 | 33.7126 | 36.2145 | 38.5171 | 40.7218 | 42.1975 | 35.8955 | 36.575 | 37.193 | 45.9879 | 49.2831
West Midlands | Cellarhead 132kV | Newcastle 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 5.5356 | 6.114 | 6.7018 | 7.3534 | 8.0771 | 9.0001 | 9.991 | 11.2599 | 12.3083 | 13.354 | 14.5279 | 15.7076 | 13.967 | 15.0558 | 16.0731 | 19.9218 | 21.9286 | 23.3517 | 13.3914 | 14.6908 | 15.9739 | 17.3939 | 18.9682 | 20.9914 | 23.1361 | 25.8223 | 28.0344 | 30.2003 | 32.622 | 35.0545 | 30.2006 | 32.4552 | 34.565 | 43.8107 | 47.9567 | 51.1084
West Midlands | Cellarhead 132kV | Newcastle 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 5.4601 | 5.9565 | 6.4922 | 7.0858 | 7.7715 | 8.5664 | 9.5223 | 10.8206 | 11.9517 | 13.0919 | 14.2806 | 15.4231 | 16.5336 | 17.5525 | 18.4975 | 19.33 | 20.7608 | 21.9028 | 13.1925 | 14.2844 | 15.4324 | 16.7041 | 18.1737 | 19.8776 | 21.93 | 24.6565 | 27.0272 | 29.3798 | 31.8215 | 34.1566 | 36.4246 | 38.5057 | 40.4365 | 42.1396 | 44.8914 | 47.4165
West Midlands | Cellarhead 132kV | SCOT HAY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.24653 | 0.28958 | 0.34257 | 0.40808 | 0.48276 | 0.57149 | 0.67663 | 0.83318 | 0.96135 | 1.1066 | 1.2438 | 1.3781 | 1.5209 | 1.6606 | 1.7974 | 1.9339 | 2.6028 | 2.8768 | 0.54927 | 0.64044 | 0.75225 | 0.89115 | 1.0497 | 1.2392 | 1.4655 | 1.7983 | 2.074 | 2.3893 | 2.6827 | 2.9651 | 3.2622 | 3.5518 | 3.8356 | 4.1184 | 5.5228 | 6.1358
West Midlands | Cellarhead 132kV | SCOT HAY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.2878 | 0.40106 | 0.54877 | 0.72428 | 0.91932 | 1.1396 | 1.3977 | 1.705 | 1.9847 | 2.2275 | 2.4592 | 2.6819 | 2.8442 | 2.9406 | 3.0113 | 3.0812 | 3.4916 | 3.8376 | 0.63906 | 0.88039 | 1.1989 | 1.575 | 1.9907 | 2.4622 | 3.0116 | 3.6612 | 4.2552 | 4.7758 | 5.2786 | 5.7603 | 6.1209 | 6.3373 | 6.5007 | 6.6635 | 7.6113 | 8.4417
West Midlands | Cellarhead 132kV | SCOT HAY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.27542 | 0.35303 | 0.43191 | 0.54323 | 0.6647 | 0.81798 | 1.004 | 1.2422 | 1.4598 | 1.6799 | 1.9178 | 2.1559 | 2.3841 | 2.5748 | 2.7537 | 2.9146 | 3.4732 | 3.693 | 0.61791 | 0.79159 | 0.96129 | 1.2041 | 1.4681 | 1.8028 | 2.2111 | 2.7244 | 3.1981 | 3.6723 | 4.1854 | 4.6995 | 5.1915 | 5.5958 | 5.9762 | 6.3204 | 7.5577 | 8.07
West Midlands | Cellarhead 132kV | SCOT HAY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.26149 | 0.32355 | 0.39705 | 0.49066 | 0.60281 | 0.74328 | 0.90672 | 1.1238 | 1.315 | 1.5286 | 1.7361 | 1.9372 | 2.1285 | 2.2948 | 2.451 | 2.5914 | 3.0516 | 3.35 | 0.58169 | 0.71612 | 0.87255 | 1.073 | 1.3148 | 1.6194 | 1.972 | 2.4331 | 2.8416 | 3.2993 | 3.7378 | 4.1617 | 4.5638 | 4.9102 | 5.2364 | 5.5313 | 6.5525 | 7.2611
West Midlands | Cellarhead 132kV | SIMPLEX 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.29608 | 0.3733 | 0.47468 | 0.59318 | 0.70926 | 0.84284 | 0.99638 | 1.2195 | 1.4023 | 1.574 | 1.7448 | 1.9183 | 2.1107 | 2.3017 | 2.4892 | 2.6762 | 3.5414 | 3.8178 | 0.66069 | 0.82394 | 1.0381 | 1.2888 | 1.5354 | 1.8198 | 2.1476 | 2.6171 | 3.0071 | 3.3669 | 3.7213 | 4.0786 | 4.4723 | 4.8625 | 5.2454 | 5.6271 | 7.4061 | 8.0062
West Midlands | Cellarhead 132kV | SIMPLEX 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.36637 | 0.55586 | 0.79926 | 1.0822 | 1.3843 | 1.7205 | 2.1103 | 2.5631 | 2.9705 | 3.2677 | 3.5399 | 3.799 | 3.9686 | 4.0706 | 4.1368 | 4.2081 | 4.5251 | 4.8135 | 0.81563 | 1.2188 | 1.7414 | 2.3486 | 2.9962 | 3.7195 | 4.5513 | 5.5082 | 6.3736 | 6.9931 | 7.5654 | 8.1086 | 8.4726 | 8.6959 | 8.8471 | 9.0085 | 9.7452 | 10.4254
West Midlands | Cellarhead 132kV | SIMPLEX 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.34698 | 0.47788 | 0.63813 | 0.8347 | 1.0374 | 1.2778 | 1.5543 | 1.8985 | 2.2101 | 2.479 | 2.7684 | 3.0522 | 3.3283 | 3.5765 | 3.8105 | 4.0243 | 4.6012 | 4.8458 | 0.78246 | 1.0728 | 1.4247 | 1.8589 | 2.3078 | 2.8402 | 3.4499 | 4.1927 | 4.872 | 5.4365 | 6.0441 | 6.6412 | 7.2218 | 7.7397 | 8.2289 | 8.6774 | 9.9404 | 10.5065
West Midlands | Cellarhead 132kV | SIMPLEX 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.32578 | 0.43955 | 0.59091 | 0.77073 | 0.96177 | 1.1888 | 1.447 | 1.7734 | 2.0625 | 2.3244 | 2.5921 | 2.8507 | 3.0993 | 3.3265 | 3.5385 | 3.7338 | 4.2063 | 4.4509 | 0.72718 | 0.97392 | 1.3028 | 1.6956 | 2.1151 | 2.6143 | 3.1771 | 3.8743 | 4.4971 | 5.0419 | 5.5942 | 6.1266 | 6.6379 | 7.1041 | 7.5398 | 7.9424 | 8.9641 | 9.5326
West Midlands | Cellarhead 132kV | Stagefields 132/33/11kV | Bulk Supply Point | 11 | Counterfactual | 1.3995 | 1.6799 | 2.0087 | 2.3816 | 2.9148 | 3.5101 | 4.1552 | 5.1142 | 5.7871 | 6.5404 | 7.356 | 8.22 | 9.201 | 10.1817 | 11.1532 | 12.1745 | 16.3387 | 17.4953 | 3.2565 | 3.8433 | 4.5241 | 5.2955 | 6.4025 | 7.6426 | 8.9837 | 10.9629 | 12.3461 | 13.9014 | 15.5903 | 17.3724 | 19.3899 | 21.4049 | 23.3974 | 25.4951 | 34.0296 | 36.4704
West Midlands | Cellarhead 132kV | Stagefields 132/33/11kV | Bulk Supply Point | 11 | Electric Engagement | 1.6764 | 2.3748 | 3.1876 | 4.3757 | 5.7812 | 7.1576 | 8.7877 | 10.538 | 12.2507 | 13.7745 | 15.2985 | 17.0393 | 17.8285 | 18.2228 | 18.4607 | 18.673 | 19.5727 | 20.3718 | 3.8573 | 5.3196 | 7.0062 | 9.4945 | 12.4595 | 15.3458 | 18.7705 | 22.3814 | 25.9275 | 29.1207 | 32.3399 | 36.0272 | 37.6958 | 38.5429 | 39.0752 | 39.5548 | 41.6304 | 43.4776
West Midlands | Cellarhead 132kV | Stagefields 132/33/11kV | Bulk Supply Point | 11 | Holistic Transition | 1.5929 | 2.0446 | 2.7964 | 3.6683 | 4.5338 | 5.5567 | 6.5008 | 8.223 | 9.7485 | 11.2819 | 12.8095 | 13.97 | 15.097 | 16.1454 | 17.1184 | 17.9764 | 20.1217 | 21.0348 | 3.7138 | 4.7031 | 6.3238 | 8.2009 | 10.0682 | 12.2945 | 14.3078 | 17.9554 | 21.1862 | 24.4225 | 27.6296 | 30.032 | 32.3656 | 34.536 | 36.5535 | 38.3401 | 42.9715 | 45.0813
West Midlands | Cellarhead 132kV | Stagefields 132/33/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | 1.5036 | 1.8735 | 2.3308 | 2.9899 | 3.7849 | 4.6527 | 5.6922 | 6.9531 | 8.1346 | 9.4448 | 10.895 | 12.3591 | 13.6136 | 14.7479 | 15.7527 | 16.5736 | 18.4362 | 19.2498 | 3.4808 | 4.2619 | 5.2148 | 6.6031 | 8.2972 | 10.1395 | 12.3517 | 14.967 | 17.4215 | 20.1529 | 23.1769 | 26.2275 | 28.8192 | 31.1606 | 33.2293 | 34.9159 | 38.8721 | 40.6987
West Midlands | Cellarhead 132kV | TALKE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.19319 | 0.24579 | 0.30951 | 0.38474 | 0.47612 | 0.5795 | 0.69968 | 0.87859 | 1.0171 | 1.184 | 1.3533 | 1.5208 | 1.706 | 1.8816 | 2.0422 | 2.2057 | 2.9621 | 3.2201 | 0.43702 | 0.5478 | 0.68061 | 0.83765 | 1.0283 | 1.2445 | 1.4963 | 1.8677 | 2.1575 | 2.5089 | 2.8628 | 3.21 | 3.5915 | 3.9525 | 4.2818 | 4.6165 | 6.1749 | 6.7327
West Midlands | Cellarhead 132kV | TALKE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.2446 | 0.37593 | 0.53719 | 0.73876 | 0.96672 | 1.2055 | 1.4962 | 1.8404 | 2.1628 | 2.4361 | 2.6911 | 2.9459 | 3.1055 | 3.2016 | 3.2712 | 3.3402 | 3.6707 | 3.9743 | 0.54862 | 0.82574 | 1.1646 | 1.5885 | 2.0668 | 2.5666 | 3.1737 | 3.8882 | 4.5607 | 5.1348 | 5.6744 | 6.212 | 6.554 | 6.7636 | 6.9194 | 7.0742 | 7.8262 | 8.5235
West Midlands | Cellarhead 132kV | TALKE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.22869 | 0.31576 | 0.42781 | 0.56353 | 0.6984 | 0.87304 | 1.096 | 1.3677 | 1.6121 | 1.8638 | 2.1125 | 2.3691 | 2.6186 | 2.8407 | 3.0511 | 3.2425 | 3.7867 | 4.0438 | 0.52116 | 0.71365 | 0.953 | 1.2453 | 1.5346 | 1.9092 | 2.3883 | 2.9625 | 3.4826 | 4.0149 | 4.5382 | 5.0774 | 5.6015 | 6.0649 | 6.5043 | 6.9058 | 8.0899 | 8.6741
West Midlands | Cellarhead 132kV | TALKE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.21343 | 0.28351 | 0.37518 | 0.49213 | 0.6245 | 0.78393 | 0.97268 | 1.2148 | 1.4447 | 1.6904 | 1.9382 | 2.1822 | 2.4137 | 2.6083 | 2.793 | 2.9601 | 3.4057 | 3.6578 | 0.48046 | 0.63026 | 0.82216 | 1.0687 | 1.349 | 1.6872 | 2.0859 | 2.5899 | 3.0728 | 3.5881 | 4.1035 | 4.6106 | 5.0906 | 5.4912 | 5.8719 | 6.2174 | 7.1777 | 7.752
West Midlands | Cellarhead 132kV | TEAN 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.26744 | 0.29917 | 0.33792 | 0.39076 | 0.45453 | 0.52898 | 0.61931 | 0.75025 | 0.86461 | 1.0019 | 1.1221 | 1.2367 | 1.3762 | 1.5044 | 1.6264 | 1.7426 | 2.2867 | 2.5797 | 0.62291 | 0.69071 | 0.77551 | 0.89064 | 1.0308 | 1.1967 | 1.4001 | 1.6911 | 1.9488 | 2.2614 | 2.528 | 2.7765 | 3.0748 | 3.3475 | 3.6068 | 3.8535 | 5.0338 | 5.7078
West Midlands | Cellarhead 132kV | TEAN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.29203 | 0.37192 | 0.50813 | 0.65096 | 0.81787 | 1.0142 | 1.239 | 1.5103 | 1.7643 | 2.0021 | 2.2453 | 2.4948 | 2.7219 | 2.8238 | 2.919 | 3.033 | 3.5112 | 3.9386 | 0.67617 | 0.84802 | 1.1547 | 1.4725 | 1.8444 | 2.2823 | 2.7807 | 3.3787 | 3.9416 | 4.4735 | 5.0203 | 5.5789 | 6.095 | 6.3285 | 6.5464 | 6.8037 | 7.9269 | 8.9708
West Midlands | Cellarhead 132kV | TEAN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.28447 | 0.34421 | 0.4099 | 0.50081 | 0.62395 | 0.77941 | 0.9776 | 1.2076 | 1.4337 | 1.6585 | 1.8898 | 2.1192 | 2.3247 | 2.4682 | 2.6173 | 2.7715 | 3.2764 | 3.4656 | 0.66317 | 0.79745 | 0.94206 | 1.1466 | 1.4229 | 1.7736 | 2.2252 | 2.7414 | 3.2546 | 3.759 | 4.2756 | 4.7894 | 5.2493 | 5.5614 | 5.8848 | 6.2182 | 7.3708 | 7.8145
West Midlands | Cellarhead 132kV | TEAN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.27679 | 0.32494 | 0.39213 | 0.46021 | 0.56903 | 0.7099 | 0.86828 | 1.0718 | 1.2573 | 1.4742 | 1.6736 | 1.8714 | 2.056 | 2.1755 | 2.298 | 2.4192 | 2.8693 | 3.2494 | 0.64292 | 0.74788 | 0.89606 | 1.0468 | 1.2928 | 1.611 | 1.9672 | 2.4176 | 2.8308 | 3.3166 | 3.7525 | 4.1837 | 4.5843 | 4.8381 | 5.0986 | 5.3578 | 6.3919 | 7.3077
West Midlands | Cellarhead 132kV | Whitfield 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 0.34796 | 0.4154 | 0.5013 | 0.595 | 0.70618 | 0.82965 | 0.96922 | 1.1852 | 1.348 | 1.5176 | 1.6947 | 1.8836 | 2.099 | 2.3215 | 2.5467 | 2.7644 | 3.6604 | 3.8689 | 0.81537 | 0.95582 | 1.1335 | 1.3274 | 1.5573 | 1.8126 | 2.1011 | 2.5432 | 2.8783 | 3.2275 | 3.591 | 3.9773 | 4.4171 | 4.8716 | 5.3325 | 5.777 | 7.6029 | 8.0471
West Midlands | Cellarhead 132kV | Whitfield 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 0.41671 | 0.58584 | 0.79342 | 1.0347 | 1.309 | 1.6068 | 1.9604 | 2.3845 | 2.7668 | 3.0833 | 3.379 | 3.6909 | 3.8755 | 3.9701 | 4.0237 | 4.0736 | 4.2933 | 4.5022 | 0.96458 | 1.3165 | 1.747 | 2.2475 | 2.8157 | 3.4324 | 4.1612 | 5.0299 | 5.8161 | 6.4702 | 7.0866 | 7.7385 | 8.1296 | 8.3343 | 8.4562 | 8.5705 | 9.0839 | 9.5695
West Midlands | Cellarhead 132kV | Whitfield 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 0.39568 | 0.50064 | 0.63922 | 0.79188 | 0.96173 | 1.1563 | 1.3668 | 1.7006 | 1.9951 | 2.3012 | 2.6229 | 2.9167 | 3.2033 | 3.4665 | 3.7083 | 3.9221 | 4.4519 | 4.66 | 0.92866 | 1.1566 | 1.4519 | 1.7777 | 2.1391 | 2.5519 | 2.9947 | 3.6914 | 4.3099 | 4.9498 | 5.6208 | 6.2304 | 6.8252 | 7.3703 | 7.8716 | 8.3169 | 9.4629 | 9.9488
West Midlands | Cellarhead 132kV | Whitfield 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 0.37262 | 0.46069 | 0.57642 | 0.71184 | 0.86686 | 1.0453 | 1.2549 | 1.5433 | 1.8001 | 2.0763 | 2.3826 | 2.6924 | 2.9714 | 3.2046 | 3.4127 | 3.5976 | 3.9888 | 4.1349 | 0.86852 | 1.0535 | 1.2945 | 1.5776 | 1.9019 | 2.2751 | 2.7109 | 3.3029 | 3.8339 | 4.4034 | 5.0352 | 5.6752 | 6.2485 | 6.7241 | 7.1476 | 7.5253 | 8.3533 | 8.691
West Midlands | East Claydon 132kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Counterfactual | 1.1292 | 1.192 | 1.2962 | 1.4238 | 1.561 | 1.6932 | 1.8219 | 1.966 | 2.0817 | 2.2093 | 2.3369 | 2.4642 | 2.6014 | 2.7358 | 2.8648 | 2.9946 | 3.6087 | 3.8663 | 2.4558 | 2.5891 | 2.8078 | 3.0751 | 3.3632 | 3.6418 | 3.9145 | 4.2172 | 4.462 | 4.7341 | 5.0043 | 5.2706 | 5.5549 | 5.8327 | 6.0984 | 6.3656 | 7.6406 | 8.1999
West Midlands | East Claydon 132kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.1704 | 1.3007 | 1.508 | 1.7573 | 2.0289 | 2.3037 | 2.5995 | 2.8961 | 3.163 | 3.3926 | 3.6052 | 3.808 | 3.958 | 4.0523 | 4.1339 | 4.2018 | 4.5255 | 4.8059 | 2.5462 | 2.8248 | 3.2725 | 3.8082 | 4.3913 | 4.9818 | 5.6161 | 6.2439 | 6.8101 | 7.2997 | 7.7562 | 8.1902 | 8.5202 | 8.7298 | 8.9179 | 9.0735 | 9.824 | 10.4887
West Midlands | East Claydon 132kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.1588 | 1.2578 | 1.4087 | 1.5998 | 1.8056 | 2.0331 | 2.2536 | 2.4774 | 2.6718 | 2.904 | 3.1192 | 3.3298 | 3.5312 | 3.7078 | 3.8751 | 4.0245 | 4.488 | 4.7101 | 2.5261 | 2.7465 | 3.0756 | 3.4917 | 3.9409 | 4.4413 | 4.9233 | 5.402 | 5.8189 | 6.3244 | 6.7821 | 7.2306 | 7.6596 | 8.0322 | 8.3862 | 8.704 | 9.7293 | 10.2427
West Midlands | East Claydon 132kV | BLOXHAM 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.1468 | 1.2274 | 1.3631 | 1.5324 | 1.7213 | 1.916 | 2.1193 | 2.3291 | 2.5086 | 2.7092 | 2.9068 | 3.0949 | 3.2735 | 3.4301 | 3.5948 | 3.7262 | 4.1071 | 4.342 | 2.4946 | 2.6686 | 2.9588 | 3.3211 | 3.7277 | 4.1475 | 4.5866 | 5.0291 | 5.4083 | 5.8322 | 6.2455 | 6.6379 | 7.0091 | 7.3334 | 7.6815 | 7.9553 | 8.7875 | 9.3311
West Midlands | East Claydon 132kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.94775 | 1.0087 | 1.0876 | 1.1701 | 1.2543 | 1.3463 | 1.458 | 1.634 | 1.776 | 1.9405 | 2.0964 | 2.2446 | 2.3999 | 2.5494 | 2.6928 | 2.8383 | 3.5877 | 4.0072 | 2.3048 | 2.4342 | 2.6019 | 2.7777 | 2.958 | 3.1563 | 3.3999 | 3.7806 | 4.0896 | 4.4525 | 4.7917 | 5.1079 | 5.4352 | 5.7481 | 6.0471 | 6.3501 | 7.9369 | 8.8636
West Midlands | East Claydon 132kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.98596 | 1.1162 | 1.3044 | 1.5067 | 1.7175 | 1.948 | 2.2442 | 2.5897 | 2.8923 | 3.1793 | 3.4601 | 3.7155 | 3.9118 | 4.0361 | 4.1801 | 4.3923 | 4.9247 | 5.3943 | 2.3874 | 2.666 | 3.0763 | 3.513 | 3.9656 | 4.4619 | 5.1062 | 5.8491 | 6.4971 | 7.1211 | 7.7377 | 8.295 | 8.7328 | 9.0102 | 9.3455 | 9.8541 | 11.0854 | 12.209
West Midlands | East Claydon 132kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.9739 | 1.0728 | 1.1821 | 1.3178 | 1.4463 | 1.6384 | 1.8625 | 2.1379 | 2.3865 | 2.7186 | 3.2108 | 3.4763 | 3.7265 | 3.9288 | 4.1252 | 4.3036 | 4.944 | 5.2321 | 2.3664 | 2.5867 | 2.8224 | 3.1184 | 3.3983 | 3.8277 | 4.3293 | 4.9319 | 5.4782 | 6.2263 | 7.3683 | 7.9474 | 8.4927 | 8.9245 | 9.3449 | 9.7291 | 11.1632 | 11.8254
West Midlands | East Claydon 132kV | EPWELL 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.96322 | 1.0439 | 1.1535 | 1.27 | 1.3936 | 1.5464 | 1.7487 | 2.0083 | 2.2265 | 2.4893 | 2.7359 | 2.9653 | 3.1772 | 3.3557 | 3.5683 | 3.8348 | 4.3927 | 4.8201 | 2.3378 | 2.5118 | 2.7472 | 2.998 | 3.266 | 3.5985 | 4.0445 | 4.605 | 5.0738 | 5.6444 | 6.1715 | 6.659 | 7.1067 | 7.4798 | 7.9416 | 8.5477 | 9.7975 | 10.8045
West Midlands | East Claydon 132kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.66355 | 0.73016 | 0.81457 | 0.91368 | 1.0277 | 1.1604 | 1.3078 | 1.5313 | 1.7153 | 1.9265 | 2.1216 | 2.3085 | 2.5067 | 2.6989 | 2.8901 | 3.0855 | 4.0974 | 4.6321 | 1.5658 | 1.7066 | 1.8858 | 2.0967 | 2.3398 | 2.6252 | 2.9458 | 3.4253 | 3.8249 | 4.2886 | 4.7091 | 5.1039 | 5.5175 | 5.9166 | 6.3141 | 6.72 | 8.858 | 10.0435
West Midlands | East Claydon 132kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.71939 | 0.87941 | 1.1056 | 1.3646 | 1.6525 | 1.9575 | 2.3169 | 2.7493 | 3.1437 | 3.4948 | 3.838 | 4.1597 | 4.3991 | 4.5425 | 4.6583 | 4.7711 | 5.4576 | 6.0879 | 1.6866 | 2.0262 | 2.5172 | 3.0753 | 3.6928 | 4.3486 | 5.118 | 6.0374 | 6.88 | 7.6379 | 8.3883 | 9.0896 | 9.625 | 9.9474 | 10.2139 | 10.4763 | 12.1001 | 13.6039
West Midlands | East Claydon 132kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.70197 | 0.81298 | 0.93106 | 1.0948 | 1.275 | 1.4843 | 1.7458 | 2.0834 | 2.3973 | 2.7137 | 3.0585 | 3.3985 | 3.8519 | 4.1164 | 4.3735 | 4.606 | 5.4139 | 5.8155 | 1.6563 | 1.9025 | 2.1555 | 2.5132 | 2.9053 | 3.3637 | 3.9419 | 4.6738 | 5.3628 | 6.0485 | 6.797 | 7.5368 | 8.5651 | 9.1282 | 9.6772 | 10.1772 | 11.9935 | 12.9142
West Midlands | East Claydon 132kV | SHIPSTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.6853 | 0.77608 | 0.89238 | 1.036 | 1.2089 | 1.4208 | 1.6544 | 1.9683 | 2.2469 | 2.5675 | 2.8729 | 3.1636 | 3.4362 | 3.6688 | 3.8948 | 4.0987 | 4.8777 | 5.4456 | 1.6123 | 1.8075 | 2.0558 | 2.3642 | 2.7384 | 3.2002 | 3.7065 | 4.3755 | 4.9733 | 5.6644 | 6.3117 | 6.9268 | 7.5012 | 7.9863 | 8.4594 | 8.89 | 10.6575 | 11.9961
West Midlands | Feckenham 66kV | BEVINGTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.98203 | 1.0294 | 1.0929 | 1.1708 | 1.2565 | 1.3609 | 1.4867 | 1.6829 | 1.8476 | 2.0297 | 2.1976 | 2.353 | 2.5185 | 2.6793 | 2.8402 | 3.005 | 3.8548 | 4.3267 | 2.3833 | 2.4825 | 2.6176 | 2.7834 | 2.9666 | 3.1912 | 3.4647 | 3.8855 | 4.2431 | 4.6427 | 5.0045 | 5.3331 | 5.6788 | 6.0128 | 6.3476 | 6.6902 | 8.4863 | 9.5292
West Midlands | Feckenham 66kV | BEVINGTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.028 | 1.1435 | 1.3217 | 1.528 | 1.7567 | 2.0116 | 2.3323 | 2.7155 | 3.0464 | 3.3433 | 3.6402 | 3.9169 | 4.1254 | 4.2634 | 4.3756 | 4.4838 | 5.2038 | 5.7486 | 2.4828 | 2.7248 | 3.1118 | 3.5564 | 4.0462 | 4.5943 | 5.282 | 6.0988 | 6.8058 | 7.4463 | 8.0951 | 8.6982 | 9.164 | 9.4728 | 9.7289 | 9.9781 | 11.6823 | 12.9789
West Midlands | Feckenham 66kV | BEVINGTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.0137 | 1.089 | 1.1788 | 1.3065 | 1.4403 | 1.635 | 1.876 | 2.1583 | 2.4239 | 2.7004 | 3 | 3.4502 | 3.8821 | 4.1169 | 4.3426 | 4.5469 | 5.263 | 5.6116 | 2.4581 | 2.6232 | 2.8152 | 3.094 | 3.3846 | 3.811 | 4.3435 | 4.9555 | 5.5389 | 6.1383 | 6.7885 | 7.8199 | 8.8066 | 9.3073 | 9.79 | 10.2298 | 11.8354 | 12.6316
West Midlands | Feckenham 66kV | BEVINGTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.99988 | 1.0622 | 1.1516 | 1.2605 | 1.3926 | 1.5621 | 1.7699 | 2.0458 | 2.2872 | 2.565 | 2.8252 | 3.0729 | 3.3045 | 3.5034 | 3.6968 | 3.8706 | 4.6319 | 5.1242 | 2.4215 | 2.5531 | 2.7439 | 2.9775 | 3.2634 | 3.6324 | 4.0833 | 4.6722 | 5.1906 | 5.7897 | 6.3415 | 6.8658 | 7.3541 | 7.7692 | 8.1745 | 8.542 | 10.291 | 11.4492
West Midlands | Feckenham 66kV | BROADWAY 66 11kV S STN | Primary Substation | 11 | Counterfactual | 1.3395 | 1.4127 | 1.4934 | 1.6053 | 1.7216 | 1.8551 | 2.0026 | 2.2346 | 2.4272 | 2.6404 | 2.8519 | 3.0418 | 3.2478 | 3.45 | 3.6499 | 3.8538 | 4.8245 | 5.2922 | 3.2738 | 3.4299 | 3.6 | 3.8354 | 4.0804 | 4.3628 | 4.6765 | 5.1644 | 5.5734 | 6.0289 | 6.4763 | 6.8721 | 7.298 | 7.7153 | 8.1279 | 8.5489 | 10.5722 | 11.5862
West Midlands | Feckenham 66kV | BROADWAY 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.397 | 1.5693 | 1.7741 | 2.0323 | 2.3116 | 2.6123 | 2.9998 | 3.4538 | 3.8481 | 4.1693 | 4.4778 | 4.7699 | 4.9795 | 4.5273 | 4.6987 | 4.8063 | 5.3317 | 5.8327 | 3.3984 | 3.7668 | 4.2041 | 4.7535 | 5.3458 | 5.9837 | 6.805 | 7.7596 | 8.5906 | 9.2705 | 9.9307 | 10.5536 | 11.0112 | 9.8378 | 10.2387 | 10.4844 | 11.7044 | 12.8757
West Midlands | Feckenham 66kV | BROADWAY 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.3797 | 1.5055 | 1.6357 | 1.8157 | 1.9907 | 2.2474 | 2.541 | 2.883 | 3.1616 | 3.5754 | 3.8998 | 4.2156 | 3.9483 | 4.2312 | 4.5006 | 4.7419 | 5.5169 | 6.5647 | 3.3686 | 3.6506 | 3.9317 | 4.3229 | 4.7019 | 5.2597 | 5.8976 | 6.6274 | 7.2235 | 8.1452 | 8.8358 | 9.509 | 8.7244 | 9.3243 | 9.8965 | 10.4123 | 12.1335 | 14.6572
West Midlands | Feckenham 66kV | BROADWAY 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.362 | 1.4608 | 1.5729 | 1.7306 | 1.9048 | 2.416 | 2.6721 | 3.0046 | 3.294 | 3.6156 | 3.913 | 4.1983 | 4.4711 | 4.7138 | 5.0024 | 5.208 | 5.8412 | 6.2974 | 3.3219 | 3.5352 | 3.7729 | 4.1087 | 4.4809 | 5.6864 | 6.2342 | 6.9352 | 7.5479 | 8.2288 | 8.8508 | 9.4469 | 10.0159 | 10.5204 | 11.1447 | 11.5756 | 12.9701 | 14.0197
West Midlands | Feckenham 66kV | BROTHERIDGE GRN 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.57137 | 0.61166 | 0.6637 | 0.72739 | 0.80037 | 0.88601 | 0.98654 | 1.1405 | 1.2634 | 1.3959 | 1.5199 | 1.6393 | 1.7673 | 1.8939 | 2.0158 | 2.1387 | 2.7584 | 3.0533 | 1.3857 | 1.4704 | 1.5805 | 1.7152 | 1.8698 | 2.0527 | 2.2692 | 2.5986 | 2.8632 | 3.1521 | 3.4191 | 3.6718 | 3.9395 | 4.2028 | 4.4552 | 4.7098 | 6.0119 | 6.6642
West Midlands | Feckenham 66kV | BROTHERIDGE GRN 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.60759 | 0.70308 | 0.84021 | 1.0004 | 1.1787 | 1.3656 | 1.6034 | 1.8811 | 2.1282 | 2.3582 | 2.5765 | 2.7773 | 2.9241 | 3.0115 | 3.0778 | 3.1403 | 3.3446 | 3.5786 | 1.4642 | 1.6651 | 1.9606 | 2.3039 | 2.6846 | 3.0842 | 3.5976 | 4.1895 | 4.7145 | 5.2115 | 5.6883 | 6.1236 | 6.4506 | 6.6474 | 6.8011 | 6.948 | 7.4254 | 7.9749
West Midlands | Feckenham 66kV | BROTHERIDGE GRN 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.59626 | 0.65748 | 0.73274 | 0.83609 | 0.93176 | 1.0848 | 1.2628 | 1.496 | 1.7013 | 1.9121 | 2.1351 | 2.3062 | 2.478 | 2.638 | 2.7871 | 2.9193 | 3.2745 | 3.6952 | 1.4446 | 1.5795 | 1.7407 | 1.9658 | 2.1732 | 2.5152 | 2.9112 | 3.4179 | 3.8652 | 4.3207 | 4.8022 | 5.1563 | 5.516 | 5.8522 | 6.1665 | 6.4467 | 7.2247 | 8.2379
West Midlands | Feckenham 66kV | BROTHERIDGE GRN 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.5855 | 0.63428 | 0.70135 | 0.79329 | 0.89206 | 1.0162 | 1.1793 | 1.392 | 1.5745 | 1.7898 | 1.9978 | 2.1935 | 2.3729 | 2.5283 | 2.6736 | 2.8036 | 3.2049 | 3.4991 | 1.416 | 1.5194 | 1.6617 | 1.8582 | 2.0706 | 2.3394 | 2.6971 | 3.1533 | 3.543 | 4.0075 | 4.4501 | 4.864 | 5.2414 | 5.5657 | 5.8699 | 6.1438 | 7.0441 | 7.7409
West Midlands | Feckenham 66kV | EVESHAM 66 11kV S STN | Primary Substation | 11 | Counterfactual | 2.3221 | 2.4835 | 2.6885 | 2.9422 | 3.2584 | 3.5998 | 3.972 | 4.5645 | 5.0173 | 5.5176 | 6.0331 | 6.5227 | 7.0545 | 7.5659 | 8.0354 | 8.5156 | 10.7826 | 11.8041 | 5.6092 | 5.9475 | 6.3758 | 6.9054 | 7.566 | 8.2813 | 9.0635 | 10.3038 | 11.2539 | 12.3154 | 13.4169 | 14.4549 | 15.5719 | 16.6386 | 17.6004 | 18.5846 | 23.266 | 25.4621
West Midlands | Feckenham 66kV | EVESHAM 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.4708 | 2.8569 | 3.3549 | 4.0178 | 4.758 | 5.4702 | 6.486 | 7.6552 | 8.4881 | 9.337 | 10.1539 | 10.7697 | 11.1771 | 11.4719 | 11.7442 | 11.9302 | 13.0528 | 14.0689 | 5.9317 | 6.7419 | 7.7929 | 9.1922 | 10.7527 | 12.2481 | 14.4107 | 16.8864 | 18.6031 | 20.4303 | 22.2037 | 23.4845 | 24.3485 | 24.9838 | 25.6031 | 26.0166 | 28.618 | 30.9729
West Midlands | Feckenham 66kV | EVESHAM 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.4256 | 2.6801 | 3.063 | 3.5329 | 3.9547 | 4.6299 | 5.3441 | 6.1875 | 6.6929 | 7.6216 | 8.2995 | 9.1512 | 9.9064 | 10.6334 | 11.2665 | 11.8307 | 13.543 | 14.8216 | 5.8537 | 6.4119 | 7.2336 | 8.2461 | 9.1514 | 10.6337 | 12.1963 | 14.0193 | 15.0459 | 17.0937 | 18.4968 | 20.3453 | 21.9444 | 23.4944 | 24.8282 | 26.023 | 29.7879 | 32.7722
West Midlands | Feckenham 66kV | EVESHAM 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.3786 | 2.5903 | 2.8754 | 3.2661 | 3.7173 | 4.2068 | 4.8713 | 5.7289 | 6.394 | 7.2382 | 8.0681 | 8.7746 | 9.3991 | 9.9695 | 10.5719 | 11.0532 | 12.5059 | 13.4257 | 5.7306 | 6.1789 | 6.7792 | 7.6059 | 8.5644 | 9.6051 | 11.0363 | 12.8624 | 14.256 | 16.0795 | 17.8617 | 19.344 | 20.6325 | 21.8076 | 23.0764 | 24.0763 | 27.2725 | 29.3743
West Midlands | Feckenham 66kV | Feckenham 66/11kVDUMMY | Primary Substation | 11 | Counterfactual | 0.076546 | 0.083338 | 0.092355 | 0.103 | 0.11512 | 0.13101 | 0.15107 | 0.18004 | 0.20506 | 0.2349 | 0.26044 | 0.28312 | 0.30594 | 0.32759 | 0.34966 | 0.37218 | 0.4968 | 0.576 | 0.18247 | 0.19732 | 0.21715 | 0.24068 | 0.26762 | 0.30314 | 0.34849 | 0.41317 | 0.46977 | 0.53808 | 0.59529 | 0.64484 | 0.69383 | 0.74 | 0.78705 | 0.83502 | 1.1067 | 1.2876
West Midlands | Feckenham 66kV | Feckenham 66/11kVDUMMY | Primary Substation | 11 | Electric Engagement | 0.081889 | 0.098968 | 0.12665 | 0.15807 | 0.19235 | 0.2329 | 0.27993 | 0.33481 | 0.38657 | 0.43577 | 0.48736 | 0.53511 | 0.57499 | 0.60098 | 0.62391 | 0.64646 | 0.76804 | 0.87717 | 0.19404 | 0.23126 | 0.29381 | 0.36386 | 0.43972 | 0.52991 | 0.63405 | 0.7547 | 0.86901 | 0.9788 | 1.0953 | 1.2029 | 1.2945 | 1.3537 | 1.4066 | 1.459 | 1.7444 | 2.0099
West Midlands | Feckenham 66kV | Feckenham 66/11kVDUMMY | Primary Substation | 11 | Holistic Transition | 0.08022 | 0.093825 | 0.10515 | 0.12484 | 0.1458 | 0.17482 | 0.21294 | 0.25878 | 0.30396 | 0.34845 | 0.39758 | 0.44614 | 0.49309 | 0.52829 | 0.56324 | 0.59536 | 0.72333 | 0.77866 | 0.19108 | 0.22232 | 0.24707 | 0.29126 | 0.33811 | 0.40356 | 0.49073 | 0.59361 | 0.69622 | 0.79588 | 0.90618 | 1.0155 | 1.121 | 1.1981 | 1.2747 | 1.3456 | 1.6388 | 1.7676
West Midlands | Feckenham 66kV | Feckenham 66/11kVDUMMY | Primary Substation | 11 | Hydrogen Evolution | 0.078677 | 0.087799 | 0.10004 | 0.11521 | 0.13471 | 0.16168 | 0.19316 | 0.23313 | 0.26985 | 0.3137 | 0.35319 | 0.39032 | 0.4249 | 0.45234 | 0.47996 | 0.5051 | 0.61505 | 0.71318 | 0.18705 | 0.20703 | 0.23393 | 0.26764 | 0.31143 | 0.37223 | 0.44293 | 0.5312 | 0.6128 | 0.71089 | 0.79739 | 0.87854 | 0.95369 | 1.0123 | 1.0714 | 1.1259 | 1.3799 | 1.6154
West Midlands | Feckenham 66kV | GREAT ALNE 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.77781 | 0.83409 | 0.90273 | 0.96955 | 1.0472 | 1.1395 | 1.244 | 1.4032 | 1.5329 | 1.6786 | 1.8183 | 1.9553 | 2.1042 | 2.2489 | 2.3927 | 2.5407 | 3.2756 | 3.6477 | 1.8812 | 2.0007 | 2.1463 | 2.2887 | 2.4542 | 2.6519 | 2.8754 | 3.2118 | 3.4887 | 3.8024 | 4.0984 | 4.3844 | 4.6922 | 4.9903 | 5.2871 | 5.5921 | 7.1297 | 7.9414
West Midlands | Feckenham 66kV | GREAT ALNE 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.82275 | 0.95386 | 1.1262 | 1.3084 | 1.5133 | 1.7473 | 2.0053 | 2.3169 | 2.5983 | 2.8429 | 3.0776 | 3.2982 | 3.4584 | 3.559 | 3.6401 | 3.7171 | 4.1409 | 4.5395 | 1.9789 | 2.2587 | 2.6308 | 3.0225 | 3.4611 | 3.9633 | 4.5088 | 5.1635 | 5.7577 | 6.2788 | 6.7846 | 7.2581 | 7.6101 | 7.8328 | 8.0161 | 8.1923 | 9.1769 | 10.1168
West Midlands | Feckenham 66kV | GREAT ALNE 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.80942 | 0.90404 | 1.0072 | 1.1244 | 1.2552 | 1.4228 | 1.6051 | 1.8447 | 2.0628 | 2.2844 | 2.5246 | 2.7605 | 2.9865 | 3.1821 | 3.3734 | 3.5458 | 4.1292 | 4.4348 | 1.9558 | 2.1668 | 2.391 | 2.6491 | 2.9362 | 3.3042 | 3.7015 | 4.2137 | 4.6856 | 5.1602 | 5.6748 | 6.1814 | 6.6663 | 7.0798 | 7.485 | 7.8526 | 9.1494 | 9.8444
West Midlands | Feckenham 66kV | GREAT ALNE 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.79668 | 0.87455 | 0.97335 | 1.0782 | 1.2043 | 1.3598 | 1.5259 | 1.7523 | 1.9507 | 2.1757 | 2.3943 | 2.6031 | 2.8022 | 2.9756 | 3.1454 | 3.2962 | 3.7914 | 4.1626 | 1.922 | 2.0905 | 2.3032 | 2.5295 | 2.8034 | 3.1423 | 3.4966 | 3.9728 | 4.3926 | 4.8702 | 5.3281 | 5.7651 | 6.1804 | 6.5398 | 6.8928 | 7.209 | 8.3056 | 9.1652
West Midlands | Feckenham 66kV | IPSLEY 66 11kV S STN | Primary Substation | 11 | Counterfactual | 3.0903 | 3.2166 | 3.3661 | 3.5118 | 3.6814 | 3.8667 | 4.0796 | 4.3574 | 4.5777 | 4.8178 | 5.0606 | 5.309 | 5.5853 | 5.8564 | 6.1305 | 6.4065 | 7.6724 | 8.1308 | 7.4123 | 7.6879 | 8.0073 | 8.3112 | 8.665 | 9.0594 | 9.5134 | 10.0863 | 10.544 | 11.0444 | 11.5467 | 12.0561 | 12.62 | 13.173 | 13.7342 | 14.297 | 16.8986 | 17.8737
West Midlands | Feckenham 66kV | IPSLEY 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 3.1862 | 3.5157 | 3.8833 | 4.2162 | 4.6031 | 5.1199 | 5.6198 | 6.1754 | 6.6735 | 7.0893 | 7.4889 | 7.8751 | 8.1369 | 8.3031 | 8.4334 | 8.5559 | 9.1604 | 9.6337 | 7.6229 | 8.3517 | 9.1519 | 9.8497 | 10.6593 | 11.7857 | 12.8353 | 13.9811 | 15.0114 | 15.8766 | 16.7124 | 17.5195 | 18.0739 | 18.4301 | 18.7156 | 18.986 | 20.3495 | 21.4241
West Midlands | Feckenham 66kV | IPSLEY 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 3.1605 | 3.4168 | 3.68 | 3.9043 | 4.2635 | 4.5703 | 4.8861 | 5.2992 | 5.6573 | 6.0395 | 6.4595 | 6.8656 | 7.2599 | 7.6196 | 7.9774 | 8.2955 | 9.2449 | 9.6995 | 7.5788 | 8.1699 | 8.7601 | 9.2433 | 10.0498 | 10.7137 | 11.3859 | 12.2494 | 13.0032 | 13.8063 | 14.6825 | 15.5295 | 16.3527 | 17.1003 | 17.8461 | 18.5125 | 20.5676 | 21.5865
West Midlands | Feckenham 66kV | IPSLEY 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 3.1322 | 3.3533 | 3.6017 | 3.8098 | 4.0555 | 4.3087 | 4.7248 | 5.1524 | 5.497 | 5.8766 | 6.2695 | 6.6549 | 7.0216 | 7.3456 | 7.6697 | 7.9503 | 8.7202 | 9.1192 | 7.5052 | 8.0071 | 8.5568 | 8.9941 | 9.5125 | 10.044 | 10.963 | 11.8558 | 12.5694 | 13.3542 | 14.1615 | 14.9561 | 15.7084 | 16.3722 | 17.0381 | 17.6175 | 19.2626 | 20.1535
West Midlands | Feckenham 66kV | LONG MARSTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.56408 | 0.62509 | 0.68938 | 0.78966 | 0.98753 | 1.1812 | 1.3924 | 1.6542 | 1.8935 | 2.1616 | 2.3982 | 2.6288 | 2.8666 | 3.1006 | 3.3337 | 3.5696 | 4.5239 | 4.8715 | 1.3517 | 1.4847 | 1.6211 | 1.8344 | 2.2621 | 2.6834 | 3.1448 | 3.7118 | 4.2345 | 4.8234 | 5.3377 | 5.8338 | 6.3415 | 6.8402 | 7.3373 | 7.8399 | 9.8817 | 10.6554
West Midlands | Feckenham 66kV | LONG MARSTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.60296 | 0.75138 | 0.91397 | 1.1271 | 1.4469 | 1.758 | 2.1052 | 2.4992 | 2.8771 | 3.2339 | 3.5653 | 3.8822 | 4.1437 | 4.3439 | 4.5238 | 4.779 | 5.4592 | 5.8816 | 1.4362 | 1.7645 | 2.1174 | 2.5775 | 3.2688 | 3.9438 | 4.6939 | 5.5398 | 6.3549 | 7.1311 | 7.8584 | 8.5523 | 9.1346 | 9.5809 | 9.9861 | 10.582 | 12.148 | 13.157
West Midlands | Feckenham 66kV | LONG MARSTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.59127 | 0.70649 | 0.80611 | 0.95777 | 1.1902 | 1.4369 | 1.7175 | 2.0486 | 2.3704 | 2.7084 | 3.2011 | 3.5302 | 3.8529 | 4.1366 | 4.4132 | 4.6725 | 5.4911 | 5.7648 | 1.4161 | 1.6815 | 1.8957 | 2.2269 | 2.7341 | 3.2766 | 3.8965 | 4.6181 | 5.325 | 6.0623 | 7.1875 | 7.907 | 8.6125 | 9.2253 | 9.8239 | 10.3881 | 12.2199 | 12.8496
West Midlands | Feckenham 66kV | LONG MARSTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.5795 | 0.68137 | 0.77082 | 0.90563 | 1.1439 | 1.391 | 1.6607 | 1.9771 | 2.2781 | 2.6173 | 2.9269 | 3.2259 | 3.5137 | 3.7745 | 4.0313 | 4.3491 | 5.1041 | 5.4792 | 1.385 | 1.6163 | 1.8077 | 2.0978 | 2.6156 | 3.157 | 3.7456 | 4.4276 | 5.0801 | 5.8171 | 6.4822 | 7.1242 | 7.7409 | 8.2972 | 8.8464 | 9.5578 | 11.2434 | 12.1305
West Midlands | Feckenham 66kV | MORETON 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.37976 | 0.45508 | 0.54718 | 0.64896 | 0.75764 | 0.88177 | 1.02 | 1.2178 | 1.3805 | 1.5559 | 1.7285 | 1.9016 | 2.0877 | 2.2716 | 2.4519 | 2.6328 | 3.4841 | 3.8981 | 0.88098 | 1.0432 | 1.2372 | 1.4508 | 1.679 | 1.9402 | 2.2321 | 2.6455 | 2.9885 | 3.3602 | 3.7229 | 4.0829 | 4.467 | 4.8466 | 5.2188 | 5.5917 | 7.3595 | 8.2493
West Midlands | Feckenham 66kV | MORETON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.42903 | 0.60143 | 0.80573 | 1.0319 | 1.2786 | 1.5538 | 1.8689 | 2.2374 | 2.5712 | 2.8614 | 3.1326 | 3.3903 | 3.577 | 3.7017 | 3.8014 | 3.8942 | 4.3451 | 4.7666 | 0.98762 | 1.3622 | 1.7988 | 2.2786 | 2.8002 | 3.3833 | 4.0471 | 4.817 | 5.517 | 6.1295 | 6.7064 | 7.2535 | 7.658 | 7.9318 | 8.1551 | 8.3646 | 9.3952 | 10.3676
West Midlands | Feckenham 66kV | MORETON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.41327 | 0.54787 | 0.69054 | 0.85463 | 1.0308 | 1.2399 | 1.4699 | 1.7668 | 2.0268 | 2.2985 | 2.5868 | 2.8646 | 3.1324 | 3.3734 | 3.6049 | 3.8123 | 4.4938 | 4.9022 | 0.96025 | 1.2663 | 1.5764 | 1.9325 | 2.3143 | 2.7671 | 3.264 | 3.8953 | 4.4501 | 5.0268 | 5.6386 | 6.2288 | 6.7982 | 7.3083 | 7.799 | 8.2412 | 9.7431 | 10.671
West Midlands | Feckenham 66kV | MORETON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.39874 | 0.50349 | 0.63195 | 0.77609 | 0.93746 | 1.1265 | 1.34 | 1.6208 | 1.8668 | 2.1361 | 2.4064 | 2.6649 | 2.9137 | 3.1355 | 3.3479 | 3.5348 | 4.1115 | 4.4962 | 0.92166 | 1.152 | 1.4266 | 1.7331 | 2.0774 | 2.4816 | 2.9355 | 3.5244 | 4.0421 | 4.6077 | 5.1717 | 5.7107 | 6.2289 | 6.6902 | 7.1323 | 7.5233 | 8.7778 | 9.6502
West Midlands | Feckenham 66kV | PERSHORE 66 11kV S STN | Primary Substation | 11 | Counterfactual | 1.9476 | 2.011 | 2.0879 | 2.1796 | 2.2843 | 2.401 | 2.529 | 2.7866 | 2.9959 | 3.2136 | 3.4322 | 3.6162 | 3.8076 | 3.9895 | 4.1632 | 4.3436 | 3.9753 | 4.3787 | 4.8068 | 4.9403 | 5.1007 | 5.2914 | 5.5091 | 5.752 | 6.0185 | 6.5585 | 6.9962 | 7.4544 | 7.9157 | 8.2995 | 8.6954 | 9.0699 | 9.4242 | 9.7924 | 8.4911 | 9.3423
West Midlands | Feckenham 66kV | PERSHORE 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.0041 | 2.1552 | 2.3308 | 2.5533 | 2.8056 | 3.0753 | 3.5476 | 4.0423 | 4.4105 | 4.7246 | 4.9898 | 5.2239 | 5.3824 | 5.5057 | 5.6 | 5.6827 | 4.8486 | 5.1802 | 4.9291 | 5.248 | 5.6166 | 6.0838 | 6.6127 | 7.1771 | 8.1955 | 9.2461 | 10.013 | 10.6769 | 11.2371 | 11.7233 | 12.058 | 12.3241 | 12.5319 | 12.7158 | 10.5426 | 11.2966
West Midlands | Feckenham 66kV | PERSHORE 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.9871 | 2.0918 | 2.223 | 2.3773 | 2.5418 | 2.9005 | 3.2347 | 3.578 | 3.8188 | 4.0718 | 4.3345 | 4.5891 | 4.8593 | 5.1105 | 5.35 | 5.5617 | 4.8904 | 5.4108 | 4.8994 | 5.1304 | 5.4127 | 5.7446 | 6.0977 | 6.893 | 7.6244 | 8.357 | 8.8595 | 9.3879 | 9.9332 | 10.4617 | 11.0269 | 11.5529 | 12.0549 | 12.5009 | 10.6184 | 11.8307
West Midlands | Feckenham 66kV | PERSHORE 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.9699 | 2.0538 | 2.1637 | 2.3022 | 2.4568 | 2.6314 | 2.9506 | 3.3332 | 3.6313 | 3.9647 | 4.2569 | 4.5125 | 4.7502 | 4.9666 | 5.1769 | 5.3581 | 4.6412 | 4.9598 | 4.8546 | 5.0332 | 5.2646 | 5.5562 | 5.8818 | 6.2493 | 6.9441 | 7.7605 | 8.3864 | 9.0927 | 9.7041 | 10.2323 | 10.7205 | 11.1659 | 11.5998 | 11.9755 | 10.0084 | 10.7226
West Midlands | Feckenham 66kV | REDDITCH SOUTH 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.78839 | 0.9821 | 1.2602 | 1.6177 | 2.0351 | 2.4903 | 2.9914 | 3.7079 | 4.3121 | 4.9486 | 5.6008 | 6.2721 | 6.9673 | 7.628 | 8.1426 | 8.658 | 10.9561 | 11.6042 | 1.7425 | 2.148 | 2.726 | 3.4688 | 4.337 | 5.2847 | 6.3291 | 7.8107 | 9.0699 | 10.3988 | 11.7578 | 13.1505 | 14.5854 | 15.946 | 16.9938 | 18.0424 | 22.7375 | 24.1212
West Midlands | Feckenham 66kV | REDDITCH SOUTH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.96404 | 1.4271 | 2.0363 | 2.7733 | 3.6363 | 4.562 | 5.6292 | 6.917 | 8.0817 | 9.0783 | 10.0002 | 10.9009 | 11.5295 | 11.9353 | 12.0946 | 12.2432 | 12.9524 | 13.5976 | 2.1241 | 3.0948 | 4.3706 | 5.9138 | 7.7236 | 9.6659 | 11.8936 | 14.5681 | 16.9953 | 19.0835 | 21.0261 | 22.9213 | 24.2647 | 25.1466 | 25.5032 | 25.8386 | 27.4658 | 28.9492
West Midlands | Feckenham 66kV | REDDITCH SOUTH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.9117 | 1.2178 | 1.6363 | 2.1575 | 2.7537 | 3.4269 | 4.1764 | 5.1664 | 6.0535 | 6.968 | 7.9377 | 8.8922 | 9.7969 | 10.6021 | 11.2161 | 11.762 | 13.2155 | 13.853 | 2.0347 | 2.7045 | 3.6015 | 4.7207 | 6.0003 | 7.4442 | 9.0441 | 11.1295 | 13.0088 | 14.938 | 16.9794 | 18.9896 | 20.8923 | 22.5799 | 23.8544 | 24.9923 | 28.1355 | 29.5979
West Midlands | Feckenham 66kV | REDDITCH SOUTH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.85305 | 1.1044 | 1.4817 | 1.9629 | 2.5338 | 3.1756 | 3.8971 | 4.8592 | 5.7112 | 6.6137 | 7.5479 | 8.461 | 9.321 | 10.087 | 10.6548 | 11.1599 | 12.3299 | 12.8481 | 1.8818 | 2.4133 | 3.2075 | 4.2238 | 5.4346 | 6.7979 | 8.3205 | 10.33 | 12.118 | 14.0063 | 15.9532 | 17.8563 | 19.6448 | 21.2336 | 22.3948 | 23.4307 | 25.9167 | 27.0912
West Midlands | Feckenham 66kV | STOW 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.16086 | 0.19458 | 0.22949 | 0.27293 | 0.32885 | 0.39384 | 0.46836 | 0.57311 | 0.66092 | 0.75765 | 0.84901 | 0.93742 | 1.0305 | 1.122 | 1.2116 | 1.3016 | 1.7361 | 1.9616 | 0.37197 | 0.44676 | 0.52165 | 0.61458 | 0.73389 | 0.87311 | 1.0338 | 1.2573 | 1.4467 | 1.6571 | 1.8531 | 2.0398 | 2.234 | 2.4249 | 2.6117 | 2.7995 | 3.7152 | 4.2117
West Midlands | Feckenham 66kV | STOW 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.18372 | 0.26852 | 0.36275 | 0.47457 | 0.60493 | 0.7523 | 0.91877 | 1.1103 | 1.2857 | 1.4419 | 1.5916 | 1.7338 | 1.8421 | 1.9128 | 1.9714 | 2.0272 | 2.3101 | 2.5773 | 0.42151 | 0.61006 | 0.81532 | 1.057 | 1.3376 | 1.6554 | 2.0124 | 2.4192 | 2.7936 | 3.1296 | 3.4551 | 3.7635 | 4.0038 | 4.162 | 4.2959 | 4.4238 | 5.079 | 5.7092
West Midlands | Feckenham 66kV | STOW 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.17647 | 0.2476 | 0.30521 | 0.38354 | 0.47617 | 0.5905 | 0.71715 | 0.87664 | 1.0169 | 1.1621 | 1.3186 | 1.469 | 1.6141 | 1.7394 | 1.8606 | 1.9698 | 2.3535 | 2.5776 | 0.4089 | 0.57545 | 0.7021 | 0.8751 | 1.0788 | 1.3303 | 1.6095 | 1.9552 | 2.2601 | 2.574 | 2.9123 | 3.2382 | 3.5529 | 3.822 | 4.0826 | 4.3193 | 5.1787 | 5.6949
West Midlands | Feckenham 66kV | STOW 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.16973 | 0.21709 | 0.26759 | 0.33273 | 0.41695 | 0.51842 | 0.6329 | 0.77975 | 0.90886 | 1.0535 | 1.1941 | 1.3264 | 1.4544 | 1.565 | 1.6715 | 1.7654 | 2.0954 | 2.3373 | 0.39097 | 0.4976 | 0.60644 | 0.74686 | 0.92941 | 1.1503 | 1.3981 | 1.7113 | 1.9876 | 2.297 | 2.5948 | 2.8745 | 3.1445 | 3.3768 | 3.6007 | 3.7991 | 4.5292 | 5.0888
West Midlands | Feckenham 66kV | STRATFORD 66 11kV S STN | Primary Substation | 11 | Counterfactual | 2.2418 | 2.4396 | 2.6829 | 2.9522 | 3.212 | 3.5235 | 3.8611 | 4.3344 | 4.7139 | 5.1094 | 5.5011 | 5.9004 | 6.3452 | 6.763 | 7.1767 | 7.5956 | 9.6035 | 10.4423 | 5.0595 | 5.478 | 5.9884 | 6.5499 | 7.0863 | 7.7327 | 8.4348 | 9.4068 | 10.1916 | 11.0137 | 11.8216 | 12.6384 | 13.544 | 14.3929 | 15.2335 | 16.0839 | 20.2038 | 22.0072
West Midlands | Feckenham 66kV | STRATFORD 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.3926 | 2.8328 | 3.3712 | 3.9706 | 4.6324 | 5.3708 | 6.2047 | 7.1453 | 7.9871 | 8.673 | 9.2966 | 9.8905 | 10.2954 | 10.4862 | 10.6716 | 10.7861 | 11.4432 | 12.2751 | 5.3904 | 6.3299 | 7.4749 | 8.7416 | 10.1453 | 11.7091 | 13.4624 | 15.4122 | 17.1636 | 18.5972 | 19.9108 | 21.1586 | 22.0282 | 22.4353 | 22.8631 | 23.1184 | 24.6164 | 26.4768
West Midlands | Feckenham 66kV | STRATFORD 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.3501 | 2.6685 | 3.0316 | 3.4503 | 3.8914 | 4.4234 | 5.0102 | 5.7173 | 6.2448 | 6.9174 | 7.5192 | 8.0956 | 8.6745 | 9.2009 | 9.7028 | 10.1524 | 11.4256 | 12.8534 | 5.3171 | 6.0243 | 6.8115 | 7.7204 | 8.6792 | 9.8325 | 11.0996 | 12.5883 | 13.6704 | 15.1049 | 16.3469 | 17.5333 | 18.7321 | 19.8234 | 20.8672 | 21.8071 | 24.5598 | 27.8848
West Midlands | Feckenham 66kV | STRATFORD 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.3073 | 2.5787 | 2.9184 | 3.2984 | 3.7192 | 4.233 | 4.7873 | 5.4695 | 6.0627 | 6.6831 | 7.306 | 7.9096 | 8.4935 | 9.2864 | 9.8169 | 10.2399 | 11.399 | 12.3015 | 5.2042 | 5.7925 | 6.5193 | 7.3285 | 8.2322 | 9.3393 | 10.5196 | 11.9378 | 13.1771 | 14.4696 | 15.7572 | 17.0033 | 18.2079 | 19.9654 | 21.0803 | 21.9547 | 24.4668 | 26.4837
West Midlands | Feckenham 66kV | STRENSHAM 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.71434 | 0.73816 | 0.76888 | 0.80663 | 0.84824 | 0.89539 | 0.94916 | 1.0456 | 1.1231 | 1.2075 | 1.2986 | 1.4426 | 1.5999 | 1.7581 | 1.9134 | 2.0564 | 2.6566 | 3.0192 | 1.5225 | 1.5721 | 1.636 | 1.7145 | 1.8011 | 1.8994 | 2.0119 | 2.2123 | 2.3745 | 2.5519 | 2.7418 | 3.0366 | 3.3574 | 3.6796 | 3.9963 | 4.2866 | 5.5088 | 6.2556
West Midlands | Feckenham 66kV | STRENSHAM 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.73686 | 0.79583 | 0.87348 | 0.96868 | 1.0759 | 1.1896 | 1.36 | 1.623 | 1.8694 | 2.0866 | 2.252 | 2.4059 | 2.5062 | 2.5747 | 2.6235 | 2.6608 | 2.8138 | 2.9663 | 1.5713 | 1.6943 | 1.8575 | 2.0573 | 2.2818 | 2.5195 | 2.8781 | 3.4222 | 3.9329 | 4.3848 | 4.7271 | 5.0457 | 5.2567 | 5.403 | 5.5096 | 5.593 | 5.9453 | 6.2965
West Midlands | Feckenham 66kV | STRENSHAM 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.72952 | 0.77281 | 0.82344 | 0.88642 | 0.94984 | 1.0594 | 1.1836 | 1.3417 | 1.4885 | 1.6324 | 1.8111 | 1.9793 | 2.142 | 2.2834 | 2.4087 | 2.5139 | 2.7858 | 2.9248 | 1.5587 | 1.6529 | 1.761 | 1.8959 | 2.0312 | 2.2671 | 2.5336 | 2.8686 | 3.1811 | 3.4802 | 3.8493 | 4.1973 | 4.5353 | 4.828 | 5.0882 | 5.3081 | 5.9004 | 6.2151
West Midlands | Feckenham 66kV | STRENSHAM 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.72186 | 0.75893 | 0.80238 | 0.85528 | 0.91576 | 0.98833 | 1.0918 | 1.2699 | 1.4715 | 1.6923 | 1.9208 | 2.142 | 2.3522 | 2.5442 | 2.7095 | 2.8455 | 3.1909 | 3.3259 | 1.5386 | 1.617 | 1.7082 | 1.8193 | 1.9466 | 2.0998 | 2.3185 | 2.6858 | 3.0999 | 3.5532 | 4.021 | 4.4737 | 4.9038 | 5.297 | 5.6342 | 5.9117 | 6.637 | 6.9442
West Midlands | Feckenham 66kV | TEWKESBURY 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.25117 | 0.26944 | 0.29545 | 0.32218 | 0.34964 | 0.38323 | 0.42636 | 0.4949 | 0.54971 | 0.61511 | 0.67693 | 0.73444 | 0.79304 | 0.84887 | 0.90112 | 0.95295 | 1.2366 | 1.3935 | 0.60608 | 0.64451 | 0.70015 | 0.75772 | 0.81741 | 0.8912 | 0.98698 | 1.1385 | 1.2601 | 1.4075 | 1.545 | 1.6702 | 1.7958 | 1.9145 | 2.0247 | 2.1339 | 2.7427 | 3.0983
West Midlands | Feckenham 66kV | TEWKESBURY 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.2646 | 0.30502 | 0.37218 | 0.43973 | 0.51265 | 0.59687 | 0.71508 | 0.84714 | 0.95867 | 1.0699 | 1.18 | 1.2793 | 1.3415 | 1.3803 | 1.4179 | 1.454 | 1.6069 | 1.8179 | 0.6352 | 0.72062 | 0.86881 | 1.017 | 1.176 | 1.3606 | 1.6241 | 1.9143 | 2.1571 | 2.4045 | 2.652 | 2.8729 | 3.0117 | 3.0992 | 3.1874 | 3.2733 | 3.6359 | 4.1444
West Midlands | Feckenham 66kV | TEWKESBURY 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.26057 | 0.28885 | 0.32288 | 0.36378 | 0.40622 | 0.48687 | 0.58078 | 0.69105 | 0.78737 | 0.88548 | 0.96855 | 1.046 | 1.1365 | 1.2135 | 1.2866 | 1.3529 | 1.5892 | 1.7037 | 0.62828 | 0.69032 | 0.76331 | 0.85384 | 0.9473 | 1.1327 | 1.3477 | 1.594 | 1.8093 | 2.0264 | 2.2039 | 2.3669 | 2.5641 | 2.7306 | 2.8891 | 3.0342 | 3.5757 | 3.8414
West Midlands | Feckenham 66kV | TEWKESBURY 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.2565 | 0.28041 | 0.31577 | 0.35213 | 0.39456 | 0.45133 | 0.53541 | 0.63639 | 0.71803 | 0.82013 | 0.91492 | 1.0021 | 1.0798 | 1.1446 | 1.206 | 1.2616 | 1.4765 | 1.662 | 0.61748 | 0.66853 | 0.74495 | 0.82411 | 0.91764 | 1.0439 | 1.2345 | 1.4582 | 1.637 | 1.8643 | 2.0717 | 2.2604 | 2.4276 | 2.5651 | 2.6959 | 2.8158 | 3.3099 | 3.7542
West Midlands | Iron Acton 132kV | ALVESTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.2906 | 1.6799 | 1.7897 | 1.9117 | 2.0694 | 2.2328 | 2.4223 | 2.6964 | 2.9281 | 3.1871 | 3.4358 | 3.7019 | 3.9864 | 4.2665 | 4.5399 | 4.7965 | 6.0022 | 6.5693 | 2.8728 | 3.6644 | 3.8969 | 4.1558 | 4.4905 | 4.8395 | 5.2475 | 5.8311 | 6.3297 | 6.8923 | 7.4242 | 7.9821 | 8.5726 | 9.1525 | 9.7191 | 10.2491 | 12.7746 | 14.0195
West Midlands | Iron Acton 132kV | ALVESTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.6455 | 1.8631 | 2.1401 | 2.4511 | 2.8159 | 3.2025 | 3.6435 | 4.1954 | 4.7051 | 5.1474 | 5.578 | 5.9896 | 6.305 | 6.5111 | 6.6715 | 6.804 | 7.512 | 8.1233 | 3.5939 | 4.0599 | 4.6616 | 5.3329 | 6.1172 | 6.9487 | 7.8926 | 9.062 | 10.1472 | 11.0969 | 12.0322 | 12.924 | 13.6244 | 14.0845 | 14.4491 | 14.7555 | 16.3994 | 17.8644
West Midlands | Iron Acton 132kV | ALVESTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.6254 | 1.7898 | 1.9556 | 2.1609 | 2.4095 | 2.6867 | 3.0081 | 3.4141 | 3.784 | 4.1682 | 4.6072 | 5.0385 | 5.4551 | 5.8114 | 6.1503 | 6.4301 | 7.3702 | 7.7882 | 3.5594 | 3.927 | 4.2876 | 4.7388 | 5.283 | 5.891 | 6.5985 | 7.4764 | 8.2837 | 9.1129 | 10.0596 | 10.9912 | 11.8902 | 12.6485 | 13.3717 | 13.9714 | 16.0649 | 17.0339
West Midlands | Iron Acton 132kV | ALVESTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.6042 | 1.7339 | 1.8839 | 2.0583 | 2.2881 | 2.5395 | 2.8272 | 3.2268 | 3.6018 | 4.0192 | 4.4251 | 4.8157 | 5.1934 | 5.5262 | 5.8435 | 6.1059 | 6.9567 | 7.4897 | 3.5037 | 3.7841 | 4.1045 | 4.4788 | 4.9757 | 5.5218 | 6.1436 | 6.9914 | 7.7889 | 8.6789 | 9.534 | 10.3558 | 11.1476 | 11.8409 | 12.5032 | 13.0524 | 14.9267 | 16.1819
West Midlands | Iron Acton 132kV | BERKELEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.213 | 1.2465 | 1.3025 | 1.3611 | 1.4235 | 1.515 | 1.5888 | 1.6968 | 1.7984 | 1.9336 | 2.0735 | 2.2165 | 2.3691 | 2.5258 | 2.7571 | 3.0453 | 4.1547 | 4.3957 | 2.9729 | 3.0435 | 3.1631 | 3.2886 | 3.4306 | 3.6423 | 3.8067 | 4.0441 | 4.2694 | 4.5709 | 4.8771 | 5.1849 | 5.5103 | 5.8438 | 6.3553 | 7.0014 | 9.402 | 9.9524
West Midlands | Iron Acton 132kV | BERKELEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.2344 | 1.3052 | 1.4337 | 1.8442 | 2.1679 | 2.3559 | 2.5694 | 2.8299 | 3.0714 | 3.2941 | 3.5618 | 3.9958 | 4.6504 | 4.8958 | 5.1279 | 5.3489 | 5.7481 | 6.0008 | 3.0192 | 3.1699 | 3.4535 | 4.442 | 5.2153 | 5.6304 | 6.0991 | 6.6678 | 7.1974 | 7.6902 | 8.2876 | 9.2849 | 10.731 | 11.2812 | 11.8039 | 12.3033 | 13.2042 | 13.8034
West Midlands | Iron Acton 132kV | BERKELEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.2275 | 1.2872 | 1.4171 | 1.622 | 1.7526 | 1.8891 | 2.1034 | 2.3332 | 2.5784 | 2.8835 | 3.3811 | 3.6419 | 4.135 | 4.38 | 4.6203 | 4.8312 | 5.4391 | 5.622 | 3.0072 | 3.1388 | 3.4389 | 3.9273 | 4.2205 | 4.5248 | 5.0049 | 5.5141 | 6.0611 | 6.7503 | 7.9104 | 8.479 | 9.5147 | 10.0502 | 10.576 | 11.0362 | 12.4346 | 12.856
West Midlands | Iron Acton 132kV | BERKELEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.2215 | 1.2721 | 1.3529 | 1.4586 | 1.6723 | 1.8966 | 2.0625 | 2.2747 | 2.4746 | 2.6972 | 2.9643 | 3.306 | 3.7381 | 4.0383 | 4.2938 | 4.6519 | 5.5122 | 5.8224 | 2.9911 | 3.0998 | 3.2747 | 3.5148 | 4.0236 | 4.547 | 4.9146 | 5.3793 | 5.8192 | 6.3114 | 6.8953 | 7.66 | 8.6519 | 9.3195 | 9.8778 | 10.6401 | 12.6767 | 13.4176
West Midlands | Iron Acton 132kV | CAMP 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.355 | 0.40184 | 0.45583 | 0.51612 | 0.58581 | 0.66416 | 0.75384 | 0.89366 | 1.0029 | 1.1219 | 1.2425 | 1.3668 | 1.5042 | 1.6413 | 1.7751 | 1.9089 | 2.5287 | 2.7513 | 0.81352 | 0.91249 | 1.025 | 1.1506 | 1.2954 | 1.4584 | 1.645 | 1.9328 | 2.1594 | 2.4067 | 2.656 | 2.9112 | 3.1917 | 3.4717 | 3.7447 | 4.0178 | 5.2892 | 5.767
West Midlands | Iron Acton 132kV | CAMP 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.39953 | 0.51663 | 0.6531 | 0.80748 | 0.98287 | 1.178 | 1.4084 | 1.6889 | 1.9357 | 2.1376 | 2.3194 | 2.4952 | 2.6072 | 2.6711 | 2.7103 | 2.7463 | 2.9753 | 3.2003 | 0.91029 | 1.1578 | 1.4435 | 1.7657 | 2.1306 | 2.5367 | 3.0141 | 3.5918 | 4.1012 | 4.52 | 4.8997 | 5.2662 | 5.5043 | 5.6435 | 5.7329 | 5.8156 | 6.3434 | 6.8627
West Midlands | Iron Acton 132kV | CAMP 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.38585 | 0.46455 | 0.54867 | 0.64476 | 0.75868 | 0.89046 | 1.0413 | 1.2446 | 1.4168 | 1.5977 | 1.7918 | 1.9806 | 2.165 | 2.3328 | 2.4891 | 2.6266 | 3.0548 | 3.2867 | 0.88674 | 1.0615 | 1.2422 | 1.449 | 1.6931 | 1.9745 | 2.2949 | 2.7199 | 3.0811 | 3.4589 | 3.8636 | 4.2574 | 4.6421 | 4.991 | 5.3168 | 5.6046 | 6.5388 | 7.0702
West Midlands | Iron Acton 132kV | CAMP 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.37143 | 0.43265 | 0.50707 | 0.59235 | 0.69495 | 0.81386 | 0.95407 | 1.1515 | 1.3165 | 1.4954 | 1.6797 | 1.8583 | 2.0309 | 2.1868 | 2.3328 | 2.4593 | 2.8146 | 3.0115 | 0.84895 | 0.97952 | 1.1356 | 1.3145 | 1.5301 | 1.7801 | 2.0732 | 2.481 | 2.8226 | 3.1919 | 3.5705 | 3.9374 | 4.2912 | 4.6104 | 4.9097 | 5.1696 | 5.932 | 6.3789
West Midlands | Iron Acton 132kV | CHERINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.27116 | 0.30004 | 0.33014 | 0.36706 | 0.41437 | 0.4708 | 0.53695 | 0.62967 | 0.70856 | 0.79803 | 0.87957 | 0.95575 | 1.0344 | 1.1109 | 1.1858 | 1.2617 | 1.6442 | 1.854 | 0.64094 | 0.70543 | 0.77056 | 0.85045 | 0.9525 | 1.075 | 1.2201 | 1.4212 | 1.5944 | 1.7928 | 1.9705 | 2.1333 | 2.2986 | 2.4595 | 2.617 | 2.7765 | 3.5925 | 4.0624
West Midlands | Iron Acton 132kV | CHERINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.29003 | 0.36507 | 0.45434 | 0.55893 | 0.67778 | 0.81326 | 0.96522 | 1.1398 | 1.3027 | 1.4487 | 1.5915 | 1.7271 | 1.8386 | 1.91 | 1.9838 | 2.0425 | 2.3488 | 2.6312 | 0.68182 | 0.85016 | 1.0489 | 1.2797 | 1.5402 | 1.8375 | 2.1692 | 2.5471 | 2.9016 | 3.2219 | 3.5387 | 3.8384 | 4.0909 | 4.2531 | 4.4178 | 4.5539 | 5.2692 | 5.9445
West Midlands | Iron Acton 132kV | CHERINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.28418 | 0.34826 | 0.39899 | 0.47087 | 0.55382 | 0.65721 | 0.77329 | 0.91658 | 1.0445 | 1.174 | 1.3159 | 1.4545 | 1.5882 | 1.6991 | 1.8238 | 1.9221 | 2.2896 | 2.4954 | 0.67168 | 0.82233 | 0.93515 | 1.0963 | 1.2812 | 1.5112 | 1.7708 | 2.0856 | 2.3685 | 2.6522 | 2.9637 | 3.2686 | 3.5628 | 3.8029 | 4.0705 | 4.2851 | 5.1159 | 5.5904
West Midlands | Iron Acton 132kV | CHERINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.27825 | 0.32322 | 0.36543 | 0.42088 | 0.49317 | 0.58275 | 0.68391 | 0.81226 | 0.92563 | 1.0562 | 1.1789 | 1.2929 | 1.404 | 1.4964 | 1.5957 | 1.6763 | 1.9901 | 2.2407 | 0.65614 | 0.75883 | 0.85059 | 0.97131 | 1.1298 | 1.3274 | 1.5495 | 1.827 | 2.0732 | 2.3572 | 2.6204 | 2.8647 | 3.1016 | 3.2972 | 3.5064 | 3.6785 | 4.3831 | 4.9696
West Midlands | Iron Acton 132kV | Chipping Sodbury 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.3881 | 1.6885 | 2.0096 | 2.3365 | 2.6537 | 3.0184 | 3.4205 | 3.9905 | 4.4457 | 4.9416 | 5.4299 | 5.9207 | 6.4493 | 6.9724 | 7.4842 | 7.96 | 10.1028 | 10.9304 | 3.0415 | 3.6826 | 4.3565 | 5.0417 | 5.7076 | 6.476 | 7.3271 | 8.522 | 9.4848 | 10.5396 | 11.5688 | 12.5922 | 13.6862 | 14.7676 | 15.8261 | 16.8063 | 21.2507 | 23.0556
West Midlands | Iron Acton 132kV | Chipping Sodbury 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.5429 | 2.1675 | 2.832 | 3.5353 | 4.2792 | 5.097 | 6.0212 | 7.1005 | 8.0629 | 8.8972 | 9.578 | 10.2342 | 10.694 | 10.9754 | 11.1734 | 11.3483 | 12.2914 | 13.1719 | 3.3785 | 4.7339 | 6.1542 | 7.6492 | 9.2269 | 10.9651 | 12.9191 | 15.1841 | 17.2102 | 18.98 | 20.431 | 21.8247 | 22.8247 | 23.4454 | 23.8894 | 24.287 | 26.4858 | 28.5659
West Midlands | Iron Acton 132kV | Chipping Sodbury 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.4997 | 2.0076 | 2.4907 | 3.0074 | 3.5147 | 4.13 | 4.8102 | 5.6644 | 6.4092 | 7.1762 | 7.8923 | 8.5671 | 9.2555 | 9.8641 | 10.4514 | 10.9656 | 12.4908 | 13.2174 | 3.304 | 4.4403 | 5.4833 | 6.6025 | 7.7003 | 9.0344 | 10.5088 | 12.3315 | 13.9294 | 15.5649 | 17.085 | 18.505 | 19.9664 | 21.2467 | 22.4836 | 23.5742 | 26.9436 | 28.6215
West Midlands | Iron Acton 132kV | Chipping Sodbury 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.4451 | 1.8708 | 2.2895 | 2.7249 | 3.1787 | 3.7217 | 4.3281 | 5.1087 | 5.7746 | 6.5027 | 7.229 | 7.9326 | 8.6162 | 9.23 | 9.8102 | 10.2978 | 11.5873 | 12.3642 | 3.165 | 4.1005 | 4.9942 | 5.9222 | 6.8922 | 8.0582 | 9.3531 | 10.9963 | 12.4029 | 13.9406 | 15.462 | 16.9341 | 18.3622 | 19.6409 | 20.8465 | 21.8684 | 24.6865 | 26.49
West Midlands | Iron Acton 132kV | COWHORN 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.96558 | 1.0766 | 1.204 | 1.3425 | 1.5063 | 1.6823 | 1.8848 | 2.203 | 2.4554 | 2.7252 | 3.0013 | 3.2893 | 3.6096 | 3.9288 | 4.241 | 4.5591 | 5.9908 | 6.3781 | 2.1065 | 2.3411 | 2.6062 | 2.8931 | 3.2319 | 3.5953 | 4.0134 | 4.6641 | 5.1836 | 5.7396 | 6.3067 | 6.8956 | 7.5481 | 8.1979 | 8.8337 | 9.4813 | 12.4062 | 13.2342
West Midlands | Iron Acton 132kV | COWHORN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.0723 | 1.3676 | 1.6767 | 2.0269 | 2.4287 | 2.8659 | 3.3879 | 4.0237 | 4.5898 | 5.0479 | 5.4718 | 5.8844 | 6.1473 | 6.3015 | 6.3946 | 6.4821 | 6.9144 | 7.2914 | 2.3386 | 2.9678 | 3.61 | 4.336 | 5.1673 | 6.0704 | 7.1444 | 8.4455 | 9.6074 | 10.5511 | 11.4315 | 12.287 | 12.8419 | 13.176 | 13.3873 | 13.587 | 14.5912 | 15.4613
West Midlands | Iron Acton 132kV | COWHORN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.0405 | 1.2377 | 1.431 | 1.6476 | 1.903 | 2.1896 | 2.5225 | 2.9818 | 3.3795 | 3.7965 | 4.257 | 4.7081 | 5.1499 | 5.5592 | 5.9398 | 6.323 | 7.2086 | 7.6188 | 2.2843 | 2.7246 | 3.1376 | 3.6009 | 4.1454 | 4.7531 | 5.4548 | 6.4086 | 7.2387 | 8.1049 | 9.0621 | 9.9997 | 10.918 | 11.7678 | 12.5594 | 13.3786 | 15.2983 | 16.2427
West Midlands | Iron Acton 132kV | COWHORN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.0036 | 1.1706 | 1.3404 | 1.5358 | 1.7694 | 2.0296 | 2.3407 | 2.7818 | 3.1611 | 3.5675 | 3.9907 | 4.4049 | 4.8076 | 5.1772 | 5.5211 | 5.8297 | 6.5772 | 6.8996 | 2.1887 | 2.5526 | 2.9066 | 3.3148 | 3.8036 | 4.3466 | 4.9926 | 5.8984 | 6.6807 | 7.5159 | 8.3826 | 9.2304 | 10.0544 | 10.8104 | 11.5145 | 12.149 | 13.7488 | 14.4795
West Midlands | Iron Acton 132kV | DUDBRIDGE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.2182 | 1.4224 | 1.6798 | 1.9674 | 2.272 | 2.5822 | 2.9313 | 3.4734 | 3.9011 | 4.3385 | 4.8105 | 5.2951 | 5.8346 | 6.3698 | 6.8902 | 7.4107 | 9.7866 | 10.6142 | 2.7929 | 3.2212 | 3.7551 | 4.3502 | 4.9793 | 5.6185 | 6.3361 | 7.4404 | 8.3167 | 9.2104 | 10.176 | 11.1636 | 12.26 | 13.3471 | 14.4041 | 15.4601 | 20.299 | 22.038
West Midlands | Iron Acton 132kV | DUDBRIDGE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.3941 | 1.8714 | 2.4477 | 3.083 | 3.8647 | 4.6727 | 5.548 | 6.6181 | 7.541 | 8.2831 | 8.956 | 9.5912 | 9.9784 | 10.2008 | 10.3254 | 10.4322 | 11.1817 | 11.8678 | 3.1741 | 4.177 | 5.3761 | 6.6939 | 8.3202 | 9.9959 | 11.7936 | 13.9804 | 15.8678 | 17.389 | 18.7756 | 20.0803 | 20.8861 | 21.3608 | 21.6386 | 21.88 | 23.5937 | 25.1483
West Midlands | Iron Acton 132kV | DUDBRIDGE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.3399 | 1.6683 | 2.0572 | 2.5045 | 3.1779 | 3.651 | 4.1832 | 4.9255 | 5.5549 | 6.2205 | 6.9404 | 7.6278 | 8.2962 | 8.9186 | 9.4997 | 10.0063 | 11.5536 | 12.3811 | 3.0807 | 3.8007 | 4.634 | 5.5907 | 7.0363 | 8.034 | 9.1477 | 10.6788 | 11.9826 | 13.3561 | 14.8404 | 16.2562 | 17.6336 | 18.9171 | 20.1174 | 21.1678 | 24.5123 | 26.3943
West Midlands | Iron Acton 132kV | DUDBRIDGE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.2847 | 1.557 | 1.9311 | 2.3499 | 2.915 | 3.3628 | 3.8823 | 4.6216 | 5.2384 | 5.9005 | 6.6076 | 7.2835 | 7.9373 | 8.5339 | 9.0886 | 9.5656 | 10.8275 | 11.447 | 2.9357 | 3.5134 | 4.2995 | 5.1774 | 6.3703 | 7.2998 | 8.3711 | 9.8805 | 11.1422 | 12.4907 | 13.9311 | 15.3062 | 16.6357 | 17.8498 | 18.9791 | 19.9527 | 22.6269 | 23.9999
West Midlands | Iron Acton 132kV | DURSLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.61243 | 0.70568 | 0.80644 | 0.9198 | 1.0642 | 1.2209 | 1.3773 | 1.6128 | 1.7993 | 2.0392 | 2.3108 | 2.5999 | 2.9035 | 3.2031 | 3.5246 | 3.8652 | 5.3258 | 5.6839 | 1.4141 | 1.6093 | 1.8189 | 2.0544 | 2.3625 | 2.6958 | 3.0215 | 3.5071 | 3.8944 | 4.3962 | 4.964 | 5.5662 | 6.1955 | 6.8159 | 7.4899 | 8.2088 | 11.2526 | 12.0182
West Midlands | Iron Acton 132kV | DURSLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.68207 | 0.88748 | 1.1229 | 1.4144 | 1.7894 | 2.1874 | 2.6453 | 3.2126 | 3.7049 | 4.1796 | 4.6131 | 5.0709 | 5.3688 | 5.5506 | 5.7056 | 5.8488 | 6.3925 | 6.7334 | 1.5652 | 1.9967 | 2.4902 | 3.1126 | 3.9286 | 4.7671 | 5.7275 | 6.9131 | 7.943 | 8.9464 | 9.8675 | 10.8554 | 11.5083 | 11.9044 | 12.2495 | 12.57 | 13.8021 | 14.5885
West Midlands | Iron Acton 132kV | DURSLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.66067 | 0.80865 | 1.0163 | 1.1997 | 1.5323 | 1.8958 | 2.3134 | 2.7489 | 3.1352 | 3.6168 | 4.0442 | 4.4556 | 4.8049 | 5.1295 | 5.4459 | 5.7267 | 6.4993 | 6.8297 | 1.5284 | 1.8508 | 2.3168 | 2.715 | 3.4338 | 4.219 | 5.119 | 6.0407 | 6.8629 | 7.8951 | 8.8185 | 9.7028 | 10.4369 | 11.1173 | 11.7831 | 12.3764 | 14.0523 | 14.8078
West Midlands | Iron Acton 132kV | DURSLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.63838 | 0.76701 | 0.93824 | 1.1234 | 1.4428 | 1.745 | 2.0783 | 2.5119 | 2.8728 | 3.3101 | 3.7285 | 4.1185 | 4.5158 | 4.8499 | 5.1614 | 5.4381 | 6.1254 | 6.4187 | 1.47 | 1.7435 | 2.1056 | 2.5067 | 3.2163 | 3.8643 | 4.573 | 5.4845 | 6.2445 | 7.1684 | 8.0463 | 8.8688 | 9.7188 | 10.4206 | 11.0713 | 11.6512 | 13.1391 | 13.8075
West Midlands | Iron Acton 132kV | HAMMERLEY DOWN 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.0989 | 1.1849 | 1.2855 | 1.3857 | 1.502 | 1.6401 | 1.8058 | 2.0558 | 2.2612 | 2.4942 | 2.7196 | 2.9866 | 3.2738 | 3.5584 | 3.8566 | 4.169 | 5.4637 | 6.1688 | 2.4201 | 2.6035 | 2.8169 | 3.0303 | 3.2779 | 3.5739 | 3.9317 | 4.4644 | 4.9075 | 5.4146 | 5.8961 | 6.4518 | 7.0434 | 7.6286 | 8.2516 | 8.9093 | 11.6161 | 13.1379
West Midlands | Iron Acton 132kV | HAMMERLEY DOWN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.1628 | 1.3603 | 1.6173 | 1.8844 | 2.182 | 2.5202 | 2.9172 | 3.453 | 3.9412 | 4.3643 | 4.7682 | 5.2027 | 5.534 | 5.7006 | 5.827 | 5.9396 | 6.6564 | 7.2573 | 2.5584 | 2.9814 | 3.5374 | 4.1115 | 4.7472 | 5.4719 | 6.3188 | 7.4452 | 8.4754 | 9.3768 | 10.2482 | 11.2024 | 11.9501 | 12.3197 | 12.6079 | 12.8689 | 14.5183 | 15.955
West Midlands | Iron Acton 132kV | HAMMERLEY DOWN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.1426 | 1.2891 | 1.4336 | 1.5983 | 1.7836 | 2.0202 | 2.3044 | 2.6718 | 2.9992 | 3.3774 | 3.885 | 4.286 | 4.6675 | 4.9859 | 5.2842 | 5.545 | 6.5095 | 6.925 | 2.5232 | 2.8524 | 3.1643 | 3.5258 | 3.9297 | 4.4474 | 5.073 | 5.8658 | 6.5785 | 7.399 | 8.519 | 9.3809 | 10.2002 | 10.8734 | 11.5062 | 12.0638 | 14.1983 | 15.1593
West Midlands | Iron Acton 132kV | HAMMERLEY DOWN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.1239 | 1.2365 | 1.3759 | 1.5219 | 1.7008 | 1.9209 | 2.1807 | 2.5758 | 2.961 | 3.3926 | 3.8151 | 4.2445 | 4.6995 | 5.0537 | 5.3695 | 5.6454 | 6.5791 | 7.1124 | 2.4736 | 2.7167 | 3.0144 | 3.3271 | 3.7124 | 4.1895 | 4.7498 | 5.5828 | 6.3937 | 7.3049 | 8.1866 | 9.0921 | 10.066 | 10.8042 | 11.4564 | 12.0299 | 14.0677 | 15.3246
West Midlands | Iron Acton 132kV | NAISHCOMBE HILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.43434 | 0.4838 | 0.53831 | 0.60021 | 0.67558 | 0.76658 | 0.87608 | 1.0385 | 1.1755 | 1.3315 | 1.4764 | 1.6137 | 1.7583 | 1.8994 | 2.0367 | 2.1792 | 2.8878 | 3.2474 | 0.93907 | 1.0466 | 1.1636 | 1.2968 | 1.4588 | 1.6555 | 1.8944 | 2.2439 | 2.5421 | 2.8851 | 3.1983 | 3.4889 | 3.7905 | 4.0845 | 4.3708 | 4.6676 | 6.1668 | 6.9661
West Midlands | Iron Acton 132kV | NAISHCOMBE HILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.47292 | 0.59579 | 0.75012 | 0.92363 | 1.1171 | 1.3417 | 1.6037 | 1.9103 | 2.1923 | 2.4442 | 2.6953 | 2.9314 | 3.1134 | 3.2264 | 3.3196 | 3.4604 | 3.9152 | 4.3363 | 1.0226 | 1.2898 | 1.6274 | 2.0039 | 2.4209 | 2.906 | 3.4693 | 4.1226 | 4.7265 | 5.2712 | 5.8212 | 6.3363 | 6.743 | 6.9967 | 7.2104 | 7.5196 | 8.586 | 9.5976
West Midlands | Iron Acton 132kV | NAISHCOMBE HILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.46092 | 0.55697 | 0.63864 | 0.74912 | 0.87272 | 1.0377 | 1.2329 | 1.4806 | 1.7015 | 1.9282 | 2.1821 | 2.4295 | 2.6673 | 2.8648 | 3.0577 | 3.2825 | 3.8722 | 4.1612 | 1.0017 | 1.2221 | 1.4003 | 1.6449 | 1.9167 | 2.2799 | 2.7124 | 3.251 | 3.7343 | 4.2261 | 4.7781 | 5.3166 | 5.8345 | 6.2579 | 6.6719 | 7.1496 | 8.4778 | 9.1477
West Midlands | Iron Acton 132kV | NAISHCOMBE HILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.44941 | 0.51551 | 0.59138 | 0.68712 | 0.8058 | 0.9549 | 1.1303 | 1.3617 | 1.5657 | 1.8005 | 2.0233 | 2.2321 | 2.4337 | 2.6018 | 2.7657 | 2.9369 | 3.4511 | 3.8311 | 0.97132 | 1.1162 | 1.2795 | 1.4859 | 1.7436 | 2.0692 | 2.4503 | 2.9449 | 3.383 | 3.8883 | 4.3611 | 4.8037 | 5.2294 | 5.5816 | 5.9251 | 6.2842 | 7.4353 | 8.3305
West Midlands | Iron Acton 132kV | NETHERHILLS 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.86079 | 1.1209 | 1.1643 | 1.203 | 1.2536 | 1.3179 | 1.4017 | 1.5322 | 1.69 | 1.8367 | 1.9777 | 2.1358 | 2.2267 | 2.3147 | 2.4345 | 2.5979 | 3.0534 | 3.311 | 1.8059 | 2.3308 | 2.4246 | 2.5072 | 2.6163 | 2.7554 | 2.9374 | 3.2178 | 3.5586 | 3.8788 | 4.1831 | 4.5202 | 4.7103 | 4.8937 | 5.1576 | 5.5301 | 6.5015 | 7.0695
West Midlands | Iron Acton 132kV | NETHERHILLS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.89331 | 1.2024 | 1.3334 | 1.4409 | 1.5973 | 2.1847 | 2.411 | 2.6696 | 2.9063 | 3.0898 | 3.271 | 3.4959 | 3.6973 | 3.7821 | 3.8646 | 3.9099 | 4.1664 | 4.4422 | 1.8779 | 2.5111 | 2.8003 | 3.035 | 3.3755 | 4.7802 | 5.2708 | 5.8275 | 6.3394 | 6.7385 | 7.137 | 7.6478 | 8.1246 | 8.3211 | 8.518 | 8.6246 | 9.2376 | 9.8995
West Midlands | Iron Acton 132kV | NETHERHILLS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.88581 | 1.1881 | 1.2708 | 1.7444 | 1.8468 | 1.9906 | 2.1685 | 2.3797 | 2.5799 | 2.7679 | 3.0486 | 3.2279 | 3.4117 | 3.5529 | 3.6571 | 3.7492 | 4.0807 | 4.2374 | 1.8647 | 2.4884 | 2.6732 | 3.8314 | 4.0546 | 4.3707 | 4.7645 | 5.2255 | 5.6662 | 6.0826 | 6.728 | 7.1229 | 7.5389 | 7.8522 | 8.0753 | 8.274 | 9.0257 | 9.3863
West Midlands | Iron Acton 132kV | NETHERHILLS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.87987 | 1.1745 | 1.2605 | 1.3449 | 1.4552 | 1.9881 | 2.1559 | 2.3608 | 2.5484 | 2.7213 | 2.886 | 3.072 | 3.299 | 3.4437 | 3.5622 | 3.6457 | 3.9543 | 4.1987 | 1.8487 | 2.4531 | 2.6418 | 2.8247 | 3.0667 | 4.3554 | 4.7216 | 5.1634 | 5.5696 | 5.9439 | 6.2957 | 6.7044 | 7.2249 | 7.5453 | 7.8025 | 7.9791 | 8.6776 | 9.2588
West Midlands | Iron Acton 132kV | OXBRIDGE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.49796 | 0.54873 | 0.6082 | 0.67447 | 0.76432 | 0.85966 | 0.97305 | 1.1447 | 1.287 | 1.4472 | 1.5994 | 1.7484 | 1.9081 | 2.0646 | 2.217 | 2.374 | 3.1362 | 3.481 | 1.0902 | 1.1984 | 1.3246 | 1.4654 | 1.6559 | 1.8594 | 2.1033 | 2.4676 | 2.7729 | 3.1196 | 3.4439 | 3.7564 | 4.0874 | 4.4111 | 4.7266 | 5.0512 | 6.6482 | 7.4081
West Midlands | Iron Acton 132kV | OXBRIDGE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.54374 | 0.67273 | 0.83495 | 1.0168 | 1.2338 | 1.4689 | 1.7457 | 2.0765 | 2.3775 | 2.6399 | 2.8974 | 3.1426 | 3.3233 | 3.4358 | 3.5236 | 3.6063 | 4.017 | 4.3994 | 1.1893 | 1.465 | 1.8144 | 2.2034 | 2.6658 | 3.1673 | 3.7551 | 4.4521 | 5.0893 | 5.6498 | 6.207 | 6.7355 | 7.1345 | 7.3849 | 7.5853 | 7.7758 | 8.7378 | 9.6507
West Midlands | Iron Acton 132kV | OXBRIDGE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.52982 | 0.62155 | 0.71003 | 0.82375 | 0.96577 | 1.1327 | 1.3326 | 1.5928 | 1.8268 | 2.0661 | 2.3309 | 2.5918 | 2.8422 | 3.0551 | 3.2594 | 3.4421 | 4.0204 | 4.2908 | 1.1652 | 1.3715 | 1.5625 | 1.8113 | 2.1204 | 2.4842 | 2.922 | 3.4812 | 3.9887 | 4.5026 | 5.0722 | 5.6338 | 6.1727 | 6.6241 | 7.0581 | 7.4489 | 8.7395 | 9.3638
West Midlands | Iron Acton 132kV | OXBRIDGE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.51571 | 0.5861 | 0.66825 | 0.7684 | 0.90458 | 1.0575 | 1.238 | 1.4814 | 1.6968 | 1.9391 | 2.174 | 2.3981 | 2.6127 | 2.798 | 2.9755 | 3.1341 | 3.6339 | 3.9746 | 1.1282 | 1.2805 | 1.4551 | 1.6688 | 1.9615 | 2.2915 | 2.679 | 3.1938 | 3.6519 | 4.1684 | 4.6627 | 5.1335 | 5.5828 | 5.9682 | 6.3379 | 6.671 | 7.7811 | 8.5817
West Midlands | Iron Acton 132kV | Ryeford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.648 | 1.8327 | 1.9417 | 2.1202 | 2.2594 | 2.3992 | 2.5505 | 2.76 | 2.8976 | 3.035 | 3.1855 | 3.3843 | 3.5908 | 3.7874 | 4.0074 | 4.2351 | 5.0163 | 5.2771 | 4.0553 | 4.4808 | 4.7079 | 5.0794 | 5.3709 | 5.6632 | 5.9785 | 6.4117 | 6.6967 | 6.9807 | 7.2917 | 7.7041 | 8.1301 | 8.5349 | 9.0024 | 9.4908 | 11.1079 | 11.661
West Midlands | Iron Acton 132kV | Ryeford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.8085 | 1.986 | 2.1977 | 2.5032 | 2.7876 | 3.086 | 3.4279 | 3.8407 | 4.1666 | 4.4233 | 4.6771 | 5.106 | 5.3254 | 5.4196 | 5.4626 | 5.5 | 5.731 | 5.9455 | 4.4395 | 4.8155 | 5.2614 | 5.9099 | 6.5134 | 7.1418 | 7.8588 | 8.7207 | 9.3981 | 9.9324 | 10.4656 | 11.4064 | 11.9033 | 12.1141 | 12.2106 | 12.2956 | 12.824 | 13.3124
West Midlands | Iron Acton 132kV | Ryeford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.7931 | 1.9258 | 2.0938 | 2.3321 | 2.5678 | 2.8163 | 3.0963 | 3.432 | 3.6884 | 3.9652 | 4.3478 | 4.6434 | 4.8413 | 5.0252 | 5.1986 | 5.3494 | 5.806 | 6.0962 | 4.4132 | 4.7034 | 5.0695 | 5.5823 | 6.0905 | 6.6256 | 7.227 | 7.9376 | 8.4804 | 9.0717 | 9.9233 | 10.5572 | 10.9655 | 11.3454 | 11.7041 | 12.0177 | 13.0049 | 13.6725
West Midlands | Iron Acton 132kV | Ryeford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.7766 | 1.8932 | 2.0452 | 2.2812 | 2.4994 | 2.7208 | 2.9693 | 3.2961 | 3.5372 | 3.7773 | 4.0427 | 4.3848 | 4.6723 | 4.8999 | 5.0745 | 5.2157 | 6.1712 | 6.3852 | 4.37 | 4.6195 | 4.9423 | 5.4473 | 5.9169 | 6.3895 | 6.9168 | 7.6034 | 8.1077 | 8.606 | 9.1574 | 9.8874 | 10.517 | 11.0057 | 11.3671 | 11.6565 | 13.9035 | 14.3833
West Midlands | Ironbr. & Shrewsb. 132kV | BAYSTON HILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.87442 | 0.95916 | 1.06 | 1.16 | 1.2846 | 1.431 | 1.5862 | 1.8234 | 2.015 | 2.2235 | 2.4436 | 2.6778 | 2.949 | 3.2479 | 3.5569 | 3.9699 | 5.288 | 5.2002 | 2.1078 | 2.2849 | 2.4936 | 2.7002 | 2.9575 | 3.2601 | 3.5807 | 4.066 | 4.4606 | 4.8907 | 5.3442 | 5.8262 | 6.3832 | 6.9996 | 7.638 | 8.4998 | 11.2212 | 10.87
West Midlands | Ironbr. & Shrewsb. 132kV | BAYSTON HILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.94701 | 1.1458 | 1.378 | 1.6325 | 1.9274 | 2.2837 | 2.6944 | 3.1977 | 3.6493 | 4.0268 | 4.3988 | 4.8135 | 5.162 | 5.3721 | 5.5448 | 5.7639 | 6.1404 | 6.0595 | 2.2653 | 2.6822 | 3.1652 | 3.6932 | 4.3045 | 5.0466 | 5.8973 | 6.9361 | 7.8702 | 8.6541 | 9.4335 | 10.3064 | 11.0546 | 11.5104 | 11.8921 | 12.3757 | 13.2224 | 12.9305
West Midlands | Ironbr. & Shrewsb. 132kV | BAYSTON HILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.92463 | 1.0565 | 1.2159 | 1.3825 | 1.6369 | 1.9245 | 2.2409 | 2.646 | 3.0089 | 3.3986 | 3.8204 | 4.236 | 4.6402 | 5.0038 | 5.3498 | 5.6767 | 6.3892 | 6.3298 | 2.2269 | 2.515 | 2.8549 | 3.2106 | 3.7551 | 4.37 | 5.0424 | 5.892 | 6.6574 | 7.4767 | 8.3623 | 9.2351 | 10.0843 | 10.8464 | 11.5733 | 12.2642 | 13.7987 | 13.5579
West Midlands | Ironbr. & Shrewsb. 132kV | BAYSTON HILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.90119 | 1.0148 | 1.1714 | 1.3231 | 1.5327 | 1.7786 | 2.0519 | 2.4347 | 2.7679 | 3.1211 | 3.5208 | 3.935 | 4.3408 | 4.7123 | 5.0526 | 5.3867 | 5.9851 | 5.8544 | 2.1655 | 2.4069 | 2.7352 | 3.0517 | 3.4926 | 4.0112 | 4.5833 | 5.3778 | 6.0714 | 6.8043 | 7.6354 | 8.4997 | 9.3465 | 10.1221 | 10.832 | 11.5345 | 12.8026 | 12.392
West Midlands | Ironbr. & Shrewsb. 132kV | BERRINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.098013 | 0.10683 | 0.11956 | 0.13594 | 0.15602 | 0.18151 | 0.21386 | 0.26012 | 0.30035 | 0.34672 | 0.38618 | 0.42074 | 0.4566 | 0.48951 | 0.52174 | 0.55499 | 0.73941 | 0.85796 | 0.23574 | 0.25432 | 0.28205 | 0.31779 | 0.3617 | 0.41803 | 0.49044 | 0.5928 | 0.6829 | 0.78814 | 0.87587 | 0.95076 | 1.027 | 1.0966 | 1.165 | 1.2352 | 1.6352 | 1.904
West Midlands | Ironbr. & Shrewsb. 132kV | BERRINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.1062 | 0.12802 | 0.16838 | 0.21417 | 0.26462 | 0.32587 | 0.39592 | 0.47565 | 0.55116 | 0.62173 | 0.69238 | 0.758 | 0.81176 | 0.84352 | 0.87149 | 0.89942 | 1.0567 | 1.2132 | 0.25344 | 0.29947 | 0.38988 | 0.4916 | 0.60289 | 0.73828 | 0.89274 | 1.0675 | 1.2338 | 1.391 | 1.551 | 1.6987 | 1.8227 | 1.896 | 1.9615 | 2.0274 | 2.4019 | 2.7815
West Midlands | Ironbr. & Shrewsb. 132kV | BERRINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.10371 | 0.11858 | 0.13451 | 0.16208 | 0.19028 | 0.23595 | 0.29165 | 0.36062 | 0.42586 | 0.48992 | 0.56126 | 0.63039 | 0.69552 | 0.74271 | 0.79168 | 0.83498 | 1.0116 | 1.094 | 0.24912 | 0.28217 | 0.31638 | 0.37805 | 0.4408 | 0.54259 | 0.66924 | 0.82306 | 0.97058 | 1.1135 | 1.273 | 1.4285 | 1.5748 | 1.678 | 1.7851 | 1.8808 | 2.2856 | 2.4747
West Midlands | Ironbr. & Shrewsb. 132kV | BERRINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.10138 | 0.113 | 0.13084 | 0.15732 | 0.18955 | 0.23183 | 0.28226 | 0.34514 | 0.40279 | 0.47337 | 0.535 | 0.5909 | 0.64502 | 0.68551 | 0.72873 | 0.76601 | 0.9409 | 1.0881 | 0.24295 | 0.26763 | 0.30643 | 0.36411 | 0.43529 | 0.5297 | 0.6418 | 0.77937 | 0.90636 | 1.0623 | 1.1962 | 1.3178 | 1.4345 | 1.5209 | 1.6131 | 1.6939 | 2.0932 | 2.4439
West Midlands | Ironbr. & Shrewsb. 132kV | BROSELEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.35537 | 0.4053 | 0.46356 | 0.53345 | 0.61884 | 0.72279 | 0.84211 | 1.0248 | 1.1745 | 1.3401 | 1.498 | 1.6525 | 1.8192 | 1.9796 | 2.1354 | 2.2959 | 3.0875 | 3.4625 | 0.83828 | 0.94189 | 1.0636 | 1.2098 | 1.3882 | 1.6064 | 1.8593 | 2.2428 | 2.56 | 2.914 | 3.2464 | 3.5673 | 3.9103 | 4.2394 | 4.5592 | 4.8899 | 6.5425 | 7.3639
West Midlands | Ironbr. & Shrewsb. 132kV | BROSELEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.40337 | 0.53047 | 0.70493 | 0.91545 | 1.1514 | 1.4234 | 1.7445 | 2.1227 | 2.4629 | 2.7534 | 3.0286 | 3.2842 | 3.4753 | 3.589 | 3.6756 | 3.7613 | 4.232 | 4.6646 | 0.94237 | 1.2092 | 1.5855 | 2.0369 | 2.5401 | 3.1213 | 3.8039 | 4.6033 | 5.3255 | 5.9457 | 6.5388 | 7.0891 | 7.5116 | 7.7658 | 7.9624 | 8.1605 | 9.2518 | 10.2762
West Midlands | Ironbr. & Shrewsb. 132kV | BROSELEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.38893 | 0.47422 | 0.57297 | 0.70869 | 0.87127 | 1.0671 | 1.2996 | 1.577 | 1.8309 | 2.0884 | 2.3731 | 2.6456 | 2.9059 | 3.12 | 3.3311 | 3.5216 | 4.1631 | 4.4825 | 0.91762 | 1.1053 | 1.3192 | 1.6154 | 1.9692 | 2.3943 | 2.9008 | 3.494 | 4.0434 | 4.5938 | 5.2035 | 5.7892 | 6.3477 | 6.8009 | 7.2481 | 7.6548 | 9.0783 | 9.8063
West Midlands | Ironbr. & Shrewsb. 132kV | BROSELEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.37344 | 0.44205 | 0.52905 | 0.64214 | 0.78332 | 0.95656 | 1.1662 | 1.4342 | 1.6681 | 1.9294 | 2.1801 | 2.4175 | 2.6469 | 2.8387 | 3.0277 | 3.1977 | 3.7536 | 4.1478 | 0.87715 | 1.0225 | 1.2065 | 1.4465 | 1.7483 | 2.1203 | 2.5686 | 3.1332 | 3.628 | 4.1818 | 4.7065 | 5.2031 | 5.6813 | 6.0786 | 6.4711 | 6.8268 | 8.0515 | 8.9645
West Midlands | Ironbr. & Shrewsb. 132kV | DONNINGTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.53161 | 0.57096 | 0.61821 | 0.67131 | 0.72999 | 0.79827 | 0.87695 | 1.0093 | 1.1124 | 1.2368 | 1.3788 | 1.5372 | 1.7227 | 1.9158 | 2.1198 | 2.3468 | 3.8552 | 4.0887 | 1.2887 | 1.3707 | 1.4688 | 1.579 | 1.7007 | 1.8422 | 2.0056 | 2.2801 | 2.4937 | 2.7539 | 3.0517 | 3.3825 | 3.7689 | 4.1711 | 4.5959 | 5.0697 | 8.2499 | 8.7494
West Midlands | Ironbr. & Shrewsb. 132kV | DONNINGTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.57275 | 0.67287 | 0.79323 | 0.93177 | 1.0882 | 1.2966 | 1.5654 | 1.9039 | 2.2062 | 2.4856 | 2.7889 | 3.121 | 3.3847 | 3.5995 | 3.7926 | 3.982 | 4.6569 | 4.872 | 1.378 | 1.5866 | 1.8377 | 2.1256 | 2.4497 | 2.8856 | 3.4548 | 4.1662 | 4.7987 | 5.3907 | 6.0394 | 6.7494 | 7.3203 | 7.7905 | 8.2171 | 8.6366 | 10.1646 | 10.6597
West Midlands | Ironbr. & Shrewsb. 132kV | DONNINGTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.56041 | 0.6231 | 0.69532 | 0.78058 | 0.87745 | 1.1034 | 1.367 | 1.6919 | 1.9908 | 2.3027 | 2.6053 | 2.9155 | 3.3773 | 3.6594 | 3.9313 | 4.1878 | 4.8494 | 5.0643 | 1.3569 | 1.4934 | 1.6474 | 1.8295 | 2.0356 | 2.5316 | 3.1048 | 3.8008 | 4.4414 | 5.1077 | 5.7514 | 6.4122 | 7.4555 | 8.0559 | 8.6357 | 9.1851 | 10.6303 | 11.1184
West Midlands | Ironbr. & Shrewsb. 132kV | DONNINGTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.54662 | 0.59824 | 0.66234 | 0.73704 | 0.82532 | 0.97918 | 1.1788 | 1.4522 | 1.6889 | 1.9545 | 2.2775 | 2.6294 | 2.9327 | 3.2179 | 3.4957 | 3.7556 | 4.4899 | 4.6846 | 1.3211 | 1.4296 | 1.5634 | 1.7193 | 1.9039 | 2.2307 | 2.6603 | 3.2406 | 3.7404 | 4.3041 | 4.991 | 5.7403 | 6.3831 | 6.9879 | 7.5782 | 8.1329 | 9.7553 | 10.1966
West Midlands | Ironbr. & Shrewsb. 132kV | DOTHILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.3465 | 1.4131 | 1.4907 | 1.581 | 1.6861 | 1.8051 | 1.9348 | 2.1264 | 2.2579 | 2.4258 | 2.6315 | 2.8518 | 3.1008 | 3.3527 | 3.6062 | 3.9896 | 5.0489 | 5.2957 | 3.2985 | 3.4371 | 3.598 | 3.7848 | 4.0025 | 4.249 | 4.5181 | 4.9157 | 5.1865 | 5.5402 | 5.9823 | 6.4525 | 6.9802 | 7.5111 | 8.0373 | 8.8424 | 11.0427 | 11.5685
West Midlands | Ironbr. & Shrewsb. 132kV | DOTHILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.3998 | 1.548 | 1.7266 | 1.9493 | 2.1972 | 2.4882 | 2.854 | 3.3184 | 3.6738 | 4.0879 | 4.4748 | 4.8157 | 5.0675 | 5.2612 | 5.4281 | 5.5943 | 5.8412 | 6.0953 | 3.4143 | 3.7236 | 4.0963 | 4.5616 | 5.0792 | 5.6893 | 6.4681 | 7.4624 | 8.2011 | 9.1102 | 9.9569 | 10.6805 | 11.2227 | 11.6461 | 12.0155 | 12.3833 | 12.9592 | 13.5356
West Midlands | Ironbr. & Shrewsb. 132kV | DOTHILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.383 | 1.4807 | 1.6173 | 1.7763 | 2.0379 | 2.3549 | 2.7515 | 3.2371 | 3.5555 | 3.8966 | 4.186 | 4.6018 | 4.8796 | 5.142 | 5.3916 | 5.5809 | 6.1026 | 6.3482 | 3.3853 | 3.5969 | 3.8893 | 4.2293 | 4.7927 | 5.4934 | 6.376 | 7.4548 | 8.1325 | 8.8694 | 9.4746 | 10.3974 | 10.9804 | 11.5321 | 12.0581 | 12.4551 | 13.6044 | 14.1632
West Midlands | Ironbr. & Shrewsb. 132kV | DOTHILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.3659 | 1.451 | 1.5752 | 1.7086 | 1.9087 | 2.1451 | 2.4312 | 2.8002 | 3.0611 | 3.4352 | 3.8492 | 4.2146 | 4.5183 | 4.8003 | 5.0707 | 5.3115 | 6.0708 | 6.302 | 3.3404 | 3.5198 | 3.7812 | 4.0618 | 4.487 | 4.991 | 5.6106 | 6.4085 | 6.9549 | 7.7733 | 8.6718 | 9.4487 | 10.0846 | 10.6755 | 11.2431 | 11.7483 | 13.5083 | 14.0333
West Midlands | Ironbr. & Shrewsb. 132kV | EASTHOPE 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.27231 | 0.28605 | 0.30061 | 0.31881 | 0.34202 | 0.36985 | 0.40088 | 0.44786 | 0.48616 | 0.52464 | 0.56324 | 0.60398 | 0.6517 | 0.6957 | 0.73738 | 0.7828 | 1.0156 | 1.1381 | 0.66656 | 0.69542 | 0.7256 | 0.76318 | 0.81095 | 0.86815 | 0.93184 | 1.0276 | 1.106 | 1.1845 | 1.2631 | 1.3458 | 1.4425 | 1.5316 | 1.616 | 1.7078 | 2.1807 | 2.4329
West Midlands | Ironbr. & Shrewsb. 132kV | EASTHOPE 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.28489 | 0.31698 | 0.35451 | 0.40234 | 0.45737 | 0.526 | 0.60376 | 0.69172 | 0.77637 | 0.85235 | 0.91991 | 0.98594 | 1.0322 | 1.0618 | 1.0867 | 1.1107 | 1.2424 | 1.3194 | 0.69377 | 0.7613 | 0.83889 | 0.93745 | 1.0508 | 1.1916 | 1.3507 | 1.5298 | 1.7026 | 1.8578 | 1.9961 | 2.1309 | 2.2263 | 2.2883 | 2.341 | 2.3922 | 2.6752 | 2.845
West Midlands | Ironbr. & Shrewsb. 132kV | EASTHOPE 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.28097 | 0.30281 | 0.32698 | 0.35991 | 0.39298 | 0.4486 | 0.50184 | 0.57554 | 0.63985 | 0.70998 | 0.78727 | 0.85908 | 0.92644 | 0.98497 | 1.0485 | 1.1012 | 1.2903 | 1.3991 | 0.68699 | 0.73531 | 0.78705 | 0.85682 | 0.92663 | 1.0422 | 1.1527 | 1.3045 | 1.4379 | 1.5824 | 1.7414 | 1.8895 | 2.0285 | 2.1494 | 2.2808 | 2.3904 | 2.7909 | 3.0271
West Midlands | Ironbr. & Shrewsb. 132kV | EASTHOPE 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.2775 | 0.29441 | 0.31576 | 0.34994 | 0.38637 | 0.43194 | 0.48678 | 0.55998 | 0.6252 | 0.70719 | 0.7844 | 0.85134 | 0.92178 | 0.9747 | 1.0348 | 1.0824 | 1.2651 | 1.3683 | 0.6776 | 0.71347 | 0.7578 | 0.82828 | 0.90322 | 0.99687 | 1.1091 | 1.2578 | 1.3908 | 1.5573 | 1.7139 | 1.8501 | 1.9932 | 2.1013 | 2.2239 | 2.3217 | 2.7014 | 2.92
West Midlands | Ironbr. & Shrewsb. 132kV | HALESFIELD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.6542 | 1.7029 | 1.7529 | 1.8111 | 1.8795 | 1.9587 | 2.0429 | 2.1793 | 2.2908 | 2.4047 | 2.5241 | 2.6498 | 2.7879 | 2.9226 | 3.0514 | 3.1875 | 3.7829 | 4.0496 | 4.0956 | 4.1982 | 4.3019 | 4.4227 | 4.5654 | 4.7293 | 4.903 | 5.1826 | 5.4118 | 5.6461 | 5.8917 | 6.1485 | 6.4299 | 6.704 | 6.9655 | 7.2416 | 8.4555 | 9.0126
West Midlands | Ironbr. & Shrewsb. 132kV | HALESFIELD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.7077 | 1.8226 | 1.9478 | 2.094 | 2.2633 | 2.4459 | 2.667 | 2.9376 | 3.1675 | 3.3622 | 3.5438 | 3.7105 | 3.8208 | 3.8906 | 3.9432 | 3.986 | 4.2341 | 4.4581 | 4.215 | 4.4571 | 4.7173 | 5.0225 | 5.3763 | 5.7527 | 6.2113 | 6.7681 | 7.2401 | 7.6427 | 8.0194 | 8.3626 | 8.5924 | 8.7401 | 8.8535 | 8.9471 | 9.5039 | 10.0038
West Midlands | Ironbr. & Shrewsb. 132kV | HALESFIELD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.7045 | 1.7852 | 1.8778 | 1.9684 | 2.0703 | 2.2101 | 2.3529 | 2.5532 | 2.7177 | 2.8905 | 3.074 | 3.2577 | 3.4393 | 3.6076 | 3.7733 | 3.9218 | 4.3561 | 4.6252 | 4.2169 | 4.3957 | 4.5982 | 4.7923 | 5.0097 | 5.3085 | 5.6107 | 6.0274 | 6.3688 | 6.7264 | 7.1049 | 7.4848 | 7.8607 | 8.2096 | 8.5532 | 8.863 | 9.7925 | 10.3926
West Midlands | Ironbr. & Shrewsb. 132kV | HALESFIELD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.6829 | 1.7461 | 1.8178 | 1.91 | 2.0168 | 2.1303 | 2.2759 | 2.4743 | 2.6432 | 2.833 | 3.0252 | 3.2056 | 3.3816 | 3.5357 | 3.6875 | 3.8177 | 4.7864 | 5.0019 | 4.161 | 4.2949 | 4.4442 | 4.6376 | 4.8629 | 5.0984 | 5.4018 | 5.8099 | 6.1563 | 6.5456 | 6.939 | 7.3072 | 7.666 | 7.9805 | 8.2904 | 8.5569 | 10.8417 | 11.3139
West Midlands | Ironbr. & Shrewsb. 132kV | HARLESCOTT 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.21026 | 0.24563 | 0.28331 | 0.32821 | 0.37317 | 0.42822 | 0.50477 | 0.59699 | 0.67188 | 0.75747 | 0.83517 | 0.90998 | 0.99037 | 1.0663 | 1.1392 | 1.2147 | 1.5954 | 1.8044 | 0.5039 | 0.57941 | 0.6591 | 0.75405 | 0.84938 | 0.96668 | 1.1354 | 1.3314 | 1.4923 | 1.6773 | 1.8431 | 2.0001 | 2.1671 | 2.3242 | 2.4752 | 2.631 | 3.4315 | 3.8878
West Midlands | Ironbr. & Shrewsb. 132kV | HARLESCOTT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.231 | 0.30836 | 0.39832 | 0.50649 | 0.61892 | 0.78253 | 0.92548 | 1.0939 | 1.2446 | 1.3787 | 1.5101 | 1.6323 | 1.7275 | 1.7883 | 1.8425 | 1.8951 | 2.1828 | 2.4161 | 0.54864 | 0.71615 | 0.9104 | 1.1424 | 1.3825 | 1.7461 | 2.0509 | 2.4072 | 2.7279 | 3.0158 | 3.3005 | 3.5643 | 3.7737 | 3.9083 | 4.0292 | 4.1477 | 4.8055 | 5.3536
West Midlands | Ironbr. & Shrewsb. 132kV | HARLESCOTT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.22955 | 0.29221 | 0.35327 | 0.43181 | 0.50165 | 0.59879 | 0.70195 | 0.83724 | 0.95892 | 1.119 | 1.2564 | 1.3905 | 1.5154 | 1.6224 | 1.7306 | 1.8287 | 2.1819 | 2.3613 | 0.54983 | 0.69121 | 0.82293 | 0.99386 | 1.1457 | 1.3566 | 1.5827 | 1.8734 | 2.1388 | 2.4971 | 2.7932 | 3.0833 | 3.3536 | 3.5809 | 3.8109 | 4.021 | 4.8036 | 5.2069
West Midlands | Ironbr. & Shrewsb. 132kV | HARLESCOTT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.21886 | 0.27025 | 0.32269 | 0.39049 | 0.4615 | 0.59345 | 0.69525 | 0.82081 | 0.93162 | 1.0625 | 1.1823 | 1.2979 | 1.4081 | 1.5026 | 1.5967 | 1.6818 | 1.9915 | 2.2154 | 0.52219 | 0.635 | 0.74694 | 0.89168 | 1.0441 | 1.3415 | 1.5603 | 1.8259 | 2.0618 | 2.3407 | 2.5931 | 2.8365 | 3.0676 | 3.2646 | 3.4612 | 3.6407 | 4.3242 | 4.839
West Midlands | Ironbr. & Shrewsb. 132kV | HORTONWOOD 132 11kV S STN | Bulk Supply Point | 11 | Counterfactual | 2.3912 | 2.4923 | 3.2452 | 3.3834 | 3.5905 | 3.8446 | 4.0774 | 4.4042 | 4.6456 | 4.9103 | 5.2012 | 5.5129 | 5.8571 | 6.2086 | 6.5513 | 6.919 | 8.9696 | 9.6544 | 5.6387 | 5.8499 | 7.6791 | 7.965 | 8.4103 | 8.9683 | 9.4622 | 10.1389 | 10.6347 | 11.1816 | 11.7865 | 12.432 | 13.142 | 13.8658 | 14.5681 | 15.3207 | 19.5666 | 21.0146
West Midlands | Ironbr. & Shrewsb. 132kV | HORTONWOOD 132 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | 2.4909 | 2.7346 | 3.0309 | 3.4726 | 4.1886 | 4.7631 | 5.4034 | 6.0892 | 6.6467 | 7.1421 | 7.6238 | 8.1221 | 8.4989 | 8.7816 | 9.0133 | 9.2913 | 10.2786 | 10.8603 | 5.857 | 6.3663 | 6.9854 | 7.939 | 9.5564 | 10.7998 | 12.1645 | 13.6006 | 14.7539 | 15.7935 | 16.8055 | 17.8481 | 18.6497 | 19.2585 | 19.7614 | 20.3898 | 22.5631 | 23.851
West Midlands | Ironbr. & Shrewsb. 132kV | HORTONWOOD 132 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | 2.4723 | 2.6321 | 3.004 | 3.3773 | 3.8321 | 4.2979 | 4.7489 | 5.2858 | 5.7272 | 6.1992 | 6.8224 | 7.3236 | 7.8177 | 8.2915 | 8.7444 | 9.1533 | 10.4966 | 11.0897 | 5.8326 | 6.1817 | 7.0315 | 7.8748 | 8.9004 | 9.9315 | 10.9067 | 12.0433 | 12.9697 | 13.9599 | 15.3102 | 16.3555 | 17.3866 | 18.3764 | 19.3237 | 20.1831 | 23.0804 | 24.4026
West Midlands | Ironbr. & Shrewsb. 132kV | HORTONWOOD 132 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | 2.4319 | 2.5633 | 2.7361 | 3.0048 | 3.5376 | 3.9542 | 4.3761 | 4.9126 | 5.3277 | 5.8041 | 6.3383 | 6.8631 | 7.3682 | 7.839 | 8.2785 | 9.0569 | 10.2445 | 10.7247 | 5.7283 | 6.0052 | 6.3654 | 6.953 | 8.1842 | 9.1081 | 10.0183 | 11.1478 | 12.009 | 13.0052 | 14.1207 | 15.2121 | 16.2596 | 17.2363 | 18.1473 | 19.9266 | 22.4575 | 23.5072
West Midlands | Ironbr. & Shrewsb. 132kV | Ketley 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 0.3968 | 0.53768 | 0.69297 | 0.8661 | 1.0621 | 1.2831 | 1.5289 | 1.9005 | 2.1977 | 2.5061 | 2.8215 | 3.1507 | 3.5428 | 3.9303 | 4.306 | 4.675 | 6.1483 | 6.5993 | 0.894 | 1.1886 | 1.5101 | 1.8684 | 2.2741 | 2.7315 | 3.2402 | 4.003 | 4.6169 | 5.2542 | 5.9046 | 6.5818 | 7.3878 | 8.1832 | 8.9538 | 9.71 | 12.7225 | 13.6825
West Midlands | Ironbr. & Shrewsb. 132kV | Ketley 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 0.52758 | 0.87704 | 1.2821 | 1.7645 | 2.1912 | 2.636 | 3.1644 | 3.8177 | 4.4552 | 4.9969 | 5.5399 | 6.0891 | 6.3443 | 6.4833 | 6.5659 | 6.6419 | 7.0738 | 7.5991 | 1.1792 | 1.9158 | 2.7638 | 3.7742 | 4.6579 | 5.5768 | 6.665 | 8.0035 | 9.3212 | 10.4489 | 11.5887 | 12.7426 | 13.2783 | 13.5757 | 13.7598 | 13.9303 | 14.9086 | 16.0894
West Midlands | Ironbr. & Shrewsb. 132kV | Ketley 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 0.49567 | 0.74759 | 1.05 | 1.4004 | 1.6537 | 1.9433 | 2.2757 | 2.8825 | 3.4332 | 3.9413 | 4.4383 | 4.8829 | 5.3118 | 5.7074 | 6.0735 | 6.4058 | 7.3622 | 7.9162 | 1.1252 | 1.6748 | 2.323 | 3.0737 | 3.6122 | 4.2275 | 4.9283 | 6.2052 | 7.3713 | 8.4373 | 9.4717 | 10.3929 | 11.281 | 12.0984 | 12.8558 | 13.5466 | 15.6056 | 16.8544
West Midlands | Ironbr. & Shrewsb. 132kV | Ketley 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 0.43754 | 0.6182 | 0.82958 | 1.0707 | 1.3447 | 1.6588 | 2.0214 | 2.5071 | 2.9848 | 3.4884 | 4.0539 | 4.6296 | 5.0722 | 5.4801 | 5.8582 | 6.1771 | 6.9405 | 7.3882 | 0.98224 | 1.3651 | 1.8067 | 2.3122 | 2.8871 | 3.5461 | 4.3046 | 5.306 | 6.3016 | 7.3494 | 8.5257 | 9.7255 | 10.6342 | 11.4701 | 12.2462 | 12.8994 | 14.5137 | 15.5103
West Midlands | Ironbr. & Shrewsb. 132kV | LEATON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.99903 | 1.0177 | 1.0438 | 1.0748 | 1.1251 | 1.1855 | 1.257 | 1.3592 | 1.4484 | 1.5619 | 1.6627 | 1.7602 | 1.8688 | 1.9689 | 2.0628 | 2.1559 | 2.5518 | 2.7705 | 2.4674 | 2.5067 | 2.5632 | 2.6304 | 2.7387 | 2.87 | 3.027 | 3.2499 | 3.4458 | 3.6975 | 3.9188 | 4.1293 | 4.3612 | 4.5738 | 4.7725 | 4.9693 | 5.8162 | 6.3076
West Midlands | Ironbr. & Shrewsb. 132kV | LEATON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.0169 | 1.0626 | 1.1393 | 1.2517 | 1.3757 | 1.5233 | 1.7013 | 1.8856 | 2.0978 | 2.3107 | 2.5248 | 2.7114 | 2.816 | 2.8757 | 2.925 | 2.9722 | 3.2407 | 3.5071 | 2.5061 | 2.6021 | 2.7717 | 3.0166 | 3.286 | 3.608 | 3.997 | 4.398 | 4.8585 | 5.3261 | 5.8002 | 6.2111 | 6.4472 | 6.5828 | 6.6971 | 6.8079 | 7.4418 | 8.0859
West Midlands | Ironbr. & Shrewsb. 132kV | LEATON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.0155 | 1.0455 | 1.096 | 1.175 | 1.2567 | 1.3864 | 1.5527 | 1.7733 | 1.9777 | 2.1633 | 2.3074 | 2.4495 | 2.579 | 2.6754 | 2.7696 | 2.8531 | 3.1713 | 3.3228 | 2.5067 | 2.5727 | 2.6814 | 2.8544 | 3.0333 | 3.3218 | 3.6948 | 4.1817 | 4.6337 | 5.0407 | 5.3565 | 5.6692 | 5.9547 | 6.1623 | 6.3656 | 6.5476 | 7.2707 | 7.6201
West Midlands | Ironbr. & Shrewsb. 132kV | LEATON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.0056 | 1.0295 | 1.0642 | 1.1299 | 1.2062 | 1.3089 | 1.435 | 1.595 | 1.7542 | 1.9308 | 2.1005 | 2.2713 | 2.3938 | 2.4928 | 2.5915 | 2.6705 | 2.9567 | 3.2002 | 2.4814 | 2.5321 | 2.6073 | 2.7493 | 2.9163 | 3.1423 | 3.4207 | 3.7701 | 4.1164 | 4.5035 | 4.8713 | 5.2402 | 5.5025 | 5.7126 | 5.9228 | 6.0923 | 6.7438 | 7.3229
West Midlands | Ironbr. & Shrewsb. 132kV | MADELEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.5005 | 1.6641 | 1.862 | 2.0707 | 2.2836 | 2.5228 | 2.7968 | 3.2244 | 3.5675 | 3.9174 | 3.3275 | 3.6981 | 4.1127 | 4.5376 | 4.9491 | 5.3568 | 7.122 | 7.644 | 3.6256 | 3.9663 | 4.3754 | 4.8069 | 5.2462 | 5.7395 | 6.3038 | 7.1771 | 7.8822 | 8.6008 | 6.9653 | 7.7208 | 8.5641 | 9.4283 | 10.265 | 11.0932 | 14.6843 | 15.799
West Midlands | Ironbr. & Shrewsb. 132kV | MADELEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.6411 | 2.0178 | 2.4602 | 2.9519 | 3.4841 | 4.0522 | 4.7349 | 5.5742 | 6.3239 | 6.935 | 6.5531 | 7.1106 | 7.4336 | 7.6104 | 7.7046 | 7.7984 | 8.3508 | 9.0042 | 3.9314 | 4.7179 | 5.6367 | 6.6567 | 7.7561 | 8.9272 | 10.3286 | 12.0447 | 13.5815 | 14.8398 | 13.6418 | 14.7947 | 15.4697 | 15.8472 | 16.0587 | 16.2692 | 17.5172 | 18.9841
West Midlands | Ironbr. & Shrewsb. 132kV | MADELEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.6008 | 1.8473 | 2.1398 | 2.4535 | 2.7682 | 3.1341 | 3.5563 | 4.1804 | 4.7184 | 5.2718 | 4.9172 | 5.4939 | 6.0551 | 6.5758 | 7.0527 | 7.4843 | 8.7127 | 9.4155 | 3.8642 | 4.3994 | 5.0236 | 5.6933 | 6.3616 | 7.1347 | 8.0216 | 9.3176 | 10.4412 | 11.5896 | 10.447 | 11.6397 | 12.7998 | 13.874 | 14.8593 | 15.7555 | 18.3952 | 19.9774
West Midlands | Ironbr. & Shrewsb. 132kV | MADELEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.5507 | 1.7606 | 2.0236 | 2.3026 | 2.6003 | 2.9424 | 3.3428 | 3.9121 | 4.41 | 4.943 | 4.5706 | 5.138 | 5.6675 | 6.1394 | 6.5799 | 6.9655 | 7.9143 | 8.4539 | 3.7342 | 4.1771 | 4.7255 | 5.3089 | 5.929 | 6.6412 | 7.4691 | 8.6343 | 9.6584 | 10.7515 | 9.5604 | 10.7216 | 11.8015 | 12.7608 | 13.657 | 14.443 | 16.4443 | 17.6479
West Midlands | Ironbr. & Shrewsb. 132kV | MALEHURST 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.48209 | 0.51112 | 0.54465 | 0.58441 | 0.63947 | 0.70292 | 0.77318 | 0.87318 | 0.9515 | 1.0313 | 1.1116 | 1.1958 | 1.2911 | 1.3826 | 1.4705 | 1.5604 | 2.0109 | 2.1949 | 1.1755 | 1.2363 | 1.3056 | 1.3878 | 1.5016 | 1.6328 | 1.7778 | 1.9821 | 2.1428 | 2.3061 | 2.4703 | 2.6418 | 2.8352 | 3.0211 | 3.1993 | 3.3814 | 4.2969 | 4.6795
West Midlands | Ironbr. & Shrewsb. 132kV | MALEHURST 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.51129 | 0.58377 | 0.68104 | 0.81309 | 0.96205 | 1.1164 | 1.2935 | 1.5015 | 1.6961 | 1.8585 | 1.9992 | 2.1366 | 2.2348 | 2.2936 | 2.3287 | 2.3682 | 2.5653 | 2.7225 | 1.239 | 1.3904 | 1.5976 | 1.8789 | 2.195 | 2.5197 | 2.8888 | 3.3208 | 3.727 | 4.0644 | 4.3565 | 4.6425 | 4.8529 | 4.9821 | 5.059 | 5.1483 | 5.5947 | 5.954
West Midlands | Ironbr. & Shrewsb. 132kV | MALEHURST 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.50403 | 0.5505 | 0.62624 | 0.71972 | 0.8096 | 0.91835 | 1.0321 | 1.1807 | 1.3103 | 1.4492 | 1.6019 | 1.7475 | 1.8843 | 2.0069 | 2.1288 | 2.2341 | 2.5542 | 2.7385 | 1.2277 | 1.3293 | 1.4959 | 1.6997 | 1.8953 | 2.1267 | 2.3654 | 2.673 | 2.9422 | 3.2284 | 3.5439 | 3.8451 | 4.1284 | 4.383 | 4.6366 | 4.8573 | 5.5483 | 5.9634
West Midlands | Ironbr. & Shrewsb. 132kV | MALEHURST 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.49271 | 0.52997 | 0.57512 | 0.64691 | 0.72874 | 0.82565 | 0.9372 | 1.0793 | 1.204 | 1.3468 | 1.4883 | 1.6202 | 1.7499 | 1.8577 | 1.9676 | 2.0601 | 2.33 | 2.469 | 1.1985 | 1.2769 | 1.3707 | 1.5203 | 1.691 | 1.893 | 2.1238 | 2.4138 | 2.6688 | 2.9591 | 3.2462 | 3.5145 | 3.7783 | 3.9983 | 4.2227 | 4.4128 | 4.9792 | 5.2804
West Midlands | Ironbr. & Shrewsb. 132kV | NEWPORT 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.3492 | 1.4232 | 1.5106 | 1.6125 | 1.7191 | 1.8354 | 1.9646 | 2.1612 | 2.3124 | 2.4726 | 2.6463 | 2.8289 | 3.0348 | 3.2511 | 3.4553 | 3.6549 | 4.4889 | 4.7788 | 3.2778 | 3.4327 | 3.6139 | 3.8246 | 4.0447 | 4.2844 | 4.5503 | 4.953 | 5.2623 | 5.5908 | 5.9487 | 6.324 | 6.7457 | 7.1895 | 7.606 | 8.0125 | 9.7071 | 10.3147
West Midlands | Ironbr. & Shrewsb. 132kV | NEWPORT 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.4148 | 1.5898 | 1.8237 | 2.0944 | 2.3897 | 2.7054 | 3.0893 | 3.5342 | 3.9466 | 4.299 | 4.6107 | 4.914 | 5.1196 | 5.2259 | 5.2704 | 5.3272 | 5.6052 | 5.9191 | 3.4203 | 3.7877 | 4.2905 | 4.8718 | 5.502 | 6.1722 | 6.9879 | 7.9248 | 8.795 | 9.5416 | 10.2019 | 10.844 | 11.2941 | 11.533 | 11.6326 | 11.7675 | 12.4274 | 13.1576
West Midlands | Ironbr. & Shrewsb. 132kV | NEWPORT 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.397 | 1.5151 | 1.677 | 1.8547 | 2.0517 | 2.2913 | 2.5259 | 2.8671 | 3.1612 | 3.4406 | 3.7288 | 3.9917 | 4.2412 | 4.4708 | 4.6854 | 4.8748 | 5.42 | 5.7501 | 3.3908 | 3.6495 | 4.0089 | 4.4005 | 4.8333 | 5.3611 | 5.8632 | 6.5826 | 7.2004 | 7.7815 | 8.3799 | 8.9248 | 9.4425 | 9.92 | 10.367 | 10.7641 | 11.955 | 12.7164
West Midlands | Ironbr. & Shrewsb. 132kV | NEWPORT 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.3728 | 1.4677 | 1.5851 | 1.7228 | 1.8738 | 2.0447 | 2.2695 | 2.5519 | 2.8024 | 3.0872 | 3.3901 | 3.6839 | 3.9468 | 4.1586 | 4.3563 | 4.5664 | 4.9566 | 5.1667 | 3.3287 | 3.5295 | 3.7751 | 4.0624 | 4.3771 | 4.7323 | 5.2068 | 5.7897 | 6.3046 | 6.8934 | 7.5191 | 8.1237 | 8.6616 | 9.0918 | 9.4934 | 9.9406 | 10.7607 | 11.2271
West Midlands | Ironbr. & Shrewsb. 132kV | PRIESTWESTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.24127 | 0.26243 | 0.28469 | 0.31117 | 0.34384 | 0.38492 | 0.43368 | 0.50467 | 0.56466 | 0.63415 | 0.69931 | 0.76052 | 0.82562 | 0.8869 | 0.94538 | 1.0066 | 1.3285 | 1.5095 | 0.58715 | 0.63383 | 0.682 | 0.73933 | 0.80984 | 0.89875 | 1.0052 | 1.1583 | 1.2892 | 1.4422 | 1.5832 | 1.713 | 1.8489 | 1.9768 | 2.0991 | 2.2266 | 2.9057 | 3.3029
West Midlands | Ironbr. & Shrewsb. 132kV | PRIESTWESTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.25607 | 0.30892 | 0.37384 | 0.451 | 0.53613 | 0.64371 | 0.76452 | 0.90302 | 1.0347 | 1.1556 | 1.2721 | 1.3825 | 1.4672 | 1.5183 | 1.5629 | 1.6062 | 1.8485 | 2.0417 | 0.61927 | 0.73591 | 0.87881 | 1.0467 | 1.2306 | 1.4628 | 1.7224 | 2.0179 | 2.2995 | 2.5597 | 2.8132 | 3.0523 | 3.2399 | 3.3537 | 3.4545 | 3.5529 | 4.1056 | 4.5666
West Midlands | Ironbr. & Shrewsb. 132kV | PRIESTWESTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.25138 | 0.29916 | 0.33297 | 0.38443 | 0.44176 | 0.52398 | 0.61301 | 0.73102 | 0.8362 | 0.94301 | 1.0614 | 1.1734 | 1.2797 | 1.3651 | 1.4533 | 1.5295 | 1.825 | 1.9772 | 0.61121 | 0.72186 | 0.79634 | 0.91031 | 1.0366 | 1.2159 | 1.4124 | 1.6684 | 1.8978 | 2.1282 | 2.3839 | 2.6269 | 2.8577 | 3.0407 | 3.2294 | 3.3941 | 4.0507 | 4.3967
West Midlands | Ironbr. & Shrewsb. 132kV | PRIESTWESTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.24648 | 0.27766 | 0.31045 | 0.35623 | 0.41027 | 0.48003 | 0.56178 | 0.67023 | 0.76808 | 0.88545 | 0.99289 | 1.0859 | 1.1802 | 1.2504 | 1.3268 | 1.39 | 1.6608 | 1.8573 | 0.59837 | 0.66765 | 0.73874 | 0.83719 | 0.95432 | 1.1061 | 1.2828 | 1.5143 | 1.7237 | 1.9739 | 2.2006 | 2.3972 | 2.5953 | 2.7424 | 2.9022 | 3.0357 | 3.6303 | 4.0822
West Midlands | Ironbr. & Shrewsb. 132kV | ROUSHILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.85933 | 0.923 | 0.99386 | 1.0713 | 1.1674 | 1.2787 | 1.4063 | 1.5946 | 1.7418 | 1.8868 | 2.0309 | 2.1794 | 2.3448 | 2.512 | 2.6732 | 2.8328 | 3.5808 | 3.8523 | 1.753 | 1.8879 | 2.0345 | 2.1949 | 2.3937 | 2.6236 | 2.8867 | 3.2717 | 3.5745 | 3.8717 | 4.1662 | 4.4686 | 4.8046 | 5.1438 | 5.4712 | 5.7947 | 7.3204 | 7.8943
West Midlands | Ironbr. & Shrewsb. 132kV | ROUSHILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.91397 | 1.0684 | 1.2317 | 1.4308 | 1.6576 | 1.8934 | 2.1711 | 2.4985 | 2.792 | 3.0287 | 3.2411 | 3.4452 | 3.5775 | 3.6617 | 3.7252 | 3.7867 | 4.1069 | 4.4109 | 1.8714 | 2.1994 | 2.5381 | 2.9516 | 3.4227 | 3.9103 | 4.4818 | 5.1503 | 5.7521 | 6.2389 | 6.6767 | 7.0961 | 7.3726 | 7.5535 | 7.6934 | 7.8298 | 8.5459 | 9.2211
West Midlands | Ironbr. & Shrewsb. 132kV | ROUSHILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.89742 | 1.0091 | 1.1269 | 1.2643 | 1.3915 | 1.5522 | 1.7283 | 1.981 | 2.1945 | 2.4198 | 2.6695 | 2.9125 | 3.1515 | 3.3771 | 3.5922 | 3.7885 | 4.3764 | 4.7277 | 1.8429 | 2.0927 | 2.3456 | 2.6405 | 2.9122 | 3.2532 | 3.6236 | 4.1481 | 4.5936 | 5.0612 | 5.579 | 6.0829 | 6.5785 | 7.047 | 7.4951 | 7.906 | 9.1749 | 9.9626
West Midlands | Ironbr. & Shrewsb. 132kV | ROUSHILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.88 | 0.96344 | 1.062 | 1.1773 | 1.3032 | 1.451 | 1.6286 | 1.8608 | 2.065 | 2.2805 | 2.5079 | 2.7332 | 2.9524 | 3.1575 | 3.3558 | 3.535 | 4.0095 | 4.2809 | 1.7974 | 1.9758 | 2.1808 | 2.4219 | 2.6844 | 2.9923 | 3.3605 | 3.835 | 4.2543 | 4.695 | 5.1588 | 5.6187 | 6.0661 | 6.4854 | 6.892 | 7.2606 | 8.2648 | 8.8567
West Midlands | Ironbr. & Shrewsb. 132kV | ROWTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.8972 | 2.9067 | 2.9181 | 2.932 | 2.9495 | 2.9723 | 2.9983 | 3.0365 | 3.0685 | 3.1022 | 3.1346 | 3.1663 | 3.2019 | 3.235 | 3.2666 | 3.3004 | 3.4823 | 3.5899 | 7.1986 | 7.2187 | 7.2428 | 7.2722 | 7.3089 | 7.3569 | 7.4121 | 7.4923 | 7.5601 | 7.632 | 7.7002 | 7.7659 | 7.8394 | 7.9074 | 7.9724 | 8.0416 | 8.4195 | 8.6484
West Midlands | Ironbr. & Shrewsb. 132kV | ROWTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.9061 | 2.9298 | 2.9711 | 3.0235 | 3.0805 | 3.1469 | 3.2189 | 3.3038 | 3.3877 | 3.4615 | 3.53 | 3.5969 | 3.6641 | 3.7238 | 3.7513 | 3.7833 | 3.9824 | 4.7004 | 7.2178 | 7.2681 | 7.36 | 7.4753 | 7.6 | 7.7437 | 7.8982 | 8.0804 | 8.2617 | 8.4205 | 8.5683 | 8.7129 | 8.86 | 8.9883 | 9.0484 | 9.1203 | 9.5606 | 11.3383
West Midlands | Ironbr. & Shrewsb. 132kV | ROWTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.9053 | 2.9226 | 2.949 | 2.9853 | 3.0219 | 3.0719 | 3.1208 | 3.1852 | 3.2451 | 3.3062 | 3.3747 | 3.4395 | 3.5093 | 3.581 | 3.6342 | 3.6805 | 5.1056 | 5.205 | 7.2179 | 7.2563 | 7.3161 | 7.3973 | 7.479 | 7.5871 | 7.6929 | 7.83 | 7.9593 | 8.089 | 8.2347 | 8.3735 | 8.5215 | 8.671 | 8.7835 | 8.8824 | 12.3717 | 12.5937
West Midlands | Ironbr. & Shrewsb. 132kV | ROWTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.9006 | 2.9134 | 2.9293 | 2.9544 | 2.9821 | 3.0191 | 3.0633 | 3.1208 | 3.1737 | 3.2384 | 3.2982 | 3.3519 | 3.4107 | 3.4624 | 3.508 | 3.5461 | 3.7165 | 4.4253 | 7.206 | 7.2332 | 7.2669 | 7.3194 | 7.3779 | 7.4562 | 7.5493 | 7.669 | 7.78 | 7.9155 | 8.0395 | 8.1512 | 8.2728 | 8.3791 | 8.4735 | 8.5534 | 8.9182 | 10.6621
West Midlands | Ironbr. & Shrewsb. 132kV | SHIFNAL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.3324 | 0.36771 | 0.41021 | 0.45406 | 0.5059 | 0.58107 | 0.72277 | 0.84409 | 0.94555 | 1.059 | 1.1757 | 1.2949 | 1.422 | 1.5555 | 1.758 | 1.8604 | 2.3369 | 2.5122 | 0.72278 | 0.79813 | 0.88866 | 0.97967 | 1.0871 | 1.2435 | 1.5626 | 1.8131 | 2.0243 | 2.2613 | 2.5043 | 2.7515 | 3.0133 | 3.2954 | 3.7545 | 3.9635 | 4.9401 | 5.313
West Midlands | Ironbr. & Shrewsb. 132kV | SHIFNAL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.36443 | 0.45801 | 0.57268 | 0.68439 | 0.84804 | 1.1963 | 1.4206 | 1.6851 | 1.8852 | 2.0527 | 2.2007 | 2.4772 | 2.5863 | 2.6619 | 2.722 | 2.7572 | 2.9512 | 3.1171 | 0.79232 | 0.99358 | 1.241 | 1.4735 | 1.817 | 2.6105 | 3.0814 | 3.6339 | 4.0488 | 4.3976 | 4.7073 | 5.3414 | 5.5809 | 5.7522 | 5.8927 | 5.9718 | 6.4125 | 6.7933
West Midlands | Ironbr. & Shrewsb. 132kV | SHIFNAL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.35479 | 0.42167 | 0.50147 | 0.60651 | 0.81086 | 0.96866 | 1.1415 | 1.3079 | 1.4585 | 1.7999 | 1.9771 | 2.1497 | 2.3165 | 2.4702 | 2.6207 | 2.7343 | 3.072 | 3.249 | 0.77577 | 0.92701 | 1.1057 | 1.3313 | 1.7969 | 2.1361 | 2.507 | 2.8555 | 3.1734 | 3.9645 | 4.3439 | 4.7138 | 5.0715 | 5.401 | 5.7244 | 5.9627 | 6.6957 | 7.0957
West Midlands | Ironbr. & Shrewsb. 132kV | SHIFNAL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.34426 | 0.39973 | 0.47104 | 0.5364 | 0.63562 | 0.91025 | 1.0513 | 1.236 | 1.3969 | 1.5693 | 1.7371 | 2.0312 | 2.1972 | 2.3376 | 2.4766 | 2.5782 | 2.8677 | 3.027 | 0.74835 | 0.87067 | 1.0279 | 1.1645 | 1.3742 | 2.0141 | 2.3119 | 2.6976 | 3.0348 | 3.3948 | 3.7431 | 4.412 | 4.7641 | 5.0623 | 5.3581 | 5.5681 | 6.1874 | 6.5441
West Midlands | Ironbr. & Shrewsb. 132kV | SNEDSHILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.3368 | 1.443 | 1.6579 | 1.8061 | 2.0084 | 2.9222 | 3.1796 | 3.544 | 3.8296 | 4.1164 | 4.3799 | 4.6533 | 4.9699 | 5.2959 | 5.5784 | 5.8533 | 6.435 | 6.7825 | 3.189 | 3.4119 | 3.8514 | 4.1586 | 4.5857 | 6.7831 | 7.3313 | 8.1062 | 8.71 | 9.3114 | 9.8633 | 10.4335 | 11.0916 | 11.7682 | 12.3486 | 12.912 | 13.8888 | 14.621
West Midlands | Ironbr. & Shrewsb. 132kV | SNEDSHILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.4122 | 1.7317 | 2.0018 | 2.4145 | 2.9897 | 3.5706 | 4.2927 | 4.926 | 5.4437 | 5.9092 | 6.3327 | 6.7163 | 6.9146 | 7.0205 | 7.0857 | 7.1467 | 7.1027 | 7.4714 | 3.3524 | 4.0173 | 4.5815 | 5.4597 | 6.7251 | 7.9905 | 9.5775 | 10.9353 | 12.0167 | 13.003 | 13.8996 | 14.7034 | 15.1191 | 15.3444 | 15.4881 | 15.6232 | 15.4235 | 16.2471
West Midlands | Ironbr. & Shrewsb. 132kV | SNEDSHILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.3984 | 1.6533 | 1.9701 | 2.3306 | 2.7803 | 3.3646 | 3.7906 | 4.3247 | 4.7581 | 5.1978 | 5.5552 | 5.9917 | 6.2994 | 6.5828 | 6.8513 | 7.093 | 7.3545 | 7.7904 | 3.3354 | 3.8786 | 4.5799 | 5.3754 | 6.3835 | 7.7136 | 8.6645 | 9.8113 | 10.7297 | 11.6611 | 12.4041 | 13.3593 | 13.9957 | 14.5819 | 15.1376 | 15.6406 | 16.0428 | 17.0172
West Midlands | Ironbr. & Shrewsb. 132kV | SNEDSHILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.3649 | 1.5914 | 1.7663 | 2.0186 | 2.4062 | 2.8076 | 3.3043 | 3.8341 | 4.2559 | 4.7214 | 5.1858 | 5.6455 | 6.0018 | 6.2821 | 6.5493 | 6.7734 | 6.9294 | 7.2752 | 3.2494 | 3.7204 | 4.0882 | 4.6309 | 5.5012 | 6.3945 | 7.5069 | 8.6572 | 9.548 | 10.5345 | 11.5119 | 12.4766 | 13.2122 | 13.7859 | 14.3329 | 14.792 | 14.9645 | 15.7209
West Midlands | Ironbr. & Shrewsb. 132kV | SPRING GARDENS 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.81021 | 1.0037 | 1.2512 | 1.5436 | 1.8757 | 2.2143 | 2.6366 | 3.1862 | 3.6342 | 4.1095 | 4.5938 | 5.088 | 5.6305 | 6.1863 | 6.8635 | 7.4164 | 9.7774 | 10.5989 | 1.8931 | 2.2993 | 2.8152 | 3.4221 | 4.1115 | 4.8145 | 5.7168 | 6.8474 | 7.7755 | 8.7627 | 9.7641 | 10.7798 | 11.8897 | 13.0358 | 14.4812 | 15.62 | 20.464 | 22.2186
West Midlands | Ironbr. & Shrewsb. 132kV | SPRING GARDENS 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.97343 | 1.433 | 2.0061 | 2.6482 | 3.3869 | 4.3124 | 5.2072 | 6.2787 | 7.2451 | 8.0514 | 8.8109 | 9.7233 | 10.2395 | 10.5915 | 10.8568 | 11.086 | 12.1309 | 13.0802 | 2.2473 | 3.2167 | 4.4258 | 5.7693 | 7.3137 | 9.3032 | 11.1596 | 13.3697 | 15.3708 | 17.0488 | 18.6375 | 20.6196 | 21.7272 | 22.4983 | 23.0943 | 23.6133 | 25.9652 | 28.1083
West Midlands | Ironbr. & Shrewsb. 132kV | SPRING GARDENS 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.92907 | 1.2523 | 1.6334 | 2.0755 | 2.676 | 3.2467 | 3.8605 | 4.6701 | 5.3939 | 6.3287 | 7.1657 | 7.9772 | 8.7631 | 9.4878 | 10.1749 | 10.7872 | 12.5456 | 13.4776 | 2.1754 | 2.8873 | 3.7117 | 4.6608 | 5.9792 | 7.1987 | 8.5028 | 10.1972 | 11.7229 | 13.7633 | 15.5244 | 17.2339 | 18.8895 | 20.4121 | 21.8588 | 23.1536 | 26.9566 | 29.0478
West Midlands | Ironbr. & Shrewsb. 132kV | SPRING GARDENS 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.87012 | 1.143 | 1.503 | 1.9063 | 2.3777 | 3.0215 | 3.5872 | 4.3624 | 5.0412 | 5.7717 | 6.5326 | 7.4499 | 8.1852 | 8.8572 | 9.5066 | 10.0671 | 11.528 | 12.3319 | 2.0222 | 2.6064 | 3.3695 | 4.2175 | 5.2117 | 6.6228 | 7.8051 | 9.4076 | 10.8173 | 12.3302 | 13.899 | 15.8714 | 17.3973 | 18.7921 | 20.1434 | 21.3126 | 24.4315 | 26.2279
West Midlands | Ironbr. & Shrewsb. 132kV | STAR ALUMINIUM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.6793 | 1.7596 | 1.8629 | 1.9882 | 2.1366 | 2.3104 | 2.5477 | 2.8287 | 3.0687 | 3.3427 | 3.6202 | 3.8945 | 4.1882 | 4.4663 | 4.6941 | 4.9199 | 5.9593 | 6.397 | 4.1048 | 4.2757 | 4.4934 | 4.7564 | 5.0684 | 5.4344 | 5.9488 | 6.5371 | 7.0446 | 7.6265 | 8.2116 | 8.7836 | 9.3928 | 9.9683 | 10.4363 | 10.8994 | 13.0462 | 13.9854
West Midlands | Ironbr. & Shrewsb. 132kV | STAR ALUMINIUM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.7548 | 1.9508 | 2.282 | 2.674 | 3.1024 | 3.6644 | 4.1919 | 4.8263 | 5.4331 | 5.9689 | 6.4355 | 6.8836 | 7.2358 | 7.4763 | 7.5803 | 7.723 | 8.4596 | 9.0437 | 4.2717 | 4.6914 | 5.4284 | 6.297 | 7.2406 | 8.4991 | 9.6435 | 11.0169 | 12.3424 | 13.5117 | 14.5287 | 15.5108 | 16.3041 | 16.8497 | 17.0835 | 17.4168 | 19.1231 | 20.5071
West Midlands | Ironbr. & Shrewsb. 132kV | STAR ALUMINIUM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.736 | 1.8934 | 2.1323 | 2.4131 | 2.8113 | 3.1662 | 3.534 | 3.9942 | 4.4144 | 4.8832 | 5.293 | 5.6845 | 6.0683 | 6.4145 | 6.7083 | 6.9735 | 7.8908 | 8.3784 | 4.2401 | 4.593 | 5.1365 | 5.7699 | 6.6791 | 7.4653 | 8.2689 | 9.2603 | 10.1727 | 11.1967 | 12.0753 | 12.9124 | 13.7329 | 14.4694 | 15.0922 | 15.6585 | 17.6815 | 18.8033
West Midlands | Ironbr. & Shrewsb. 132kV | STAR ALUMINIUM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.7147 | 1.8437 | 2.0054 | 2.1983 | 2.4392 | 2.8071 | 3.1338 | 3.5561 | 3.9369 | 4.3703 | 4.7673 | 5.1324 | 5.474 | 5.7762 | 6.0297 | 6.253 | 6.9548 | 7.3684 | 4.1843 | 4.4656 | 4.8133 | 5.2261 | 5.7444 | 6.567 | 7.2686 | 8.1632 | 8.9752 | 9.8984 | 10.7338 | 11.503 | 12.2149 | 12.8437 | 13.367 | 13.8312 | 15.3452 | 16.2822
West Midlands | Ironbr. & Shrewsb. 132kV | WEIR HILL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.35152 | 0.43173 | 0.51312 | 0.60174 | 0.67406 | 0.75103 | 0.84246 | 0.97335 | 1.0862 | 1.1993 | 1.2945 | 1.3901 | 1.4932 | 1.598 | 1.6978 | 1.797 | 2.2715 | 2.4223 | 0.85011 | 1.0192 | 1.1909 | 1.3779 | 1.5318 | 1.6962 | 1.8914 | 2.1673 | 2.4083 | 2.651 | 2.8473 | 3.0431 | 3.2535 | 3.4666 | 3.6698 | 3.8714 | 4.8441 | 5.1706
West Midlands | Ironbr. & Shrewsb. 132kV | WEIR HILL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.39181 | 0.54418 | 0.72328 | 0.91341 | 1.1086 | 1.3144 | 1.5433 | 1.8082 | 2.0542 | 2.2605 | 2.4054 | 2.5485 | 2.6485 | 2.7049 | 2.7375 | 2.777 | 2.9757 | 3.1762 | 0.93924 | 1.2659 | 1.656 | 2.0709 | 2.4971 | 2.9466 | 3.4414 | 4.0089 | 4.5401 | 4.9887 | 5.2947 | 5.5966 | 5.815 | 5.9415 | 6.0164 | 6.1084 | 6.5716 | 7.0372
West Midlands | Ironbr. & Shrewsb. 132kV | WEIR HILL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.38304 | 0.50312 | 0.64181 | 0.7854 | 0.91803 | 1.0662 | 1.219 | 1.4221 | 1.6003 | 1.7848 | 1.9456 | 2.1012 | 2.2522 | 2.39 | 2.5205 | 2.6396 | 2.9839 | 3.1608 | 0.92593 | 1.1907 | 1.4989 | 1.8207 | 2.1208 | 2.4541 | 2.7935 | 3.2348 | 3.6262 | 4.0281 | 4.3651 | 4.6918 | 5.0085 | 5.2961 | 5.5694 | 5.8201 | 6.573 | 6.9787
West Midlands | Ironbr. & Shrewsb. 132kV | WEIR HILL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.36865 | 0.47978 | 0.60054 | 0.72344 | 0.83968 | 0.97087 | 1.1192 | 1.3048 | 1.4745 | 1.6507 | 1.794 | 1.9353 | 2.0727 | 2.1983 | 2.3159 | 2.425 | 2.7119 | 2.8646 | 0.88878 | 1.1307 | 1.3939 | 1.6639 | 1.9214 | 2.2123 | 2.538 | 2.9377 | 3.306 | 3.6873 | 3.9819 | 4.2721 | 4.5538 | 4.8111 | 5.0527 | 5.2778 | 5.8936 | 6.2413
West Midlands | Ironbr. & Shrewsb. 132kV | WORFIELD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.14535 | 0.15596 | 0.17075 | 0.18928 | 0.21208 | 0.24037 | 0.27534 | 0.32638 | 0.37028 | 0.41907 | 0.46185 | 0.50216 | 0.54435 | 0.58407 | 0.62252 | 0.6624 | 0.88983 | 1.0214 | 0.34839 | 0.3706 | 0.40228 | 0.44211 | 0.49115 | 0.55258 | 0.62935 | 0.74005 | 0.83633 | 0.94464 | 1.0379 | 1.1237 | 1.2121 | 1.295 | 1.3754 | 1.4586 | 1.9408 | 2.2322
West Midlands | Ironbr. & Shrewsb. 132kV | WORFIELD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.15634 | 0.18337 | 0.22754 | 0.27946 | 0.3375 | 0.40809 | 0.49002 | 0.58416 | 0.67422 | 0.75878 | 0.84021 | 0.9169 | 0.97533 | 1.009 | 1.037 | 1.0639 | 1.2125 | 1.3598 | 0.37223 | 0.42878 | 0.52578 | 0.63872 | 0.76429 | 0.91712 | 1.0938 | 1.2955 | 1.489 | 1.6722 | 1.8512 | 2.0188 | 2.1499 | 2.2261 | 2.2907 | 2.3535 | 2.7039 | 3.0576
West Midlands | Ironbr. & Shrewsb. 132kV | WORFIELD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.15303 | 0.17086 | 0.19071 | 0.22318 | 0.25601 | 0.30815 | 0.37051 | 0.45102 | 0.52665 | 0.60403 | 0.68886 | 0.77159 | 0.84815 | 0.90617 | 0.96468 | 1.0157 | 1.2015 | 1.2931 | 0.36652 | 0.40558 | 0.44799 | 0.51933 | 0.59106 | 0.70507 | 0.84337 | 1.0188 | 1.1853 | 1.3532 | 1.5379 | 1.7186 | 1.8859 | 2.0103 | 2.1357 | 2.2463 | 2.6658 | 2.8742
West Midlands | Ironbr. & Shrewsb. 132kV | WORFIELD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.14955 | 0.16391 | 0.18463 | 0.21564 | 0.25188 | 0.29951 | 0.35642 | 0.42935 | 0.49654 | 0.57857 | 0.6528 | 0.72087 | 0.78493 | 0.83368 | 0.88457 | 0.92778 | 1.1049 | 1.2462 | 0.35743 | 0.38775 | 0.43224 | 0.49879 | 0.57741 | 0.68168 | 0.8055 | 0.96177 | 1.1064 | 1.2833 | 1.441 | 1.5858 | 1.7214 | 1.8238 | 1.931 | 2.0231 | 2.4214 | 2.7539
West Midlands | Kitwell 132kV | BARTLEY GREEN 132 11kV SUBSTN | Bulk Supply Point | 11 | Counterfactual | 1.3464 | 1.523 | 1.7268 | 1.9576 | 2.2052 | 2.477 | 2.7832 | 3.7832 | 4.1718 | 4.5754 | 4.9967 | 5.4956 | 6.0554 | 6.6181 | 7.1689 | 7.7129 | 10.105 | 10.9294 | 2.8096 | 3.1769 | 3.5983 | 4.0748 | 4.5844 | 5.143 | 5.7711 | 8.0397 | 8.8389 | 9.6636 | 10.5226 | 11.5357 | 12.6696 | 13.8088 | 14.9238 | 16.0245 | 20.8669 | 22.5883
West Midlands | Kitwell 132kV | BARTLEY GREEN 132 11kV SUBSTN | Bulk Supply Point | 11 | Electric Engagement | 1.5224 | 1.9473 | 2.4504 | 3.0176 | 3.6463 | 4.3259 | 5.6451 | 6.7128 | 7.6813 | 8.4403 | 9.103 | 9.751 | 10.1299 | 10.3293 | 10.422 | 10.5009 | 10.8274 | 11.38 | 3.1919 | 4.0764 | 5.1177 | 6.2889 | 7.5829 | 8.9794 | 11.9075 | 14.0799 | 16.0655 | 17.616 | 18.9752 | 20.3027 | 21.0903 | 21.5159 | 21.7266 | 21.9096 | 22.693 | 23.9558
West Midlands | Kitwell 132kV | BARTLEY GREEN 132 11kV SUBSTN | Bulk Supply Point | 11 | Holistic Transition | 1.4666 | 1.7299 | 2.0425 | 2.3876 | 2.7629 | 3.6914 | 4.1891 | 4.8927 | 5.5154 | 6.1704 | 6.8975 | 7.6448 | 8.3738 | 9.0422 | 9.6455 | 10.1512 | 11.2754 | 11.8689 | 3.0957 | 3.6665 | 4.3328 | 5.0674 | 5.8621 | 8.0167 | 9.0576 | 10.509 | 11.8097 | 13.1593 | 14.6533 | 16.1903 | 17.6902 | 19.0646 | 20.3076 | 21.3507 | 23.7637 | 25.1392
West Midlands | Kitwell 132kV | BARTLEY GREEN 132 11kV SUBSTN | Bulk Supply Point | 11 | Hydrogen Evolution | 1.4145 | 1.6372 | 1.9206 | 2.2358 | 2.5833 | 2.98 | 3.4525 | 4.6911 | 5.3752 | 6.0769 | 6.8166 | 7.5419 | 8.2519 | 8.9045 | 9.4961 | 10.0074 | 11.0348 | 11.4605 | 2.956 | 3.4242 | 4.0141 | 4.6704 | 5.3917 | 6.2132 | 7.1868 | 9.9437 | 11.3515 | 12.7781 | 14.279 | 15.7495 | 17.1901 | 18.5135 | 19.7136 | 20.752 | 22.8914 | 23.8565
West Midlands | Kitwell 132kV | Bournville 132/11kV | Bulk Supply Point | 11 | Counterfactual | 0.9926 | 1.3036 | 1.7417 | 2.1697 | 2.5504 | 2.9736 | 3.4479 | 4.1883 | 4.779 | 5.3982 | 5.9996 | 6.631 | 7.3386 | 8.0438 | 8.7346 | 9.4207 | 12.4086 | 13.2811 | 2.1419 | 2.7936 | 3.7314 | 4.621 | 5.407 | 6.2796 | 7.2551 | 8.7641 | 9.9807 | 11.2493 | 12.4766 | 13.7624 | 15.1992 | 16.6302 | 18.0321 | 19.4234 | 25.4843 | 27.3296
West Midlands | Kitwell 132kV | Bournville 132/11kV | Bulk Supply Point | 11 | Electric Engagement | 1.2437 | 2.0113 | 2.8148 | 3.7568 | 4.6868 | 5.7048 | 6.9159 | 8.3963 | 9.7335 | 10.7936 | 11.6897 | 12.5476 | 13.0534 | 13.3212 | 13.4496 | 13.5672 | 14.094 | 14.8667 | 2.6894 | 4.33 | 6.0026 | 7.972 | 9.8938 | 11.9952 | 14.4838 | 17.5101 | 20.2648 | 22.4447 | 24.2891 | 26.0514 | 27.1047 | 27.6795 | 27.9738 | 28.2458 | 29.4981 | 31.2649
West Midlands | Kitwell 132kV | Bournville 132/11kV | Bulk Supply Point | 11 | Holistic Transition | 1.2383 | 1.713 | 2.2568 | 2.8985 | 3.4751 | 4.1521 | 4.9309 | 5.9977 | 6.9447 | 7.9141 | 8.8776 | 9.8422 | 10.7911 | 11.6669 | 12.4713 | 13.1536 | 14.7697 | 15.6672 | 2.7348 | 3.7727 | 4.9382 | 6.3217 | 7.5489 | 8.9832 | 10.6206 | 12.8307 | 14.8151 | 16.8252 | 18.8106 | 20.8008 | 22.7593 | 24.5676 | 26.2313 | 27.6444 | 31.1247 | 33.1979
West Midlands | Kitwell 132kV | Bournville 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | 1.0862 | 1.5557 | 2.0439 | 2.6296 | 3.1574 | 3.7739 | 4.4996 | 5.5297 | 6.4357 | 7.3678 | 8.3009 | 9.195 | 10.0738 | 10.8776 | 11.614 | 12.2503 | 13.5219 | 14.151 | 2.3455 | 3.3683 | 4.3932 | 5.6336 | 6.7352 | 8.0199 | 9.5232 | 11.6351 | 13.513 | 15.4226 | 17.3232 | 19.1406 | 20.9283 | 22.563 | 24.0616 | 25.3579 | 28.0241 | 29.4372
West Midlands | Kitwell 132kV | Chad Valley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 0.62571 | 0.91547 | 1.3217 | 1.751 | 2.1733 | 2.6484 | 3.1789 | 3.9867 | 4.6451 | 5.3975 | 6.1996 | 7.0528 | 7.9672 | 8.8652 | 9.7354 | 10.5673 | 14.1124 | 15.1519 | 1.3566 | 1.962 | 2.799 | 3.6925 | 4.565 | 5.5447 | 6.6349 | 8.281 | 9.6371 | 11.1858 | 12.8386 | 14.5932 | 16.4666 | 18.3039 | 20.0843 | 21.7825 | 28.9996 | 31.1851
West Midlands | Kitwell 132kV | Chad Valley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 0.88216 | 1.5763 | 2.4424 | 3.4278 | 4.4212 | 5.5752 | 6.9392 | 8.6714 | 10.2737 | 11.6222 | 12.9894 | 14.2319 | 14.9623 | 15.4361 | 15.7697 | 16.1087 | 17.7219 | 19.3847 | 1.9145 | 3.3692 | 5.163 | 7.2302 | 9.2913 | 11.6783 | 14.4885 | 18.0512 | 21.3745 | 24.173 | 27.0166 | 29.5882 | 31.1011 | 32.0966 | 32.81 | 33.5349 | 36.9968 | 40.5533
West Midlands | Kitwell 132kV | Chad Valley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 0.80432 | 1.2695 | 1.8479 | 2.5209 | 3.1398 | 4.0245 | 5.0723 | 6.4189 | 7.6794 | 8.9936 | 10.2312 | 11.4426 | 12.6379 | 13.7643 | 14.8029 | 15.7377 | 18.4467 | 20.077 | 1.7809 | 2.7945 | 4.0226 | 5.4845 | 6.801 | 8.6836 | 10.9017 | 13.714 | 16.3777 | 19.1372 | 21.6868 | 24.1773 | 26.6352 | 28.9523 | 31.0918 | 33.0213 | 38.7337 | 42.2893
West Midlands | Kitwell 132kV | Chad Valley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 0.72253 | 1.1174 | 1.6983 | 2.3025 | 2.8944 | 3.6733 | 4.5883 | 5.9023 | 7.0868 | 8.3265 | 9.6618 | 10.7844 | 11.83 | 12.8108 | 13.7125 | 14.552 | 16.6819 | 17.8606 | 1.5658 | 2.4017 | 3.6088 | 4.8934 | 6.1362 | 7.7676 | 9.6739 | 12.3949 | 14.8717 | 17.4435 | 20.203 | 22.4976 | 24.6267 | 26.6239 | 28.4614 | 30.1745 | 34.5983 | 37.1213
West Midlands | Kitwell 132kV | Halesowen 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 2.3328 | 2.9054 | 3.1667 | 3.4435 | 3.7712 | 4.1866 | 4.6736 | 5.3787 | 5.958 | 6.5079 | 7.0483 | 7.6309 | 8.2856 | 8.9275 | 9.5545 | 10.1928 | 13.1643 | 14.1988 | 5.6554 | 6.8218 | 7.3633 | 7.9372 | 8.6159 | 9.4772 | 10.488 | 11.9394 | 13.1394 | 14.2767 | 15.3888 | 16.5825 | 17.9191 | 19.2282 | 20.5059 | 21.8072 | 27.8898 | 30.0817
West Midlands | Kitwell 132kV | Halesowen 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 2.882 | 3.4557 | 4.1275 | 4.8257 | 5.7061 | 6.6409 | 7.6986 | 8.9736 | 10.0828 | 11.0225 | 11.8659 | 12.7098 | 13.281 | 13.639 | 13.8841 | 14.1335 | 15.3294 | 16.4012 | 6.7885 | 7.996 | 9.3991 | 10.8508 | 12.6866 | 14.6308 | 16.8208 | 19.4441 | 21.7272 | 23.6732 | 25.4259 | 27.176 | 28.3802 | 29.1482 | 29.6886 | 30.2401 | 32.9245 | 35.3293
West Midlands | Kitwell 132kV | Halesowen 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 2.8204 | 3.2301 | 3.6362 | 4.1462 | 4.7805 | 5.4096 | 6.1195 | 7.0702 | 7.8808 | 8.734 | 9.6564 | 10.6039 | 11.5348 | 12.4009 | 13.2142 | 13.9521 | 16.0612 | 17.1954 | 6.6823 | 7.5787 | 8.4454 | 9.538 | 10.8965 | 12.2361 | 13.7397 | 15.7219 | 17.4178 | 19.1954 | 21.1102 | 23.0762 | 25.0098 | 26.8049 | 28.4934 | 30.0332 | 34.5775 | 37.1289
West Midlands | Kitwell 132kV | Halesowen 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 2.7584 | 3.1025 | 3.5139 | 3.9577 | 4.542 | 5.1014 | 5.7674 | 6.6855 | 7.456 | 8.2974 | 9.1592 | 10.0212 | 10.8667 | 11.6344 | 12.3587 | 13.0085 | 15.5286 | 16.4499 | 6.5188 | 7.2492 | 8.11 | 9.0401 | 10.2715 | 11.4407 | 12.8309 | 14.7236 | 16.3133 | 18.0484 | 19.8144 | 21.5826 | 23.3165 | 24.8891 | 26.3741 | 27.713 | 33.3704 | 35.4144
West Midlands | Kitwell 132kV | Hall Green 132/11kV | Bulk Supply Point | 11 | Counterfactual | 0.74364 | 1.0005 | 1.2994 | 1.6289 | 1.9876 | 2.3821 | 2.8414 | 3.559 | 4.1088 | 4.6887 | 5.2858 | 5.9197 | 6.6315 | 7.3439 | 8.0465 | 8.7422 | 11.7996 | 12.6596 | 1.6224 | 2.1588 | 2.7767 | 3.457 | 4.1959 | 5.0069 | 5.954 | 7.4124 | 8.5354 | 9.7181 | 10.9347 | 12.2236 | 13.6673 | 15.1115 | 16.5373 | 17.9494 | 24.1463 | 25.966
West Midlands | Kitwell 132kV | Hall Green 132/11kV | Bulk Supply Point | 11 | Electric Engagement | 0.99671 | 1.6302 | 2.3528 | 3.1649 | 4.0754 | 5.0526 | 6.2261 | 7.6674 | 8.934 | 9.9432 | 10.8334 | 11.7233 | 12.2567 | 12.5232 | 12.6468 | 12.7639 | 13.3074 | 14.1078 | 2.1731 | 3.4964 | 4.9916 | 6.669 | 8.5446 | 10.5522 | 12.9527 | 15.8874 | 18.4709 | 20.5343 | 22.3611 | 24.196 | 25.3152 | 25.8862 | 26.1692 | 26.4404 | 27.7208 | 29.5404
West Midlands | Kitwell 132kV | Hall Green 132/11kV | Bulk Supply Point | 11 | Holistic Transition | 0.9204 | 1.3237 | 1.7811 | 2.2846 | 2.83 | 3.4481 | 4.1687 | 5.1843 | 6.0461 | 6.9691 | 7.9869 | 8.9728 | 9.9421 | 10.839 | 11.6671 | 12.3722 | 14.0415 | 14.9604 | 2.0427 | 2.9222 | 3.8993 | 4.9731 | 6.1305 | 7.4333 | 8.9399 | 11.0335 | 12.8172 | 14.7242 | 16.8355 | 18.8664 | 20.8633 | 22.712 | 24.4222 | 25.8809 | 29.4658 | 31.5814
West Midlands | Kitwell 132kV | Hall Green 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | 0.8356 | 1.1684 | 1.5732 | 2.0191 | 2.5161 | 3.0809 | 3.7555 | 4.7381 | 5.5598 | 6.4346 | 7.3634 | 8.2799 | 9.1992 | 10.0263 | 10.7771 | 11.4334 | 12.751 | 13.4081 | 1.8212 | 2.5228 | 3.3655 | 4.2945 | 5.3268 | 6.4959 | 7.8847 | 9.8882 | 11.5681 | 13.3488 | 15.236 | 17.102 | 18.9838 | 20.6679 | 22.1942 | 23.5308 | 26.2882 | 27.7564
West Midlands | Kitwell 132kV | Highters Heath 132/11kV | Bulk Supply Point | 11 | Counterfactual | 0.7102 | 0.91648 | 1.158 | 1.4274 | 1.7214 | 2.0559 | 2.4342 | 3.0376 | 3.5059 | 3.9939 | 4.4984 | 5.0305 | 5.6263 | 6.2383 | 6.9006 | 7.4882 | 10.0917 | 10.8696 | 1.5539 | 1.983 | 2.4823 | 3.0407 | 3.6471 | 4.3358 | 5.114 | 6.344 | 7.3039 | 8.3037 | 9.3348 | 10.4188 | 11.6292 | 12.8783 | 14.2556 | 15.4485 | 20.7436 | 22.3962
West Midlands | Kitwell 132kV | Highters Heath 132/11kV | Bulk Supply Point | 11 | Electric Engagement | 0.91823 | 1.4291 | 2.0222 | 2.7063 | 3.4593 | 4.2728 | 5.2448 | 6.4436 | 7.4969 | 8.3411 | 9.0974 | 9.9575 | 10.4076 | 10.6521 | 10.7859 | 10.9265 | 11.5551 | 12.3147 | 2.0063 | 3.0698 | 4.2986 | 5.7208 | 7.2736 | 8.9482 | 10.9407 | 13.3859 | 15.539 | 17.2698 | 18.828 | 20.6555 | 21.5971 | 22.1225 | 22.4268 | 22.746 | 24.1989 | 25.9261
West Midlands | Kitwell 132kV | Highters Heath 132/11kV | Bulk Supply Point | 11 | Holistic Transition | 0.85512 | 1.1725 | 1.5442 | 1.9663 | 2.4121 | 2.9258 | 3.527 | 4.3744 | 5.0949 | 6.0228 | 6.8452 | 7.6655 | 8.4685 | 9.2156 | 9.9198 | 10.5312 | 12.08 | 12.8777 | 1.8985 | 2.5874 | 3.3792 | 4.2859 | 5.2311 | 6.3153 | 7.5757 | 9.3266 | 10.8225 | 12.8095 | 14.5067 | 16.201 | 17.8604 | 19.4029 | 20.8616 | 22.1314 | 25.4659 | 27.2943
West Midlands | Kitwell 132kV | Highters Heath 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | 0.78555 | 1.0521 | 1.3825 | 1.7637 | 2.1685 | 2.6478 | 3.216 | 4.034 | 4.7262 | 5.4672 | 6.2492 | 7.1477 | 7.9 | 8.5953 | 9.2396 | 9.8176 | 11.079 | 11.6936 | 1.7167 | 2.2763 | 2.9633 | 3.7646 | 4.6058 | 5.6 | 6.7725 | 8.444 | 9.8628 | 11.3757 | 12.9683 | 14.8571 | 16.3893 | 17.8046 | 19.1192 | 20.301 | 22.9616 | 24.3446
West Midlands | Kitwell 132kV | Longbridge 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.0744 | 1.3931 | 1.7822 | 2.2505 | 2.6901 | 3.1607 | 3.6997 | 4.5581 | 5.2278 | 5.9376 | 6.6494 | 7.4141 | 8.2653 | 9.1158 | 9.9561 | 10.7886 | 14.4032 | 15.5102 | 2.3459 | 3.0119 | 3.8192 | 4.8038 | 5.7153 | 6.6892 | 7.8038 | 9.5616 | 10.9422 | 12.4068 | 13.868 | 15.4295 | 17.161 | 18.8897 | 20.5983 | 22.2899 | 29.6537 | 32.0187
West Midlands | Kitwell 132kV | Longbridge 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.3617 | 2.1156 | 3.0122 | 4.1455 | 5.2477 | 6.4032 | 7.8076 | 9.5543 | 11.0877 | 12.3264 | 13.4208 | 14.459 | 15.0902 | 15.4265 | 15.6035 | 15.7639 | 16.5401 | 17.5637 | 2.9719 | 4.55 | 6.4204 | 8.8292 | 11.1196 | 13.5106 | 16.405 | 19.9844 | 23.1316 | 25.6854 | 27.9529 | 30.1007 | 31.4307 | 32.1584 | 32.5665 | 32.941 | 34.7783 | 37.151
West Midlands | Kitwell 132kV | Longbridge 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.2761 | 1.7662 | 2.3365 | 3.1122 | 3.7792 | 4.5243 | 5.4199 | 6.6488 | 7.6924 | 8.8048 | 9.9756 | 11.125 | 12.2509 | 13.2757 | 14.2167 | 15.021 | 17.0209 | 18.0618 | 2.8262 | 3.8955 | 5.1155 | 6.8222 | 8.2456 | 9.8277 | 11.7202 | 14.2766 | 16.4578 | 18.7695 | 21.1957 | 23.5818 | 25.9192 | 28.0403 | 29.9931 | 31.6659 | 35.9971 | 38.4062
West Midlands | Kitwell 132kV | Longbridge 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.1772 | 1.5886 | 2.1019 | 2.8011 | 3.4201 | 4.1043 | 4.9366 | 6.1358 | 7.1599 | 8.2604 | 9.3957 | 10.486 | 11.5547 | 12.5304 | 13.4332 | 14.2176 | 15.8976 | 16.7424 | 2.5693 | 3.4393 | 4.5155 | 6.0309 | 7.3334 | 8.7638 | 10.4948 | 12.9601 | 15.0693 | 17.3304 | 19.6501 | 21.874 | 24.0542 | 26.0416 | 27.8828 | 29.4859 | 33.0432 | 34.9757
West Midlands | Kitwell 132kV | Rednal 132/11kV | Bulk Supply Point | 11 | Counterfactual | 0.83581 | 0.9626 | 1.1123 | 1.2835 | 1.4652 | 1.6662 | 1.8976 | 2.2703 | 2.5967 | 2.9168 | 3.2617 | 3.3996 | 3.8008 | 4.2066 | 4.6669 | 5.1068 | 6.8643 | 7.4287 | 1.9348 | 2.2001 | 2.5111 | 2.8684 | 3.2487 | 3.6676 | 4.1483 | 4.9148 | 5.6052 | 6.2704 | 6.9845 | 7.1714 | 7.9942 | 8.8263 | 9.7762 | 10.6819 | 14.298 | 15.5078
West Midlands | Kitwell 132kV | Rednal 132/11kV | Bulk Supply Point | 11 | Electric Engagement | 0.95372 | 1.2553 | 1.6226 | 2.0547 | 2.5372 | 3.0463 | 3.6729 | 4.4512 | 5.2057 | 5.7674 | 6.3117 | 6.6077 | 6.9448 | 7.161 | 7.3266 | 7.4817 | 8.0257 | 8.566 | 2.1908 | 2.8233 | 3.5911 | 4.5009 | 5.5184 | 6.5775 | 7.8776 | 9.486 | 11.0817 | 12.2514 | 13.3954 | 13.9283 | 14.6489 | 15.12 | 15.4924 | 15.8427 | 17.1014 | 18.3547
West Midlands | Kitwell 132kV | Rednal 132/11kV | Bulk Supply Point | 11 | Holistic Transition | 0.91652 | 1.1189 | 1.3447 | 1.6373 | 1.9291 | 2.2982 | 2.7599 | 3.3515 | 3.9402 | 4.4799 | 5.0131 | 5.3059 | 5.8167 | 6.283 | 6.7388 | 7.1285 | 8.175 | 8.6958 | 2.1263 | 2.57 | 3.0529 | 3.6941 | 4.3218 | 5.1109 | 6.0967 | 7.3393 | 8.6137 | 9.7481 | 10.8633 | 11.3867 | 12.4564 | 13.4294 | 14.3841 | 15.2031 | 17.484 | 18.6784
West Midlands | Kitwell 132kV | Rednal 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | 0.88167 | 1.0483 | 1.2582 | 1.5077 | 1.8007 | 2.1313 | 2.5369 | 3.1129 | 3.6719 | 4.1886 | 4.7408 | 5.0279 | 5.5185 | 5.9757 | 6.4169 | 6.8082 | 7.6922 | 8.1611 | 2.0335 | 2.3866 | 2.8256 | 3.3565 | 3.9857 | 4.6824 | 5.5331 | 6.729 | 7.9253 | 8.9989 | 10.1424 | 10.6377 | 11.6485 | 12.5891 | 13.5009 | 14.3125 | 16.2092 | 17.2809
West Midlands | Kitwell 132kV | Selly Oak 132/11kV | Bulk Supply Point | 11 | Counterfactual | 3.6714 | 3.9983 | 4.2441 | 4.4826 | 4.6817 | 4.8549 | 5.0503 | 5.3659 | 5.6417 | 5.9992 | 6.3003 | 6.6198 | 6.9683 | 7.3121 | 7.6456 | 7.9718 | 9.3603 | 9.7498 | 8.9322 | 9.6933 | 10.1973 | 10.7096 | 11.1221 | 11.4787 | 11.8794 | 12.5209 | 13.1002 | 13.8708 | 14.4886 | 15.1427 | 15.8535 | 16.5538 | 17.2327 | 17.8958 | 20.713 | 21.5374
West Midlands | Kitwell 132kV | Selly Oak 132/11kV | Bulk Supply Point | 11 | Electric Engagement | 3.7851 | 4.2874 | 4.7332 | 5.31 | 5.7712 | 6.2229 | 6.765 | 7.4443 | 8.256 | 8.8107 | 9.273 | 9.6974 | 9.9256 | 10.0432 | 10.0957 | 7.1197 | 7.3254 | 7.6734 | 9.1797 | 10.3093 | 11.2309 | 12.4964 | 13.4564 | 14.3869 | 15.4992 | 16.8881 | 18.6475 | 19.8161 | 20.7751 | 21.6511 | 22.1264 | 22.3786 | 22.4999 | 15.052 | 15.5475 | 16.3424
West Midlands | Kitwell 132kV | Selly Oak 132/11kV | Bulk Supply Point | 11 | Holistic Transition | 3.751 | 3.9604 | 4.2868 | 4.7316 | 5.0226 | 5.3366 | 5.7098 | 6.2076 | 6.9126 | 7.3792 | 7.8228 | 8.2659 | 5.6771 | 6.0789 | 6.4446 | 6.7529 | 7.4608 | 10.8779 | 9.1212 | 9.5779 | 10.2658 | 11.276 | 11.8974 | 12.5632 | 13.3495 | 14.382 | 15.9652 | 16.9354 | 17.8498 | 18.7629 | 12.1004 | 12.9288 | 13.6839 | 14.3213 | 15.8434 | 24.3137
West Midlands | Kitwell 132kV | Selly Oak 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | 3.7137 | 4.0822 | 4.3854 | 4.801 | 5.0765 | 5.3525 | 5.6802 | 6.1599 | 6.7589 | 7.2784 | 9.2644 | 9.6794 | 10.0761 | 10.4417 | 10.7741 | 11.0616 | 11.7173 | 11.997 | 9.0237 | 9.877 | 10.506 | 11.442 | 12.0232 | 12.5982 | 13.2769 | 14.2621 | 15.5811 | 16.6845 | 21.4382 | 22.2826 | 23.0892 | 23.8321 | 24.5079 | 25.093 | 26.504 | 27.1333
West Midlands | Kitwell 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.2545 | 1.479 | 1.7282 | 2.003 | 2.311 | 2.6642 | 3.073 | 3.7007 | 4.2021 | 4.7378 | 5.325 | 5.9391 | 6.6393 | 7.3315 | 8.0981 | 8.8318 | 11.6577 | 12.655 | 2.7202 | 3.1927 | 3.7104 | 4.2813 | 4.9209 | 5.6549 | 6.5063 | 7.8013 | 8.8434 | 9.9608 | 11.1805 | 12.4496 | 13.8918 | 15.3154 | 16.9039 | 18.4223 | 24.2475 | 26.384
West Midlands | Kitwell 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.4477 | 1.9795 | 2.5825 | 3.3284 | 4.094 | 4.9763 | 6.0091 | 7.308 | 8.4444 | 9.3934 | 10.3535 | 11.3278 | 12.0215 | 12.4183 | 12.7347 | 12.9726 | 14.1211 | 15.1686 | 3.1405 | 4.266 | 5.5284 | 7.1108 | 8.7036 | 10.5456 | 12.6909 | 15.382 | 17.7414 | 19.7234 | 21.7486 | 23.8137 | 25.311 | 26.1721 | 26.8744 | 27.4063 | 30.0101 | 32.4078
West Midlands | Kitwell 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.3894 | 1.7504 | 2.1302 | 2.5675 | 3.1649 | 3.84 | 4.6057 | 5.5864 | 6.4506 | 7.3717 | 8.3668 | 9.2757 | 10.1315 | 10.9137 | 11.6624 | 12.3137 | 14.2407 | 15.179 | 3.0401 | 3.8369 | 4.6463 | 5.5823 | 6.8619 | 8.3075 | 9.9439 | 12.0061 | 13.8379 | 15.7833 | 17.8905 | 19.8016 | 21.5972 | 23.2287 | 24.7952 | 26.1605 | 30.3425 | 32.4653
West Midlands | Kitwell 132kV | Shirley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.331 | 1.6401 | 1.9948 | 2.3825 | 2.8623 | 3.4563 | 4.1306 | 5.0905 | 5.8981 | 6.7728 | 7.7388 | 8.6673 | 9.5594 | 10.3237 | 11.0441 | 11.6494 | 13.2502 | 14.1543 | 2.8859 | 3.5507 | 4.2925 | 5.1052 | 6.115 | 7.3693 | 8.7847 | 10.7806 | 12.4651 | 14.2885 | 16.2983 | 18.2304 | 20.09 | 21.668 | 23.1567 | 24.4069 | 27.8426 | 29.889
West Midlands | Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.176 | 0.23671 | 0.307 | 0.39131 | 0.47968 | 0.57528 | 0.67026 | 0.8236 | 0.96028 | 1.2136 | 1.3735 | 1.528 | 1.6911 | 1.8514 | 2.0044 | 2.155 | 2.5917 | 2.8008 | 0.38854 | 0.51604 | 0.66232 | 0.83722 | 1.0201 | 1.2179 | 1.4136 | 1.7309 | 2.0205 | 2.597 | 2.9374 | 3.262 | 3.5984 | 3.9285 | 4.2423 | 4.551 | 5.4662 | 5.9161
West Midlands | Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.22235 | 0.37329 | 0.56767 | 0.78611 | 1.0136 | 1.3755 | 1.6642 | 1.9661 | 2.2539 | 2.5003 | 2.6534 | 2.7487 | 2.8217 | 2.8852 | 2.9547 | 3.0204 | 3.339 | 3.5784 | 0.48841 | 0.80985 | 1.2194 | 1.6785 | 2.156 | 2.961 | 3.5879 | 4.224 | 4.8362 | 5.3625 | 5.7001 | 5.9144 | 6.0778 | 6.2183 | 6.3703 | 6.5155 | 7.2275 | 7.7777
West Midlands | Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.20524 | 0.32667 | 0.48107 | 0.64893 | 0.91302 | 1.1891 | 1.3743 | 1.6268 | 1.846 | 2.0732 | 2.2927 | 2.4924 | 2.6915 | 2.8727 | 3.006 | 3.0811 | 3.4259 | 3.6418 | 0.45787 | 0.72369 | 1.0559 | 1.4165 | 2.0172 | 2.6369 | 3.0438 | 3.5917 | 4.0666 | 4.5583 | 5.0231 | 5.4418 | 5.8594 | 6.2368 | 6.5182 | 6.6831 | 7.4484 | 7.9303
West Midlands | Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.19078 | 0.26781 | 0.36758 | 0.48601 | 0.61105 | 0.75443 | 1.0227 | 1.3167 | 1.553 | 1.8086 | 2.054 | 2.2852 | 2.5061 | 2.6889 | 2.8201 | 2.8883 | 3.1939 | 3.4146 | 0.42048 | 0.58469 | 0.79461 | 1.0437 | 1.3058 | 1.606 | 2.2133 | 2.856 | 3.3634 | 3.9111 | 4.4305 | 4.9189 | 5.3808 | 5.7577 | 6.0313 | 6.1793 | 6.8543 | 7.3488
West Midlands | Lea Marston 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Counterfactual | 3.7761 | 3.9729 | 4.2016 | 4.4549 | 4.7408 | 5.065 | 5.4285 | 6.0039 | 6.4579 | 6.9346 | 7.4249 | 7.9425 | 8.5176 | 9.0914 | 9.6487 | 10.2019 | 12.6236 | 13.3019 | 9.1549 | 9.5657 | 10.0386 | 10.5629 | 11.1537 | 11.8222 | 12.5689 | 13.7401 | 14.6741 | 15.6494 | 16.6512 | 17.7069 | 18.8761 | 20.0415 | 21.1733 | 22.2955 | 27.2062 | 28.6417
West Midlands | Lea Marston 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Electric Engagement | 3.9729 | 4.4625 | 5.0201 | 5.6604 | 6.3903 | 7.1833 | 8.132 | 9.3021 | 10.3619 | 11.2103 | 11.9547 | 12.6613 | 13.0653 | 13.2798 | 13.3813 | 13.4886 | 13.9721 | 11.6384 | 9.5828 | 10.6047 | 11.7582 | 13.0849 | 14.5972 | 16.2305 | 18.1762 | 20.5659 | 22.7462 | 24.4897 | 26.0231 | 27.4744 | 28.3139 | 28.7721 | 29.0028 | 29.2472 | 30.3692 | 24.3772
West Midlands | Lea Marston 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Holistic Transition | 3.9144 | 4.2244 | 4.5799 | 4.9909 | 5.421 | 5.9531 | 6.5748 | 7.4182 | 8.172 | 8.952 | 9.7186 | 10.4936 | 11.2505 | 11.9582 | 12.6156 | 13.1821 | 14.5465 | 12.2993 | 9.4834 | 10.1587 | 10.9177 | 11.8014 | 12.7164 | 13.8425 | 15.1482 | 16.8943 | 18.4719 | 20.0888 | 21.6657 | 23.2609 | 24.8193 | 26.2772 | 27.6347 | 28.8066 | 31.7331 | 25.9612
West Midlands | Lea Marston 132kV | Boughton Road 132/11kv | Bulk Supply Point | 11 | Hydrogen Evolution | 3.8474 | 4.1038 | 4.4172 | 4.7722 | 5.1761 | 5.6541 | 6.2161 | 7.0304 | 7.7443 | 8.4897 | 9.2531 | 9.9659 | 10.6597 | 11.2984 | 11.8858 | 12.4077 | 13.4838 | 11.0199 | 9.3089 | 9.8488 | 10.5011 | 11.2446 | 12.0912 | 13.0861 | 14.2488 | 15.9177 | 17.3962 | 18.9238 | 20.4815 | 21.9298 | 23.3393 | 24.6369 | 25.831 | 26.8945 | 29.147 | 22.8447
West Midlands | Lea Marston 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 3.9812 | 4.1438 | 8.3497 | 8.4614 | 8.5778 | 8.7042 | 8.8444 | 9.0643 | 9.3587 | 9.9016 | 10.085 | 10.2748 | 10.4881 | 10.6992 | 10.9055 | 11.1133 | 12.0172 | 12.3016 | 9.89 | 10.2225 | 20.6405 | 20.8784 | 21.1216 | 21.3841 | 21.6732 | 22.1223 | 22.7815 | 24.0567 | 24.4317 | 24.8184 | 25.2518 | 25.6802 | 26.099 | 26.5204 | 28.3591 | 28.9613
West Midlands | Lea Marston 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 4.055 | 4.4448 | 8.6612 | 8.9604 | 9.262 | 9.5626 | 9.9226 | 10.3609 | 11.5852 | 12.1484 | 12.4186 | 12.6761 | 12.8353 | 12.9236 | 12.9719 | 13.0173 | 13.2315 | 13.4757 | 10.0503 | 10.8479 | 21.2971 | 21.9424 | 22.5783 | 23.1992 | 23.9399 | 24.8367 | 27.7239 | 28.9936 | 29.551 | 30.0806 | 30.4131 | 30.6022 | 30.7108 | 30.8132 | 31.3125 | 31.8717
West Midlands | Lea Marston 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 4.0331 | 4.3574 | 8.4954 | 8.7185 | 8.8979 | 9.0989 | 9.3279 | 9.6419 | 10.9938 | 11.2738 | 11.5653 | 11.85 | 12.1303 | 12.3902 | 12.6341 | 12.8434 | 13.3688 | 13.6885 | 10.0131 | 10.6853 | 20.9805 | 21.4845 | 21.8711 | 22.2969 | 22.779 | 23.4292 | 26.6968 | 27.2763 | 27.8777 | 28.4661 | 29.0462 | 29.5843 | 30.0898 | 30.5244 | 31.6567 | 32.3962
West Midlands | Lea Marston 132kV | Castle Bromwich 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 4.008 | 4.309 | 8.4297 | 8.6221 | 8.8058 | 8.989 | 9.205 | 9.5115 | 10.5249 | 11.1379 | 11.4235 | 11.6959 | 11.9658 | 12.2092 | 12.4373 | 12.6323 | 15.0624 | 15.2753 | 9.9477 | 10.5611 | 20.8127 | 21.2377 | 21.6327 | 22.0151 | 22.4625 | 23.091 | 25.5094 | 26.9152 | 27.4986 | 28.0538 | 28.6041 | 29.1002 | 29.5655 | 29.964 | 35.8711 | 36.3502
West Midlands | Lea Marston 132kV | CHELMSLEY WOOD | Bulk Supply Point | 11 | Counterfactual | 0.39822 | 0.52148 | 0.66415 | 0.81117 | 0.98215 | 1.1686 | 1.3812 | 1.7149 | 1.997 | 2.2905 | 2.5986 | 2.9375 | 3.3318 | 3.7474 | 4.3319 | 4.8714 | 6.545 | 6.9473 | 0.8849 | 1.1477 | 1.4413 | 1.7446 | 2.0967 | 2.4808 | 2.9183 | 3.5989 | 4.1795 | 4.7836 | 5.4169 | 6.1132 | 6.9228 | 7.7769 | 9.0041 | 10.1419 | 13.5854 | 14.4382
West Midlands | Lea Marston 132kV | CHELMSLEY WOOD | Bulk Supply Point | 11 | Electric Engagement | 0.50489 | 0.82558 | 1.147 | 1.5016 | 1.9057 | 2.3696 | 2.9386 | 3.6673 | 4.338 | 4.854 | 5.391 | 6.0472 | 6.6135 | 6.9365 | 7.1747 | 7.2867 | 7.8082 | 8.3165 | 1.1175 | 1.8097 | 2.4744 | 3.208 | 4.0427 | 5.0033 | 6.1793 | 7.6828 | 9.0726 | 10.1416 | 11.2607 | 12.6641 | 13.8988 | 14.5943 | 15.1166 | 15.3623 | 16.5161 | 17.6363
West Midlands | Lea Marston 132kV | CHELMSLEY WOOD | Bulk Supply Point | 11 | Holistic Transition | 0.47389 | 0.69811 | 0.90251 | 1.1262 | 1.383 | 1.7639 | 2.2425 | 2.8035 | 3.3621 | 3.8955 | 4.5956 | 5.1607 | 5.7501 | 6.253 | 6.6727 | 7.0248 | 8.023 | 8.5529 | 1.0649 | 1.5703 | 2.0049 | 2.4818 | 3.0277 | 3.84 | 4.8595 | 6.0339 | 7.2148 | 8.343 | 9.8554 | 11.0347 | 12.2693 | 13.3174 | 14.1886 | 14.9198 | 17.0511 | 18.2304
West Midlands | Lea Marston 132kV | CHELMSLEY WOOD | Bulk Supply Point | 11 | Hydrogen Evolution | 0.43817 | 0.63628 | 0.82634 | 1.0278 | 1.2541 | 1.5682 | 1.9575 | 2.511 | 3.0129 | 3.4906 | 4.0508 | 4.6613 | 5.3503 | 5.8852 | 6.3283 | 6.6529 | 7.458 | 7.8463 | 0.97173 | 1.4114 | 1.8053 | 2.2252 | 2.6958 | 3.3552 | 4.1704 | 5.3203 | 6.3695 | 7.3576 | 8.5201 | 9.8026 | 11.2777 | 12.3977 | 13.3157 | 13.9811 | 15.6734 | 16.5273
West Midlands | Lea Marston 132kV | Copt Heath 132/11kV | Bulk Supply Point | 11 | Counterfactual | 0.73023 | 0.81464 | 1.1024 | 1.2358 | 1.3738 | 1.5328 | 1.7178 | 2.0026 | 2.2301 | 2.4825 | 2.7492 | 3.0569 | 3.3776 | 3.6846 | 3.9793 | 4.2626 | 5.4617 | 5.8937 | 1.6246 | 1.8004 | 2.3853 | 2.6637 | 2.9514 | 3.284 | 3.6724 | 4.2644 | 4.7416 | 5.274 | 5.8323 | 6.4737 | 7.1375 | 7.7711 | 8.3787 | 8.9617 | 11.4406 | 12.3818
West Midlands | Lea Marston 132kV | Copt Heath 132/11kV | Bulk Supply Point | 11 | Electric Engagement | 0.81313 | 1.194 | 1.4718 | 1.7914 | 2.1373 | 2.5299 | 2.997 | 3.6082 | 4.1366 | 4.547 | 4.952 | 5.3719 | 5.673 | 5.7954 | 5.8707 | 5.9702 | 6.4462 | 6.9161 | 1.8046 | 2.5838 | 3.169 | 3.8406 | 4.5644 | 5.3887 | 6.365 | 7.6413 | 8.7467 | 9.6018 | 10.4593 | 11.3523 | 12.0056 | 12.2749 | 12.4488 | 12.6767 | 13.7853 | 14.8885
West Midlands | Lea Marston 132kV | Copt Heath 132/11kV | Bulk Supply Point | 11 | Holistic Transition | 0.78795 | 1.0921 | 1.2596 | 1.4662 | 1.7269 | 2.0277 | 2.4008 | 2.8489 | 3.2315 | 3.6192 | 4.0277 | 4.4246 | 4.7757 | 5.0851 | 5.3913 | 5.6734 | 6.4927 | 6.8703 | 1.7615 | 2.3923 | 2.7496 | 3.1935 | 3.7535 | 4.4013 | 5.2059 | 6.1494 | 6.9625 | 7.7832 | 8.6472 | 9.4879 | 10.2274 | 10.8726 | 11.5146 | 12.1095 | 13.9097 | 14.7777
West Midlands | Lea Marston 132kV | Copt Heath 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | 0.76081 | 1.0441 | 1.2007 | 1.3839 | 1.5942 | 1.857 | 2.1658 | 2.625 | 2.9971 | 3.3841 | 3.7902 | 4.2198 | 4.5442 | 4.8321 | 5.1059 | 5.3657 | 6.0595 | 6.4722 | 1.6905 | 2.2685 | 2.5973 | 2.9841 | 3.4294 | 3.9887 | 4.6426 | 5.6074 | 6.3905 | 7.2039 | 8.0517 | 8.9512 | 9.6195 | 10.2093 | 10.7722 | 11.3113 | 12.8224 | 13.7796
West Midlands | Lea Marston 132kV | Elmdon 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 5.082 | 6.1375 | 6.1901 | 6.2657 | 6.3548 | 6.45 | 6.5836 | 6.7533 | 6.8725 | 7.0193 | 7.188 | 7.358 | 7.5358 | 4.9863 | 5.6212 | 6.7213 | 8.176 | 8.5144 | 12.4984 | 15.1173 | 15.2273 | 15.3851 | 15.571 | 15.7707 | 16.0592 | 16.4139 | 16.6651 | 16.9763 | 17.3313 | 17.6867 | 18.0558 | 11.6069 | 13.1224 | 15.7871 | 19.0598 | 19.7805
West Midlands | Lea Marston 132kV | Elmdon 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 5.0373 | 5.1398 | 6.2781 | 6.4408 | 6.6245 | 4.1458 | 4.4222 | 4.7442 | 5.0081 | 5.2364 | 5.486 | 6.613 | 8.0196 | 8.4546 | 8.7875 | 8.7881 | 9.1769 | 9.4071 | 12.4146 | 12.6303 | 15.4262 | 15.7702 | 16.1578 | 9.8693 | 10.4547 | 11.1299 | 11.6827 | 12.1635 | 12.6955 | 15.4271 | 18.8903 | 19.9412 | 20.7446 | 20.719 | 21.5906 | 22.1199
West Midlands | Lea Marston 132kV | Elmdon 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 5.025 | 6.1036 | 6.1802 | 6.291 | 6.5213 | 3.9775 | 4.1736 | 4.4101 | 4.6002 | 5.053 | 6.5225 | 7.4306 | 7.4431 | 7.9598 | 8.4788 | 8.651 | 9.1689 | 10.0635 | 12.393 | 15.0681 | 15.2317 | 15.4709 | 15.9692 | 9.5488 | 9.9703 | 10.4708 | 10.8674 | 11.9126 | 15.5006 | 17.6911 | 17.6459 | 18.863 | 20.0864 | 20.4521 | 21.5769 | 23.758
West Midlands | Lea Marston 132kV | Elmdon 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 5.016 | 5.0729 | 6.157 | 6.2631 | 6.4268 | 3.8849 | 4.0852 | 4.344 | 4.7931 | 5.0283 | 5.2884 | 5.9384 | 7.5182 | 8.3949 | 8.9096 | 9.4108 | 10.4607 | 10.7188 | 12.3682 | 12.4885 | 15.1682 | 15.3922 | 15.7422 | 9.3223 | 9.7495 | 10.2952 | 11.336 | 11.8335 | 12.3825 | 13.9165 | 17.7802 | 19.8933 | 21.1034 | 22.2885 | 24.7505 | 25.342
West Midlands | Lea Marston 132kV | Hams Hall South 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.6391 | 1.7616 | 1.9246 | 2.3443 | 2.6701 | 3.0483 | 3.3927 | 3.8101 | 4.1507 | 4.4961 | 4.7696 | 5.0197 | 5.2637 | 5.4938 | 5.6899 | 5.887 | 6.8102 | 7.2151 | 4.0248 | 4.287 | 4.6354 | 5.6135 | 6.35 | 7.1815 | 7.9209 | 8.8139 | 9.5469 | 10.2862 | 10.8658 | 11.3875 | 11.8908 | 12.364 | 12.7688 | 13.1755 | 15.1075 | 16.0003
West Midlands | Lea Marston 132kV | Hams Hall South 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.6968 | 1.891 | 2.1874 | 3.4758 | 4.4167 | 4.9476 | 5.5063 | 6.0702 | 6.608 | 7.0346 | 7.3352 | 7.599 | 7.7905 | 7.9049 | 8.0261 | 8.101 | 8.5224 | 8.9091 | 4.1499 | 4.5736 | 5.2292 | 8.3281 | 10.5454 | 11.7231 | 12.9436 | 14.164 | 15.3352 | 16.2527 | 16.8916 | 17.4463 | 17.8595 | 18.1052 | 18.3842 | 18.5496 | 19.5145 | 20.4175
West Midlands | Lea Marston 132kV | Hams Hall South 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.6797 | 1.8252 | 2.0866 | 3.5201 | 3.9558 | 4.3422 | 4.634 | 5.0268 | 5.3214 | 5.6409 | 5.9186 | 6.1836 | 6.5118 | 6.7619 | 6.9976 | 6.9142 | 7.571 | 8.6911 | 4.1205 | 4.4523 | 5.0364 | 8.5344 | 9.5686 | 10.4439 | 11.0948 | 11.953 | 12.5856 | 13.278 | 13.8566 | 14.406 | 15.118 | 15.6411 | 16.1353 | 15.8428 | 17.2856 | 20.0135
West Midlands | Lea Marston 132kV | Hams Hall South 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.6615 | 1.785 | 1.9738 | 3.1334 | 3.8923 | 4.3409 | 4.7353 | 5.1557 | 5.5613 | 5.9259 | 6.4896 | 6.775 | 7.044 | 7.2814 | 7.5435 | 7.7449 | 8.3943 | 8.8506 | 4.0728 | 4.349 | 4.7709 | 7.5853 | 9.4142 | 10.4349 | 11.3086 | 12.2255 | 13.117 | 13.8988 | 15.19 | 15.7888 | 16.3516 | 16.8442 | 17.4047 | 17.8264 | 19.2725 | 20.3414
West Midlands | Lea Marston 132kV | Kitts Green 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.0361 | 1.3745 | 1.7919 | 2.2484 | 2.7318 | 3.2704 | 3.8793 | 4.9123 | 5.6712 | 6.442 | 7.242 | 8.085 | 9.0314 | 9.9788 | 10.9081 | 11.8316 | 15.9028 | 17.0484 | 2.2805 | 2.9849 | 3.8467 | 4.7889 | 5.7839 | 6.8907 | 8.1395 | 10.2693 | 11.8255 | 13.3974 | 15.0272 | 16.741 | 18.66 | 20.5804 | 22.4639 | 24.3341 | 32.5864 | 35.0095
West Midlands | Lea Marston 132kV | Kitts Green 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.3732 | 2.207 | 3.1893 | 4.2966 | 5.5164 | 6.8123 | 8.4346 | 10.3623 | 12.0758 | 13.4176 | 14.6168 | 15.7785 | 16.4647 | 16.8308 | 17.0078 | 17.2112 | 18.1344 | 19.2946 | 3.014 | 4.7503 | 6.7827 | 9.0705 | 11.582 | 14.2431 | 17.5889 | 21.5138 | 25.0209 | 27.7629 | 30.222 | 32.6011 | 34.0254 | 34.8059 | 35.2056 | 35.6642 | 37.7767 | 40.3826
West Midlands | Lea Marston 132kV | Kitts Green 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.2717 | 1.7922 | 2.4235 | 3.1156 | 3.8304 | 4.713 | 5.6669 | 7.0197 | 8.189 | 9.3912 | 10.6937 | 11.9846 | 13.252 | 14.4388 | 15.556 | 16.5273 | 18.9481 | 20.2277 | 2.8409 | 3.9706 | 5.3164 | 6.791 | 8.3048 | 10.1891 | 12.1818 | 14.9707 | 17.4015 | 19.8776 | 22.5539 | 25.2087 | 27.8156 | 30.258 | 32.5644 | 34.5741 | 39.7538 | 42.6726
West Midlands | Lea Marston 132kV | Kitts Green 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.1576 | 1.5966 | 2.159 | 2.7803 | 3.4317 | 4.1844 | 5.0855 | 6.4614 | 7.5859 | 8.7527 | 9.9946 | 11.207 | 12.3943 | 13.4861 | 14.5003 | 15.4154 | 17.3526 | 18.2629 | 2.5436 | 3.4663 | 4.6369 | 5.9318 | 7.2821 | 8.8395 | 10.6935 | 13.529 | 15.8405 | 18.2149 | 20.7373 | 23.1977 | 25.6084 | 27.8245 | 29.8855 | 31.7511 | 35.8037 | 37.829
West Midlands | Lea Marston 132kV | Solihull 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.1783 | 1.3291 | 1.5158 | 1.7207 | 1.9688 | 2.734 | 3.0339 | 3.4991 | 3.8664 | 4.247 | 4.7023 | 5.192 | 5.7347 | 6.3329 | 6.9055 | 7.4345 | 9.4943 | 10.1033 | 2.7022 | 3.0161 | 3.4013 | 3.8241 | 4.3358 | 6.1266 | 6.7431 | 7.6915 | 8.4442 | 9.2238 | 10.1605 | 11.1679 | 12.2807 | 13.5124 | 14.6897 | 15.7746 | 19.9746 | 21.2564
West Midlands | Lea Marston 132kV | Solihull 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.3267 | 1.6946 | 2.1349 | 2.6342 | 3.2213 | 3.8795 | 4.6395 | 5.6005 | 6.4402 | 7.1407 | 7.8894 | 8.6217 | 9.0641 | 9.3978 | 9.498 | 9.6432 | 9.9985 | 10.6616 | 3.0245 | 3.7913 | 4.7023 | 5.7343 | 6.9484 | 8.3116 | 9.8754 | 11.8474 | 13.573 | 15.0179 | 16.58 | 18.1085 | 19.039 | 19.7586 | 19.9792 | 20.2982 | 21.0022 | 22.4649
West Midlands | Lea Marston 132kV | Solihull 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.2813 | 1.5157 | 1.803 | 2.1239 | 2.544 | 3.0588 | 3.6263 | 4.346 | 4.9754 | 5.6557 | 6.3612 | 7.0314 | 7.3446 | 7.9586 | 8.4886 | 8.9749 | 10.2573 | 11.292 | 2.9466 | 3.4561 | 4.0676 | 4.7507 | 5.6466 | 6.743 | 7.9425 | 9.44 | 10.7527 | 12.1709 | 13.6341 | 15.0215 | 15.5308 | 16.8038 | 17.8998 | 18.9098 | 21.6257 | 24.0278
West Midlands | Lea Marston 132kV | Solihull 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.233 | 1.4285 | 1.6847 | 1.9712 | 2.322 | 2.7655 | 3.2584 | 3.9721 | 4.7326 | 5.3801 | 6.1593 | 6.8607 | 7.4987 | 8.1233 | 8.5987 | 9.056 | 10.1506 | 10.6877 | 2.8203 | 3.2306 | 3.7623 | 4.3592 | 5.0916 | 6.0214 | 7.0463 | 8.5189 | 10.1603 | 11.4951 | 13.1113 | 14.5574 | 15.866 | 17.1544 | 18.1208 | 19.0567 | 21.352 | 22.5263
West Midlands | Lea Marston 132kV | Sutton Coldfield 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.8381 | 2.0609 | 2.3223 | 2.611 | 2.9202 | 3.275 | 3.6778 | 4.3202 | 4.8185 | 5.367 | 5.9562 | 6.5745 | 7.252 | 7.9217 | 8.5748 | 9.2163 | 11.9577 | 12.7332 | 4.1842 | 4.6495 | 5.1907 | 5.7883 | 6.4271 | 7.1592 | 7.9889 | 9.2995 | 10.3232 | 11.4509 | 12.6616 | 13.9278 | 15.3098 | 16.6742 | 18.0043 | 19.3091 | 24.8827 | 26.5349
West Midlands | Lea Marston 132kV | Sutton Coldfield 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 2.0606 | 2.613 | 3.2534 | 3.9804 | 4.7866 | 5.6937 | 6.7782 | 8.1206 | 9.3109 | 10.277 | 11.177 | 12.0054 | 12.4669 | 12.7058 | 12.8212 | 12.9203 | 13.1367 | 13.8331 | 4.6683 | 5.8219 | 7.1509 | 8.6583 | 10.3252 | 12.1994 | 14.4302 | 17.1782 | 19.6231 | 21.6132 | 23.4813 | 25.1924 | 26.1571 | 26.67 | 26.9353 | 27.1659 | 27.6521 | 29.2515
West Midlands | Lea Marston 132kV | Sutton Coldfield 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.9936 | 2.342 | 2.7425 | 3.1942 | 3.6734 | 4.297 | 5.0296 | 6.0101 | 6.8534 | 7.753 | 8.6298 | 9.4949 | 10.3467 | 11.1343 | 11.6095 | 12.2157 | 13.6383 | 14.5202 | 4.5538 | 5.3137 | 6.1689 | 7.1373 | 8.1565 | 9.481 | 11.0262 | 13.0629 | 14.8206 | 16.6893 | 18.4984 | 20.2825 | 22.041 | 23.6667 | 24.5431 | 25.7976 | 28.8572 | 30.92
West Midlands | Lea Marston 132kV | Sutton Coldfield 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.9193 | 2.2085 | 2.5648 | 2.9636 | 3.4065 | 3.9606 | 4.6171 | 5.5667 | 6.3729 | 7.229 | 8.1691 | 8.9934 | 9.7854 | 10.5107 | 11.176 | 11.749 | 12.9113 | 13.5037 | 4.3598 | 4.9696 | 5.7125 | 6.5464 | 7.472 | 8.6296 | 9.9932 | 11.9473 | 13.6126 | 15.3719 | 17.3097 | 18.9909 | 20.6044 | 22.0806 | 23.4354 | 24.6034 | 27.0505 | 28.3956
West Midlands | Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.0522 | 1.0928 | 1.1403 | 1.1944 | 1.2565 | 1.3358 | 1.423 | 1.5763 | 1.7162 | 1.8721 | 2.0211 | 2.1584 | 2.3032 | 2.4478 | 2.5888 | 2.7323 | 3.1686 | 3.4358 | 2.5923 | 2.6774 | 2.7758 | 2.8878 | 3.0162 | 3.1791 | 3.3581 | 3.6799 | 3.9797 | 4.317 | 4.6342 | 4.9215 | 5.2207 | 5.5195 | 5.8106 | 6.1065 | 7.0414 | 7.637
West Midlands | Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.0984 | 1.1941 | 1.356 | 1.5363 | 1.7326 | 1.9593 | 2.2188 | 2.5668 | 2.9115 | 3.2027 | 3.4028 | 3.5542 | 3.7167 | 3.8416 | 3.9408 | 4.0594 | 4.6456 | 5.0608 | 2.692 | 2.8931 | 3.2458 | 3.6381 | 4.0618 | 4.5462 | 5.0929 | 5.839 | 6.5875 | 7.2215 | 7.6709 | 8.022 | 8.4033 | 8.6901 | 8.9111 | 9.1823 | 10.518 | 11.5131
West Midlands | Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.0813 | 1.1509 | 1.2665 | 1.3853 | 1.5178 | 1.6688 | 1.862 | 2.1405 | 2.3765 | 2.636 | 2.8925 | 3.1347 | 3.3696 | 3.5749 | 3.7292 | 3.8291 | 4.3314 | 4.6025 | 2.6615 | 2.8142 | 3.0738 | 3.3394 | 3.6341 | 3.9594 | 4.3823 | 4.993 | 5.5079 | 6.0746 | 6.6279 | 7.1509 | 7.6569 | 8.0932 | 8.4267 | 8.6514 | 9.7884 | 10.4121
West Midlands | Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.0664 | 1.1222 | 1.1956 | 1.2741 | 1.3648 | 1.481 | 1.6145 | 1.8262 | 2.0214 | 2.2534 | 2.475 | 2.6861 | 2.8897 | 3.0668 | 3.188 | 3.2547 | 3.6071 | 3.9398 | 2.6231 | 2.7414 | 2.8953 | 3.0591 | 3.2482 | 3.489 | 3.7643 | 4.2093 | 4.6234 | 5.1223 | 5.5915 | 6.0364 | 6.4628 | 6.8303 | 7.0855 | 7.2334 | 8.0331 | 8.8034
West Midlands | Nechells 132kV | Bordesley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.9275 | 2.186 | 2.6071 | 3.1319 | 3.5943 | 4.081 | 4.5652 | 5.1012 | 5.6489 | 6.2601 | 6.5355 | 6.838 | 7.1765 | 7.5437 | 7.995 | 8.6226 | 10.1452 | 10.4858 | 4.7183 | 5.2663 | 6.1424 | 7.2379 | 8.2069 | 9.2282 | 10.2456 | 11.3714 | 12.532 | 13.8353 | 14.4102 | 15.0412 | 15.7473 | 16.5152 | 17.4597 | 18.7819 | 21.9476 | 22.6482
West Midlands | Nechells 132kV | Bordesley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.9611 | 2.343 | 2.9129 | 3.5696 | 4.2194 | 4.9623 | 5.757 | 6.6545 | 7.6102 | 8.5108 | 9.0934 | 9.7303 | 10.351 | 10.95 | 11.6086 | 12.0114 | 13.085 | 13.8093 | 4.7919 | 5.6227 | 6.84 | 8.2552 | 9.6663 | 11.2752 | 12.9907 | 14.9224 | 17.004 | 18.9494 | 20.1778 | 21.532 | 22.8575 | 24.1396 | 25.5406 | 26.3908 | 28.6005 | 30.0946
West Midlands | Nechells 132kV | Bordesley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.9518 | 2.3165 | 2.8357 | 3.4945 | 4.0564 | 4.8678 | 5.7485 | 6.6626 | 7.6833 | 8.5894 | 9.1679 | 9.7572 | 10.3484 | 10.9317 | 11.5708 | 11.8786 | 13.0511 | 13.7509 | 4.7751 | 5.5771 | 6.6959 | 8.13 | 9.3551 | 11.1233 | 13.0387 | 15.0142 | 17.2503 | 19.2178 | 20.4448 | 21.6944 | 22.9482 | 24.1862 | 25.5357 | 26.1664 | 28.5747 | 30.03
West Midlands | Nechells 132kV | Bordesley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.9461 | 2.288 | 2.8333 | 3.4847 | 4.0696 | 4.8036 | 5.5853 | 6.4817 | 7.4256 | 8.3607 | 8.9224 | 9.5075 | 10.1007 | 10.6748 | 11.3178 | 11.6748 | 12.6337 | 13.1192 | 4.7593 | 5.5036 | 6.6685 | 8.0737 | 9.3471 | 10.9421 | 12.6339 | 14.5652 | 16.6208 | 18.6401 | 19.8308 | 21.0764 | 22.3387 | 23.5627 | 24.9243 | 25.6671 | 27.6211 | 28.6229
West Midlands | Nechells 132kV | Cheapside 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 0.63328 | 0.86858 | 1.2729 | 1.687 | 1.9883 | 2.1557 | 2.3298 | 2.5848 | 2.8447 | 3.1913 | 3.7695 | 4.3741 | 4.9477 | 5.4645 | 5.9364 | 6.3391 | 7.5743 | 7.9435 | 1.3091 | 1.8072 | 2.6437 | 3.5077 | 4.1382 | 4.487 | 4.8475 | 5.3703 | 5.929 | 6.6537 | 7.876 | 9.1526 | 10.3589 | 11.4432 | 12.432 | 13.2716 | 15.8178 | 16.5919
West Midlands | Nechells 132kV | Cheapside 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 0.71172 | 1.1098 | 1.7025 | 2.3218 | 2.851 | 3.3635 | 3.9587 | 4.7997 | 5.6902 | 6.4326 | 7.4616 | 8.1636 | 8.3771 | 8.4982 | 8.5813 | 8.6329 | 8.8664 | 9.4722 | 1.481 | 2.3385 | 3.5881 | 4.9123 | 6.0448 | 7.1314 | 8.3901 | 10.1733 | 12.1123 | 13.7012 | 15.9281 | 17.4351 | 17.8869 | 18.1479 | 18.3321 | 18.4489 | 18.9985 | 20.2905
West Midlands | Nechells 132kV | Cheapside 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 0.68968 | 1.0309 | 1.5521 | 2.1143 | 2.519 | 3.1831 | 4.0043 | 4.8366 | 5.7687 | 6.693 | 7.1275 | 7.4558 | 7.7771 | 8.0774 | 8.3592 | 8.5777 | 9.1328 | 9.802 | 1.4426 | 2.1946 | 3.3062 | 4.5305 | 5.4087 | 6.853 | 8.637 | 10.4268 | 12.482 | 14.4793 | 15.3955 | 16.0786 | 16.7476 | 17.3735 | 17.962 | 18.4175 | 19.6238 | 21.0635
West Midlands | Nechells 132kV | Cheapside 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 0.66969 | 0.97612 | 1.4787 | 2.0098 | 2.418 | 2.8959 | 3.4403 | 4.2377 | 5.0669 | 5.8525 | 6.8541 | 7.2802 | 7.5805 | 7.8553 | 8.1108 | 8.3098 | 8.7433 | 9.3311 | 1.3894 | 2.0533 | 3.1169 | 4.2602 | 5.1434 | 6.1723 | 7.3405 | 9.0461 | 10.8676 | 12.5514 | 14.7077 | 15.5992 | 16.2152 | 16.7797 | 17.3052 | 17.7126 | 18.6287 | 19.8597
West Midlands | Nechells 132kV | Chester Street 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 0.34365 | 0.47806 | 0.63683 | 0.8496 | 1.0502 | 1.2582 | 1.4755 | 1.7924 | 2.1007 | 2.4243 | 2.7301 | 3.0553 | 3.4 | 3.732 | 4.0482 | 4.4546 | 6.8718 | 7.3282 | 0.80445 | 1.0906 | 1.4248 | 1.8819 | 2.309 | 2.7484 | 3.2022 | 3.8552 | 4.5171 | 5.2069 | 5.8391 | 6.5096 | 7.2172 | 7.8978 | 8.5453 | 9.3856 | 14.4341 | 15.3881
West Midlands | Nechells 132kV | Chester Street 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 0.43461 | 0.71177 | 1.029 | 1.475 | 1.943 | 2.3997 | 2.9335 | 3.605 | 4.3972 | 4.9772 | 5.4441 | 5.8509 | 6.0684 | 6.1966 | 6.2753 | 6.6333 | 8.0957 | 8.439 | 1.0011 | 1.5889 | 2.2515 | 3.2148 | 4.2225 | 5.1744 | 6.2832 | 7.6742 | 9.3997 | 10.633 | 11.6114 | 12.4569 | 12.9102 | 13.1834 | 13.3569 | 14.1469 | 17.4001 | 18.1798
West Midlands | Nechells 132kV | Chester Street 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 0.40626 | 0.60752 | 0.83274 | 1.2122 | 1.5101 | 1.8995 | 2.3481 | 2.8915 | 3.6007 | 4.137 | 4.5168 | 4.9118 | 5.298 | 5.6573 | 5.9948 | 6.5692 | 8.4352 | 8.855 | 0.95161 | 1.3961 | 1.8801 | 2.7369 | 3.3871 | 4.2212 | 5.1784 | 6.3205 | 7.9045 | 9.0453 | 9.8289 | 10.6447 | 11.443 | 12.1862 | 12.8854 | 14.1135 | 18.189 | 19.1456
West Midlands | Nechells 132kV | Chester Street 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 0.38091 | 0.54706 | 0.75126 | 1.065 | 1.3923 | 1.7315 | 2.1112 | 2.6457 | 3.279 | 3.8454 | 4.3109 | 4.6873 | 5.0421 | 5.3627 | 5.6614 | 6.2054 | 7.9214 | 8.2351 | 0.88394 | 1.2394 | 1.6692 | 2.3574 | 3.0764 | 3.796 | 4.5938 | 5.7075 | 7.101 | 8.3073 | 9.271 | 10.0398 | 10.763 | 11.4166 | 12.0261 | 13.1832 | 16.9053 | 17.5974
West Midlands | Nechells 132kV | ERDINGTON 11kV S STN | Bulk Supply Point | 11 | Counterfactual | 0.70855 | 0.88445 | 1.1273 | 1.3626 | 1.6067 | 1.879 | 2.1853 | 2.6709 | 3.0713 | 3.4726 | 3.892 | 4.3293 | 4.8172 | 5.3034 | 5.7804 | 6.2498 | 8.2973 | 8.9293 | 1.5808 | 1.9487 | 2.4483 | 2.935 | 3.4378 | 3.9974 | 4.6249 | 5.6126 | 6.4406 | 7.26 | 8.1158 | 9.006 | 9.9963 | 10.9828 | 11.9496 | 12.9006 | 17.0514 | 18.3805
West Midlands | Nechells 132kV | ERDINGTON 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | 0.87265 | 1.2953 | 1.8164 | 2.3771 | 2.9823 | 3.6495 | 4.4583 | 5.4394 | 6.3571 | 7.0644 | 7.7728 | 8.4498 | 8.8966 | 9.1872 | 9.3826 | 9.6006 | 10.6816 | 11.8329 | 1.9375 | 2.8226 | 3.8993 | 5.0629 | 6.3112 | 7.6819 | 9.3414 | 11.3435 | 13.243 | 14.6922 | 16.1444 | 17.5282 | 18.4494 | 19.0562 | 19.4714 | 19.9317 | 22.2263 | 24.6732
West Midlands | Nechells 132kV | ERDINGTON 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | 0.8229 | 1.0978 | 1.4607 | 1.8246 | 2.1969 | 2.6455 | 3.1568 | 3.8602 | 4.5173 | 5.1483 | 5.9026 | 6.6545 | 7.3941 | 8.0874 | 8.7293 | 9.3059 | 11.0225 | 12.1106 | 1.8523 | 2.4537 | 3.222 | 4.0025 | 4.7922 | 5.7408 | 6.8125 | 8.2653 | 9.65 | 10.9526 | 12.4992 | 14.0433 | 15.5626 | 16.9866 | 18.3065 | 19.4915 | 23.0883 | 25.4448
West Midlands | Nechells 132kV | ERDINGTON 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | 0.76988 | 0.99614 | 1.3503 | 1.6847 | 2.0395 | 2.4502 | 2.9452 | 3.6443 | 4.2866 | 4.921 | 5.6176 | 6.2878 | 6.9467 | 7.5555 | 8.1182 | 8.6415 | 9.9975 | 10.8092 | 1.7132 | 2.1914 | 2.9229 | 3.6227 | 4.3602 | 5.209 | 6.2305 | 7.6591 | 8.9981 | 10.2919 | 11.7086 | 13.0687 | 14.4062 | 15.6418 | 16.7841 | 17.8464 | 20.6401 | 22.3644
West Midlands | Nechells 132kV | Hockley 132/11kv | Bulk Supply Point | 11 | Counterfactual | 0.85218 | 1.0782 | 1.359 | 1.736 | 1.9681 | 2.2882 | 2.6186 | 3.0373 | 4.1351 | 4.5956 | 5.0579 | 5.5431 | 6.0248 | 6.4735 | 6.8526 | 7.3765 | 10.5818 | 11.1588 | 1.7537 | 2.2305 | 2.8141 | 3.598 | 4.0892 | 4.7644 | 5.4592 | 6.3322 | 8.9281 | 9.8977 | 10.8717 | 11.8916 | 12.8998 | 13.8375 | 14.6251 | 15.7221 | 22.4881 | 23.6799
West Midlands | Nechells 132kV | Hockley 132/11kv | Bulk Supply Point | 11 | Electric Engagement | 0.93712 | 1.3117 | 1.7802 | 2.3952 | 2.8268 | 3.4438 | 4.1273 | 4.9827 | 7.5452 | 8.3004 | 9.0422 | 9.5994 | 9.8571 | 10.0445 | 10.1613 | 10.7525 | 13.1334 | 13.467 | 1.9407 | 2.75 | 3.7459 | 5.0683 | 5.992 | 7.3063 | 8.7588 | 10.5727 | 16.6861 | 18.3023 | 19.8951 | 21.0814 | 21.6265 | 22.0277 | 22.2795 | 23.5788 | 28.8459 | 29.5996
West Midlands | Nechells 132kV | Hockley 132/11kv | Bulk Supply Point | 11 | Holistic Transition | 0.91265 | 1.24 | 1.6408 | 2.2013 | 2.5117 | 3.1782 | 3.9349 | 4.7425 | 7.2885 | 8.1293 | 8.5601 | 8.9388 | 9.307 | 9.6564 | 9.958 | 10.7077 | 13.3852 | 13.8156 | 1.8963 | 2.6206 | 3.4864 | 4.7166 | 5.3896 | 6.8356 | 8.4753 | 10.2074 | 16.3073 | 18.119 | 19.0251 | 19.8168 | 20.5878 | 21.3205 | 21.9497 | 23.5719 | 29.4404 | 30.4082
West Midlands | Nechells 132kV | Hockley 132/11kv | Bulk Supply Point | 11 | Hydrogen Evolution | 0.90479 | 1.1933 | 1.5815 | 2.1146 | 2.4517 | 3.0175 | 3.6362 | 4.4489 | 6.9535 | 7.7514 | 8.5072 | 8.948 | 9.318 | 9.6541 | 9.9365 | 10.6689 | 13.2275 | 13.5737 | 1.8698 | 2.4954 | 3.3248 | 4.4768 | 5.2052 | 6.422 | 7.7475 | 9.478 | 15.4728 | 17.1752 | 18.7836 | 19.7009 | 20.4645 | 21.1596 | 21.7393 | 23.3174 | 28.8987 | 29.6507
West Midlands | Nechells 132kV | Nechells West 132/25/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 6.2887 | 6.4877 | 6.72 | 6.9888 | 7.2731 | 7.5861 | 7.9352 | 8.4941 | 8.9344 | 9.4149 | 9.9333 | 10.4784 | 11.0834 | 11.6826 | 12.2722 | 12.8881 | 15.3802 | 16.1786 | 15.5708 | 15.9889 | 16.469 | 17.0348 | 17.6251 | 18.2714 | 18.9877 | 20.1238 | 21.0277 | 22.0104 | 23.0715 | 24.1849 | 25.417 | 26.6367 | 27.8373 | 29.0933 | 34.1628 | 35.8389
West Midlands | Nechells 132kV | Nechells West 132/25/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 6.4806 | 6.9765 | 7.5332 | 8.2418 | 8.9816 | 9.7689 | 10.7109 | 11.8824 | 12.9356 | 13.7918 | 14.5776 | 15.3185 | 15.7676 | 13.1253 | 13.2896 | 13.4195 | 13.9397 | 14.5728 | 15.9869 | 17.0287 | 18.1807 | 19.6847 | 21.2282 | 22.8507 | 24.7851 | 27.1814 | 29.351 | 31.1148 | 32.7426 | 34.2729 | 35.2115 | 28.5093 | 28.8752 | 29.1684 | 30.3837 | 31.8277
West Midlands | Nechells 132kV | Nechells West 132/25/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 6.4225 | 6.749 | 7.1079 | 7.6057 | 8.0513 | 8.6134 | 9.2642 | 10.1337 | 10.9079 | 11.7152 | 12.5099 | 13.2947 | 11.1513 | 11.8671 | 12.536 | 13.0803 | 14.1546 | 17.8407 | 15.887 | 16.6057 | 17.3728 | 18.478 | 19.4311 | 20.6221 | 21.9924 | 23.7955 | 25.4185 | 27.0972 | 28.7384 | 30.3622 | 24.6736 | 26.1565 | 27.5445 | 28.6736 | 30.8906 | 39.9426
West Midlands | Nechells 132kV | Nechells West 132/25/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 6.3607 | 6.6229 | 6.937 | 7.3725 | 7.811 | 8.3048 | 8.8905 | 9.7386 | 10.4791 | 11.2628 | 13.544 | 14.3036 | 15.0434 | 15.7188 | 16.3476 | 18.1351 | 19.2114 | 19.7784 | 15.7255 | 16.2808 | 16.9341 | 17.8773 | 18.8056 | 19.8336 | 21.045 | 22.7846 | 24.3179 | 25.9259 | 31.2573 | 32.8076 | 34.3177 | 35.6971 | 36.9823 | 41.2104 | 43.4686 | 44.7263
West Midlands | Nechells 132kV | Sparkbrook 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 0.73891 | 0.98722 | 1.3691 | 1.7212 | 2.0774 | 2.46 | 2.8855 | 3.5469 | 4.1043 | 4.6683 | 5.2343 | 5.8353 | 6.5042 | 7.1697 | 7.8202 | 8.4678 | 11.3572 | 12.4085 | 1.702 | 2.2225 | 3.0065 | 3.7366 | 4.4709 | 5.2563 | 6.1273 | 7.4703 | 8.6242 | 9.7796 | 10.9319 | 12.1523 | 13.5076 | 14.8557 | 16.1735 | 17.4846 | 23.34 | 25.5321
West Midlands | Nechells 132kV | Sparkbrook 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 0.95701 | 1.539 | 2.3016 | 3.1074 | 3.953 | 4.8695 | 5.9542 | 7.2778 | 8.561 | 9.5291 | 10.5518 | 11.5506 | 12.2477 | 12.7422 | 13.1158 | 13.4969 | 15.3862 | 17.3963 | 2.1748 | 3.3968 | 4.9707 | 6.6513 | 8.3989 | 10.2793 | 12.4979 | 15.1931 | 17.8619 | 19.8453 | 21.9341 | 23.9702 | 25.4009 | 26.4248 | 27.2053 | 28.0003 | 31.9692 | 36.2084
West Midlands | Nechells 132kV | Sparkbrook 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 0.89067 | 1.2828 | 1.8131 | 2.3601 | 2.8953 | 3.5063 | 4.198 | 5.1529 | 6.0947 | 6.9557 | 8.0635 | 9.1926 | 10.3027 | 11.3507 | 12.3296 | 13.2016 | 16.0132 | 17.8703 | 2.0601 | 2.9191 | 4.04 | 5.219 | 6.3542 | 7.6366 | 9.0787 | 11.0445 | 13.0424 | 14.8155 | 17.0818 | 19.3946 | 21.6692 | 23.8166 | 25.8245 | 27.6125 | 33.5036 | 37.4701
West Midlands | Nechells 132kV | Sparkbrook 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 0.82357 | 1.1485 | 1.6951 | 2.2119 | 2.7331 | 3.3145 | 3.9954 | 4.953 | 5.8818 | 6.7673 | 7.7488 | 8.7163 | 9.6688 | 10.546 | 11.367 | 12.1333 | 14.2512 | 15.6515 | 1.884 | 2.5717 | 3.6988 | 4.787 | 5.8722 | 7.0706 | 8.4682 | 10.4182 | 12.3633 | 14.1693 | 16.1598 | 18.1202 | 20.0526 | 21.8322 | 23.498 | 25.0527 | 29.4041 | 32.364
West Midlands | Nechells 132kV | Summer Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 0.95157 | 1.044 | 1.1505 | 1.3106 | 1.4859 | 1.7203 | 1.9663 | 2.2736 | 2.7526 | 3.0807 | 3.1656 | 3.2558 | 3.3568 | 3.4576 | 3.5552 | 3.6756 | 4.3749 | 4.6224 | 2.3135 | 2.5101 | 2.7331 | 3.0756 | 3.4341 | 3.9146 | 4.4194 | 5.0498 | 6.1263 | 6.8963 | 7.0689 | 7.2519 | 7.4564 | 7.6605 | 7.858 | 8.104 | 9.5535 | 10.0662
West Midlands | Nechells 132kV | Summer Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 0.98498 | 1.138 | 1.3163 | 1.6186 | 1.9717 | 2.3937 | 2.8499 | 3.3617 | 4.6536 | 4.9809 | 5.1 | 5.2128 | 5.2879 | 5.3407 | 5.3795 | 5.4796 | 5.0839 | 5.2262 | 2.3865 | 2.7188 | 3.0975 | 3.7708 | 4.5293 | 5.4291 | 6.3973 | 7.4767 | 10.525 | 11.2727 | 11.5188 | 11.7515 | 11.9087 | 12.0211 | 12.105 | 12.3259 | 11.2341 | 11.5582
West Midlands | Nechells 132kV | Summer Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 0.97506 | 1.1107 | 1.2612 | 1.5469 | 1.8159 | 2.1731 | 2.5498 | 2.9868 | 4.3645 | 4.5302 | 4.6613 | 4.7976 | 4.141 | 4.2636 | 4.3782 | 4.5442 | 5.0675 | 6.0418 | 2.3684 | 2.671 | 2.9962 | 3.6469 | 4.23 | 5.0028 | 5.8144 | 6.7464 | 10.0453 | 10.3942 | 10.6658 | 10.9486 | 9.2519 | 9.5069 | 9.7457 | 10.1003 | 11.2479 | 13.6398
West Midlands | Nechells 132kV | Summer Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 0.97227 | 1.0863 | 1.2308 | 1.4946 | 1.7789 | 2.1336 | 2.5085 | 2.9502 | 4.124 | 4.5027 | 5.0324 | 5.1656 | 5.2942 | 5.4113 | 5.5181 | 5.6787 | 6.1481 | 6.3049 | 2.3586 | 2.6066 | 2.9147 | 3.5076 | 4.125 | 4.8884 | 5.6908 | 6.6269 | 9.4099 | 10.2833 | 11.5444 | 11.8154 | 12.0775 | 12.3164 | 12.5345 | 12.874 | 13.8907 | 14.2311
West Midlands | Ocker Hill 132kV | Black Lake 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 9.8168 | 10.0689 | 10.353 | 10.67 | 11.0198 | 11.4564 | 11.9786 | 12.7898 | 13.4976 | 14.0734 | 14.6696 | 15.3005 | 16.0024 | 16.763 | 17.4838 | 18.1502 | 21.1573 | 22.2678 | 24.258 | 24.7867 | 25.3748 | 26.0298 | 26.7511 | 27.6528 | 28.7321 | 30.398 | 31.8643 | 33.046 | 34.2691 | 35.5601 | 36.9932 | 38.5731 | 40.0686 | 41.4254 | 47.5551 | 49.8721
West Midlands | Ocker Hill 132kV | Black Lake 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 10.0123 | 10.7044 | 11.4878 | 12.2098 | 13.0513 | 13.9682 | 15.0197 | 16.3517 | 17.5059 | 18.4657 | 19.3753 | 20.4355 | 21.0435 | 21.4632 | 21.7492 | 22.0132 | 20.6686 | 21.7186 | 24.6803 | 26.147 | 27.7836 | 29.2784 | 31.021 | 32.9166 | 35.0793 | 37.8134 | 40.1845 | 42.1627 | 44.0498 | 46.3149 | 47.587 | 48.4808 | 49.1012 | 49.6763 | 45.9794 | 48.2881
West Midlands | Ocker Hill 132kV | Black Lake 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 9.9457 | 10.4818 | 10.9501 | 11.5139 | 12.0747 | 12.7005 | 13.3948 | 14.4001 | 15.2451 | 16.3629 | 17.3409 | 18.3382 | 19.3216 | 20.2128 | 21.0641 | 21.8233 | 20.8516 | 22.0216 | 24.5636 | 25.7366 | 26.7365 | 27.941 | 29.1344 | 30.4579 | 31.9158 | 34.0051 | 35.7658 | 38.1846 | 40.2093 | 42.2729 | 44.3095 | 46.1412 | 47.9061 | 49.4858 | 46.2982 | 48.916
West Midlands | Ocker Hill 132kV | Black Lake 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 9.897 | 10.3678 | 10.8989 | 11.3795 | 11.884 | 12.4623 | 13.1398 | 14.138 | 14.9681 | 15.8505 | 16.7829 | 17.883 | 18.7879 | 19.6275 | 20.389 | 23.3566 | 22.5321 | 23.3771 | 24.4282 | 25.4366 | 26.5526 | 27.5573 | 28.6077 | 29.8104 | 31.2133 | 33.2671 | 34.9776 | 36.7879 | 38.6975 | 41.0321 | 42.8877 | 44.6115 | 46.1732 | 53.2926 | 50.5665 | 52.4107
West Midlands | Ocker Hill 132kV | Ocker Hill B 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.6599 | 1.8553 | 2.0677 | 2.3249 | 2.6333 | 2.966 | 3.3589 | 3.9341 | 4.4065 | 4.8384 | 5.2887 | 5.7689 | 6.3078 | 6.8389 | 7.3482 | 7.8699 | 10.2404 | 11.182 | 4.0472 | 4.457 | 4.8978 | 5.4296 | 6.0733 | 6.76 | 7.5713 | 8.75 | 9.7239 | 10.6091 | 11.5329 | 12.5149 | 13.614 | 14.6954 | 15.7311 | 16.7925 | 21.6262 | 23.5846
West Midlands | Ocker Hill 132kV | Ocker Hill B 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.8285 | 2.3146 | 2.8826 | 3.4463 | 4.1221 | 4.8303 | 5.6496 | 6.6347 | 7.4979 | 8.2274 | 8.8876 | 9.5336 | 9.9754 | 10.2694 | 10.4896 | 10.695 | 11.6465 | 11.2498 | 4.4163 | 5.4471 | 6.6319 | 7.8001 | 9.2033 | 10.6671 | 12.3601 | 14.3808 | 16.153 | 17.6582 | 19.0241 | 20.3524 | 21.2751 | 21.9008 | 22.3781 | 22.8261 | 24.9429 | 23.7168
West Midlands | Ocker Hill 132kV | Ocker Hill B 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.7751 | 2.1419 | 2.4921 | 2.9378 | 3.4049 | 3.9064 | 4.4509 | 5.1865 | 5.8138 | 6.4646 | 7.1881 | 7.9311 | 8.6588 | 9.348 | 10.0016 | 10.5879 | 12.2482 | 11.9328 | 4.3219 | 5.1277 | 5.8763 | 6.8295 | 7.8265 | 8.8931 | 10.0417 | 11.5688 | 12.8753 | 14.2226 | 15.7188 | 17.2552 | 18.7618 | 20.1896 | 21.5459 | 22.7676 | 26.3323 | 25.3047
West Midlands | Ocker Hill 132kV | Ocker Hill B 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.745 | 2.0604 | 2.4445 | 2.8426 | 3.2736 | 3.7199 | 4.254 | 5.0096 | 5.6407 | 6.3256 | 7.0449 | 7.7368 | 8.4259 | 9.0485 | 9.6447 | 10.1664 | 11.5236 | 10.9891 | 4.2328 | 4.9093 | 5.715 | 6.5479 | 7.4479 | 8.3732 | 9.4836 | 11.0365 | 12.3341 | 13.7389 | 15.2118 | 16.6262 | 18.0365 | 19.3126 | 20.5351 | 21.6088 | 24.472 | 22.9252
West Midlands | Oldbury 132kV | Birchfield Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.2724 | 1.4949 | 1.7769 | 2.083 | 2.421 | 2.8183 | 3.2918 | 4.0047 | 4.5854 | 5.1486 | 5.739 | 6.3626 | 7.0672 | 7.766 | 8.4668 | 9.1528 | 12.2773 | 13.2198 | 2.993 | 3.458 | 4.0402 | 4.6727 | 5.3698 | 6.1884 | 7.1641 | 8.6193 | 9.8129 | 10.9661 | 12.1742 | 13.4478 | 14.8834 | 16.3087 | 17.7442 | 19.1407 | 25.509 | 27.4926
West Midlands | Oldbury 132kV | Birchfield Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.4937 | 2.0909 | 2.827 | 3.5785 | 4.4458 | 5.387 | 6.4912 | 7.8567 | 9.0719 | 10.0652 | 10.9826 | 11.9306 | 12.5393 | 12.9337 | 13.1961 | 13.458 | 14.6801 | 15.7583 | 3.4739 | 4.7245 | 6.2508 | 7.8043 | 9.5972 | 11.5381 | 13.8037 | 16.5954 | 19.0862 | 21.127 | 23.0178 | 24.9842 | 26.2546 | 27.0946 | 27.6683 | 28.2411 | 30.9462 | 33.3183
West Midlands | Oldbury 132kV | Birchfield Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.4274 | 1.8294 | 2.2927 | 2.7984 | 3.3789 | 4.0047 | 4.7188 | 5.7232 | 6.5951 | 7.5494 | 8.5622 | 9.5892 | 10.602 | 11.5537 | 12.4458 | 13.2509 | 15.4907 | 16.6693 | 3.3606 | 4.2369 | 5.2213 | 6.3004 | 7.5359 | 8.8574 | 10.3546 | 12.4343 | 14.2486 | 16.2439 | 18.3357 | 20.4567 | 22.5499 | 24.5188 | 26.3664 | 28.0402 | 32.8313 | 35.4641
West Midlands | Oldbury 132kV | Birchfield Lane 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.3532 | 1.6912 | 2.16 | 2.5954 | 3.1125 | 3.6747 | 4.3463 | 5.3132 | 6.1362 | 7.0094 | 7.944 | 8.9018 | 9.8129 | 10.6541 | 11.4419 | 12.1506 | 13.9223 | 14.7829 | 3.1673 | 3.8825 | 4.8592 | 5.7668 | 6.8458 | 8.0133 | 9.4021 | 11.3844 | 13.0777 | 14.8646 | 16.7743 | 18.7485 | 20.6128 | 22.3357 | 23.9499 | 25.4061 | 29.1359 | 31.0134
West Midlands | Oldbury 132kV | Oldbury B 11kV | Bulk Supply Point | 11 | Counterfactual | 3.7162 | 3.7733 | 3.8418 | 3.9186 | 4.003 | 4.1037 | 4.2232 | 4.4208 | 4.5866 | 4.7273 | 4.8738 | 5.0287 | 5.2024 | 5.3747 | 5.5461 | 5.7162 | 6.4818 | 6.7672 | 9.2564 | 9.3765 | 9.5182 | 9.6768 | 9.8512 | 10.0589 | 10.3052 | 10.7102 | 11.0528 | 11.341 | 11.6409 | 11.9572 | 12.3111 | 12.662 | 13.0111 | 13.3573 | 14.919 | 15.5143
West Midlands | Oldbury 132kV | Oldbury B 11kV | Bulk Supply Point | 11 | Electric Engagement | 3.768 | 3.9162 | 4.095 | 4.2723 | 4.4963 | 4.7433 | 5.028 | 5.3496 | 5.639 | 5.8791 | 6.1059 | 6.3257 | 6.4793 | 6.5814 | 6.6593 | 6.7308 | 7.073 | 7.3855 | 9.3684 | 9.6812 | 10.0531 | 10.4204 | 10.8854 | 11.3977 | 11.9858 | 12.6432 | 13.2373 | 13.7318 | 14.2 | 14.6528 | 14.9735 | 15.1904 | 15.359 | 15.5145 | 16.2768 | 16.9753
West Midlands | Oldbury 132kV | Oldbury B 11kV | Bulk Supply Point | 11 | Holistic Transition | 3.7518 | 3.8566 | 3.9672 | 4.1014 | 4.2517 | 4.4261 | 4.615 | 4.8642 | 5.0755 | 5.2998 | 5.5448 | 5.7937 | 6.0702 | 6.3019 | 6.5216 | 6.718 | 7.3624 | 7.6699 | 9.3401 | 9.5708 | 9.8073 | 10.0945 | 10.4151 | 10.7851 | 11.1828 | 11.6993 | 12.1395 | 12.6047 | 13.1116 | 13.6264 | 14.2126 | 14.6928 | 15.1488 | 15.5582 | 16.9655 | 17.6502
West Midlands | Oldbury 132kV | Oldbury B 11kV | Bulk Supply Point | 11 | Hydrogen Evolution | 3.737 | 3.8232 | 3.9404 | 4.0645 | 4.2019 | 4.3585 | 4.5431 | 4.7835 | 4.9924 | 5.2163 | 5.4515 | 5.6824 | 5.9131 | 6.1214 | 6.3192 | 6.4951 | 8.5665 | 8.8377 | 9.3008 | 9.484 | 9.7292 | 9.9886 | 10.2754 | 10.6023 | 10.9853 | 11.4777 | 11.9074 | 12.3656 | 12.8463 | 13.3186 | 13.7907 | 14.2177 | 14.6234 | 14.9854 | 19.9828 | 20.5833
West Midlands | Oldbury 132kV | Tividale 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 0.95561 | 1.0372 | 1.1359 | 1.2454 | 1.3789 | 1.5639 | 1.7752 | 2.0926 | 2.3676 | 1.9598 | 2.1682 | 2.3907 | 2.6427 | 2.8948 | 3.1357 | 3.382 | 4.5271 | 4.9411 | 2.3278 | 2.499 | 2.7033 | 2.9297 | 3.2063 | 3.5908 | 4.0288 | 4.6821 | 5.2527 | 4.1342 | 4.5608 | 5.0155 | 5.5291 | 6.0426 | 6.5332 | 7.0346 | 9.3705 | 10.2356
West Midlands | Oldbury 132kV | Tividale 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.0292 | 1.2993 | 1.6273 | 1.8921 | 2.2208 | 2.5718 | 2.9882 | 3.4731 | 3.9027 | 3.6546 | 3.9816 | 4.3155 | 4.5411 | 4.695 | 4.8049 | 4.9085 | 5.3978 | 5.8213 | 2.4869 | 3.0592 | 3.7466 | 4.2955 | 4.9811 | 5.7071 | 6.5656 | 7.5583 | 8.4392 | 7.6524 | 8.3269 | 9.014 | 9.4845 | 9.8111 | 10.0485 | 10.274 | 11.3553 | 12.2843
West Midlands | Oldbury 132kV | Tividale 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.0053 | 1.2173 | 1.402 | 1.6326 | 1.857 | 2.1138 | 2.392 | 2.7557 | 3.07 | 2.7906 | 3.1555 | 3.5333 | 3.9103 | 4.2598 | 4.5882 | 4.8899 | 5.7369 | 6.2021 | 2.4453 | 2.909 | 3.3056 | 3.8002 | 4.2798 | 4.8233 | 5.4088 | 6.1623 | 6.8162 | 5.9705 | 6.7242 | 7.5045 | 8.2834 | 9.0068 | 9.687 | 10.3142 | 12.1275 | 13.1623
West Midlands | Oldbury 132kV | Tividale 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 0.98324 | 1.1698 | 1.3959 | 1.5659 | 1.7694 | 1.9951 | 2.262 | 2.6115 | 2.9111 | 2.6255 | 2.963 | 3.2983 | 3.6312 | 3.9332 | 4.2187 | 4.4718 | 5.1347 | 5.4784 | 2.3867 | 2.7861 | 3.2635 | 3.6189 | 4.0482 | 4.5195 | 5.0734 | 5.7899 | 6.4059 | 5.5392 | 6.2286 | 6.9145 | 7.596 | 8.2148 | 8.8001 | 9.3209 | 10.7188 | 11.4657
West Midlands | Penn 132kV | Coseley 132/11kV | Bulk Supply Point | 11 | Counterfactual | 6.8693 | 7.1176 | 7.4719 | 7.8643 | 8.2992 | 8.7152 | 9.1941 | 9.9149 | 10.4648 | 11.0678 | 11.6803 | 12.3319 | 13.0596 | 13.768 | 14.4483 | 15.151 | 18.3194 | 19.4658 | 16.9587 | 17.4777 | 18.2061 | 19.0181 | 19.9181 | 20.7757 | 21.7689 | 23.2408 | 24.3675 | 25.6045 | 26.8601 | 28.1931 | 29.6774 | 31.1199 | 32.5051 | 33.9388 | 40.3917 | 42.7932
West Midlands | Penn 132kV | Coseley 132/11kV | Bulk Supply Point | 11 | Electric Engagement | 7.0951 | 7.81 | 8.5602 | 9.326 | 10.1812 | 11.1617 | 12.3577 | 13.7961 | 15.022 | 16.0466 | 16.9506 | 17.8691 | 18.4827 | 18.8144 | 19.0422 | 19.2821 | 20.4047 | 21.4649 | 17.4469 | 18.9401 | 20.4991 | 22.0814 | 23.8445 | 25.865 | 28.3349 | 31.2856 | 33.7948 | 35.9046 | 37.7688 | 39.6747 | 40.9717 | 41.6772 | 42.1758 | 42.705 | 45.2258 | 47.5811
West Midlands | Penn 132kV | Coseley 132/11kV | Bulk Supply Point | 11 | Holistic Transition | 7.0211 | 7.5327 | 8.0531 | 8.5275 | 9.0654 | 9.7801 | 10.5731 | 11.6243 | 12.4831 | 13.4179 | 14.4679 | 15.4984 | 16.5038 | 17.4323 | 18.3169 | 19.119 | 21.3373 | 22.4866 | 17.3178 | 18.4207 | 19.5354 | 20.5443 | 21.6839 | 23.2052 | 24.8781 | 27.0595 | 28.8415 | 30.7837 | 32.9788 | 35.1058 | 37.1824 | 39.0983 | 40.9287 | 42.5967 | 47.364 | 49.9559
West Midlands | Penn 132kV | Coseley 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | 6.9575 | 7.4026 | 7.8743 | 8.3133 | 8.8128 | 9.4434 | 10.1952 | 11.237 | 12.0778 | 12.9985 | 13.9427 | 14.8979 | 15.8634 | 16.6937 | 17.4589 | 18.1483 | 22.9045 | 23.7593 | 17.1471 | 18.082 | 19.0696 | 19.9832 | 21.0219 | 22.3343 | 23.9009 | 26.0444 | 27.77 | 29.6581 | 31.5872 | 33.5472 | 35.5428 | 37.2421 | 38.8054 | 40.2199 | 51.4407 | 53.3233
West Midlands | Penn 132kV | Dudley 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 3.9412 | 4.2479 | 4.5972 | 4.9774 | 5.3949 | 5.8961 | 6.4663 | 7.3502 | 8.1111 | 8.8714 | 9.6194 | 10.4158 | 11.3055 | 9.8477 | 10.6568 | 11.4957 | 15.2173 | 16.4605 | 9.604 | 10.244 | 10.9668 | 11.7523 | 12.613 | 13.6457 | 14.8189 | 16.6259 | 18.1932 | 19.7564 | 21.2914 | 22.9216 | 24.7377 | 20.6906 | 22.3339 | 24.0396 | 31.5362 | 34.1476
West Midlands | Penn 132kV | Dudley 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 4.2155 | 4.9366 | 5.7594 | 6.7099 | 7.8375 | 6.7281 | 8.1819 | 9.9136 | 11.451 | 12.7505 | 13.911 | 15.0588 | 15.817 | 16.2946 | 16.5764 | 16.8808 | 18.1486 | 19.4855 | 10.1987 | 11.7053 | 13.4091 | 15.3755 | 17.7099 | 14.4074 | 17.411 | 20.961 | 24.1149 | 26.7974 | 29.1935 | 31.5559 | 33.1384 | 34.1547 | 34.7692 | 35.434 | 38.1887 | 41.12
West Midlands | Penn 132kV | Dudley 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 4.1303 | 4.6075 | 5.1369 | 5.7596 | 6.5694 | 5.0979 | 6.0532 | 7.3308 | 8.4432 | 9.6222 | 10.8849 | 12.1797 | 13.4558 | 14.6469 | 15.7177 | 16.6831 | 19.2503 | 20.7031 | 10.0516 | 11.0894 | 12.2178 | 13.5445 | 15.2708 | 11.275 | 13.2906 | 15.942 | 18.2562 | 20.7039 | 23.3103 | 25.9817 | 28.6167 | 31.0771 | 33.2872 | 35.2794 | 40.7038 | 43.9506
West Midlands | Penn 132kV | Dudley 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 4.045 | 4.4428 | 4.9382 | 5.5049 | 6.2494 | 4.6685 | 5.5741 | 6.809 | 7.8706 | 9.0241 | 10.2108 | 11.3781 | 12.5226 | 13.5639 | 14.4969 | 15.3646 | 17.334 | 18.4134 | 9.827 | 10.6645 | 11.6958 | 12.8777 | 14.4388 | 10.1734 | 12.0624 | 14.603 | 16.7889 | 19.1624 | 21.5923 | 23.98 | 26.3208 | 28.4512 | 30.3549 | 32.137 | 36.2079 | 38.5641
West Midlands | Penn 132kV | Hinksford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 2.13 | 2.3116 | 2.5199 | 2.7562 | 3.0309 | 3.3458 | 3.6948 | 4.2437 | 4.6912 | 5.1842 | 5.7235 | 4.8315 | 5.4332 | 6.0221 | 6.6216 | 7.1703 | 9.6817 | 10.6053 | 5.126 | 5.5072 | 5.9402 | 6.4312 | 7.0013 | 7.6555 | 8.3805 | 9.5086 | 10.4358 | 11.4596 | 12.5781 | 10.1035 | 11.338 | 12.5441 | 13.775 | 14.8955 | 20.0371 | 21.9916
West Midlands | Penn 132kV | Hinksford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 2.3009 | 2.7498 | 3.2847 | 3.8872 | 4.5797 | 5.3765 | 6.3228 | 7.5254 | 8.5325 | 9.3561 | 10.1509 | 9.4591 | 9.9597 | 10.2811 | 10.5305 | 10.7319 | 11.6943 | 12.5969 | 5.4965 | 6.4391 | 7.5564 | 8.8112 | 10.2526 | 11.9114 | 13.8746 | 16.3638 | 18.4465 | 20.1529 | 21.8129 | 19.7649 | 20.8236 | 21.5136 | 22.0628 | 22.5091 | 24.6847 | 26.7233
West Midlands | Penn 132kV | Hinksford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 2.2476 | 2.5579 | 2.8935 | 3.3 | 3.8152 | 4.4089 | 5.0762 | 5.9594 | 6.67 | 7.3996 | 8.2328 | 7.6154 | 8.4219 | 9.1633 | 9.8893 | 10.5081 | 12.248 | 13.1383 | 5.4038 | 6.0844 | 6.8025 | 7.6735 | 8.7777 | 10.0426 | 11.4607 | 13.3088 | 14.7995 | 16.3183 | 18.0548 | 16.1631 | 17.8421 | 19.3807 | 20.8926 | 22.184 | 25.943 | 27.9508
West Midlands | Penn 132kV | Hinksford 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 2.1981 | 2.4516 | 2.7892 | 3.1488 | 3.5934 | 4.1274 | 4.7386 | 5.613 | 6.3088 | 7.0387 | 7.8258 | 7.1267 | 7.8537 | 8.5104 | 9.1501 | 9.6819 | 11.0726 | 11.8348 | 5.2723 | 5.8095 | 6.5167 | 7.2703 | 8.2059 | 9.3299 | 10.6085 | 12.4231 | 13.8646 | 15.3688 | 16.9891 | 14.9071 | 16.4003 | 17.7474 | 19.0644 | 20.1594 | 23.1204 | 24.8198
West Midlands | Penn 132kV | Lye 11kV DUMMY | Bulk Supply Point | 11 | Counterfactual | 1.592 | 1.8936 | 2.2592 | 2.6372 | 3.0742 | 3.5865 | 4.1603 | 5.0419 | 5.7289 | 6.4357 | 7.1961 | 7.9985 | 8.9002 | 9.788 | 10.6699 | 11.5604 | 15.7864 | 17.1439 | 3.6672 | 4.2995 | 5.0567 | 5.8391 | 6.7431 | 7.802 | 8.9857 | 10.7869 | 12.1984 | 13.6487 | 15.2089 | 16.8478 | 18.6845 | 20.491 | 22.2867 | 24.0994 | 32.7265 | 35.5913
West Midlands | Penn 132kV | Lye 11kV DUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.8908 | 2.6499 | 3.5531 | 4.5469 | 5.6777 | 6.897 | 8.369 | 10.1667 | 11.7304 | 12.9922 | 14.1921 | 15.3739 | 16.1419 | 16.6125 | 16.9318 | 17.2421 | 18.7568 | 20.1441 | 4.3172 | 5.9088 | 7.7857 | 9.8473 | 12.1896 | 14.7056 | 17.7339 | 21.414 | 24.6189 | 27.2085 | 29.6882 | 32.1238 | 33.7313 | 34.7355 | 35.4385 | 36.1232 | 39.5192 | 42.6135
West Midlands | Penn 132kV | Lye 11kV DUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.8017 | 2.3024 | 2.8759 | 3.5283 | 4.265 | 5.1008 | 6.052 | 7.3721 | 8.4738 | 9.6073 | 10.9169 | 12.2514 | 13.5664 | 14.7875 | 15.918 | 16.9566 | 19.8475 | 21.3974 | 4.1638 | 5.2601 | 6.4879 | 7.8815 | 9.4505 | 11.2197 | 13.2203 | 15.9576 | 18.2473 | 20.5902 | 23.2994 | 26.0556 | 28.7743 | 31.2972 | 33.6265 | 35.7868 | 42.005 | 45.5146
West Midlands | Penn 132kV | Lye 11kV DUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.709 | 2.1209 | 2.6591 | 3.2361 | 3.9114 | 4.666 | 5.5574 | 6.8201 | 7.8687 | 8.9676 | 10.1843 | 11.378 | 12.5477 | 13.6115 | 14.6208 | 15.5697 | 17.8674 | 19.0029 | 3.9205 | 4.7921 | 5.9158 | 7.1222 | 8.5361 | 10.1083 | 11.9564 | 14.5473 | 16.7025 | 18.9471 | 21.4358 | 23.8751 | 26.2663 | 28.4404 | 30.5071 | 32.4764 | 37.3429 | 39.8537
West Midlands | Penn 132kV | PATTINGHAM 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.061304 | 0.074342 | 0.08518 | 0.10411 | 0.1264 | 0.15344 | 0.18449 | 0.23197 | 0.27026 | 0.31193 | 0.35118 | 0.39014 | 0.4324 | 0.47356 | 0.51356 | 0.55376 | 0.75215 | 0.87917 | 0.13675 | 0.16415 | 0.18746 | 0.22737 | 0.27437 | 0.33169 | 0.39821 | 0.49878 | 0.58084 | 0.67106 | 0.75461 | 0.83609 | 0.92354 | 1.0084 | 1.0909 | 1.1737 | 1.5882 | 1.8611
West Midlands | Penn 132kV | PATTINGHAM 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.071145 | 0.093725 | 0.13167 | 0.17763 | 0.22871 | 0.28648 | 0.35204 | 0.43001 | 0.50098 | 0.5645 | 0.62624 | 0.68482 | 0.72829 | 0.75537 | 0.77753 | 0.79823 | 0.91116 | 1.0165 | 0.15763 | 0.20594 | 0.28784 | 0.38609 | 0.49477 | 0.61795 | 0.75748 | 0.92244 | 1.0734 | 1.2097 | 1.3439 | 1.4707 | 1.5672 | 1.6274 | 1.6774 | 1.7246 | 1.9853 | 2.2361
West Midlands | Penn 132kV | PATTINGHAM 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.066238 | 0.082803 | 0.1014 | 0.13013 | 0.15941 | 0.19953 | 0.24722 | 0.30859 | 0.36447 | 0.4214 | 0.48257 | 0.54517 | 0.60409 | 0.65182 | 0.69891 | 0.74027 | 0.88236 | 0.94968 | 0.1485 | 0.18576 | 0.22541 | 0.28764 | 0.35087 | 0.43777 | 0.54239 | 0.6746 | 0.79652 | 0.91929 | 1.0514 | 1.1866 | 1.3137 | 1.4147 | 1.5145 | 1.6029 | 1.9195 | 2.0735
West Midlands | Penn 132kV | PATTINGHAM 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.068353 | 0.080509 | 0.10242 | 0.13103 | 0.16394 | 0.20674 | 0.2559 | 0.32229 | 0.38002 | 0.44623 | 0.50938 | 0.56915 | 0.626 | 0.67313 | 0.71841 | 0.75759 | 0.89448 | 0.99271 | 0.15122 | 0.17746 | 0.22355 | 0.28404 | 0.35405 | 0.4456 | 0.5505 | 0.69006 | 0.81226 | 0.95286 | 1.0853 | 1.2105 | 1.3292 | 1.4266 | 1.5203 | 1.6022 | 1.9037 | 2.1331
West Midlands | Penn 132kV | Wolverhampton West 132/33/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.11 | 1.3651 | 1.6789 | 2.0368 | 2.4238 | 2.9005 | 3.4347 | 4.2549 | 4.8966 | 5.6009 | 6.3229 | 7.0797 | 7.9086 | 8.7126 | 9.4973 | 10.266 | 13.633 | 14.7187 | 2.523 | 3.0543 | 3.7039 | 4.4446 | 5.2442 | 6.2305 | 7.3359 | 9.0171 | 10.3416 | 11.7979 | 13.2871 | 14.8416 | 16.537 | 18.1774 | 19.7778 | 21.3439 | 28.1973 | 30.5094
West Midlands | Penn 132kV | Wolverhampton West 132/33/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.3685 | 1.9999 | 2.7655 | 3.6349 | 4.6124 | 5.7698 | 7.1424 | 8.8177 | 10.2731 | 11.4548 | 12.514 | 13.5267 | 14.1628 | 14.5019 | 14.728 | 14.977 | 16.0613 | 17.2897 | 3.0847 | 4.4002 | 5.99 | 7.7923 | 9.8138 | 12.217 | 15.0547 | 18.5026 | 21.4999 | 23.9414 | 26.137 | 28.2283 | 29.5639 | 30.29 | 30.7958 | 31.352 | 33.8063 | 36.5639
West Midlands | Penn 132kV | Wolverhampton West 132/33/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.288 | 1.685 | 2.1699 | 2.7116 | 3.3955 | 4.2095 | 5.1521 | 6.3455 | 7.3303 | 8.3559 | 9.4725 | 10.629 | 11.7618 | 12.7744 | 13.7588 | 14.6413 | 16.8918 | 18.0835 | 2.946 | 3.8084 | 4.8405 | 5.9962 | 7.4536 | 9.1874 | 11.1848 | 13.6701 | 15.725 | 17.8538 | 20.1657 | 22.5599 | 24.9051 | 26.9942 | 29.0354 | 30.8717 | 35.7032 | 38.4064
West Midlands | Penn 132kV | Wolverhampton West 132/33/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.2078 | 1.538 | 1.9858 | 2.4802 | 3.0636 | 3.7982 | 4.6587 | 5.8495 | 6.8293 | 7.8562 | 8.9152 | 9.9474 | 10.9513 | 11.8366 | 12.6845 | 13.4434 | 15.1927 | 16.1402 | 2.7338 | 3.4282 | 4.361 | 5.3935 | 6.6143 | 8.1574 | 9.9557 | 12.417 | 14.4447 | 16.5601 | 18.7298 | 20.8414 | 22.8948 | 24.6982 | 26.4324 | 27.9875 | 31.6866 | 33.8095
West Midlands | Penn 132kV | Woodside 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 0.70973 | 0.84184 | 0.98622 | 1.1468 | 1.3764 | 1.624 | 1.903 | 2.3201 | 2.716 | 3.1224 | 3.5087 | 3.9086 | 4.3539 | 4.8344 | 5.322 | 5.7698 | 7.6129 | 8.3191 | 1.516 | 1.7956 | 2.0957 | 2.4287 | 2.9188 | 3.4328 | 4.0103 | 4.8685 | 5.6893 | 6.5323 | 7.3333 | 8.1579 | 9.0732 | 10.0634 | 11.0689 | 11.9884 | 15.7612 | 17.2345
West Midlands | Penn 132kV | Woodside 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 0.8263 | 1.1688 | 1.5392 | 1.9488 | 2.4948 | 3.0655 | 3.7128 | 4.486 | 5.2104 | 5.8713 | 6.4532 | 7.0108 | 7.4143 | 7.7634 | 8.0837 | 8.3277 | 9.2064 | 9.8527 | 1.768 | 2.4946 | 3.2661 | 4.1181 | 5.2634 | 6.4491 | 7.799 | 9.3953 | 10.8935 | 12.276 | 13.4924 | 14.6491 | 15.4975 | 16.2452 | 16.9411 | 17.4738 | 19.4256 | 20.8544
West Midlands | Penn 132kV | Woodside 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 0.79079 | 1.0433 | 1.2967 | 1.5849 | 2.0214 | 2.439 | 2.8855 | 3.4746 | 4.0243 | 4.6288 | 5.2498 | 5.87 | 6.4857 | 7.1188 | 7.759 | 8.292 | 9.7025 | 10.4297 | 1.7059 | 2.2654 | 2.8124 | 3.4307 | 4.3683 | 5.2673 | 6.2177 | 7.4477 | 8.6011 | 9.8699 | 11.1632 | 12.4536 | 13.7356 | 15.0605 | 16.4054 | 17.5259 | 20.5629 | 22.1845
West Midlands | Penn 132kV | Woodside 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 0.75911 | 0.96182 | 1.1946 | 1.4618 | 1.8787 | 2.2207 | 2.6491 | 3.2345 | 3.773 | 4.3919 | 4.9911 | 5.5675 | 6.1381 | 6.7119 | 7.2891 | 7.7565 | 8.8908 | 9.4535 | 1.6215 | 2.0547 | 2.5413 | 3.1009 | 3.9869 | 4.6993 | 5.6001 | 6.8111 | 7.9282 | 9.2164 | 10.4566 | 11.6455 | 12.8214 | 14.0119 | 15.2156 | 16.1891 | 18.5949 | 19.8167
West Midlands | Port Ham 132kV | ALDERTON 66 11kV S STN | Primary Substation | 11 | Counterfactual | 0.52809 | 0.56823 | 0.61643 | 0.67227 | 0.73457 | 0.80658 | 0.89538 | 1.0501 | 1.1646 | 1.299 | 1.4413 | 1.582 | 1.7308 | 1.8751 | 2.0079 | 2.1393 | 2.7882 | 3.0954 | 1.2691 | 1.3533 | 1.4545 | 1.5718 | 1.7027 | 1.8548 | 2.0434 | 2.3737 | 2.6167 | 2.906 | 3.2122 | 3.5112 | 3.824 | 4.1253 | 4.3994 | 4.6701 | 6.0218 | 6.6885
West Midlands | Port Ham 132kV | ALDERTON 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.56625 | 0.66444 | 0.79348 | 0.93873 | 1.0994 | 1.2859 | 1.5711 | 1.8869 | 2.1347 | 2.3771 | 2.6049 | 2.8032 | 2.9423 | 3.0298 | 3.0949 | 3.1542 | 3.5149 | 3.8299 | 1.3517 | 1.5577 | 1.832 | 2.1393 | 2.4775 | 2.8715 | 3.4948 | 4.1722 | 4.6926 | 5.2159 | 5.7108 | 6.1345 | 6.4391 | 6.6329 | 6.7813 | 6.9184 | 7.7744 | 8.5134
West Midlands | Port Ham 132kV | ALDERTON 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.55401 | 0.61764 | 0.68805 | 0.77624 | 0.87778 | 1.0756 | 1.2839 | 1.5286 | 1.7229 | 1.9333 | 2.1534 | 2.4908 | 2.6976 | 2.8744 | 3.0405 | 3.1874 | 3.6539 | 3.899 | 1.3303 | 1.4701 | 1.6204 | 1.811 | 2.0292 | 2.4792 | 2.9457 | 3.4778 | 3.895 | 4.3454 | 4.8147 | 5.5793 | 6.0209 | 6.3943 | 6.7462 | 7.0592 | 8.0965 | 8.6578
West Midlands | Port Ham 132kV | ALDERTON 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.54322 | 0.59573 | 0.66419 | 0.74377 | 0.83864 | 0.95921 | 1.1596 | 1.4029 | 1.583 | 1.8085 | 2.0329 | 2.2355 | 2.4182 | 2.5792 | 2.7299 | 2.8625 | 3.3275 | 3.6066 | 1.3015 | 1.4126 | 1.5567 | 1.7247 | 1.9259 | 2.1831 | 2.6284 | 3.1545 | 3.5341 | 4.02 | 4.498 | 4.924 | 5.3049 | 5.6389 | 5.9525 | 6.2301 | 7.2743 | 7.9229
West Midlands | Port Ham 132kV | BILSON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.37153 | 0.44311 | 0.52117 | 0.62299 | 0.73572 | 0.86703 | 1.0177 | 1.2731 | 1.4503 | 1.6991 | 2.0468 | 2.4397 | 2.9145 | 3.4571 | 3.8144 | 4.0385 | 5.0216 | 5.406 | 0.87303 | 1.0227 | 1.1847 | 1.3951 | 1.6277 | 1.901 | 2.2139 | 2.7508 | 3.1152 | 3.6481 | 4.4282 | 5.3149 | 6.3948 | 7.6448 | 8.435 | 8.8917 | 10.9002 | 11.7037
West Midlands | Port Ham 132kV | BILSON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.43738 | 0.59941 | 0.79991 | 1.0367 | 1.3007 | 1.6261 | 2.1096 | 2.741 | 3.1149 | 3.8553 | 4.6581 | 5.1761 | 5.5651 | 5.8899 | 5.9683 | 6.0389 | 6.3523 | 6.6226 | 1.015 | 1.3551 | 1.7713 | 2.2624 | 2.8086 | 3.497 | 4.5538 | 5.9452 | 6.7153 | 8.4263 | 10.312 | 11.4855 | 12.3892 | 13.1621 | 13.3357 | 13.4933 | 14.2095 | 14.8264
West Midlands | Port Ham 132kV | BILSON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.41395 | 0.5206 | 0.64913 | 0.80426 | 1.0057 | 1.3618 | 1.8462 | 2.5417 | 2.8279 | 3.7558 | 4.2857 | 4.8062 | 5.3063 | 5.5726 | 5.8231 | 6.0451 | 6.651 | 6.9388 | 0.9734 | 1.2078 | 1.4823 | 1.8134 | 2.2534 | 3.0673 | 4.188 | 5.7964 | 6.3997 | 8.5915 | 9.7853 | 10.9588 | 12.0887 | 12.6422 | 13.1637 | 13.6282 | 14.9409 | 15.5982
West Midlands | Port Ham 132kV | BILSON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.40218 | 0.48838 | 0.60858 | 0.75531 | 0.92085 | 1.1112 | 1.4978 | 2.0142 | 2.2919 | 2.9643 | 3.7402 | 4.4101 | 4.909 | 5.3834 | 5.6282 | 5.842 | 6.3655 | 6.5999 | 0.93772 | 1.1202 | 1.3703 | 1.676 | 2.0207 | 2.4167 | 3.2854 | 4.4336 | 5.007 | 6.5495 | 8.347 | 9.8827 | 11.0008 | 12.0687 | 12.5712 | 13.0116 | 14.1231 | 14.6486
West Midlands | Port Ham 132kV | BISHOPS CLEEVE 66 11kV S STN | Primary Substation | 11 | Counterfactual | 3.9787 | 4.1318 | 4.3133 | 4.526 | 4.7532 | 4.9976 | 5.2703 | 5.6384 | 5.955 | 6.3028 | 6.6231 | 6.9158 | 7.1953 | 7.4525 | 6.8031 | 7.0003 | 7.9259 | 6.9364 | 9.8186 | 10.1401 | 10.5195 | 10.9631 | 11.4382 | 11.9514 | 12.526 | 13.3035 | 13.9726 | 14.7149 | 15.4017 | 16.0245 | 16.6141 | 17.1534 | 15.4405 | 15.8454 | 17.7628 | 15.1849
West Midlands | Port Ham 132kV | BISHOPS CLEEVE 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 4.0416 | 4.3073 | 4.627 | 5.0022 | 5.4127 | 5.8664 | 6.4437 | 7.1132 | 7.6597 | 8.1996 | 8.6477 | 7.6722 | 7.903 | 8.0424 | 7.2558 | 7.3107 | 7.6852 | 8.0058 | 9.9558 | 10.5204 | 11.2013 | 11.9983 | 12.8714 | 13.8413 | 15.0922 | 16.5388 | 17.699 | 18.8722 | 19.8473 | 17.2765 | 17.7741 | 18.0782 | 16.0974 | 16.2225 | 17.0991 | 17.8372
West Midlands | Port Ham 132kV | BISHOPS CLEEVE 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 4.0229 | 4.2311 | 4.4675 | 4.7554 | 5.0754 | 5.5121 | 6.0062 | 6.547 | 6.9565 | 7.4083 | 7.8125 | 6.8485 | 7.3155 | 7.6059 | 6.9848 | 7.1885 | 7.3731 | 8.3831 | 9.9237 | 10.3775 | 10.8861 | 11.5073 | 12.1995 | 13.1718 | 14.2716 | 15.45 | 16.3179 | 17.2834 | 18.139 | 15.5883 | 16.6279 | 17.2395 | 15.5941 | 16.0228 | 16.2944 | 18.7491
West Midlands | Port Ham 132kV | BISHOPS CLEEVE 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 4.0019 | 4.1936 | 4.4217 | 4.6948 | 4.9992 | 5.3483 | 5.7912 | 6.3355 | 6.7675 | 7.2709 | 7.7169 | 7.1101 | 7.434 | 7.7158 | 7.087 | 7.2847 | 7.9111 | 8.2539 | 9.8691 | 10.2809 | 10.7681 | 11.3516 | 12.0061 | 12.761 | 13.7332 | 14.9203 | 15.8449 | 16.9392 | 17.899 | 16.2384 | 16.9184 | 17.5067 | 15.8401 | 16.2517 | 17.6425 | 18.4349
West Midlands | Port Ham 132kV | BIXHEAD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.3524 | 2.4057 | 2.469 | 2.5442 | 2.6266 | 2.7137 | 2.8106 | 2.974 | 3.1038 | 3.2462 | 3.4021 | 3.5706 | 3.7633 | 3.9308 | 4.1587 | 2.6366 | 3.3542 | 3.5966 | 5.8224 | 5.9342 | 6.0655 | 6.2211 | 6.3915 | 6.5708 | 6.7697 | 7.1051 | 7.3716 | 7.665 | 7.9884 | 8.337 | 8.7349 | 9.0782 | 9.55 | 5.664 | 7.1277 | 7.6382
West Midlands | Port Ham 132kV | BIXHEAD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.4032 | 2.5336 | 2.6862 | 2.8667 | 3.0677 | 3.2819 | 3.5566 | 3.8916 | 4.1753 | 4.4261 | 4.6581 | 4.8843 | 5.1298 | 5.2101 | 5.3046 | 3.6515 | 3.9274 | 4.1095 | 5.9326 | 6.2061 | 6.5223 | 6.896 | 7.311 | 7.7523 | 8.3252 | 9.0186 | 9.6003 | 10.1224 | 10.6075 | 11.0775 | 11.6041 | 11.777 | 11.9991 | 7.8543 | 8.4923 | 8.9068
West Midlands | Port Ham 132kV | BIXHEAD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.3875 | 2.4734 | 2.5735 | 2.6926 | 2.8243 | 2.9954 | 3.1838 | 3.438 | 3.7579 | 4.0689 | 4.3063 | 4.6343 | 4.8604 | 5.0717 | 5.2676 | 3.735 | 4.1788 | 4.3963 | 5.9055 | 6.094 | 6.3085 | 6.5626 | 6.8431 | 7.2146 | 7.6188 | 8.1526 | 8.8325 | 9.516 | 10.0088 | 10.7271 | 11.1967 | 11.6362 | 12.0443 | 8.1437 | 9.1037 | 9.6021
West Midlands | Port Ham 132kV | BIXHEAD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.3717 | 2.4405 | 2.528 | 2.6342 | 2.7529 | 2.8838 | 3.0624 | 3.3112 | 3.6237 | 3.8526 | 4.0887 | 4.3209 | 4.5302 | 4.7266 | 4.953 | 3.4134 | 3.8284 | 3.9876 | 5.8638 | 6.0093 | 6.1919 | 6.4135 | 6.6609 | 6.9322 | 7.31 | 7.8284 | 8.4878 | 8.9629 | 9.4512 | 9.9299 | 10.3583 | 10.7613 | 11.2455 | 7.3259 | 8.2215 | 8.575
West Midlands | Port Ham 132kV | BROCKWORTH 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.089 | 2.1753 | 2.265 | 2.3628 | 2.4787 | 2.6188 | 2.7596 | 2.9891 | 3.1585 | 3.3632 | 3.6133 | 3.8672 | 4.1307 | 4.3842 | 4.5962 | 4.8032 | 5.6923 | 6.0014 | 5.1183 | 5.2992 | 5.4855 | 5.6885 | 5.9321 | 6.2299 | 6.5234 | 7.0059 | 7.3573 | 7.7917 | 8.3369 | 8.8849 | 9.4491 | 9.9862 | 10.4218 | 10.847 | 12.6713 | 13.3291
West Midlands | Port Ham 132kV | BROCKWORTH 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.15 | 2.3311 | 2.5293 | 2.7588 | 3.0661 | 3.3551 | 3.7796 | 4.2908 | 4.6484 | 5.109 | 5.5049 | 5.7815 | 5.9723 | 6.1024 | 6.1959 | 6.2802 | 6.5918 | 6.8798 | 5.2511 | 5.6329 | 6.047 | 6.5304 | 7.1961 | 7.8021 | 8.7238 | 9.8295 | 10.5703 | 11.5963 | 12.4743 | 13.0546 | 13.4611 | 13.7434 | 13.9507 | 14.1388 | 14.8465 | 15.4974
West Midlands | Port Ham 132kV | BROCKWORTH 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.1315 | 2.2596 | 2.4151 | 2.5827 | 2.7646 | 3.0744 | 3.437 | 3.9155 | 4.1855 | 4.5627 | 4.8582 | 5.157 | 5.4504 | 5.7269 | 5.9851 | 6.2147 | 6.8063 | 7.169 | 5.2191 | 5.499 | 5.8399 | 6.2077 | 6.6025 | 7.3035 | 8.1248 | 9.1981 | 9.7687 | 10.5985 | 11.2158 | 11.8389 | 12.4513 | 13.0292 | 13.57 | 14.0532 | 15.3337 | 16.1676
West Midlands | Port Ham 132kV | BROCKWORTH 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.1139 | 2.2252 | 2.3475 | 2.4922 | 2.7053 | 2.9016 | 3.1977 | 3.5937 | 3.8477 | 4.257 | 4.6567 | 4.9727 | 5.2467 | 5.5029 | 5.7752 | 5.9868 | 6.6785 | 6.9467 | 5.1723 | 5.4095 | 5.6663 | 5.9751 | 6.4474 | 6.8661 | 7.5211 | 8.388 | 8.9172 | 9.8267 | 10.7044 | 11.3744 | 11.9416 | 12.4722 | 13.0511 | 13.4917 | 15.0414 | 15.643
West Midlands | Port Ham 132kV | Cheltenham 132/66/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.5534 | 1.7149 | 1.9705 | 2.1562 | 2.3756 | 2.6385 | 2.9438 | 3.448 | 3.8732 | 4.3564 | 4.9573 | 5.4438 | 5.9898 | 6.5289 | 6.9595 | 7.3868 | 9.2995 | 9.8594 | 3.4283 | 3.7706 | 4.334 | 4.722 | 5.18 | 5.7328 | 6.373 | 7.4275 | 8.3105 | 9.3298 | 10.6222 | 11.6668 | 12.8349 | 13.984 | 14.8628 | 15.7338 | 19.6455 | 20.8407
West Midlands | Port Ham 132kV | Cheltenham 132/66/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.7075 | 2.1895 | 2.6968 | 3.1986 | 3.853 | 4.5466 | 5.4631 | 6.5708 | 7.3774 | 8.2962 | 9.1629 | 9.7555 | 10.1243 | 10.3193 | 10.4461 | 10.5625 | 11.0899 | 11.6062 | 3.7672 | 4.8187 | 5.8996 | 6.9582 | 8.3506 | 9.8179 | 11.7865 | 14.1556 | 15.8206 | 17.834 | 19.7534 | 21.0089 | 21.8013 | 22.2247 | 22.5129 | 22.7798 | 24.0134 | 25.2106
West Midlands | Port Ham 132kV | Cheltenham 132/66/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.7276 | 2.0198 | 2.3785 | 2.7496 | 3.1749 | 3.7913 | 4.524 | 5.4589 | 6.0421 | 6.9155 | 7.611 | 8.2277 | 8.8021 | 9.3329 | 9.8356 | 10.2804 | 11.4476 | 11.9814 | 3.8511 | 4.5023 | 5.2993 | 6.1142 | 7.0438 | 8.4262 | 10.0699 | 12.1328 | 13.359 | 15.293 | 16.7674 | 18.063 | 19.2574 | 20.3596 | 21.4069 | 22.3378 | 24.8774 | 26.1128
West Midlands | Port Ham 132kV | Cheltenham 132/66/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.6176 | 1.9301 | 2.2486 | 2.5771 | 2.9874 | 3.4489 | 4.0641 | 4.8928 | 5.4453 | 6.257 | 7.1073 | 7.7931 | 8.3642 | 8.8621 | 9.3338 | 9.7485 | 10.7093 | 11.147 | 3.571 | 4.2711 | 4.9605 | 5.6653 | 6.5553 | 7.5505 | 8.8973 | 10.6898 | 11.8355 | 13.6093 | 15.4677 | 16.9319 | 18.1157 | 19.1346 | 20.1028 | 20.9567 | 23.0086 | 24.0051
West Midlands | Port Ham 132kV | COMMERCIAL RD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 4.0644 | 4.339 | 4.5408 | 4.773 | 5.0298 | 5.3198 | 5.6487 | 6.1588 | 6.5551 | 6.9984 | 7.4687 | 7.948 | 8.4622 | 8.9533 | 8.8628 | 9.3188 | 11.4035 | 12.2086 | 10.0033 | 10.6242 | 11.0438 | 11.5269 | 12.0608 | 12.6648 | 13.3511 | 14.4123 | 15.2377 | 16.1694 | 17.16 | 18.1626 | 19.2304 | 20.2454 | 19.8109 | 20.7442 | 25.0318 | 26.7486
West Midlands | Port Ham 132kV | COMMERCIAL RD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 4.3129 | 4.709 | 5.1938 | 5.7553 | 6.3776 | 7.0244 | 7.8516 | 8.8489 | 9.6785 | 10.4489 | 11.1589 | 11.7847 | 12.2192 | 12.5051 | 12.1626 | 12.3563 | 13.2562 | 14.1242 | 10.5781 | 11.4137 | 12.4311 | 13.6085 | 14.9105 | 16.2605 | 18.0091 | 20.1035 | 21.8264 | 23.4654 | 24.9799 | 26.2905 | 27.217 | 27.8348 | 26.9189 | 27.3504 | 29.3892 | 31.3528
West Midlands | Port Ham 132kV | COMMERCIAL RD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 4.2689 | 4.5443 | 4.8691 | 5.2556 | 5.6745 | 6.2068 | 6.8323 | 7.6369 | 8.2531 | 8.9158 | 9.6092 | 10.3086 | 10.9871 | 11.6116 | 11.642 | 12.1639 | 12.9101 | 13.7472 | 10.5014 | 11.1069 | 11.8011 | 12.6312 | 13.5287 | 14.694 | 16.0602 | 17.7854 | 19.0858 | 20.4903 | 21.9425 | 23.4069 | 24.8282 | 26.1307 | 25.9682 | 27.0634 | 28.4237 | 30.3132
West Midlands | Port Ham 132kV | COMMERCIAL RD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 4.2302 | 4.443 | 4.7262 | 5.0549 | 5.4289 | 5.8672 | 6.4369 | 7.1984 | 7.8062 | 8.5208 | 9.2508 | 9.9281 | 10.5535 | 11.1186 | 11.0962 | 11.5622 | 12.8338 | 13.5724 | 10.3981 | 10.8499 | 11.4429 | 12.1342 | 12.9218 | 13.8465 | 15.0667 | 16.6766 | 17.9442 | 19.4594 | 20.9953 | 22.4036 | 23.6946 | 24.8582 | 24.5702 | 25.5341 | 28.2628 | 29.9213
West Midlands | Port Ham 132kV | Eastern Avenue 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.5577 | 1.8108 | 2.0224 | 2.3473 | 2.6133 | 2.9092 | 3.2411 | 3.7746 | 4.1787 | 4.6127 | 5.0788 | 5.5673 | 6.1065 | 6.6464 | 7.1536 | 7.653 | 9.9153 | 10.5899 | 3.7229 | 4.245 | 4.6829 | 5.3957 | 5.9449 | 6.5553 | 7.2392 | 8.3396 | 9.1702 | 10.0675 | 11.0378 | 12.0503 | 13.1622 | 14.2729 | 15.3077 | 16.3258 | 20.9403 | 22.3664
West Midlands | Port Ham 132kV | Eastern Avenue 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.7208 | 2.2172 | 2.8499 | 3.4511 | 4.1322 | 4.8964 | 5.8789 | 7.0469 | 8.0059 | 8.8355 | 9.5705 | 10.2676 | 10.7509 | 11.0549 | 11.2271 | 11.412 | 12.2149 | 12.9893 | 4.0771 | 5.1075 | 6.4804 | 7.7488 | 9.1792 | 10.7826 | 12.8689 | 15.3294 | 17.3278 | 19.0801 | 20.6329 | 22.0911 | 23.1299 | 23.7975 | 24.1817 | 24.6028 | 26.4488 | 28.2105
West Midlands | Port Ham 132kV | Eastern Avenue 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.6704 | 2.1115 | 2.4697 | 2.8608 | 3.3109 | 3.9404 | 4.6008 | 5.4277 | 6.0862 | 6.782 | 7.5178 | 8.2643 | 8.9997 | 9.6888 | 10.3242 | 10.8904 | 12.3953 | 13.1781 | 3.9907 | 4.9679 | 5.7478 | 6.5966 | 7.5708 | 8.9596 | 10.394 | 12.1451 | 13.5212 | 14.9742 | 16.503 | 18.0529 | 19.5801 | 21.0129 | 22.3365 | 23.5204 | 26.7733 | 28.5662
West Midlands | Port Ham 132kV | Eastern Avenue 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.6182 | 1.9223 | 2.3083 | 2.6304 | 3.0076 | 3.4406 | 4.0379 | 4.8361 | 5.442 | 6.1311 | 6.8475 | 7.5256 | 8.1741 | 8.7844 | 9.3468 | 9.8423 | 11.0136 | 11.5514 | 3.8531 | 4.4868 | 5.3314 | 6.0039 | 6.7919 | 7.6964 | 8.9742 | 10.6537 | 11.9032 | 13.3425 | 14.8302 | 16.2248 | 17.5536 | 18.8055 | 19.9599 | 20.9794 | 23.4594 | 24.6565
West Midlands | Port Ham 132kV | ELTON 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.38328 | 0.40809 | 0.44377 | 0.48802 | 0.53879 | 0.59867 | 0.67126 | 0.78368 | 0.8761 | 0.98481 | 1.0856 | 1.1807 | 1.2792 | 1.3742 | 1.4658 | 1.5581 | 2.0273 | 2.2839 | 0.93116 | 0.98311 | 1.0597 | 1.1549 | 1.2646 | 1.3955 | 1.5564 | 1.8023 | 2.0068 | 2.2504 | 2.4719 | 2.6764 | 2.8851 | 3.085 | 3.2773 | 3.4713 | 4.477 | 5.0575
West Midlands | Port Ham 132kV | ELTON 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.4073 | 0.4688 | 0.5737 | 0.69436 | 0.82459 | 0.97299 | 1.1526 | 1.3649 | 1.5573 | 1.7319 | 1.9072 | 2.07 | 2.1988 | 2.2756 | 2.3617 | 2.4218 | 2.7289 | 3.0538 | 0.98305 | 1.112 | 1.3433 | 1.6072 | 1.8904 | 2.2149 | 2.6082 | 3.0685 | 3.4866 | 3.8715 | 4.2634 | 4.6253 | 4.9193 | 5.0948 | 5.3001 | 5.4423 | 6.1816 | 6.9719
West Midlands | Port Ham 132kV | ELTON 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.39948 | 0.4396 | 0.48669 | 0.561 | 0.64052 | 0.75312 | 0.89216 | 1.0641 | 1.2287 | 1.4301 | 1.6009 | 1.7728 | 1.9354 | 2.0604 | 2.1793 | 2.2869 | 2.662 | 2.8179 | 0.96937 | 1.0575 | 1.1581 | 1.3221 | 1.4966 | 1.7494 | 2.0636 | 2.4438 | 2.8113 | 3.2695 | 3.6471 | 4.0283 | 4.3887 | 4.6587 | 4.9165 | 5.1516 | 6.0118 | 6.3775
West Midlands | Port Ham 132kV | ELTON 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.39296 | 0.42586 | 0.47625 | 0.54289 | 0.62406 | 0.72537 | 0.84885 | 1.0085 | 1.1509 | 1.3136 | 1.4647 | 1.6094 | 1.7443 | 1.8563 | 1.9862 | 2.0822 | 2.432 | 2.7148 | 0.95182 | 1.0214 | 1.1297 | 1.2742 | 1.4521 | 1.6762 | 1.9502 | 2.2976 | 2.6082 | 2.9663 | 3.2926 | 3.6039 | 3.8927 | 4.129 | 4.4135 | 4.619 | 5.422 | 6.1057
West Midlands | Port Ham 132kV | Hereford Central 66/11kv | Primary Substation | 11 | Counterfactual | 0.26109 | 0.34311 | 0.43421 | 0.53248 | 0.65624 | 0.79386 | 0.94557 | 1.1835 | 1.3815 | 1.5884 | 1.8073 | 2.0395 | 2.2907 | 2.542 | 2.7881 | 3.0406 | 4.1069 | 4.501 | 0.58429 | 0.75721 | 0.94557 | 1.1487 | 1.4051 | 1.6893 | 2.0015 | 2.4865 | 2.8932 | 3.3181 | 3.7674 | 4.2429 | 4.7557 | 5.2682 | 5.7709 | 6.2862 | 8.4623 | 9.2843
West Midlands | Port Ham 132kV | Hereford Central 66/11kv | Primary Substation | 11 | Electric Engagement | 0.33327 | 0.53942 | 0.77207 | 1.0242 | 1.3296 | 1.651 | 2.0308 | 2.4931 | 2.9057 | 3.2553 | 3.5862 | 3.9043 | 4.1186 | 4.2586 | 4.3656 | 4.4601 | 4.8404 | 5.1702 | 0.7401 | 1.1762 | 1.6591 | 2.1826 | 2.8177 | 3.4815 | 4.2627 | 5.2084 | 6.0557 | 6.7765 | 7.4611 | 8.119 | 8.5685 | 8.8675 | 9.1006 | 9.3088 | 10.1627 | 10.8975
West Midlands | Port Ham 132kV | Hereford Central 66/11kv | Primary Substation | 11 | Holistic Transition | 0.3105 | 0.45841 | 0.61353 | 0.78101 | 0.97586 | 1.1987 | 1.4533 | 1.7999 | 2.1061 | 2.4345 | 2.7925 | 3.1436 | 3.484 | 3.7939 | 4.0875 | 4.3501 | 5.0548 | 5.4313 | 0.70037 | 1.0286 | 1.3641 | 1.7223 | 2.1372 | 2.6095 | 3.1442 | 3.8625 | 4.5011 | 5.1835 | 5.9259 | 6.6549 | 7.362 | 8.0061 | 8.6175 | 9.167 | 10.6849 | 11.5312
West Midlands | Port Ham 132kV | Hereford Central 66/11kv | Primary Substation | 11 | Hydrogen Evolution | 0.29008 | 0.40669 | 0.54788 | 0.70883 | 0.89755 | 1.1052 | 1.3487 | 1.6904 | 1.9919 | 2.3181 | 2.6633 | 3.0064 | 3.3319 | 3.6283 | 3.9074 | 4.1537 | 4.7316 | 5.0156 | 0.64607 | 0.89443 | 1.1888 | 1.5255 | 1.9215 | 2.353 | 2.8563 | 3.5554 | 4.1756 | 4.8443 | 5.5514 | 6.2544 | 6.922 | 7.5295 | 8.1028 | 8.6102 | 9.8307 | 10.4516
West Midlands | Port Ham 132kV | HEREFORD NORTH 66 11kV S STN | Primary Substation | 11 | Counterfactual | 1.1418 | 1.2748 | 1.4348 | 1.6037 | 1.7991 | 2.0225 | 2.3502 | 2.7695 | 3.1793 | 3.5891 | 3.9887 | 4.4083 | 4.8556 | 5.252 | 5.6378 | 6 | 7.662 | 8.2225 | 2.5181 | 2.7985 | 3.1338 | 3.4829 | 3.89 | 4.3547 | 5.062 | 5.9224 | 6.7732 | 7.6234 | 8.4506 | 9.3164 | 10.2358 | 11.0456 | 11.8371 | 12.5788 | 15.9676 | 17.1425
West Midlands | Port Ham 132kV | HEREFORD NORTH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.2587 | 1.5863 | 1.9761 | 2.4021 | 2.9178 | 3.703 | 4.3848 | 5.2539 | 6.0354 | 6.6902 | 7.279 | 7.8679 | 8.2559 | 8.4765 | 8.6096 | 8.7087 | 9.2283 | 9.682 | 2.7721 | 3.4668 | 4.2915 | 5.1804 | 6.2645 | 7.9905 | 9.4032 | 11.2007 | 12.8205 | 14.1804 | 15.4059 | 16.64 | 17.4657 | 17.9375 | 18.2297 | 18.4484 | 19.6144 | 20.6295
West Midlands | Port Ham 132kV | HEREFORD NORTH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.2239 | 1.4491 | 1.7493 | 2.0289 | 2.5284 | 2.9301 | 3.4028 | 4.0764 | 4.6752 | 5.2998 | 5.9835 | 6.5817 | 7.1325 | 7.6294 | 8.0748 | 8.4466 | 9.4779 | 9.9903 | 2.7127 | 3.2127 | 3.8795 | 4.4783 | 5.6097 | 6.4631 | 7.463 | 8.8744 | 10.1342 | 11.4457 | 12.8929 | 14.1359 | 15.2787 | 16.3111 | 17.2354 | 18.0074 | 20.2196 | 21.3759
West Midlands | Port Ham 132kV | HEREFORD NORTH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.1847 | 1.3739 | 1.6181 | 1.8824 | 2.2163 | 2.8106 | 3.2627 | 3.9171 | 4.4969 | 5.0954 | 5.6989 | 6.2955 | 6.8512 | 7.3315 | 7.7546 | 8.0999 | 8.9641 | 9.3634 | 2.6108 | 3.0193 | 3.5438 | 4.1012 | 4.8144 | 6.1523 | 7.097 | 8.4571 | 9.6652 | 10.9051 | 12.1495 | 13.3847 | 14.5398 | 15.5306 | 16.3984 | 17.1058 | 18.9329 | 19.8185
West Midlands | Port Ham 132kV | HEREFORD SOUTH 66 11kV S STN | Primary Substation | 11 | Counterfactual | 4.3188 | 4.4736 | 4.6547 | 4.8501 | 5.0876 | 5.3585 | 5.6903 | 6.1532 | 6.5191 | 6.9131 | 7.3123 | 7.7274 | 8.1757 | 8.6586 | 9.1151 | 9.5816 | 11.5871 | 12.352 | 10.6727 | 11.0049 | 11.3915 | 11.8073 | 12.3125 | 12.8875 | 13.5969 | 14.5646 | 15.3354 | 16.1686 | 17.0073 | 17.8733 | 18.7946 | 19.7945 | 20.7383 | 21.7021 | 25.8557 | 27.5101
West Midlands | Port Ham 132kV | HEREFORD SOUTH 66 11kV S STN | Primary Substation | 11 | Electric Engagement | 4.4485 | 4.8028 | 5.2477 | 5.7385 | 6.3388 | 7.035 | 7.7962 | 8.6661 | 9.4157 | 10.052 | 10.6436 | 11.2049 | 11.6065 | 11.8759 | 12.0811 | 11.6319 | 12.419 | 13.0889 | 10.9542 | 11.7047 | 12.6502 | 13.688 | 14.9578 | 16.445 | 18.0426 | 19.8416 | 21.3898 | 22.7131 | 23.9499 | 25.1193 | 25.9748 | 26.5588 | 27.0156 | 25.8451 | 27.6502 | 29.2092
West Midlands | Port Ham 132kV | HEREFORD SOUTH 66 11kV S STN | Primary Substation | 11 | Holistic Transition | 4.41 | 4.6504 | 4.9396 | 5.2757 | 5.6911 | 6.1656 | 6.6794 | 7.3383 | 7.8256 | 8.3849 | 8.9924 | 9.6029 | 9.5595 | 10.1254 | 10.6648 | 11.1487 | 13.1482 | 13.8815 | 10.8887 | 11.4227 | 12.0591 | 12.7877 | 13.6981 | 14.7284 | 15.8279 | 17.2124 | 18.213 | 19.3713 | 20.6313 | 21.9105 | 21.5608 | 22.7494 | 23.8848 | 24.9093 | 29.4876 | 31.1886
West Midlands | Port Ham 132kV | HEREFORD SOUTH 66 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 4.3664 | 4.5559 | 4.8047 | 5.1065 | 5.4703 | 5.9332 | 6.736 | 7.377 | 7.8882 | 8.4502 | 9.0419 | 9.614 | 10.1833 | 10.7179 | 11.2168 | 11.6525 | 12.7127 | 13.1145 | 10.7752 | 11.1804 | 11.7094 | 12.3511 | 13.1283 | 14.1324 | 15.9518 | 17.2873 | 18.3434 | 19.5002 | 20.7174 | 21.8916 | 23.0649 | 24.1696 | 25.2005 | 26.1011 | 28.3725 | 29.2562
West Midlands | Port Ham 132kV | Lydney 33/11kVDUMMY | Primary Substation | 11 | Counterfactual | 0.26579 | 0.31548 | 0.37218 | 0.44528 | 0.53129 | 0.64472 | 0.78132 | 0.98481 | 1.1325 | 1.3129 | 1.5535 | 1.787 | 2.0324 | 2.2584 | 2.3797 | 2.5008 | 3.0545 | 3.2596 | 0.62287 | 0.72701 | 0.84525 | 0.99741 | 1.1766 | 1.4138 | 1.7005 | 2.1375 | 2.4475 | 2.8415 | 3.3869 | 3.9183 | 4.4758 | 4.985 | 5.2333 | 5.481 | 6.621 | 7.0612
West Midlands | Port Ham 132kV | Lydney 33/11kVDUMMY | Primary Substation | 11 | Electric Engagement | 0.30314 | 0.41117 | 0.54901 | 0.7118 | 0.90086 | 1.1312 | 1.5392 | 2.0318 | 2.3112 | 2.8093 | 3.2917 | 3.5238 | 3.6599 | 3.7308 | 3.7776 | 3.8242 | 4.0335 | 4.2323 | 0.70377 | 0.93133 | 1.2236 | 1.5678 | 1.9672 | 2.4566 | 3.3712 | 4.4803 | 5.0699 | 6.2285 | 7.36 | 7.8742 | 8.1762 | 8.3327 | 8.4387 | 8.5458 | 9.0355 | 9.5018
West Midlands | Port Ham 132kV | Lydney 33/11kVDUMMY | Primary Substation | 11 | Holistic Transition | 0.29089 | 0.36613 | 0.45639 | 0.56977 | 0.70198 | 1.0285 | 1.4528 | 1.9901 | 2.2102 | 2.6955 | 2.9593 | 3.1682 | 3.3429 | 3.4993 | 3.6452 | 3.7757 | 4.1404 | 4.311 | 0.68237 | 0.84711 | 1.042 | 1.2871 | 1.5728 | 2.3309 | 3.3215 | 4.575 | 5.0476 | 6.1836 | 6.7629 | 7.2121 | 7.5799 | 7.9072 | 8.2133 | 8.4884 | 9.2898 | 9.6843
West Midlands | Port Ham 132kV | Lydney 33/11kVDUMMY | Primary Substation | 11 | Hydrogen Evolution | 0.28102 | 0.34486 | 0.42556 | 0.52517 | 0.64552 | 0.80855 | 1.1222 | 1.5286 | 1.736 | 2.1777 | 2.6362 | 2.9453 | 3.1267 | 3.2728 | 3.4088 | 3.5294 | 3.8349 | 3.9975 | 0.65539 | 0.79124 | 0.96125 | 1.1716 | 1.4271 | 1.7758 | 2.4882 | 3.4115 | 3.8498 | 4.8733 | 5.9376 | 6.6356 | 7.019 | 7.32 | 7.6005 | 7.8505 | 8.5118 | 8.887
West Midlands | Port Ham 132kV | Marle Hill 132/66/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 0.66456 | 0.78657 | 0.92345 | 1.071 | 1.2415 | 1.443 | 1.6736 | 2.0384 | 2.3214 | 2.6073 | 2.9059 | 3.2223 | 3.5793 | 3.9377 | 4.2922 | 4.6448 | 6.2263 | 6.6776 | 1.5305 | 1.7882 | 2.0726 | 2.3787 | 2.7318 | 3.1492 | 3.6264 | 4.3762 | 4.9599 | 5.5497 | 6.1659 | 6.8157 | 7.5464 | 8.2792 | 9.0028 | 9.722 | 12.954 | 13.9153
West Midlands | Port Ham 132kV | Marle Hill 132/66/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 0.78099 | 1.0886 | 1.4502 | 1.943 | 2.4014 | 2.9005 | 3.4899 | 4.2022 | 4.8098 | 5.3167 | 5.7635 | 6.195 | 6.4688 | 6.6297 | 6.7352 | 6.8315 | 7.2802 | 7.7005 | 1.7834 | 2.4327 | 3.1872 | 4.2578 | 5.2094 | 6.2447 | 7.469 | 8.9371 | 10.1837 | 11.2342 | 12.1641 | 13.056 | 13.6328 | 13.9815 | 14.2207 | 14.4406 | 15.4863 | 16.4563
West Midlands | Port Ham 132kV | Marle Hill 132/66/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 0.74612 | 0.95311 | 1.1752 | 1.4367 | 1.7323 | 2.0854 | 2.463 | 2.972 | 3.3858 | 3.8294 | 4.2991 | 4.7805 | 5.2581 | 5.7064 | 6.1321 | 6.5087 | 7.424 | 7.9041 | 1.7237 | 2.1824 | 2.6594 | 3.221 | 3.8533 | 4.6154 | 5.4203 | 6.4826 | 7.3423 | 8.2625 | 9.2339 | 10.2312 | 11.2223 | 12.1534 | 13.0408 | 13.8295 | 15.799 | 16.909
West Midlands | Port Ham 132kV | Marle Hill 132/66/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 0.70718 | 0.86886 | 1.076 | 1.3019 | 1.5649 | 1.8512 | 2.2031 | 2.6976 | 3.0965 | 3.5386 | 3.9982 | 4.449 | 4.8896 | 5.2987 | 5.6875 | 6.028 | 6.8169 | 7.1863 | 1.6225 | 1.9668 | 2.4014 | 2.8745 | 3.4255 | 4.0232 | 4.762 | 5.7848 | 6.6051 | 7.5172 | 8.4612 | 9.3839 | 10.2853 | 11.123 | 11.9214 | 12.6224 | 14.3037 | 15.1342
West Midlands | Port Ham 132kV | MEAD LA 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.73765 | 0.75466 | 0.77322 | 0.79646 | 0.83019 | 0.86832 | 0.90324 | 0.97073 | 1.0228 | 1.3535 | 1.4654 | 1.5761 | 1.6983 | 1.8189 | 1.9201 | 2.0047 | 2.2428 | 2.3583 | 1.8046 | 1.8405 | 1.8795 | 1.9282 | 1.9989 | 2.0791 | 2.1528 | 2.2994 | 2.413 | 3.2218 | 3.4828 | 3.7396 | 4.0224 | 4.3008 | 4.5314 | 4.7206 | 5.2138 | 5.4594
West Midlands | Port Ham 132kV | MEAD LA 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.75179 | 0.79021 | 0.85718 | 0.9348 | 1.2785 | 1.3782 | 1.5372 | 1.7645 | 1.9278 | 2.21 | 2.4454 | 2.6163 | 2.7656 | 2.8463 | 2.9383 | 2.9718 | 3.1632 | 3.2877 | 1.8348 | 1.9164 | 2.0651 | 2.237 | 3.068 | 3.2858 | 3.6494 | 4.1757 | 4.5477 | 5.2229 | 5.7845 | 6.1859 | 6.5424 | 6.7336 | 6.9564 | 7.0347 | 7.471 | 7.7702
West Midlands | Port Ham 132kV | MEAD LA 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.74677 | 0.77395 | 0.81846 | 1.1223 | 1.1882 | 1.326 | 1.5097 | 1.7804 | 1.9256 | 2.2787 | 2.4438 | 2.5957 | 2.703 | 2.7663 | 2.8279 | 2.8849 | 3.1171 | 3.2062 | 1.8258 | 1.8864 | 1.9872 | 2.734 | 2.8813 | 3.2046 | 3.6432 | 4.2907 | 4.6285 | 5.4843 | 5.8683 | 6.2204 | 6.4624 | 6.5965 | 6.7275 | 6.8496 | 7.3569 | 7.5647
West Midlands | Port Ham 132kV | MEAD LA 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.74446 | 0.76566 | 0.79396 | 0.82943 | 0.87981 | 1.1912 | 1.2999 | 1.4738 | 1.5884 | 1.8299 | 2.0442 | 2.2168 | 2.382 | 2.4978 | 2.619 | 2.6678 | 2.8326 | 2.9164 | 1.8188 | 1.8641 | 1.9235 | 1.998 | 2.1049 | 2.8613 | 3.1109 | 3.5127 | 3.7706 | 4.3431 | 4.8469 | 5.2479 | 5.6308 | 5.894 | 6.1723 | 6.2739 | 6.6289 | 6.8226
West Midlands | Port Ham 132kV | MITCHELDEAN 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.16386 | 0.18763 | 0.21619 | 0.25055 | 0.28906 | 0.33447 | 0.38212 | 0.46171 | 0.52141 | 0.59523 | 0.68927 | 0.79275 | 0.91379 | 1.046 | 1.1405 | 1.219 | 1.5674 | 1.7224 | 0.37802 | 0.42824 | 0.488 | 0.55986 | 0.64039 | 0.7353 | 0.83557 | 1.0029 | 1.1282 | 1.2867 | 1.4934 | 1.7212 | 1.989 | 2.2853 | 2.4882 | 2.6493 | 3.3704 | 3.7024
West Midlands | Port Ham 132kV | MITCHELDEAN 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.18533 | 0.24395 | 0.31632 | 0.40212 | 0.49729 | 0.60459 | 0.74421 | 0.92649 | 1.0618 | 1.252 | 1.4539 | 1.6005 | 1.7172 | 1.7979 | 1.8362 | 1.8741 | 2.0404 | 2.1816 | 0.42435 | 0.54826 | 0.70123 | 0.88181 | 1.0814 | 1.3061 | 1.6053 | 1.9984 | 2.281 | 2.7093 | 3.1717 | 3.4975 | 3.762 | 3.9479 | 4.0331 | 4.1178 | 4.5002 | 4.8298
West Midlands | Port Ham 132kV | MITCHELDEAN 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.17845 | 0.21902 | 0.26332 | 0.32059 | 0.3831 | 0.48176 | 0.60691 | 0.78684 | 0.89615 | 1.1217 | 1.2717 | 1.4272 | 1.5692 | 1.6678 | 1.7646 | 1.8482 | 2.106 | 2.2298 | 0.41226 | 0.50227 | 0.59724 | 0.7206 | 0.85479 | 1.0734 | 1.3562 | 1.7616 | 1.9955 | 2.5154 | 2.8471 | 3.1905 | 3.5033 | 3.7102 | 3.9135 | 4.0903 | 4.6561 | 4.938
West Midlands | Port Ham 132kV | MITCHELDEAN 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.1726 | 0.2044 | 0.24469 | 0.29536 | 0.35361 | 0.42419 | 0.51848 | 0.65908 | 0.75809 | 0.9309 | 1.1208 | 1.288 | 1.4301 | 1.5511 | 1.6368 | 1.7147 | 1.9275 | 2.0569 | 0.39662 | 0.46432 | 0.54899 | 0.65574 | 0.77879 | 0.92771 | 1.1325 | 1.4379 | 1.6452 | 2.0321 | 2.4603 | 2.8339 | 3.1445 | 3.4082 | 3.5856 | 3.7476 | 4.2108 | 4.5067
West Midlands | Port Ham 132kV | Montpellier 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.4063 | 1.6357 | 1.9831 | 2.2651 | 2.5903 | 2.9611 | 3.3871 | 4.0684 | 4.5934 | 5.3326 | 5.8967 | 6.4974 | 7.1764 | 7.8631 | 8.543 | 9.2187 | 12.2312 | 13.0631 | 3.2584 | 3.7394 | 4.4533 | 5.0372 | 5.709 | 6.4749 | 7.3532 | 8.749 | 9.8278 | 11.4313 | 12.5917 | 13.823 | 15.21 | 16.6118 | 17.9983 | 19.3749 | 25.5237 | 27.2939
West Midlands | Port Ham 132kV | Montpellier 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.6321 | 2.3066 | 2.9766 | 3.8896 | 4.7266 | 5.6321 | 6.7532 | 8.1066 | 9.2683 | 10.2286 | 11.066 | 11.8904 | 12.4029 | 12.7038 | 12.8975 | 13.0743 | 13.887 | 14.679 | 3.7496 | 5.1562 | 6.549 | 8.52 | 10.2495 | 12.1182 | 14.439 | 17.2181 | 19.5957 | 21.5769 | 23.3115 | 25.0123 | 26.0897 | 26.7401 | 27.1787 | 27.5821 | 29.4627 | 31.2759
West Midlands | Port Ham 132kV | Montpellier 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.5644 | 2.0368 | 2.6349 | 3.0986 | 3.6209 | 4.2417 | 4.948 | 5.9099 | 6.7076 | 7.5562 | 8.4566 | 9.3708 | 10.2757 | 11.1246 | 11.9294 | 12.2541 | 14.1207 | 15.4062 | 3.6341 | 4.6539 | 6.0024 | 6.9947 | 8.1068 | 9.4398 | 10.9383 | 12.9396 | 14.5958 | 16.3536 | 18.2127 | 20.1043 | 21.9787 | 23.738 | 25.4114 | 25.9305 | 29.9729 | 33.0134
West Midlands | Port Ham 132kV | Montpellier 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.487 | 1.8873 | 2.2596 | 2.6577 | 3.312 | 3.8311 | 4.492 | 5.42 | 6.1785 | 7.0074 | 8.0772 | 8.9399 | 9.7802 | 10.5666 | 11.3124 | 11.9702 | 13.4735 | 14.145 | 3.4329 | 4.2706 | 5.049 | 5.8799 | 7.3226 | 8.4019 | 9.7847 | 11.6977 | 13.2543 | 14.9582 | 17.2403 | 19.004 | 20.7208 | 22.3287 | 23.8583 | 25.2108 | 28.4022 | 29.9114
West Midlands | Port Ham 132kV | PRINCESS ROYAL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.30847 | 0.35026 | 0.40043 | 0.46046 | 0.52641 | 0.59752 | 0.67569 | 0.81365 | 0.9223 | 1.0577 | 1.2368 | 1.4393 | 1.6726 | 1.8982 | 2.0472 | 2.1865 | 2.7713 | 2.9677 | 0.70071 | 0.78839 | 0.8925 | 1.017 | 1.1535 | 1.3004 | 1.4616 | 1.749 | 1.9749 | 2.2645 | 2.6613 | 3.1129 | 3.6352 | 4.1393 | 4.4503 | 4.7388 | 5.9352 | 6.3509
West Midlands | Port Ham 132kV | PRINCESS ROYAL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.34907 | 0.45287 | 0.57628 | 0.72434 | 0.88957 | 1.0663 | 1.3235 | 1.6689 | 1.9259 | 2.3086 | 2.7167 | 2.9903 | 3.2139 | 3.2863 | 3.3357 | 3.3818 | 3.5974 | 3.7666 | 0.7889 | 1.0068 | 1.2637 | 1.5712 | 1.9135 | 2.2791 | 2.83 | 3.5782 | 4.1176 | 4.9894 | 5.9338 | 6.5448 | 7.0301 | 7.1861 | 7.2958 | 7.3988 | 7.8875 | 8.2762
West Midlands | Port Ham 132kV | PRINCESS ROYAL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.33703 | 0.40588 | 0.48571 | 0.58455 | 0.69262 | 0.87042 | 1.1114 | 1.4671 | 1.6834 | 2.1554 | 2.4382 | 2.6701 | 2.9054 | 3.0723 | 3.2286 | 3.3674 | 3.7565 | 3.9398 | 0.7684 | 0.91984 | 1.0909 | 1.3021 | 1.5326 | 1.9308 | 2.4795 | 3.2889 | 3.7578 | 4.8595 | 5.4879 | 5.9898 | 6.4759 | 6.8231 | 7.1489 | 7.4397 | 8.2826 | 8.7013
West Midlands | Port Ham 132kV | PRINCESS ROYAL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.32358 | 0.37812 | 0.44771 | 0.53298 | 0.62844 | 0.73685 | 0.90557 | 1.1665 | 1.3568 | 1.7034 | 2.0763 | 2.397 | 2.6517 | 2.8142 | 2.9601 | 3.0885 | 3.4037 | 3.5591 | 0.73327 | 0.8488 | 0.9943 | 1.1728 | 1.3725 | 1.5985 | 1.9666 | 2.5385 | 2.9419 | 3.7279 | 4.5818 | 5.3055 | 5.8526 | 6.1894 | 6.4893 | 6.7543 | 7.4267 | 7.7752
West Midlands | Port Ham 132kV | ROTOL 33 11kV S STN | Primary Substation | 11 | Counterfactual | 1.4199 | 1.5877 | 1.7635 | 1.9412 | 2.1988 | 2.4572 | 2.7002 | 3.044 | 3.2928 | 3.5631 | 3.8657 | 4.1665 | 4.4889 | 4.8028 | 5.0888 | 5.379 | 6.6274 | 7.1015 | 3.4519 | 3.8058 | 4.1722 | 4.5425 | 5.0891 | 5.6407 | 6.151 | 6.8782 | 7.3986 | 7.9725 | 8.6194 | 9.2576 | 9.9352 | 10.5915 | 11.1805 | 11.7773 | 14.3523 | 15.3734
West Midlands | Port Ham 132kV | ROTOL 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 1.5013 | 1.8344 | 2.186 | 2.5736 | 3.1226 | 3.5846 | 4.2221 | 4.8968 | 5.4078 | 5.8954 | 6.3433 | 6.7343 | 6.9898 | 7.1537 | 7.2734 | 7.3824 | 7.8198 | 8.2715 | 3.6295 | 4.3427 | 5.0873 | 5.9187 | 7.1226 | 8.1008 | 9.4913 | 10.9372 | 12.0034 | 13.0544 | 14.0216 | 14.8476 | 15.3931 | 15.7484 | 16.0157 | 16.2588 | 17.2534 | 18.2775
West Midlands | Port Ham 132kV | ROTOL 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 1.4763 | 1.7365 | 2.0604 | 2.3581 | 2.6654 | 3.1653 | 3.6456 | 4.1783 | 4.5715 | 4.9867 | 5.3895 | 5.7916 | 6.1889 | 6.566 | 6.9139 | 7.2255 | 8.044 | 8.5008 | 3.5863 | 4.1589 | 4.8794 | 5.53 | 6.1964 | 7.327 | 8.3985 | 9.5566 | 10.3936 | 11.2789 | 12.1198 | 12.9569 | 13.7865 | 14.5748 | 15.3042 | 15.9594 | 17.7323 | 18.7681
West Midlands | Port Ham 132kV | ROTOL 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 1.4517 | 1.6894 | 1.9318 | 2.2187 | 2.6065 | 2.9447 | 3.4018 | 3.9231 | 4.2856 | 4.7298 | 5.1759 | 5.5813 | 5.9519 | 6.2964 | 6.6172 | 6.902 | 7.8332 | 8.2745 | 3.5212 | 4.037 | 4.552 | 5.1742 | 6.0426 | 6.771 | 7.7856 | 8.915 | 9.6763 | 10.6331 | 11.5851 | 12.4358 | 13.2064 | 13.9209 | 14.5879 | 15.1818 | 17.2643 | 18.2698
West Midlands | Port Ham 132kV | STOWFIELD 33 11kV S STN | Primary Substation | 11 | Counterfactual | 0.23409 | 0.24655 | 0.25985 | 0.27682 | 0.29641 | 0.31881 | 0.34426 | 0.38825 | 0.41887 | 0.45783 | 0.50537 | 0.55305 | 0.60309 | 0.64962 | 0.68783 | 0.72673 | 0.91434 | 1.0132 | 0.56714 | 0.59338 | 0.62114 | 0.65644 | 0.69709 | 0.74371 | 0.79675 | 0.88937 | 0.9529 | 1.0364 | 1.1404 | 1.2434 | 1.3503 | 1.4487 | 1.5266 | 1.6058 | 1.9911 | 2.1981
West Midlands | Port Ham 132kV | STOWFIELD 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 0.24522 | 0.27463 | 0.31106 | 0.35396 | 0.401 | 0.45359 | 0.53409 | 0.64527 | 0.71432 | 0.80475 | 0.88395 | 0.93802 | 0.97476 | 0.99772 | 1.0155 | 1.0308 | 1.1003 | 1.1865 | 0.59099 | 0.65309 | 0.72941 | 0.81892 | 0.91669 | 1.0259 | 1.2005 | 1.4445 | 1.5873 | 1.7877 | 1.9625 | 2.0757 | 2.154 | 2.2034 | 2.2423 | 2.2766 | 2.4371 | 2.6411
West Midlands | Port Ham 132kV | STOWFIELD 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 0.24113 | 0.26129 | 0.28321 | 0.31 | 0.34 | 0.39777 | 0.48105 | 0.57889 | 0.63151 | 0.69661 | 0.75689 | 0.81586 | 0.87033 | 0.91742 | 0.9623 | 1.0019 | 1.1646 | 1.2193 | 0.58356 | 0.62845 | 0.67528 | 0.73257 | 0.79645 | 0.92706 | 1.1189 | 1.3394 | 1.4502 | 1.5899 | 1.7159 | 1.8396 | 1.9538 | 2.052 | 2.1457 | 2.229 | 2.5991 | 2.7241
West Midlands | Port Ham 132kV | STOWFIELD 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 0.23921 | 0.2553 | 0.27645 | 0.30178 | 0.33129 | 0.36722 | 0.42555 | 0.51755 | 0.57056 | 0.65694 | 0.73964 | 0.80591 | 0.8608 | 0.9086 | 0.95335 | 0.99218 | 1.0962 | 1.1742 | 0.5779 | 0.61211 | 0.65618 | 0.70887 | 0.77038 | 0.84529 | 0.97326 | 1.1763 | 1.2857 | 1.4756 | 1.6553 | 1.7945 | 1.9073 | 2.0051 | 2.097 | 2.1771 | 2.4013 | 2.5843
West Midlands | Port Ham 132kV | Tewkesbury Grid 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 2.9193 | 3.057 | 3.2429 | 3.4505 | 3.6667 | 3.884 | 4.0996 | 4.4521 | 4.7502 | 5.0685 | 5.3604 | 5.6575 | 5.9804 | 6.2969 | 6.6079 | 6.9144 | 8.4 | 8.9738 | 7.0676 | 7.3646 | 7.7545 | 8.1877 | 8.6406 | 9.0968 | 9.5487 | 10.2838 | 10.909 | 11.58 | 12.1918 | 12.8103 | 13.4783 | 14.1321 | 14.7733 | 15.4036 | 18.4737 | 19.6943
West Midlands | Port Ham 132kV | Tewkesbury Grid 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 3.0214 | 3.3414 | 3.7184 | 4.1137 | 4.5631 | 5.0251 | 5.6759 | 6.4222 | 7.0995 | 7.7094 | 8.1032 | 8.478 | 8.7319 | 8.902 | 9.0237 | 9.1331 | 9.6823 | 10.2448 | 7.2951 | 7.9952 | 8.7984 | 9.6347 | 10.5888 | 11.5623 | 12.9463 | 14.5199 | 15.9483 | 17.2463 | 18.0748 | 18.8578 | 19.3991 | 19.7673 | 20.0387 | 20.2834 | 21.5371 | 22.8184
West Midlands | Port Ham 132kV | Tewkesbury Grid 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 2.9954 | 3.2447 | 3.5306 | 3.8208 | 4.1408 | 4.6359 | 5.1381 | 5.7426 | 6.2643 | 6.6973 | 7.1131 | 7.5337 | 7.9479 | 8.3362 | 8.6991 | 9.022 | 9.0775 | 9.7627 | 7.2499 | 7.8165 | 8.4401 | 9.0668 | 9.757 | 10.8365 | 11.9226 | 13.2109 | 14.3175 | 15.2268 | 16.0954 | 16.9718 | 17.8377 | 18.6497 | 19.4105 | 20.0902 | 19.9191 | 21.4952
West Midlands | Port Ham 132kV | Tewkesbury Grid 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 2.9716 | 3.1881 | 3.4487 | 3.721 | 4.032 | 4.351 | 4.7413 | 5.2435 | 5.6824 | 6.1583 | 6.5939 | 7.0133 | 7.4173 | 7.7929 | 8.143 | 8.4544 | 9.3878 | 9.9009 | 7.1867 | 7.6701 | 8.2284 | 8.8084 | 9.4768 | 10.157 | 10.9922 | 12.0503 | 12.9751 | 13.98 | 14.8878 | 15.7584 | 16.597 | 17.3768 | 18.1046 | 18.7532 | 20.7682 | 21.9191
West Midlands | Port Ham 132kV | TUFFLEY 33 11kV S STN | Primary Substation | 11 | Counterfactual | 2.7098 | 3.0756 | 3.4024 | 3.6721 | 3.9713 | 4.2969 | 4.658 | 5.162 | 5.5843 | 6.0528 | 6.5423 | 7.0575 | 7.6284 | 8.2726 | 8.9106 | 9.5354 | 11.4323 | 12.0701 | 6.4974 | 7.2417 | 7.913 | 8.4748 | 9.0984 | 9.7789 | 10.5354 | 11.5886 | 12.4737 | 13.4607 | 14.4925 | 15.5723 | 16.7633 | 18.1104 | 19.4515 | 20.7723 | 24.7012 | 26.061
West Midlands | Port Ham 132kV | TUFFLEY 33 11kV S STN | Primary Substation | 11 | Electric Engagement | 2.8196 | 3.4677 | 3.9061 | 4.4141 | 4.9988 | 6.1867 | 7.0163 | 7.9808 | 8.8242 | 9.5918 | 10.3515 | 11.1971 | 11.9143 | 12.4609 | 12.7911 | 13.0938 | 13.8921 | 14.5428 | 6.7353 | 8.0618 | 8.9864 | 10.0566 | 11.2883 | 13.9954 | 15.7643 | 17.8004 | 19.5728 | 21.2047 | 22.8277 | 24.6501 | 26.2214 | 27.4158 | 28.1444 | 28.8178 | 30.6238 | 32.1052
West Midlands | Port Ham 132kV | TUFFLEY 33 11kV S STN | Primary Substation | 11 | Holistic Transition | 2.7849 | 3.337 | 3.6426 | 4.0192 | 4.5092 | 5.1334 | 5.8088 | 6.5995 | 7.301 | 8.0633 | 8.9465 | 9.7428 | 10.5158 | 11.2145 | 11.8408 | 12.3917 | 13.6617 | 14.2616 | 6.6751 | 7.8174 | 8.472 | 9.2824 | 10.3388 | 11.7073 | 13.1767 | 14.8674 | 16.367 | 18.0009 | 19.9156 | 21.6101 | 23.2555 | 24.7365 | 26.0625 | 27.2329 | 29.9924 | 31.3437
West Midlands | Port Ham 132kV | TUFFLEY 33 11kV S STN | Primary Substation | 11 | Hydrogen Evolution | 2.7543 | 3.2742 | 3.5901 | 3.9551 | 4.3985 | 5.4089 | 6.0281 | 6.8018 | 7.463 | 8.1902 | 8.9599 | 9.7584 | 10.5942 | 11.3292 | 11.9118 | 12.4321 | 13.5111 | 14.0592 | 6.5924 | 7.6533 | 8.3219 | 9.0955 | 10.041 | 12.3845 | 13.7204 | 15.3645 | 16.7625 | 18.306 | 19.9334 | 21.6288 | 23.4214 | 24.9813 | 26.205 | 27.3041 | 29.6242 | 30.861
West Midlands | Rugeley 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.4591 | 1.7245 | 2.0386 | 2.3843 | 2.782 | 3.2254 | 3.7369 | 4.5604 | 5.1794 | 5.8719 | 6.6059 | 7.3571 | 8.1811 | 8.9943 | 9.7547 | 10.5176 | 13.9407 | 15.0353 | 3.1362 | 3.6911 | 4.3424 | 5.0593 | 5.886 | 6.8056 | 7.8648 | 9.5714 | 10.8501 | 12.2924 | 13.8292 | 15.3911 | 17.0932 | 18.7667 | 20.3189 | 21.8757 | 28.8775 | 31.2088
West Midlands | Rugeley 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.709 | 2.3576 | 3.1199 | 4.0113 | 5.023 | 6.0972 | 7.5473 | 9.258 | 10.6359 | 11.8799 | 13.0041 | 14.0243 | 14.7085 | 15.1491 | 15.4486 | 15.7401 | 17.1265 | 18.3402 | 3.6786 | 5.0369 | 6.6256 | 8.4849 | 10.5943 | 12.8211 | 15.8869 | 19.4691 | 22.3064 | 24.9287 | 27.3012 | 29.4232 | 30.8713 | 31.8207 | 32.4849 | 33.133 | 36.2563 | 38.9991
West Midlands | Rugeley 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.633 | 2.0574 | 2.5961 | 3.1603 | 3.7785 | 4.7028 | 5.7172 | 6.9996 | 7.9811 | 9.0507 | 10.1959 | 11.3105 | 12.4309 | 13.4635 | 14.4334 | 15.3045 | 17.7815 | 18.9849 | 3.5481 | 4.4764 | 5.6359 | 6.8433 | 8.1613 | 10.1955 | 12.4091 | 15.1381 | 17.1951 | 19.4392 | 21.8279 | 24.1473 | 26.4821 | 28.6286 | 30.6476 | 32.4681 | 37.8141 | 40.5312
West Midlands | Rugeley 132kV | Burntwood 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.5514 | 1.8968 | 2.3337 | 2.8355 | 3.4192 | 4.0904 | 5.0194 | 6.2684 | 7.2029 | 8.3204 | 9.4552 | 10.5166 | 11.5446 | 12.4679 | 13.3342 | 14.0971 | 16.0379 | 17.041 | 3.335 | 4.064 | 4.9756 | 6.0293 | 7.2587 | 8.6632 | 10.6571 | 13.292 | 15.2224 | 17.571 | 19.9365 | 22.1273 | 24.2407 | 26.1329 | 27.9085 | 29.4766 | 33.5973 | 35.8373
West Midlands | Rugeley 132kV | Cannock 132/11kV | Bulk Supply Point | 11 | Counterfactual | 6.2559 | 6.7141 | 7.1221 | 7.5903 | 8.1255 | 8.7068 | 9.3553 | 10.3988 | 11.2145 | 12.1583 | 13.2442 | 11.7243 | 13.0366 | 14.4013 | 15.5537 | 16.5667 | 19.2188 | 20.7487 | 15.1168 | 16.0637 | 16.9071 | 17.8749 | 18.9848 | 20.1876 | 21.5277 | 23.6818 | 25.3648 | 27.3386 | 29.6478 | 25.4167 | 28.2132 | 31.1456 | 33.5579 | 35.6231 | 40.187 | 43.4365
West Midlands | Rugeley 132kV | Cannock 132/11kV | Bulk Supply Point | 11 | Electric Engagement | 6.6692 | 7.5098 | 8.4818 | 9.6314 | 10.9355 | 12.388 | 14.2479 | 16.5682 | 18.3783 | 20.3177 | 22.202 | 21.0597 | 22.1342 | 22.8772 | 23.2272 | 23.553 | 23.2595 | 24.7522 | 15.985 | 17.7438 | 19.7624 | 22.1545 | 24.8678 | 27.8815 | 31.793 | 36.6743 | 40.4009 | 44.6063 | 48.7503 | 45.3368 | 47.6852 | 49.3563 | 50.1332 | 50.8603 | 49.7596 | 53.1456
West Midlands | Rugeley 132kV | Cannock 132/11kV | Bulk Supply Point | 11 | Holistic Transition | 6.5568 | 7.1109 | 7.7908 | 8.5188 | 9.4847 | 10.6589 | 12.0578 | 13.9817 | 15.2762 | 17.2442 | 18.8965 | 17.8663 | 19.4802 | 20.779 | 22.0362 | 23.1208 | 24.256 | 25.8032 | 15.78 | 16.9877 | 18.4443 | 19.9929 | 22.051 | 24.6102 | 27.677 | 31.8624 | 34.5712 | 38.926 | 42.4467 | 39.2651 | 42.7073 | 45.3991 | 48.0256 | 50.2862 | 52.0833 | 55.5672
West Midlands | Rugeley 132kV | Cannock 132/11kV | Bulk Supply Point | 11 | Hydrogen Evolution | 6.4826 | 6.9358 | 7.5227 | 8.2032 | 9.0348 | 9.934 | 11.1 | 12.7776 | 14.0095 | 15.7206 | 17.5686 | 16.5927 | 18.1081 | 19.5189 | 20.6373 | 21.6197 | 22.2349 | 23.5821 | 15.5844 | 16.5409 | 17.7657 | 19.1926 | 20.9467 | 22.8297 | 25.3141 | 28.8714 | 31.4157 | 35.1131 | 39.1211 | 36.0811 | 39.283 | 42.2694 | 44.5637 | 46.585 | 47.1969 | 50.2046
West Midlands | Rugeley 132kV | Lichfield 132/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 3.131 | 3.3931 | 3.7126 | 4.0663 | 4.6863 | 5.3497 | 6.055 | 7.0202 | 7.8045 | 8.6196 | 9.4021 | 10.1594 | 10.9695 | 11.7508 | 12.468 | 13.1926 | 16.3492 | 17.4206 | 7.0779 | 7.6341 | 8.3086 | 9.0511 | 10.3727 | 11.7921 | 13.2985 | 15.3381 | 17.003 | 18.744 | 20.3997 | 21.9839 | 23.6657 | 25.2797 | 26.7617 | 28.261 | 34.7957 | 37.119
West Midlands | Rugeley 132kV | Lichfield 132/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 3.349 | 4.0072 | 4.8506 | 6.1448 | 7.7358 | 9.1841 | 10.8715 | 12.5122 | 13.9366 | 15.1691 | 16.1911 | 17.1686 | 17.8699 | 18.2069 | 18.4967 | 18.7859 | 19.8679 | 21.0494 | 7.5563 | 8.964 | 10.776 | 13.5684 | 17.0501 | 20.1797 | 23.7994 | 27.2561 | 30.2479 | 32.8555 | 35.026 | 37.1009 | 38.6291 | 39.3631 | 40.0062 | 40.6408 | 43.1578 | 45.9676
West Midlands | Rugeley 132kV | Lichfield 132/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 3.2866 | 3.7691 | 4.7682 | 5.7554 | 6.8475 | 8.0377 | 9.0342 | 10.2604 | 11.2379 | 12.1906 | 13.2432 | 14.2363 | 15.1308 | 15.9526 | 16.7763 | 17.5423 | 19.6422 | 20.562 | 7.4486 | 8.5229 | 10.7427 | 12.8956 | 15.2957 | 17.9066 | 20.0578 | 22.6646 | 24.7133 | 26.7129 | 28.9412 | 31.0334 | 32.9082 | 34.6279 | 36.3504 | 37.9568 | 42.6106 | 44.7466
West Midlands | Rugeley 132kV | Lichfield 132/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 3.2238 | 3.5834 | 4.0337 | 4.8234 | 5.8429 | 6.8447 | 7.9198 | 9.1701 | 10.2121 | 11.2944 | 12.3805 | 13.4207 | 14.4597 | 15.3062 | 16.1215 | 16.8429 | 18.6658 | 19.5971 | 7.2834 | 8.0629 | 9.0301 | 10.7448 | 13.0146 | 15.2138 | 17.5445 | 20.192 | 22.3932 | 24.6685 | 26.9409 | 29.1129 | 31.2949 | 33.0515 | 34.7372 | 36.228 | 40.1749 | 42.3201
West Midlands | Rugeley 132kV | RUGELEY TOWN 132 11kV S STN | Bulk Supply Point | 11 | Counterfactual | 0.75245 | 0.91428 | 1.1153 | 1.3483 | 1.6775 | 2.0394 | 2.4252 | 2.9938 | 3.4164 | 3.8936 | 4.3901 | 4.8963 | 5.4555 | 6.0261 | 6.532 | 7.0041 | 9.2352 | 10.1061 | 1.6808 | 2.021 | 2.4425 | 2.9316 | 3.6254 | 4.3911 | 5.2098 | 6.4048 | 7.2987 | 8.3205 | 9.3844 | 10.4605 | 11.6445 | 12.857 | 13.9129 | 14.884 | 19.5163 | 21.4222
West Midlands | Rugeley 132kV | RUGELEY TOWN 132 11kV S STN | Bulk Supply Point | 11 | Electric Engagement | 0.90314 | 1.2958 | 1.8024 | 2.4961 | 3.2975 | 4.0645 | 4.9475 | 6.0196 | 6.9233 | 7.8343 | 8.7064 | 9.4525 | 9.9858 | 10.3348 | 10.5986 | 10.7982 | 11.7903 | 12.7553 | 2.0092 | 2.8355 | 3.912 | 5.3893 | 7.1003 | 8.7292 | 10.6001 | 12.8675 | 14.7615 | 16.7405 | 18.6591 | 20.2684 | 21.4485 | 22.2364 | 22.8246 | 23.2852 | 25.6081 | 27.8874
West Midlands | Rugeley 132kV | RUGELEY TOWN 132 11kV S STN | Bulk Supply Point | 11 | Holistic Transition | 0.85828 | 1.1215 | 1.5401 | 2.0271 | 2.5062 | 3.0478 | 3.7136 | 4.6299 | 5.3192 | 6.1926 | 7.002 | 7.8019 | 8.5829 | 9.2189 | 9.8696 | 10.4022 | 11.9987 | 12.7592 | 1.932 | 2.5113 | 3.4195 | 4.4746 | 5.5142 | 6.6985 | 8.1685 | 10.1725 | 11.6513 | 13.5705 | 15.3118 | 17.0348 | 18.7168 | 20.0559 | 21.4234 | 22.5537 | 26.0894 | 27.8413
West Midlands | Rugeley 132kV | RUGELEY TOWN 132 11kV S STN | Bulk Supply Point | 11 | Hydrogen Evolution | 0.81122 | 1.0224 | 1.3007 | 1.7148 | 2.2053 | 2.7293 | 3.3508 | 4.1372 | 4.7654 | 5.5801 | 6.4105 | 7.1774 | 7.8726 | 8.496 | 9.058 | 9.5304 | 10.8695 | 11.7153 | 1.8087 | 2.2572 | 2.845 | 3.7304 | 4.7902 | 5.9181 | 7.2579 | 8.9326 | 10.2559 | 12.0207 | 13.8111 | 15.45 | 16.9182 | 18.2313 | 19.3947 | 20.3793 | 23.319 | 25.2903
West Midlands | Willenhall 132kV | Willenhall 132/25/11kVDUMMY | Bulk Supply Point | 11 | Counterfactual | 1.248 | 1.4042 | 1.5634 | 1.7503 | 1.9569 | 2.2102 | 2.5003 | 2.9427 | 3.3178 | 3.6998 | 4.1084 | 4.5374 | 5.0132 | 5.468 | 5.8996 | 6.3435 | 8.2793 | 9.0851 | 3.0351 | 3.3669 | 3.6976 | 4.0847 | 4.5118 | 5.0346 | 5.6376 | 6.5468 | 7.3195 | 8.1079 | 8.9549 | 9.84 | 10.8178 | 11.7498 | 12.6324 | 13.5402 | 17.4911 | 19.1721
West Midlands | Willenhall 132kV | Willenhall 132/25/11kVDUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.3787 | 1.7584 | 2.1468 | 2.5868 | 3.0934 | 3.6944 | 4.4518 | 5.3528 | 6.1498 | 6.8311 | 7.4232 | 7.9937 | 8.3881 | 8.6273 | 8.8109 | 8.9787 | 9.7392 | 10.3782 | 3.3171 | 4.127 | 4.9325 | 5.8428 | 6.8892 | 8.1323 | 9.7186 | 11.5899 | 13.2355 | 14.6589 | 15.8965 | 17.0865 | 17.924 | 18.4343 | 18.8344 | 19.204 | 20.9217 | 22.3536
West Midlands | Willenhall 132kV | Willenhall 132/25/11kVDUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.3377 | 1.6097 | 1.8701 | 2.1597 | 2.5071 | 3.0125 | 3.5647 | 4.2693 | 4.8666 | 5.4616 | 6.1172 | 6.7443 | 7.3582 | 7.9284 | 8.4899 | 8.9832 | 10.3731 | 11.1465 | 3.2458 | 3.8533 | 4.4117 | 5.0306 | 5.7713 | 6.8656 | 8.0521 | 9.5342 | 10.7846 | 12.0293 | 13.4078 | 14.7087 | 15.9831 | 17.1673 | 18.3359 | 19.3679 | 22.3692 | 24.1077
West Midlands | Willenhall 132kV | Willenhall 132/25/11kVDUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 1.3015 | 1.5218 | 1.7482 | 2.0124 | 2.3241 | 2.7067 | 3.2042 | 3.8861 | 4.4613 | 5.0909 | 5.7289 | 6.3389 | 6.9444 | 7.4604 | 7.9588 | 8.7815 | 9.8754 | 10.4718 | 3.1488 | 3.6257 | 4.0977 | 4.6465 | 5.2938 | 6.0902 | 7.1419 | 8.5631 | 9.7538 | 11.0605 | 12.3811 | 13.6417 | 14.8983 | 15.9609 | 16.9848 | 18.8562 | 21.175 | 22.479
West Midlands | Willenhall 132kV | Wolverhampton 132/33/11kV DUMMY | Bulk Supply Point | 11 | Counterfactual | 0.94438 | 1.0739 | 1.2593 | 1.7146 | 2.0023 | 2.1847 | 2.3886 | 2.69 | 2.9285 | 3.2018 | 3.4989 | 3.8324 | 4.205 | 4.6258 | 5.0614 | 5.5185 | 7.7613 | 8.3959 | 2.2529 | 2.5295 | 2.9157 | 3.8495 | 4.4489 | 4.8266 | 5.2493 | 5.8654 | 6.3558 | 6.9188 | 7.5318 | 8.2191 | 8.9856 | 9.8557 | 10.7678 | 11.7309 | 16.4079 | 17.7275
West Midlands | Willenhall 132kV | Wolverhampton 132/33/11kV DUMMY | Bulk Supply Point | 11 | Electric Engagement | 1.0342 | 1.3246 | 1.6909 | 2.3446 | 2.8865 | 3.3075 | 3.796 | 4.3908 | 4.9979 | 5.5274 | 6.0666 | 6.7629 | 7.2976 | 7.7551 | 8.0552 | 8.2477 | 9.1951 | 9.6587 | 2.4464 | 3.0717 | 3.8402 | 5.2001 | 6.3444 | 7.217 | 8.2272 | 9.4504 | 10.714 | 11.8213 | 12.9589 | 14.461 | 15.6333 | 16.6261 | 17.279 | 17.6978 | 19.7974 | 20.8077
West Midlands | Willenhall 132kV | Wolverhampton 132/33/11kV DUMMY | Bulk Supply Point | 11 | Holistic Transition | 1.0063 | 1.2303 | 1.5181 | 2.0795 | 2.494 | 2.8174 | 3.1713 | 3.7382 | 4.3059 | 4.931 | 5.6659 | 6.2442 | 6.7407 | 7.3452 | 7.8045 | 8.2153 | 9.5869 | 10.0792 | 2.3971 | 2.9001 | 3.5213 | 4.7035 | 5.5958 | 6.2827 | 7.0306 | 8.2228 | 9.4288 | 10.7646 | 12.3636 | 13.583 | 14.6061 | 15.888 | 16.8486 | 17.7121 | 20.6782 | 21.7391
West Midlands | Willenhall 132kV | Wolverhampton 132/33/11kV DUMMY | Bulk Supply Point | 11 | Hydrogen Evolution | 0.98668 | 1.1672 | 1.4299 | 1.9792 | 2.3832 | 2.6699 | 3.0026 | 3.4664 | 3.9374 | 4.4365 | 4.9899 | 5.5836 | 6.2023 | 6.818 | 7.2954 | 7.7327 | 9.1107 | 9.6069 | 2.3429 | 2.7361 | 3.2904 | 4.4367 | 5.2965 | 5.8951 | 6.5867 | 7.5414 | 8.5246 | 9.5618 | 10.7163 | 11.9709 | 13.2993 | 14.6082 | 15.6067 | 16.5245 | 19.4872 | 20.5593